## Sheet1
TIME_MESSAGE | MESSAGE | REGION
9/9/2024 2:01:15 PM | Mindanao Grid-09/09/2024 14:08: Lake Mainit HEP online at 1400H (Unplanned Outage) [WEBSMS] | CMIN
9/9/2024 1:29:30 PM | Luzon Grid-09/09/2024 13:29: EERI Unit 1 online at 1320H. (On-going test and commissioning.) [WEBSMS] | CLUZ
9/9/2024 12:52:51 PM | [NSO Update] Luzon Grid-09/09/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15307MW, PK=11426MW, RR=433MW, NetOpMargin: PM=3448, EVE=2826 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @300MW, Masinloc 2 @300MW, Masinloc 3 @300MW, Calaca 1 @180MW, Calaca 2 @240MW, Limay 4 @60MW [WEBSMS] | CLUZ
9/9/2024 12:42:53 PM | [NSO Update] Mindanao Grid-09/09/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3263MW, PK=2491MW, RR=73MW, NetOpMargin: PM=699, EVE=776 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @37.5MW, MA2 @35.5MW, MCC @100MW [WEBSMS] | CMIN
9/9/2024 12:41:48 PM | Luzon Grid-09/09/2024 12:41: Dasmarinas-Ternate 115kV line (CO) was energized at 1241H. (Unplanned Outage) [WEBSMS] | CLUZ
9/9/2024 12:39:37 PM | [NSO Update] Visayas Grid-09/09/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2696MW, PK=2347MW, RR=31MW, NetOpMargin: PM=318, EVE=329 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @182MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PGPP2-SOG1 @15MW, PDPP1-5 @4.3MW, PDPP3-E @8MW, PDPP3-G @10MW [WEBSMS] | CVIS
9/9/2024 12:39:31 PM | Visayas Grid-09/09/2024 12:39: Barotac SS 138kV Bus 1 energized at 1225H. (Planned Outage) [WEBSMS] | CVIS
9/9/2024 12:32:10 PM | Luzon Grid-09/09/2024 12:32: Laoag-Balaoi 115kV line was de-energized at 1228H. (Unplanned Outage) [WEBSMS] | CLUZ
9/9/2024 11:53:01 AM | Visayas Grid-09/09/2024 11:53: Lapulapu-Pajo 69kV Line energized at 1149H. (Planned Outage) [WEBSMS] | CVIS
9/9/2024 11:03:57 AM | Mindanao Grid-09/09/2024 11:11: WMPC DG07 online at 1100H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/9/2024 10:47:43 AM | Mindanao Grid-09/09/2024 10:54: WMPC DG10 online at 0936H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/9/2024 10:46:35 AM | Luzon Grid-09/09/2024 10:46: Dasmarinas-Ternate 115kV line (CO) was de-energized at 1044H. (Unplanned Outage) [WEBSMS] | CLUZ
9/9/2024 10:24:06 AM | [NSO Update] Visayas Grid-09/09/2024 10:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1020H with power going to Visayas. [WEBSMS] | CVIS
9/9/2024 10:23:39 AM | [NSO Update] Luzon Grid-09/09/2024 10:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1020H with power going to Visayas. [WEBSMS] | CLUZ
9/9/2024 10:03:38 AM | [NSO Update] Visayas Grid-09/09/2024 10:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1002H from forward power direction. [WEBSMS] | CVIS
9/9/2024 10:03:23 AM | [NSO Update] Luzon Grid-09/09/2024 10:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1002H from forward power direction. [WEBSMS] | CLUZ
9/9/2024 9:51:26 AM | Mindanao Grid-09/09/2024 09:58: Agus 6 SY - Agus 6 HEP 69kV L3 de-energized at 0908H. (Planned Outage) [WEBSMS] | CMIN
9/9/2024 9:03:57 AM | Mindanao Grid-09/09/2024 09:11: Agus 6 HEPP Unit 3 shutdown at 0902H (Planned Outage) [WEBSMS] | CMIN
9/9/2024 8:16:05 AM | Mindanao Grid-09/09/2024 08:23: Lake Mainit HEP with 6.8MW load shutdown at 0800H due to low lake water level (Unplanned Outage) [WEBSMS] | CMIN
9/9/2024 8:08:29 AM | Visayas Grid-09/09/2024 08:08: Lapulapu-Pajo 69kV Line de-energized at 0807H. (Planned Outage) [WEBSMS] | CVIS
9/9/2024 7:22:05 AM | Visayas Grid-09/09/2024 07:22: Compostela SS 230kV Bus 2 de-energized at 0720H. (Planned Outage) [WEBSMS] | CVIS
9/9/2024 6:58:32 AM | [NSO Update] Visayas Grid-09/09/2024 06:58: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0656H with power going to Luzon. [WEBSMS] | CVIS
9/9/2024 6:58:19 AM | [NSO Update] Luzon Grid-09/09/2024 06:58: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0656H with power going to Luzon. [WEBSMS] | CLUZ
9/9/2024 6:48:34 AM | [NSO Update] Luzon Grid-09/09/2024 06:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0646H from reverse power direction. [WEBSMS] | CLUZ
9/9/2024 6:48:10 AM | [NSO Update] Visayas Grid-09/09/2024 06:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0646H from reverse power direction. [WEBSMS] | CVIS
9/9/2024 6:35:44 AM | Visayas Grid-09/09/2024 06:35: Nasulo cut-in at 0632H. (Unplanned Outage) [WEBSMS] | CVIS
9/9/2024 6:23:36 AM | Visayas Grid-09/09/2024 06:23: Barotac SS 138kV Bus 1 de-energized at 0620H. (Planned Outage) [WEBSMS] | CVIS
9/9/2024 5:54:03 AM | [NSO Update] Mindanao Grid-09/09/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3275MW, PK=2381MW, RR=73MW, NetOpMargin: AM=821, PM=726, EVE=822 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @37.5MW, MA2 @35.5MW [WEBSMS] | CMIN
9/9/2024 5:53:24 AM | [NSO Update] Visayas Grid-09/09/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2711MW, PK=2351MW, RR=31MW, NetOpMargin: AM=330, PM=247, EVE=245 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @180MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PGPP2-SOG1 @15MW, PDPP1-5 @4.3MW [WEBSMS] | CVIS
9/9/2024 5:51:35 AM | [NSO Update] Luzon Grid-09/09/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15395MW, PK=11309MW, RR=429MW, NetOpMargin: AM=3657, PM=3262, EVE=2829 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @300MW, Masinloc 2 @300MW, Masinloc 3 @300MW, Calaca 1 @160MW, Calaca 2 @240MW, Limay 4 @60MW, SCPC 1 @90MW [WEBSMS] | CLUZ
9/9/2024 5:51:17 AM | Visayas Grid-09/09/2024 05:51: Colon - Madugo 138KV Line 2 de-energized at 0550H. (Planned Outage) [WEBSMS] | CVIS
9/9/2024 5:24:32 AM | Mindanao Grid-09/09/2024 05:31: LIBERTAD POWER online at 0449H (Unplanned Outage) [WEBSMS] | CMIN
9/9/2024 5:23:57 AM | Mindanao Grid-09/09/2024 05:31: LIBERTAD POWER with 6MW load tripped at 0443H. Indication (initial): Rate of change (Unplanned Outage) [WEBSMS] | CMIN
9/9/2024 4:48:15 AM | [NSO Update] Mindanao Grid-09/09/2024 04:55: Weather Update: Southwest Monsoon affecting Luzon. Meanwhile, at 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,155 km East Northeast of Extreme Northern Luzon (24.0 N, 132.5 E). [WEBSMS] | CMIN
9/9/2024 4:48:01 AM | [NSO Update] Visayas Grid-09/09/2024 04:48: Weather Update: Southwest Monsoon affecting Luzon. Meanwhile, at 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,155 km East Northeast of Extreme Northern Luzon (24.0 N, 132.5 E). [WEBSMS] | CVIS
9/9/2024 4:47:53 AM | [NSO Update] Luzon Grid-09/09/2024 04:48: Weather Update: Southwest Monsoon affecting Luzon. Meanwhile, at 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,155 km East Northeast of Extreme Northern Luzon (24.0 N, 132.5 E). [WEBSMS] | CLUZ
9/9/2024 4:45:08 AM | [NSO Update] Visayas Grid-09/09/2024 04:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0402H with power going to Visayas [WEBSMS] | CVIS
9/9/2024 4:44:53 AM | [NSO Update] Luzon Grid-09/09/2024 04:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0402H with power going to Visayas [WEBSMS] | CLUZ
9/9/2024 4:43:50 AM | [NSO Update] Visayas Grid-09/09/2024 04:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0351H from forward power direction [WEBSMS] | CVIS
9/9/2024 4:43:27 AM | [NSO Update] Luzon Grid-09/09/2024 04:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0351H from forward power direction [WEBSMS] | CLUZ
9/9/2024 12:04:52 AM | Mindanao Grid-09/09/2024 00:12: Bunawan - Toril 230kV L2 (8LI2BUN-TOR) auto tripped and successfully auto reclosed at 2345H (Single Pole auto-reclosing (SPAR)). (Unplanned Outage) [WEBSMS] | CMIN
9/8/2024 11:55:46 PM | Mindanao Grid-09/09/2024 00:03: Lala -Aurora 138 kV Line 2 (7LI2LLA-AUR) energized/restored at 2351H. From Planned Outage/GOMP. [WEBSMS] | CMIN
9/8/2024 11:22:20 PM | Luzon Grid-09/08/2024 23:22: Binan SS 230kV Bus 1 restored at 2322H (Planned Outage) [WEBSMS] | CLUZ
9/8/2024 11:18:38 PM | Mindanao Grid-09/08/2024 23:25: POWERSOURCE online at 2314H (Unplanned Outage) [WEBSMS] | CMIN
9/8/2024 10:40:04 PM | Luzon Grid-09/08/2024 22:40: San Esteban-Bacnotan 230kV Line restored at 2208H (Planned Outage) [WEBSMS] | CLUZ
9/8/2024 10:08:27 PM | Luzon Grid-09/08/2024 22:08: Pagbilao 1 emergency shutdown at 2207H (Unplanned Outage) [WEBSMS] | CLUZ
9/8/2024 8:37:49 PM | Visayas Grid-09/08/2024 20:37: Naga - TPVI 138 kV Line 2 energized at 2036H. (Planned Outage) [WEBSMS] | CVIS
9/8/2024 8:11:19 PM | Luzon Grid-09/08/2024 20:11: Botolan-Subic 230kV Line restored at 2011H (Planned Outage) [WEBSMS] | CLUZ
9/8/2024 7:30:00 PM | [NSO Update] Visayas Grid-09/08/2024 19:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1917H with power going to Luzon [WEBSMS] | CVIS
9/8/2024 7:29:44 PM | [NSO Update] Luzon Grid-09/08/2024 19:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1917H with power going to Luzon [WEBSMS] | CLUZ
9/8/2024 7:22:03 PM | [NSO Update] Visayas Grid-09/08/2024 19:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1907H from reverse power direction [WEBSMS] | CVIS
9/8/2024 7:21:56 PM | [NSO Update] Luzon Grid-09/08/2024 19:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1907H from reverse power direction [WEBSMS] | CLUZ
9/8/2024 6:58:23 PM | Luzon Grid-09/08/2024 18:58: Bacnotan-CIP 2 69kV Line restored at 1857H (Planned Outage) [WEBSMS] | CLUZ
9/8/2024 6:12:27 PM | Luzon Grid-09/08/2024 18:12: Bauang-Bacnotan 230kV Line restored at 1810H (Planned Outage) [WEBSMS] | CLUZ
9/8/2024 5:54:33 PM | [NSO Update] Mindanao Grid-09/08/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3255MW, PK=2205MW, RR=73MW, NetOpMargin: EVE=977 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @37.5MW, MA2 @35.5MW [WEBSMS] | CMIN
9/8/2024 5:53:34 PM | [NSO Update] Visayas Grid-09/08/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2541MW, PK=2193MW, RR=31MW, NetOpMargin: EVE=316 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @248MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PGPP2-SOG1 @16MW, PDPP1-5 @4.3MW, PDPP3-G @10MW [WEBSMS] | CVIS
9/8/2024 5:52:35 PM | [NSO Update] Luzon Grid-09/08/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14456MW, PK=10152MW, RR=313MW, NetOpMargin: EVE=3991 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @300MW, Masinloc 2 @300MW, Masinloc 3 @200MW, Calaca 1 @160MW, Calaca 2 @240MW, Limay 4 @60MW, Pagbilao 1 @120MW [WEBSMS] | CLUZ
9/8/2024 5:27:58 PM | Mindanao Grid-09/08/2024 17:35: POWER SOURCE with 3MW load tripped at 1711H due to turbine trip (Unplanned Outage) [WEBSMS] | CMIN
9/8/2024 5:12:00 PM | Visayas Grid-09/08/2024 17:12: Barotac Viejo - Dingle 138 kV Line 2 energized at 1711H (Planned Outage) [WEBSMS] | CVIS
9/8/2024 4:18:19 PM | Mindanao Grid-09/08/2024 16:25: POWER SOURCE online at 1613H (Unplanned Outage) [WEBSMS] | CMIN
9/8/2024 2:02:30 PM | Mindanao Grid-09/08/2024 14:09: LAKE MAINIT online at 1400H (Unplanned Outage) [WEBSMS] | CMIN
9/8/2024 12:37:30 PM | [NSO Update] Mindanao Grid-09/08/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3300MW, PK=2080MW, RR=73MW, NetOpMargin: PM=1148, EVE=917 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @37.5MW, MA2 @35.5MW, MCC @100MW [WEBSMS] | CMIN
9/8/2024 12:35:22 PM | [NSO Update] Visayas Grid-09/08/2024 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2673MW, PK=2040MW, RR=31MW, NetOpMargin: PM=602, EVE=298 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @240MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PGPP2-SOG1 @16MW, PDPP1-5 @4.3MW [WEBSMS] | CVIS
9/8/2024 12:34:22 PM | [NSO Update] Luzon Grid-09/08/2024 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15439MW, PK=9620MW, RR=345MW, NetOpMargin: PM=5474, EVE=4242 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @260MW, Masinloc 2 @300MW, Masinloc 3 @200MW, Calaca 1 @160MW, Calaca 2 @240MW, Limay 4 @60MW [WEBSMS] | CLUZ
9/8/2024 11:53:59 AM | Luzon Grid-09/08/2024 11:53: Balsik PCB 9-01CB04BIK restored at 1152H (Planned Outage) [WEBSMS] | CLUZ
9/8/2024 9:15:46 AM | Luzon Grid-09/08/2024 09:15: Balsik PCB 9-01CB04BIK de-energized at 0913H (Planned Outage) [WEBSMS] | CLUZ
9/8/2024 9:14:00 AM | Luzon Grid-09/08/2024 09:14: Balsik PCB 9-01CB24BIK restored at 0912H (Planned Outage) [WEBSMS] | CLUZ
9/8/2024 8:17:01 AM | [NSO Update] Luzon Grid-09/08/2024 08:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0815H with power going to Visayas. [WEBSMS] | CLUZ
9/8/2024 8:16:57 AM | [NSO Update] Visayas Grid-09/08/2024 08:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0815H with power going to Visayas. [WEBSMS] | CVIS
9/8/2024 8:12:00 AM | Luzon Grid-09/08/2024 08:11: Botolan-Subic 230kV Line de-energized at 0811H (Planned Outage) [WEBSMS] | CLUZ
9/8/2024 8:07:16 AM | [NSO Update] Luzon Grid-09/08/2024 08:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0805H from forward power direction. [WEBSMS] | CLUZ
9/8/2024 8:06:52 AM | [NSO Update] Visayas Grid-09/08/2024 08:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0805H from forward power direction. [WEBSMS] | CVIS
9/8/2024 8:05:38 AM | Mindanao Grid-09/08/2024 08:12: LAKE MAINIT Hydro shutdown at 0801H due to low lake water level (Unplanned Outage) [WEBSMS] | CMIN
9/8/2024 8:02:30 AM | Luzon Grid-09/08/2024 08:02: Balsik PCB 9-01CB24BIK de-energized at 0800H (Planned Outage) [WEBSMS] | CLUZ
9/8/2024 6:54:26 AM | [NSO Update] Visayas Grid-09/08/2024 06:54: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0652H with power going to Luzon. [WEBSMS] | CVIS
9/8/2024 6:54:24 AM | [NSO Update] Luzon Grid-09/08/2024 06:54: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0652H with power going to Luzon. [WEBSMS] | CLUZ
9/8/2024 6:51:21 AM | Visayas Grid-09/08/2024 06:51: Barotac Viejo - Dingle 138 kV Line 2 de-energized at 0650H (Planned Outage) [WEBSMS] | CVIS
9/8/2024 6:51:01 AM | [NSO Update] Luzon Grid-09/08/2024 06:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0642H from reverse power direction. [WEBSMS] | CLUZ
9/8/2024 6:50:16 AM | Luzon Grid-09/08/2024 06:50: Bauang-Bacnotan 230kV Line de-energized at 0648H (Planned Outage) [WEBSMS] | CLUZ
9/8/2024 6:42:54 AM | [NSO Update] Visayas Grid-09/08/2024 06:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0642H from reverse power direction. [WEBSMS] | CVIS
9/8/2024 6:13:54 AM | Luzon Grid-09/08/2024 06:14: Bacnotan-CIP 2 69kV Line de-energized at 0608H (Planned Outage) [WEBSMS] | CLUZ
9/8/2024 6:13:54 AM | Mindanao Grid-09/08/2024 06:21: Lala -Aurora 138 kV Line 2 (7LI2LLA-AUR) de-energized at 0610H�planned Outage. [WEBSMS] | CMIN
9/8/2024 5:39:21 AM | [NSO Update] Luzon Grid-09/08/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15496MW, PK=9083MW, RR=333MW, NetOpMargin: AM=6080, PM=5662, EVE=4702 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @250MW, Masinloc 2 @250MW, Masinloc 3 @210MW, Calaca 1 @160MW, Calaca 2 @240MW, Limay 4 @60MW [WEBSMS] | CLUZ
9/8/2024 5:24:32 AM | [NSO Update] Mindanao Grid-09/08/2024 05:31: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3314MW, PK=1872MW, RR=73MW, NetOpMargin: AM=1369, PM=1266, EVE=989 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @37.5MW, MA2 @35.5MW [WEBSMS] | CMIN
9/8/2024 5:23:15 AM | [NSO Update] Visayas Grid-09/08/2024 05:23: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2551MW, PK=1914MW, RR=31MW, NetOpMargin: AM=606, PM=567, EVE=470 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @235MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PGPP2-SOG1 @16MW, PDPP1-5 @4.3MW, PDPP3-E @8MW, PDPP3-G @10MW [WEBSMS] | CVIS
9/8/2024 4:41:28 AM | [NSO Update] Luzon Grid-09/08/2024 04:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0434H with power going to Visayas. [WEBSMS] | CLUZ
9/8/2024 4:40:58 AM | [NSO Update] Visayas Grid-09/08/2024 04:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0434H with power going to Visayas. [WEBSMS] | CVIS
9/8/2024 4:29:00 AM | [NSO Update] Visayas Grid-09/08/2024 04:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0424H from forward power direction. [WEBSMS] | CVIS
9/8/2024 4:27:11 AM | [NSO Update] Luzon Grid-09/08/2024 04:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0424H from forward power direction. [WEBSMS] | CLUZ
9/8/2024 4:09:56 AM | [NSO Update] Luzon Grid-09/08/2024 04:10: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CLUZ
9/8/2024 4:08:11 AM | [NSO Update] Mindanao Grid-09/08/2024 04:15: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CMIN
9/8/2024 4:07:52 AM | [NSO Update] Visayas Grid-09/08/2024 04:07: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CVIS
9/8/2024 12:11:21 AM | Luzon Grid-09/08/2024 00:11: Pagbilao Unit 1 online at 0008H (Planned Outage / Ongoing Testing) [WEBSMS] | CLUZ
9/8/2024 12:10:51 AM | Luzon Grid-09/08/2024 00:10: Binan SS 230kV Bus 1 de-energized at 0010H (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 11:46:30 PM | Visayas Grid-09/07/2024 23:46: Daanbantayan SS 150MVA Transformer 1 energized without load at 2344H. (Planned Outage) [WEBSMS] | CVIS
9/7/2024 11:26:31 PM | Luzon Grid-09/07/2024 23:26: Pagbilao Unit 1 shutdown at 2259H (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 11:22:06 PM | Visayas Grid-09/07/2024 23:22: Naga - TPVI 138 kV Line 2 de-energized at 2319H. (Planned Outage) [WEBSMS] | CVIS
9/7/2024 10:37:19 PM | Visayas Grid-09/07/2024 22:37: Naga - TPVI 138 kV Line 1 energized at 2233H. (Planned Outage) [WEBSMS] | CVIS
9/7/2024 9:52:13 PM | Mindanao Grid-09/07/2024 21:59: WMPC DG10 shutdown at 2146H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/7/2024 9:20:23 PM | [NSO Update] Visayas Grid-09/07/2024 21:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2118H with power going to Luzon. [WEBSMS] | CVIS
9/7/2024 9:20:04 PM | [NSO Update] Luzon Grid-09/07/2024 21:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2118H with power going to Luzon. [WEBSMS] | CLUZ
9/7/2024 9:09:13 PM | [NSO Update] Luzon Grid-09/07/2024 21:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2107H from reverse power direction [WEBSMS] | CLUZ
9/7/2024 9:08:45 PM | [NSO Update] Visayas Grid-09/07/2024 21:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2107H from reverse power direction [WEBSMS] | CVIS
9/7/2024 6:06:37 PM | [NSO Update] Luzon Grid-09/07/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14263MW, PK=10236MW, RR=317MW, NetOpMargin: EVE=3709 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @225MW, Masinloc 2 @225MW, Masinloc 3 @200MW, Calaca 1 @160MW, Calaca 2 @221MW, Limay 4 @60MW [WEBSMS] | CLUZ
9/7/2024 6:00:42 PM | Mindanao Grid-09/07/2024 18:07: Toril SS 300MVA Power Transformer T2 (8XF02TOR) energized at 1756H. Planned Outage. [WEBSMS] | CMIN
9/7/2024 5:59:20 PM | Visayas Grid-09/07/2024 17:59: Barotac Viejo - Dingle 138 kV Line 1 energized at 1758H (Planned Outage) [WEBSMS] | CVIS
9/7/2024 5:48:09 PM | Visayas Grid-09/07/2024 17:48: Cebu - Magdugo 230 kV Line 1 energized at 1747H (Planned Outage) [WEBSMS] | CVIS
9/7/2024 5:38:57 PM | Visayas Grid-09/07/2024 17:39: Daanbantayan SS 230 kV Bus 2 energized at 1734HH (Unplanned Outage) [WEBSMS] | CVIS
9/7/2024 5:34:32 PM | [NSO Update] Mindanao Grid-09/07/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2957MW, PK=2329MW, RR=73MW, NetOpMargin: EVE=555 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @37.5MW, MA2 @35.5MW [WEBSMS] | CMIN
9/7/2024 5:34:11 PM | Mindanao Grid-09/07/2024 17:41: Baloi- Agus6 138 kV L2 (7LI2BLO-AG6) energized at 1720H. Planned Outage. [WEBSMS] | CMIN
9/7/2024 5:28:50 PM | [NSO Update] Visayas Grid-09/07/2024 17:28: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2677MW, PK=2331MW, RR=31MW, NetOpMargin: EVE=315 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @235MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PGPP2-SOG1 @16MW, PDPP1-5 @4.3MW, PDPP3-G @10MW [WEBSMS] | CVIS
9/7/2024 5:20:37 PM | Mindanao Grid-09/07/2024 17:27: Baloi SS 138kV Bus 1 (7BS01BLO) energized/restored at 1719H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
9/7/2024 4:57:51 PM | Mindanao Grid-09/07/2024 17:05: Villanueva SS 230kV Power Transformer No. 1 energized at 1641H (Planned Outage) [WEBSMS] | CMIN
9/7/2024 4:46:04 PM | Luzon Grid-09/07/2024 16:46: Muntinlupa 115kV Bus 2 restored at 1643H (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 4:25:32 PM | Luzon Grid-09/07/2024 16:25: San Jose PCB 8-05CB08SJO restored at 1622H (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2024 4:05:49 PM | Luzon Grid-09/07/2024 16:05: Ambuklao SS 230kV Bus 2 restored at 1605H (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 3:36:49 PM | Mindanao Grid-09/07/2024 15:44: WMPC DG07 shutdown at 1534H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/7/2024 3:31:15 PM | Visayas Grid-09/07/2024 15:31: IASCO - PASAR 138 kV Line energized at 1524H (Planned Outage) [WEBSMS] | CVIS
9/7/2024 2:34:33 PM | Luzon Grid-09/07/2024 14:34: Lumban 230kV Bus 2 restored at 1433H (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 1:56:16 PM | Mindanao Grid-09/07/2024 14:03: Baloi SS 138kV Bus 1 (7BS01BLO) de-energized at 1355H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
9/7/2024 1:46:16 PM | Mindanao Grid-09/07/2024 13:53: Baloi- Agus6 138 kV L2 (7LI2BLO-AG6) de-energized at 1345H. Planned Outage. [WEBSMS] | CMIN
9/7/2024 1:33:48 PM | Mindanao Grid-09/07/2024 13:41: WMPC DG7 online at 1328H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/7/2024 1:01:00 PM | [NSO Update] Mindanao Grid-09/07/2024 13:08: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3000MW, PK=2309MW, RR=73MW, NetOpMargin: PM=618, EVE=581 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @37.5MW, MA2 @35.5MW [WEBSMS] | CMIN
9/7/2024 12:59:48 PM | [NSO Update] Visayas Grid-09/07/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2632MW, PK=2261MW, RR=31MW, NetOpMargin: PM=340, EVE=291 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @235MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PGPP2-SOG1 @16MW, PDPP1-5 @4.3MW, PDPP3-C @12MW, PDPP3-G @10MW [WEBSMS] | CVIS
9/7/2024 12:58:33 PM | [NSO Update] Luzon Grid-09/07/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14940MW, PK=10741MW, RR=345MW, NetOpMargin: PM=3853, EVE=3274 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @150MW, Masinloc 2 @150MW, Masinloc 3 @190MW, Calaca 1 @160MW, Calaca 2 @200MW, Limay 4 @60MW [WEBSMS] | CLUZ
9/7/2024 12:47:05 PM | Luzon Grid-09/07/2024 12:47: EERI 1 online at 1241H (On Commissioning Test) [WEBSMS] | CLUZ
9/7/2024 12:21:35 PM | Luzon Grid-09/07/2024 12:21: Muntinlupa 115kV Bus 1 restored at 1218H (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 11:38:31 AM | Mindanao Grid-09/07/2024 11:45: Baloi SS 50MVA Power Transformer 1 (7XF01BLO) energized at 1138H. (Planned Outage/Non-GOMP). [WEBSMS] | CMIN
9/7/2024 11:34:52 AM | Mindanao Grid-09/07/2024 11:42: Agus 2 - Baloi 138kV L2 (7LI2BLO-AG2) energized at 1132H. (Planned Outage/Non-GOMP) [WEBSMS] | CMIN
9/7/2024 11:32:39 AM | Mindanao Grid-09/07/2024 11:39: Agus 4 - Baloi 138kV L2 (7LI2BLO-AG4) energized at 1125H. (Planned Outage/Non-GOMP). [WEBSMS] | CMIN
9/7/2024 11:20:36 AM | Mindanao Grid-09/07/2024 11:27: Baloi SS 138kV Bus 2 (7BS02BLO) energized at 1119H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
9/7/2024 10:31:27 AM | Mindanao Grid-09/07/2024 10:38: WMPC DG10 online at 1028H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/7/2024 10:31:14 AM | Mindanao Grid-09/07/2024 10:38: Jasaan SS 138 kV transformer No.1 (7XF01JAS), 100 MVA energized at 1028H. Planned Outage /Non-Gomp. [WEBSMS] | CMIN
9/7/2024 10:18:10 AM | Luzon Grid-09/07/2024 10:18: Pagbilao 1 online at 1015H (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2024 9:55:55 AM | Luzon Grid-09/07/2024 09:56: Pagbilao 1 emergency shutdown at 0954H (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2024 9:44:51 AM | Luzon Grid-09/07/2024 09:44: San Jose PCB 8-05CB08SJO de-energized at 0934H. San Jose 300MVA TO3 looped at 0931H and San Jose 300MVA TO1 unloop at 0932H at secondary side(115kV) as contingency for the said shutdown (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2024 9:10:05 AM | Mindanao Grid-09/07/2024 09:17: Toril SS 300MVA Power Transformer T2 (8XF02TOR) de-energized at 0905H. Planned Outage. [WEBSMS] | CMIN
9/7/2024 8:40:13 AM | [NSO Update] Visayas Grid-09/07/2024 08:40: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0833H with power going to Visayas (Planned Outage) [WEBSMS] | CVIS
9/7/2024 8:39:58 AM | [NSO Update] Luzon Grid-09/07/2024 08:40: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0833H with power going to Visayas (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 8:34:40 AM | Luzon Grid-09/07/2024 08:34: Lumban 230kV Bus 2 de-energized at 0834H (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 8:26:31 AM | [NSO Update] Visayas Grid-09/07/2024 08:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-energized at 0627H (Planned Outage) [WEBSMS] | CVIS
9/7/2024 8:23:22 AM | Mindanao Grid-09/07/2024 08:30: Villanueva SS 230kV Power Transformer No. 1 deenergized at 0819H (Planned Outage) [WEBSMS] | CMIN
9/7/2024 8:22:01 AM | Visayas Grid-09/07/2024 08:22: Naga - TPVI 138 kV Line 1 de-energized at 0820H (Planned Outage) [WEBSMS] | CVIS
9/7/2024 8:17:09 AM | Visayas Grid-09/07/2024 08:17: Daanbantayan SS 230 kV Bus 2 de-energized at 0814H (Unplanned Outage) [WEBSMS] | CVIS
9/7/2024 8:08:51 AM | [NSO Update] Luzon Grid-09/07/2024 08:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-energized at 0627H (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 8:07:04 AM | Mindanao Grid-09/07/2024 08:14: LAKE MAINIT with 6.5MW load shutdown at 0801H due to critical water level (Unplanned Outage) [WEBSMS] | CMIN
9/7/2024 7:56:08 AM | Visayas Grid-09/07/2024 07:56: Sta. Rita SS 50 MVA Transformer energized at 0751H (Planned Outage) [WEBSMS] | CVIS
9/7/2024 7:54:50 AM | Visayas Grid-09/07/2024 07:54: Babatngon - Paranas 138 kV Line 2 energized at 0749H (Planned Outage) [WEBSMS] | CVIS
9/7/2024 7:39:38 AM | Mindanao Grid-09/07/2024 07:46: Jasaan SS 138 kV transformer No.1 (7XF01JAS), 100 MVA de-energized at 0729H . Planned Outage /Non-Gomp. [WEBSMS] | CMIN
9/7/2024 7:12:41 AM | Mindanao Grid-09/07/2024 07:19: UPDATED: Agus 4 - Baloi 138kV L2 (7LI2BLO-AG4) de-energized at 0600H. (Planned Outage/Non-GOMP). Note: Directly affected by the planned outage of Baloi SS 138kV Bus 2 (P&E Requested S/D). [WEBSMS] | CMIN
9/7/2024 6:48:53 AM | Visayas Grid-09/07/2024 06:48: Barotac Viejo - Dingle 138 kV Line 1 de-energized at 0648H (Planned Outage) [WEBSMS] | CVIS
9/7/2024 6:45:57 AM | Luzon Grid-09/07/2024 06:46: Muntinlupa 115kV Bus 1 de-energized at 0643H (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 6:40:27 AM | Mindanao Grid-09/07/2024 06:47: Baloi SS 138kV Bus 2 (7BS02BLO) de-energized at 0635H. Planned Outage/Non-GOMP. (Note: P&E Requested S/D with MD2 approved Ride-On Activities) [WEBSMS] | CMIN
9/7/2024 6:36:39 AM | [NSO Update] Visayas Grid-09/07/2024 06:36: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0625H from reverse power direction [WEBSMS] | CVIS
9/7/2024 6:36:25 AM | [NSO Update] Luzon Grid-09/07/2024 06:36: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0625H from reverse power direction [WEBSMS] | CLUZ
9/7/2024 6:32:53 AM | Visayas Grid-09/07/2024 06:32: IASCO - PASAR 138 kV Line de-energized at 0631H (Planned Outage) [WEBSMS] | CVIS
9/7/2024 6:27:58 AM | Mindanao Grid-09/07/2024 06:35: Agus 4 - Baloi 138kV L2 (7LI2BLO-AG4) de-energized at 0545H. (Planned Outage/Non-GOMP). Note: Directly affected by the planned outage of Baloi SS 138kV Bus 2 (P&E Requested S/D). [WEBSMS] | CMIN
9/7/2024 6:25:14 AM | Mindanao Grid-09/07/2024 06:32: Agus 2 - Baloi 138kV L2 (7LI2BLO-AG2) de-energized at 0545H. (Planned Outage/Non-GOMP). Note: Directly affected by the planned outage of Baloi SS 138kV Bus 2 (P&E Requested S/D). [WEBSMS] | CMIN
9/7/2024 6:20:56 AM | Mindanao Grid-09/07/2024 06:28: Baloi SS 50MVA Power Transformer 1 (7XF01BLO) de-energized at 0527H. (Planned Outage/Non-GOMP). Note: Directly affected by the planned outage of Baloi SS 138kV Bus 2 & no line customers were affected. [WEBSMS] | CMIN
9/7/2024 6:20:00 AM | Visayas Grid-09/07/2024 06:20: Cebu - Magdugo 230 kV Line 1 de-energized at 0616H (Planned Outage) [WEBSMS] | CVIS
9/7/2024 6:06:32 AM | Luzon Grid-09/07/2024 06:06: SCPC 1 online at 0603H (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2024 6:04:00 AM | Luzon Grid-09/07/2024 06:04: San Esteban-Bacnotan 230kV Line de-energized at 0603H (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 6:01:26 AM | Luzon Grid-09/07/2024 06:01: Pagbilao 1 online at 0558H (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 5:47:13 AM | Visayas Grid-09/07/2024 05:47: Correction: Babatngon-Paranas 138kV Line 2 de-energized at 0514H. (Planned Outage) [WEBSMS] | CVIS
9/7/2024 5:41:45 AM | [NSO Update] Luzon Grid-09/07/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14711MW, PK=9859MW, RR=339MW, NetOpMargin: AM=4513, PM=3879, EVE=3793 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @600MW, Masinloc 1 @150MW, Masinloc 2 @150MW, Masinloc 3 @160MW, Calaca 1 @160MW, Calaca 2 @200MW, SLTEC 2 @119MW, Limay 4 @60MW [WEBSMS] | CLUZ
9/7/2024 5:38:36 AM | [NSO Update] Mindanao Grid-09/07/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3011MW, PK=2138MW, RR=73MW, NetOpMargin: AM=800, PM=722, EVE=677 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @37.5MW, MA2 @35.5MW [WEBSMS] | CMIN
9/7/2024 5:38:30 AM | [NSO Update] Visayas Grid-09/07/2024 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2685MW, PK=2151MW, RR=31MW, NetOpMargin: AM=503, PM=329, EVE=353 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @232MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PGPP2-SOG1 @16MW, PDPP1-5 @4.3MW, PDPP3-E @8MW, PDPP3-G @10MW [WEBSMS] | CVIS
9/7/2024 5:21:46 AM | Luzon Grid-09/07/2024 05:21: Ambuklao SS 230kV Bus 2 de-energized at 0521H (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 5:20:40 AM | Visayas Grid-09/07/2024 05:20: Babatngon-Paranas 138kV Line 2 de-energized at 0514H. (Unplanned Outage) [WEBSMS] | CVIS
9/7/2024 5:18:24 AM | Visayas Grid-09/07/2024 05:18: Sta. Rita SS 50MVA Transformer de-energized at 0509H. (Planned Outage) [WEBSMS] | CVIS
9/7/2024 5:06:49 AM | Mindanao Grid-09/07/2024 05:14: Agus 4 HEPP U3 shutdown at 0505H (Unplanned Outage) [WEBSMS] | CMIN
9/7/2024 5:03:21 AM | [NSO Update] Visayas Grid-09/07/2024 05:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0459H with power going to Visayas [WEBSMS] | CVIS
9/7/2024 5:03:18 AM | [NSO Update] Luzon Grid-09/07/2024 05:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0459H with power going to Visayas [WEBSMS] | CLUZ
9/7/2024 5:00:00 AM | [NSO Update] Visayas Grid-09/07/2024 05:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0447H from forward power direction [WEBSMS] | CVIS
9/7/2024 4:59:56 AM | [NSO Update] Luzon Grid-09/07/2024 05:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0447H from forward power direction [WEBSMS] | CLUZ
9/7/2024 4:04:55 AM | [NSO Update] Mindanao Grid-09/07/2024 04:12: Weather Advisory: Southwest Monsoon affecting Luzon. [WEBSMS] | CMIN
9/7/2024 4:04:52 AM | [NSO Update] Visayas Grid-09/07/2024 04:04: Weather Advisory: Southwest Monsoon affecting Luzon. [WEBSMS] | CVIS
9/7/2024 4:04:50 AM | [NSO Update] Luzon Grid-09/07/2024 04:04: Weather Advisory: Southwest Monsoon affecting Luzon. [WEBSMS] | CLUZ
9/7/2024 3:10:40 AM | Luzon Grid-09/07/2024 03:10: SCPC U1 (150MW) tripped at 0301H, lowest frequency - 59.68Hz. [WEBSMS] | CLUZ
9/7/2024 2:07:36 AM | Luzon Grid-09/07/2024 02:07: Quezon 300MVA T07 and T08 (CO) energized at 0202H/0203H respectively (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2024 2:04:42 AM | Luzon Grid-09/07/2024 02:04: Quezon 300MVA T03 (CO) energized at 0200H (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2024 2:02:08 AM | Luzon Grid-09/07/2024 02:02: Quezon 230kV Bus 2 (CO) energized at 0157H (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2024 12:32:46 AM | Luzon Grid-09/07/2024 00:32: Correction: Quezon 230kV Bus 2 (CO) de-energized at 0023H (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2024 12:23:54 AM | Luzon Grid-09/07/2024 00:23: Quezon 230kV Bus 2 de-energized at 1223H (Planned Outage) [WEBSMS] | CLUZ
9/7/2024 12:21:30 AM | Luzon Grid-09/07/2024 00:21: Quezon 300MVA T03 (CO) de-energized at 0021H (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2024 12:20:03 AM | Luzon Grid-09/07/2024 00:20: Quezon 300MVA T07 and T08 (CO) de-energized both at 0019H (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2024 12:17:56 AM | Mindanao Grid-09/07/2024 00:25: Minergy Coal U1 shutdown at 0004H (Planned Outage) [WEBSMS] | CMIN
9/6/2024 11:24:39 PM | Visayas Grid-09/06/2024 23:24: Daanbantayan SS 230kV Bus 1 energized at 2321H. (Planned Outage) [WEBSMS] | CVIS
9/6/2024 9:51:23 PM | [NSO Update] Visayas Grid-09/06/2024 21:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2150H with power going to Luzon [WEBSMS] | CVIS
9/6/2024 9:51:22 PM | [NSO Update] Luzon Grid-09/06/2024 21:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2150H with power going to Luzon [WEBSMS] | CLUZ
9/6/2024 9:41:59 PM | [NSO Update] Luzon Grid-09/06/2024 21:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2140H from reverse power direction [WEBSMS] | CLUZ
9/6/2024 9:41:22 PM | [NSO Update] Visayas Grid-09/06/2024 21:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2140H from reverse power direction [WEBSMS] | CVIS
9/6/2024 8:43:07 PM | Mindanao Grid-09/06/2024 20:50: WMPC DG10 shutdown at 2042H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/6/2024 6:12:35 PM | Mindanao Grid-09/06/2024 18:19: Kibawe - Tacurong 138kVL (7LI1KIB-TAC) energized/restored at 1700H. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
9/6/2024 6:09:21 PM | Mindanao Grid-09/06/2024 18:16: Kibawe - Tacurong 138kVL (7LI1KIB-TAC) energized/restored at 1700H. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
9/6/2024 5:54:10 PM | [NSO Update] Mindanao Grid-09/06/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3315MW, PK=2290MW, RR=73MW, NetOpMargin: EVE=952 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @40MW, MA2 @38MW [WEBSMS] | CMIN
9/6/2024 5:54:05 PM | [NSO Update] Visayas Grid-09/06/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2752MW, PK=2358MW, RR=31MW, NetOpMargin: EVE=363 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @228MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PGPP2-SOG1 @15MW, PDPP1-5 @4.3MW [WEBSMS] | CVIS
9/6/2024 5:53:57 PM | [NSO Update] Luzon Grid-09/06/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14143MW, PK=10353MW, RR=328MW, NetOpMargin: EVE=3462 Highest Unit O/L: SUAL 1&2 @ 647MW Derated Plant: GNPD 1 @550MW, GNPD 2 @600MW, Masinloc 1 @270MW, Masinloc 2 @270MW, Masinloc 3 @235MW, Calaca 1 @160MW, Calaca 2 @180MW, SLTEC 2 @119MW, SLTEC 1 @120MW [WEBSMS] | CLUZ
9/6/2024 4:12:11 PM | Mindanao Grid-09/06/2024 16:19: WMPC DG07 shutdown at 1611H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/6/2024 4:00:49 PM | Mindanao Grid-09/06/2024 16:07: Agusan Power Corp. HEPP with 5.5MW and ASIGA HEPP with 4MW load tripped at 1548H. Affected by the tripping of Butuan - Santiago 69kV line. (Unplanned Outage) [WEBSMS] | CMIN
9/6/2024 3:04:41 PM | Visayas Grid-09/06/2024 15:04: Magdugo - Calongcalong 138 kV Line 1 energized at 1503H (Planned Outage) [WEBSMS] | CVIS
9/6/2024 2:12:36 PM | Mindanao Grid-09/06/2024 14:19: SEDI (EEI) Unit1 & 3 with 9.2MW total load emergency shutdown at 1410H (Unplanned Outage) [WEBSMS] | CMIN
9/6/2024 1:08:09 PM | [NSO Update] Mindanao Grid-09/06/2024 13:15: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3358MW, PK=2483MW, RR=73MW, NetOpMargin: PM=803, EVE=898 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @40MW, MA2 @38MW [WEBSMS] | CMIN
9/6/2024 1:05:41 PM | [NSO Update] Visayas Grid-09/06/2024 13:05: GRID UPDATE AS OF 1:00 PM System Condition: CAP=2825MW, PK=2401MW, RR=31MW, NetOpMargin: PM=392, EVE=361 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @230MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PGPP2-SOG1 @15MW [WEBSMS] | CVIS
9/6/2024 1:04:18 PM | Mindanao Grid-09/06/2024 13:11: Agusan Power Corp HEPP online at 1300H (Unplanned Outage) [WEBSMS] | CMIN
9/6/2024 12:59:05 PM | [NSO Update] Visayas Grid-09/06/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2825MW, PK=2401MW, RR=31MW, NetOpMargin: PM=392, EVE=361 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @230MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PGPP2-SOG1 @15MW [WEBSMS] | CVIS
9/6/2024 12:55:45 PM | [NSO Update] Luzon Grid-09/06/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14864MW, PK=10667MW, RR=396MW, NetOpMargin: PM=3802, EVE=3866 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @270MW, Masinloc 2 @270MW, Masinloc 3 @250MW, Calaca 1 @160MW, Calaca 2 @150MW, SLTEC 2 @119MW, SLTEC 1 @120MW [WEBSMS] | CLUZ
9/6/2024 12:29:48 PM | [NSO Update] Visayas Grid-09/06/2024 12:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1221H with power going to Visayas [WEBSMS] | CVIS
9/6/2024 12:29:05 PM | [NSO Update] Luzon Grid-09/06/2024 12:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1221H with power going to Visayas [WEBSMS] | CLUZ
9/6/2024 12:14:18 PM | [NSO Update] Visayas Grid-09/06/2024 12:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1211H from forward power direction [WEBSMS] | CVIS
9/6/2024 12:13:38 PM | [NSO Update] Luzon Grid-09/06/2024 12:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1211H from forward power direction [WEBSMS] | CLUZ
9/6/2024 12:09:32 PM | Luzon Grid-09/06/2024 12:09: Tayabas PCB 9-03CB04TAY restored at 1208H (Planned Outage) [WEBSMS] | CLUZ
9/6/2024 10:28:03 AM | Mindanao Grid-09/06/2024 10:35: WMPC DG07 online at 1020H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/6/2024 9:38:16 AM | Luzon Grid-09/06/2024 09:38: Tayabas PCB 9-03CB04TAY de-energized at 0932H (Planned Outage) [WEBSMS] | CLUZ
9/6/2024 9:12:50 AM | Mindanao Grid-09/06/2024 09:20: WMPC DG10 online at 0909H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/6/2024 9:04:58 AM | Mindanao Grid-09/06/2024 09:12: Agusan Power Lake HEPP shutdown at 0901H (Unplanned Outage) [WEBSMS] | CMIN
9/6/2024 9:01:56 AM | [NSO Update] Visayas Grid-09/06/2024 09:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0858H with power going to Luzon [WEBSMS] | CVIS
9/6/2024 9:01:27 AM | [NSO Update] Luzon Grid-09/06/2024 09:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0858H with power going to Luzon [WEBSMS] | CLUZ
9/6/2024 8:18:25 AM | Visayas Grid-09/06/2024 08:18: DaanBantayan SS 230 kV bus 1 de-energized at 0816H (Planned Outage) [WEBSMS] | CVIS
9/6/2024 8:16:01 AM | Mindanao Grid-09/06/2024 08:23: Kibawe - Tacurong 138kVL (7LI1KIB-TAC) deenergized at 0810H. Planned Outage/Non-GOMP. (Note: Approved shutdown request by MD6) [WEBSMS] | CMIN
9/6/2024 8:14:07 AM | [NSO Update] Visayas Grid-09/06/2024 08:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0811H from forward power direction [WEBSMS] | CVIS
9/6/2024 8:13:31 AM | [NSO Update] Luzon Grid-09/06/2024 08:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0811H from forward power direction [WEBSMS] | CLUZ
9/6/2024 6:26:37 AM | [NSO Update] Visayas Grid-09/06/2024 06:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0622H with power going to Luzon [WEBSMS] | CVIS
9/6/2024 6:26:08 AM | [NSO Update] Luzon Grid-09/06/2024 06:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0622H with power going to Luzon [WEBSMS] | CLUZ
9/6/2024 6:20:04 AM | [NSO Update] Visayas Grid-09/06/2024 06:20: undefined at 0612H Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0612H from reverse power direction [WEBSMS] | CVIS
9/6/2024 6:19:41 AM | [NSO Update] Luzon Grid-09/06/2024 06:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0612H from reverse power direction [WEBSMS] | CLUZ
9/6/2024 5:36:00 AM | Visayas Grid-09/06/2024 05:36: Magdugo - Calongcalong 138 kV Line 1 de-energized at 0535H (Planned Outage) [WEBSMS] | CVIS
9/6/2024 5:26:50 AM | [NSO Update] Mindanao Grid-09/06/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3371MW, PK=2409MW, RR=73MW, NetOpMargin: AM=889, PM=859, EVE=880 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @40MW, MA2 @38MW [WEBSMS] | CMIN
9/6/2024 5:24:55 AM | [NSO Update] Visayas Grid-09/06/2024 05:24: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2830MW, PK=2268MW, RR=31MW, NetOpMargin: AM=531, PM=359, EVE=389 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @235MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PGPP2-SOG1 @15MW, PDPP3-G @10MW, PDPP3-E @8MW [WEBSMS] | CVIS
9/6/2024 5:23:36 AM | [NSO Update] Luzon Grid-09/06/2024 05:23: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15235MW, PK=10061MW, RR=390MW, NetOpMargin: AM=4784, PM=4512, EVE=4288 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @310MW, Masinloc 2 @310MW, Masinloc 3 @280MW, Calaca 1 @160MW, Calaca 2 @150MW, SLTEC 2 @119MW, SLTEC 1 @120MW [WEBSMS] | CLUZ
9/6/2024 4:16:49 AM | [NSO Update] Mindanao Grid-09/06/2024 04:23: Weather Advisory: Trough of Super Typhoon {YAGI} (formerly "ENTENG") affecting Extreme Northern Luzon. Southwest Monsoon affecting the rest of Luzon. [WEBSMS] | CMIN
9/6/2024 4:16:32 AM | [NSO Update] Visayas Grid-09/06/2024 04:16: Weather Advisory: Trough of Super Typhoon {YAGI} (formerly "ENTENG") affecting Extreme Northern Luzon. Southwest Monsoon affecting the rest of Luzon. [WEBSMS] | CVIS
9/6/2024 4:16:17 AM | [NSO Update] Luzon Grid-09/06/2024 04:16: Weather Advisory: Trough of Super Typhoon {YAGI} (formerly "ENTENG") affecting Extreme Northern Luzon. Southwest Monsoon affecting the rest of Luzon. [WEBSMS] | CLUZ
9/6/2024 1:28:09 AM | [NSO Update] Luzon Grid-09/06/2024 01:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0126H with power going to Visayas. [WEBSMS] | CLUZ
9/6/2024 1:27:36 AM | [NSO Update] Visayas Grid-09/06/2024 01:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0126H with power going to Visayas. [WEBSMS] | CVIS
9/6/2024 1:15:03 AM | [NSO Update] Visayas Grid-09/06/2024 01:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0113H from forward power direction. [WEBSMS] | CVIS
9/6/2024 1:14:53 AM | [NSO Update] Luzon Grid-09/06/2024 01:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0113H from forward power direction. [WEBSMS] | CLUZ
9/5/2024 9:25:57 PM | Mindanao Grid-09/05/2024 21:33: WMPC DG10 shutdown at 2123H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/5/2024 9:22:18 PM | [NSO Update] Visayas Grid-09/05/2024 21:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2121H with power going to Luzon. [WEBSMS] | CVIS
9/5/2024 9:22:15 PM | [NSO Update] Luzon Grid-09/05/2024 21:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2121H with power going to Luzon. [WEBSMS] | CLUZ
9/5/2024 9:12:21 PM | [NSO Update] Luzon Grid-09/05/2024 21:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2111H from reverse power direction. [WEBSMS] | CLUZ
9/5/2024 9:12:18 PM | [NSO Update] Visayas Grid-09/05/2024 21:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2111H from reverse power direction. [WEBSMS] | CVIS
9/5/2024 5:48:31 PM | [NSO Update] Luzon Grid-09/05/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14367MW, PK=9898MW, RR=328MW, NetOpMargin: EVE=4141 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @310MW, Masinloc 2 @310MW, Masinloc 3 @265MW, Calaca 1 @163MW, Calaca 2 @170MW, SLTEC 2 @118MW [WEBSMS] | CLUZ
9/5/2024 5:37:42 PM | [NSO Update] Visayas Grid-09/05/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2651MW, PK=2252MW, RR=31MW, NetOpMargin: EVE=368 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @227MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PGPP2-SOG1 @15MW, PDPP3-G @10MW, PDPP3-E @8MW, PEDC 3 @130MW [WEBSMS] | CVIS
9/5/2024 5:37:18 PM | [NSO Update] Mindanao Grid-09/05/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3308MW, PK=2330MW, RR=73MW, NetOpMargin: EVE=905 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @37.5MW, MA2 @35.5MW [WEBSMS] | CMIN
9/5/2024 4:58:22 PM | Mindanao Grid-09/05/2024 17:05: Pitogo SS 138 kV Transformer T1, 100 MVA (7XF01PIT) energized at 1656H. Planned Outage/ GOMP [WEBSMS] | CMIN
9/5/2024 4:29:41 PM | Mindanao Grid-09/05/2024 16:36: Nabunturan -Masara 138 kV Line de-energized at 0850H.Planned Outage /Non-GOMP. [WEBSMS] | CMIN
9/5/2024 4:27:28 PM | Mindanao Grid-09/05/2024 16:34: Nabunturan -Masara 138 kV Line energized at 1621H from Planned outage /Non-GOMP. [WEBSMS] | CMIN
9/5/2024 3:59:20 PM | Mindanao Grid-09/05/2024 16:06: WMPC DG01 shutdown at 1557H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/5/2024 1:47:04 PM | [NSO Update] Luzon Grid-09/05/2024 13:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1337H with power going to Visayas. [WEBSMS] | CLUZ
9/5/2024 1:46:45 PM | [NSO Update] Visayas Grid-09/05/2024 13:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1337H with power going to Visayas. [WEBSMS] | CVIS
9/5/2024 1:33:26 PM | [NSO Update] Visayas Grid-09/05/2024 13:33: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1323H from forward power direction. [WEBSMS] | CVIS
9/5/2024 1:32:50 PM | [NSO Update] Luzon Grid-09/05/2024 13:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1323H from forward power direction. [WEBSMS] | CLUZ
9/5/2024 12:43:18 PM | [NSO Update] Mindanao Grid-09/05/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3346MW, PK=2459MW, RR=73MW, NetOpMargin: PM=814, EVE=933 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @37.5MW, MA2 @35.5MW [WEBSMS] | CMIN
9/5/2024 12:41:19 PM | [NSO Update] Visayas Grid-09/05/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2820MW, PK=2442MW, RR=31MW, NetOpMargin: PM=347, EVE=377 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @227MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PGPP2-SOG1 @15MW, PDPP3-G @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
9/5/2024 12:39:47 PM | [NSO Update] Luzon Grid-09/05/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14786MW, PK=10009MW, RR=436MW, NetOpMargin: PM=4342, EVE=4069 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @300MW, Masinloc 2 @300MW, Masinloc 3 @280MW, Calaca 1 @140MW, Calaca 2 @150MW, SLTEC 2 @120MW [WEBSMS] | CLUZ
9/5/2024 10:34:30 AM | Mindanao Grid-09/05/2024 10:41: WMPC DG 01 online at 1031H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/5/2024 10:30:24 AM | [NSO Update] Luzon Grid-09/05/2024 10:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1026H with power going to Luzon. [WEBSMS] | CLUZ
9/5/2024 10:27:58 AM | [NSO Update] Visayas Grid-09/05/2024 10:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1026H with power going to Luzon. [WEBSMS] | CVIS
9/5/2024 10:18:59 AM | [NSO Update] Visayas Grid-09/05/2024 10:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1016H from reverse power direction. [WEBSMS] | CVIS
9/5/2024 10:18:56 AM | [NSO Update] Luzon Grid-09/05/2024 10:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1016H from reverse power direction. [WEBSMS] | CLUZ
9/5/2024 9:29:30 AM | Mindanao Grid-09/05/2024 09:36: WMPC DG10 online at 0925H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/5/2024 8:42:16 AM | Mindanao Grid-09/05/2024 08:49: Pitogo SS 138 kV Transformer T1, 100 MVA (7XF01PIT) de-energized at 0830H. Planned Outage/ GOMP [WEBSMS] | CMIN
9/5/2024 8:39:16 AM | Mindanao Grid-09/05/2024 08:46: Bunawan SS 138 kV PCB 7-08CB08BUN de-energized at at 0830H. Planned Outage. [WEBSMS] | CMIN
9/5/2024 8:21:21 AM | Mindanao Grid-09/05/2024 08:28: Pitogo SS 138kV Transformer T2, 100MVA , energized at 0810H (Planned Outage) [WEBSMS] | CMIN
9/5/2024 7:15:44 AM | [NSO Update] Luzon Grid-09/05/2024 07:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0713H with power going to Visayas. [WEBSMS] | CLUZ
9/5/2024 7:14:58 AM | [NSO Update] Visayas Grid-09/05/2024 07:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0713H with power going to Visayas. [WEBSMS] | CVIS
9/5/2024 6:49:47 AM | [NSO Update] Luzon Grid-09/05/2024 06:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0645H from reverse power direction. [WEBSMS] | CLUZ
9/5/2024 6:48:39 AM | [NSO Update] Visayas Grid-09/05/2024 06:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0645H from reverse power direction. [WEBSMS] | CVIS
9/5/2024 6:20:40 AM | Mindanao Grid-09/05/2024 06:27: Pitogo SS 138 kV Transformer T2, 100 MVA de-energized at 0611H. Planned Outage. [WEBSMS] | CMIN
9/5/2024 6:03:19 AM | Mindanao Grid-09/05/2024 06:10: Tagoloan - Villanueva 138kV L2 energized at 0559H. (Planned Outage) [WEBSMS] | CMIN
9/5/2024 5:41:45 AM | [NSO Update] Luzon Grid-09/05/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15071MW, PK=10302MW, RR=430MW, NetOpMargin: AM=4339, PM=3540, EVE=3777 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @300MW, Masinloc 2 @300MW, Masinloc 3 @280MW, Calaca 1 @140MW, Calaca 2 @150MW, SLTEC 2 @120MW [WEBSMS] | CLUZ
9/5/2024 5:37:04 AM | [NSO Update] Mindanao Grid-09/05/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3364MW, PK=2313MW, RR=73MW, NetOpMargin: AM=978, PM=744, EVE=890 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
9/5/2024 5:36:00 AM | [NSO Update] Visayas Grid-09/05/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2818MW, PK=2299MW, RR=31MW, NetOpMargin: AM=488, PM=321, EVE=361 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @232MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PGPP2-SOG1 @15MW, PDPP3-G @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
9/5/2024 4:19:58 AM | [NSO Update] Mindanao Grid-09/05/2024 04:27: Weather Advisory: Trough of Typhoon {YAGI} (formerly "ENTENG") affecting the western section of Northern Luzon. Southwest Monsoon affecting Central and Southern Luzon. [WEBSMS] | CMIN
9/5/2024 4:19:44 AM | [NSO Update] Luzon Grid-09/05/2024 04:20: Weather Advisory: Trough of Typhoon {YAGI} (formerly "ENTENG") affecting the western section of Northern Luzon. Southwest Monsoon affecting Central and Southern Luzon. [WEBSMS] | CLUZ
9/5/2024 4:19:31 AM | [NSO Update] Visayas Grid-09/05/2024 04:19: Weather Advisory: Trough of Typhoon {YAGI} (formerly "ENTENG") affecting the western section of Northern Luzon. Southwest Monsoon affecting Central and Southern Luzon. [WEBSMS] | CVIS
9/5/2024 4:13:48 AM | Mindanao Grid-09/05/2024 04:21: Tagoloan - Villanueva 138kV Line 2 de-energized/shutdown at 0404H. (Planned Outage) [WEBSMS] | CMIN
9/4/2024 9:20:49 PM | Mindanao Grid-09/04/2024 21:28: WMPC DG10 shutdown at 2116H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/4/2024 9:12:32 PM | Mindanao Grid-09/04/2024 21:19: Correction: Agus 6 HEPP Unit 1 online at 2042H (Unplanned Outage) [WEBSMS] | CMIN
9/4/2024 9:03:09 PM | Mindanao Grid-09/04/2024 21:10: WMPC DG06 shutdown at 2101H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/4/2024 8:44:29 PM | Mindanao Grid-09/04/2024 20:51: Agus 6 HEPP Unit 1 online at 0842H (Unplanned Outage) [WEBSMS] | CMIN
9/4/2024 6:28:10 PM | Visayas Grid-09/04/2024 18:28: PGPP 2 Sogongon U1 cut in at 1826H. (Unplanned Outage) [WEBSMS] | CVIS
9/4/2024 6:13:00 PM | Visayas Grid-09/04/2024 18:13: PGPP 2 Sogongon U1 tripped at 1810H. (Unplanned Outage) [WEBSMS] | CVIS
9/4/2024 6:05:28 PM | [NSO Update] Mindanao Grid-09/04/2024 18:12: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3291MW, PK=2341MW, RR=73MW, NetOpMargin: EVE=876 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
9/4/2024 6:03:06 PM | [NSO Update] Visayas Grid-09/04/2024 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2667MW, PK=2285MW, RR=31MW, NetOpMargin: EVE=351 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @228MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PGPP2-SOG1 @16MW, PDPP3-G @10MW [WEBSMS] | CVIS
9/4/2024 5:55:42 PM | [NSO Update] Luzon Grid-09/04/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13659MW, PK=9868MW, RR=408MW, NetOpMargin: EVE=3383 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Masinloc 1 @300MW, Masinloc 2 @300MW, Masinloc 3 @280MW, Calaca 1 @160MW, Calaca 2 @170MW, SLTEC 2 @120MW [WEBSMS] | CLUZ
9/4/2024 5:35:01 PM | Luzon Grid-09/04/2024 17:35: GNPD 2 online at 1732H (Unplanned Outage) [WEBSMS] | CLUZ
9/4/2024 3:50:03 PM | Visayas Grid-09/04/2024 15:50: Ormoc SS 150MVA TR 2 energized at 1547H. (Planned Outage) [WEBSMS] | CVIS
9/4/2024 1:01:54 PM | [NSO Update] Mindanao Grid-09/04/2024 13:09: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3329MW, PK=2546MW, RR=73MW, NetOpMargin: PM=709, EVE=787 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
9/4/2024 12:51:41 PM | [NSO Update] Luzon Grid-09/04/2024 12:51: MINDANAO GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3329MW, PK=2546MW, RR=73MW, NetOpMargin: PM=709, EVE=787 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CLUZ
9/4/2024 12:40:04 PM | [NSO Update] Visayas Grid-09/04/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2787MW, PK=2412MW, RR=31MW, NetOpMargin: PM=343, EVE=327 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @228MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PGPP2-SOG1 @16MW, PDPP3-G @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
9/4/2024 12:40:00 PM | [NSO Update] Luzon Grid-09/04/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14170MW, PK=10391MW, RR=436MW, NetOpMargin: PM=3343, EVE=3196 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @300MW, Masinloc 2 @300MW, Masinloc 3 @280MW, Calaca 1 @160MW, Calaca 2 @170MW [WEBSMS] | CLUZ
9/4/2024 11:53:14 AM | [NSO Update] Visayas Grid-09/04/2024 11:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1152H with power going to Visayas. [WEBSMS] | CVIS
9/4/2024 11:53:10 AM | [NSO Update] Luzon Grid-09/04/2024 11:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1152H with power going to Visayas. [WEBSMS] | CLUZ
9/4/2024 11:46:57 AM | [NSO Update] Visayas Grid-09/04/2024 11:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1142H from forward power direction [WEBSMS] | CVIS
9/4/2024 11:46:31 AM | [NSO Update] Luzon Grid-09/04/2024 11:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1142H from forward power direction [WEBSMS] | CLUZ
9/4/2024 9:08:02 AM | [NSO Update] Visayas Grid-09/04/2024 09:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0901H with power going to Luzon. [WEBSMS] | CVIS
9/4/2024 9:07:22 AM | [NSO Update] Luzon Grid-09/04/2024 09:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0901H with power going to Luzon. [WEBSMS] | CLUZ
9/4/2024 9:05:50 AM | [NSO Update] Visayas Grid-09/04/2024 09:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0851H from reverse power direction. [WEBSMS] | CVIS
9/4/2024 9:05:11 AM | [NSO Update] Luzon Grid-09/04/2024 09:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0851H from reverse power direction [WEBSMS] | CLUZ
9/4/2024 8:22:46 AM | Luzon Grid-09/04/2024 08:22: For info: LRCC resumed normal dispatch function at 0821H. [WEBSMS] | CLUZ
9/4/2024 8:07:11 AM | Luzon Grid-09/04/2024 08:07: For info: LRCC was evacuated at 0803H due to an earthquake. The dispatch function was performed at MDC building. ACCs were informed and advised to monitor the transmission lines and equipment under their AOR. No tripping of generating plant, transmission lines, and feeders. [WEBSMS] | CLUZ
9/4/2024 8:04:01 AM | Luzon Grid-09/04/2024 08:04: For info: LRCC was evacuated at 0803H due to an earthquake. The dispatch function was performed at MDC building. ACCs were informed and advised to monitor the transmission lines and equipment under their AOR. No tripping of generating plant, transmission lines, and feeders. [WEBSMS] | CLUZ
9/4/2024 8:03:24 AM | Luzon Grid-09/04/2024 08:03: For info: LRCC was evacuated at 0803H due to an earthquake. The dispatch function was performed at MDC building. ACCs were informed and advised to monitor the transmission lines and equipment under their AOR. No tripping of generating plant, transmission lines, and feeders. [WEBSMS] | CLUZ
9/4/2024 7:11:09 AM | Luzon Grid-09/04/2024 07:11: GNPD Unit 2 with 400MW tripped at 0709H. Lowest system frequency was 59.346Hz. (Unplanned Outage) [WEBSMS] | CLUZ
9/4/2024 6:28:47 AM | Luzon Grid-09/04/2024 06:29: Bayombong-Matuno HEPP 69kV Line (CO) restored at 0628H (Planned Outage) [WEBSMS] | CLUZ
9/4/2024 6:09:33 AM | Luzon Grid-09/04/2024 06:09: Bayombong-Matuno HEPP 69kV Line (CO) de-energized at 0605H (Planned Outage) [WEBSMS] | CLUZ
9/4/2024 5:53:27 AM | [NSO Update] Luzon Grid-09/04/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15046MW, PK=10512MW, RR=430MW, NetOpMargin: AM=4104, PM=3729, EVE=3721 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @290MW, Masinloc 2 @300MW, Masinloc 3 @265MW, Calaca 1 @160MW, Calaca 2 @170MW [WEBSMS] | CLUZ
9/4/2024 5:05:56 AM | [NSO Update] Luzon Grid-09/04/2024 05:06: Weather Disturbance Alert Notice (WDAN) for Tropical Depression now Severe Tropical Storm ENTENG has been lifted today, September 04, 2024, at 0500H, as it is now outside the Philippine Area of Responsibility (PAR). The center of Severe Tropical Storm ENTENG was estimated based on all available data at 265 km West Northwest of Laoag City, Ilocos Norte (OUTSIDE PAR) (18.8 �N, 118.1 �E ) [WEBSMS] | CLUZ
9/3/2024 10:50:53 PM | Luzon Grid-09/03/2024 22:51: SCPC 1 online at 2248H (Planned Outage) [WEBSMS] | CLUZ
9/3/2024 10:48:12 PM | [NSO Update] Luzon Grid-09/03/2024 22:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2246H with power going to Visayas [WEBSMS] | CLUZ
9/3/2024 10:44:59 PM | [NSO Update] Luzon Grid-09/03/2024 22:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2236H from forward power direction [WEBSMS] | CLUZ
9/3/2024 9:44:58 PM | [NSO Update] Luzon Grid-09/03/2024 21:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2141H from power to Luzon. [WEBSMS] | CLUZ
9/3/2024 9:41:17 PM | [NSO Update] Luzon Grid-09/03/2024 21:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2131H from reverse power direction. [WEBSMS] | CLUZ
9/3/2024 5:46:53 PM | [NSO Update] Luzon Grid-09/03/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14273MW, PK=10176MW, RR=362MW, NetOpMargin: EVE=3735 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @315MW, Masinloc 2 @300MW, Masinloc 3 @285MW, Calaca 1 @200MW, Calaca 2 @200MW, MPGC 3 @90MW [WEBSMS] | CLUZ
9/3/2024 5:42:03 PM | [NSO Update] Visayas Grid-09/03/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2704MW, PK=2313MW, RR=31MW, NetOpMargin: EVE=360 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @233MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PGPP2-SOG1 @16MW, PDPP3-G @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
9/3/2024 5:41:56 PM | [NSO Update] Mindanao Grid-09/03/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3265MW, PK=2402MW, RR=73MW, NetOpMargin: EVE=790 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
9/3/2024 5:19:11 PM | Mindanao Grid-09/03/2024 17:26: WMPC DG06 shutdown at 1716H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/3/2024 5:08:50 PM | [NSO Update] Mindanao Grid-09/03/2024 17:16: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm "ENTENG" {YAGI} was estimated based on all available data at 165 km West Northwest of Laoag City, Ilocos Norte (18.5�N, 119.0�E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 115 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting Central Luzon and Southern Luzon. [WEBSMS] | CMIN
9/3/2024 5:08:46 PM | [NSO Update] Visayas Grid-09/03/2024 17:09: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm "ENTENG" {YAGI} was estimated based on all available data at 165 km West Northwest of Laoag City, Ilocos Norte (18.5�N, 119.0�E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 115 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting Central Luzon and Southern Luzon. [WEBSMS] | CVIS
9/3/2024 5:08:43 PM | [NSO Update] Luzon Grid-09/03/2024 17:08: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm "ENTENG" {YAGI} was estimated based on all available data at 165 km West Northwest of Laoag City, Ilocos Norte (18.5�N, 119.0�E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 115 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting Central Luzon and Southern Luzon. [WEBSMS] | CLUZ
9/3/2024 1:37:59 PM | Mindanao Grid-09/03/2024 13:45: WMPC DG06 online at 1334H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/3/2024 1:14:38 PM | Mindanao Grid-09/03/2024 13:21: AGUS 7 Unit 1 online at 1311H Unplanned Outage) [WEBSMS] | CMIN
9/3/2024 12:58:58 PM | [NSO Update] Mindanao Grid-09/03/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3306MW, PK=2440MW, RR=73MW, NetOpMargin: PM=793, EVE=852 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
9/3/2024 12:56:48 PM | [NSO Update] Visayas Grid-09/03/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2745MW, PK=2337MW, RR=31MW, NetOpMargin: PM=377, EVE=396 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @228MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PGPP2-SOG1 @16MW, PDPP3-G @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
9/3/2024 12:55:59 PM | [NSO Update] Luzon Grid-09/03/2024 12:56: Correction: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14882MW, PK=10822MW, RR=396MW, NetOpMargin: PM=3664, EVE=3753 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @315MW, Masinloc 2 @300MW, Masinloc 3 @285MW, Calaca 1 @200MW, Calaca 2 @200MW, MPGC 3 @90MW [WEBSMS] | CLUZ
9/3/2024 12:52:44 PM | [NSO Update] Luzon Grid-09/03/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14882MW, PK=10822MW, RR=396MW, NetOpMargin: PM=3664, EVE=3753 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Masinloc 1 @315MW, Masinloc 2 @300MW, Masinloc 3 @285MW, Calaca 1 @200MW, Calaca 2 @200MW, MPGC 3 @90MW [WEBSMS] | CLUZ
9/3/2024 11:01:48 AM | Mindanao Grid-09/03/2024 11:09: Agus6-Agus7 138 kV Line 1(7LI1AG6-AP7) energized at 1050H from unplanned Outage. [WEBSMS] | CMIN
9/3/2024 9:36:54 AM | Mindanao Grid-09/03/2024 09:44: WMPC DG10 online at 0934H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/3/2024 5:44:01 AM | [NSO Update] Mindanao Grid-09/03/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3318MW, PK=2333MW, RR=73MW, NetOpMargin: AM=912, PM=804, EVE=822 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
9/3/2024 5:43:03 AM | [NSO Update] Visayas Grid-09/03/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2838MW, PK=2164MW, RR=31MW, NetOpMargin: AM=643, PM=543, EVE=372 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @245MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PGPP2-SOG1 @16MW, TGPP @111.2MW, PDPP3-G @10MW, PB104-4 @6MW, PDPP3-H @8MW [WEBSMS] | CVIS
9/3/2024 5:41:35 AM | [NSO Update] Luzon Grid-09/03/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15353MW, PK=10288MW, RR=383MW, NetOpMargin: AM=4681, PM=4298, EVE=4138 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @315MW, MSLC2 @300MW, MSLC3 @300MW [WEBSMS] | CLUZ
9/3/2024 4:39:27 AM | [NSO Update] Mindanao Grid-09/03/2024 04:46: Weather Update: At 3:00 AM today, the center of Tropical Storm ENTENG was estimated based on all available data in the vicinity of Batac City, Ilocos Norte (18.1 N, 120.6 E) with maximum sustained winds of 75 km/h near the center and gustiness of up to 125 km/h. It is moving Northwestward at 25 km/h. Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CMIN
9/3/2024 4:39:11 AM | [NSO Update] Visayas Grid-09/03/2024 04:39: Weather Update: At 3:00 AM today, the center of Tropical Storm ENTENG was estimated based on all available data in the vicinity of Batac City, Ilocos Norte (18.1 N, 120.6 E) with maximum sustained winds of 75 km/h near the center and gustiness of up to 125 km/h. It is moving Northwestward at 25 km/h. Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CVIS
9/3/2024 4:38:59 AM | [NSO Update] Luzon Grid-09/03/2024 04:39: Weather Update: At 3:00 AM today, the center of Tropical Storm ENTENG was estimated based on all available data in the vicinity of Batac City, Ilocos Norte (18.1 N, 120.6 E) with maximum sustained winds of 75 km/h near the center and gustiness of up to 125 km/h. It is moving Northwestward at 25 km/h. Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CLUZ
9/3/2024 4:38:09 AM | [NSO Update] Visayas Grid-09/03/2024 04:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0435H with power going to Visayas [WEBSMS] | CVIS
9/3/2024 4:37:56 AM | [NSO Update] Luzon Grid-09/03/2024 04:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0435H with power going to Visayas [WEBSMS] | CLUZ
9/3/2024 4:35:32 AM | [NSO Update] Visayas Grid-09/03/2024 04:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0425H from forward power direction [WEBSMS] | CVIS
9/3/2024 4:35:17 AM | [NSO Update] Luzon Grid-09/03/2024 04:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0425H from forward power direction [WEBSMS] | CLUZ
9/3/2024 3:40:27 AM | [NSO Update] Luzon Grid-09/03/2024 03:40: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0258H from reverse power direction [WEBSMS] | CLUZ
9/3/2024 3:39:30 AM | [NSO Update] Visayas Grid-09/03/2024 03:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0335H with power going to Luzon [WEBSMS] | CVIS
9/3/2024 3:39:14 AM | [NSO Update] Luzon Grid-09/03/2024 03:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0335H with power going to Luzon [WEBSMS] | CLUZ
9/3/2024 2:59:46 AM | [NSO Update] Visayas Grid-09/03/2024 02:59: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0258H from reverse power direction [WEBSMS] | CVIS
9/2/2024 11:50:19 PM | Visayas Grid-09/02/2024 23:50: Paranas-Calbayog 138 kV Line 2 energized at 2347H (Unplanned Outage) [WEBSMS] | CVIS
9/2/2024 10:12:59 PM | Visayas Grid-09/02/2024 22:13: Paranas-Calbayog 138 kV Line 2 tripped at 2209H (Unplanned Outage) [WEBSMS] | CVIS
9/2/2024 8:17:57 PM | Mindanao Grid-09/02/2024 20:25: WMPC DG10 shutdown at 2016H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/2/2024 8:00:08 PM | Visayas Grid-09/02/2024 20:00: Calongcalong - Toledo Solar 69 kV Line energized at 1959H (Unplanned Outage) [WEBSMS] | CVIS
9/2/2024 6:07:30 PM | Visayas Grid-09/02/2024 18:07: Calongcalong - Toledo Solar 69 kV Line tripped at 1800H (Unplanned Outage) [WEBSMS] | CVIS
9/2/2024 5:54:39 PM | [NSO Update] Mindanao Grid-09/02/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3305MW, PK=2325MW, RR=73MW, NetOpMargin: EVE=907 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
9/2/2024 5:52:53 PM | [NSO Update] Visayas Grid-09/02/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2713MW, PK=2124MW, RR=31MW, NetOpMargin: EVE=558 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @237MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PGPP2-SOG1 @16MW, PDPP3-E @8MW, PDPP3-G @10MW, PB104-4 @6MW, PDPP3-H @8MW [WEBSMS] | CVIS
9/2/2024 5:51:00 PM | [NSO Update] Luzon Grid-09/02/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14472MW, PK=9106MW, RR=444MW, NetOpMargin: EVE=4922 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @315MW, Masinloc 2 @300MW, Masinloc 3 @305MW [WEBSMS] | CLUZ
9/2/2024 5:01:04 PM | [NSO Update] Mindanao Grid-09/02/2024 17:08: Weather Update: At 3:00 PM today, the center of Tropical Storm ENTENG was estimated based on all available data in the vicinity of Casiguran, Aurora (16.3N, 122.0E) with maximum sustained winds of 85 km/h near the center and gustiness of up to 140 km/h. It is moving North Northwestward at 20 km/h. Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CMIN
9/2/2024 5:00:51 PM | [NSO Update] Visayas Grid-09/02/2024 17:01: Weather Update: At 3:00 PM today, the center of Tropical Storm ENTENG was estimated based on all available data in the vicinity of Casiguran, Aurora (16.3N, 122.0E) with maximum sustained winds of 85 km/h near the center and gustiness of up to 140 km/h. It is moving North Northwestward at 20 km/h. Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CVIS
9/2/2024 5:00:36 PM | [NSO Update] Luzon Grid-09/02/2024 17:00: Weather Update: At 3:00 PM today, the center of Tropical Storm ENTENG was estimated based on all available data in the vicinity of Casiguran, Aurora (16.3N, 122.0E) with maximum sustained winds of 85 km/h near the center and gustiness of up to 140 km/h. It is moving North Northwestward at 20 km/h. Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CLUZ
9/2/2024 3:20:33 PM | [NSO Update] Visayas Grid-09/02/2024 15:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1519H with power going to Visayas [WEBSMS] | CVIS
9/2/2024 3:20:22 PM | [NSO Update] Luzon Grid-09/02/2024 15:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1519H with power going to Visayas [WEBSMS] | CLUZ
9/2/2024 3:05:54 PM | [NSO Update] Visayas Grid-09/02/2024 15:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1501H from reverse power direction [WEBSMS] | CVIS
9/2/2024 3:05:41 PM | [NSO Update] Luzon Grid-09/02/2024 15:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1501H from reverse power direction [WEBSMS] | CLUZ
9/2/2024 2:48:00 PM | Luzon Grid-09/02/2024 14:48: Quezon-Duhat 230kV Line restored at 1447H (Unplanned Outage) [WEBSMS] | CLUZ
9/2/2024 2:26:17 PM | Visayas Grid-09/02/2024 14:26: Leyte-A - MAHA A U1 cut-in at 1413H (Unplanned Outage) [WEBSMS] | CVIS
9/2/2024 12:45:23 PM | [NSO Update] Mindanao Grid-09/02/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3348MW, PK=2312MW, RR=73MW, NetOpMargin: PM=963, EVE=989 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
9/2/2024 12:44:28 PM | [NSO Update] Visayas Grid-09/02/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2803MW, PK=2203MW, RR=31MW, NetOpMargin: PM=569, EVE=544 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @230MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PGPP2 SOG1 @16MW, PDPP3_E @8MW, PDPP3_G @10MW [WEBSMS] | CVIS
9/2/2024 12:43:17 PM | [NSO Update] Luzon Grid-09/02/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14911MW, PK=9846MW, RR=472MW, NetOpMargin: PM=4593, EVE=3889 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @305MW, Masinloc 2 @300MW, Masinloc 3 @305MW [WEBSMS] | CLUZ
9/2/2024 10:49:06 AM | Mindanao Grid-09/02/2024 10:56: Agus 5 HEPP U1 online at 1043H (Planned Outage) [WEBSMS] | CMIN
9/2/2024 10:33:22 AM | Mindanao Grid-09/02/2024 10:40: Agus5 Switchyard - Agus5 HEPP 138kV Line 1 energized at 1028H. (Planned Outage) [WEBSMS] | CMIN
9/2/2024 10:24:35 AM | Mindanao Grid-09/02/2024 10:31: WMPC DG10 online at 1022H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/2/2024 9:25:45 AM | Luzon Grid-09/02/2024 09:25: Quezon-Duhat 230kV Line tripped at 0915H, reclosed at Duhat side, and retripped at Duhat side at 0917H (Unplanned Outage) [WEBSMS] | CLUZ
9/2/2024 9:22:10 AM | Luzon Grid-09/02/2024 09:22: Quezon-Duhat 230kV Line tripped/reclosed at 0912H (Unplanned Outage) [WEBSMS] | CLUZ
9/2/2024 9:03:30 AM | Mindanao Grid-09/02/2024 09:10: Agus 6 U4 shutdown at 0902H. (Planned Outage) [WEBSMS] | CMIN
9/2/2024 8:33:45 AM | [NSO Update] Visayas Grid-09/02/2024 08:33: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0831H with power going to Visayas. [WEBSMS] | CVIS
9/2/2024 8:33:28 AM | [NSO Update] Luzon Grid-09/02/2024 08:33: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0831H with power going to Visayas. [WEBSMS] | CLUZ
9/2/2024 8:28:24 AM | [NSO Update] Visayas Grid-09/02/2024 08:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0819H from forward power direction. [WEBSMS] | CVIS
9/2/2024 8:28:12 AM | [NSO Update] Luzon Grid-09/02/2024 08:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0819H from forward power direction. [WEBSMS] | CLUZ
9/2/2024 8:15:39 AM | Mindanao Grid-09/02/2024 08:22: Agus5 Switchyard - Agus5 HEPP 138kV Line 1 de-energized/shutdown at 0806H .(Planned Outage) [WEBSMS] | CMIN
9/2/2024 8:05:03 AM | Mindanao Grid-09/02/2024 08:12: Agus 5 Unit 1 shutdown at 0805H. (Planned Outage) [WEBSMS] | CMIN
9/2/2024 8:01:52 AM | Mindanao Grid-09/02/2024 08:09: SMC Unit2 online at 0758H from FO. (Unplanned Outage) [WEBSMS] | CMIN
9/2/2024 6:39:22 AM | [NSO Update] Visayas Grid-09/02/2024 06:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0637H with power going to Luzon. [WEBSMS] | CVIS
9/2/2024 6:39:01 AM | [NSO Update] Luzon Grid-09/02/2024 06:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0637H with power going to Luzon. [WEBSMS] | CLUZ
9/2/2024 6:28:12 AM | [NSO Update] Visayas Grid-09/02/2024 06:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0627H from reverse power direction. [WEBSMS] | CVIS
9/2/2024 6:27:59 AM | [NSO Update] Luzon Grid-09/02/2024 06:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0627H from reverse power direction. [WEBSMS] | CLUZ
9/2/2024 5:45:18 AM | [NSO Update] Luzon Grid-09/02/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15179MW, PK=10298MW, RR=451MW, NetOpMargin: AM=4430, PM=2787, EVE=3638 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @305MW, Masinloc 2 @300MW, Masinloc 3 @305MW, SLTEC 2 @120MW [WEBSMS] | CLUZ
9/2/2024 5:40:27 AM | [NSO Update] Mindanao Grid-09/02/2024 05:47: Weather Update: At 3:00 AM today, the center of Tropical Storm "ENTENG" was estimated based on all available data over the coastal waters of Vinzons, Camarines Norte (14.6N, 123.3E) with maximum sustained winds of 75 km/h near the center and gustiness of up to 90 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CMIN
9/2/2024 5:39:37 AM | [NSO Update] Visayas Grid-09/02/2024 05:39: Weather Update: At 3:00 AM today, the center of Tropical Storm "ENTENG" was estimated based on all available data over the coastal waters of Vinzons, Camarines Norte (14.6N, 123.3E) with maximum sustained winds of 75 km/h near the center andgustiness of up to 90 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CVIS
9/2/2024 5:39:02 AM | [NSO Update] Luzon Grid-09/02/2024 05:39: Weather Update: At 3:00 AM today, the center of Tropical Storm "ENTENG" was estimated based on all available data over the coastal waters of Vinzons, Camarines Norte (14.6N, 123.3E) with maximum sustained winds of 75 km/h near the center andgustiness of up to 90 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CLUZ
9/2/2024 5:27:44 AM | [NSO Update] Mindanao Grid-09/02/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3208MW, PK=2183MW, RR=73MW, NetOpMargin: AM=953, PM=844, EVE=932 Highest Unit O/L: GNPK 1@151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
9/2/2024 5:26:25 AM | [NSO Update] Visayas Grid-09/02/2024 05:26: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2734MW, PK=2155MW, RR=31MW, NetOpMargin: AM=548, PM=401, EVE=360 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @242MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PB104-3 @5MW, 08PDPP3_E @8MW, 08PDPP3_G @10MW, 08PDPP3_H @8MW [WEBSMS] | CVIS
9/2/2024 5:05:46 AM | [NSO Update] Luzon Grid-09/02/2024 05:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0503H with power going to Visayas. [WEBSMS] | CLUZ
9/2/2024 5:05:28 AM | [NSO Update] Visayas Grid-09/02/2024 05:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0503H with power going to Visayas. [WEBSMS] | CVIS
9/2/2024 4:56:00 AM | [NSO Update] Luzon Grid-09/02/2024 04:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0453H from forward power direction. [WEBSMS] | CLUZ
9/2/2024 4:55:34 AM | [NSO Update] Visayas Grid-09/02/2024 04:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0453H from forward power direction. [WEBSMS] | CVIS
9/2/2024 4:46:04 AM | Mindanao Grid-09/02/2024 04:53: Agus 7 HEP U1 tripped at 0301H due to governor problem. Unplanned Outage. [WEBSMS] | CMIN
9/2/2024 2:19:07 AM | Luzon Grid-09/02/2024 02:19: QPPL online at 0200H (Unplanned Outage) [WEBSMS] | CLUZ
9/2/2024 2:09:02 AM | Luzon Grid-09/02/2024 02:09: QPPL online at 0200H (Planned Outage) [WEBSMS] | CLUZ
9/2/2024 1:33:31 AM | Luzon Grid-09/02/2024 01:33: Concepcion-San Manuel 230kV Line 1 restored at 0133H (Planned Outage) [WEBSMS] | CLUZ
9/2/2024 12:56:03 AM | Visayas Grid-09/02/2024 00:56: PGPP2 Sog 1 re-online/tripped at 2327/0051H (Unplanned Outage) [WEBSMS] | CVIS
9/1/2024 11:54:18 PM | Mindanao Grid-09/02/2024 00:01: Lala - Aurora 138kV L1 (7LI1LLA-AUR) energized at 2350H. (Planned Outage/GOMP). [WEBSMS] | CMIN
9/1/2024 7:07:49 PM | [NSO Update] Mindanao Grid-09/01/2024 19:15: The Luzon Grid is on "BLUE ALERT" due to Tropical Depression "ENTENG" is forecast to move generally northwestward until tomorrow (2 September) early morning and may make landfall in the vicinity of Catanduanes or Albay in the next 12 hours. [WEBSMS] | CMIN
9/1/2024 7:07:19 PM | [NSO Update] Visayas Grid-09/01/2024 19:07: The Luzon Grid is on "BLUE ALERT" due to Tropical Depression "ENTENG" is forecast to move generally northwestward until tomorrow (2 September) early morning and may make landfall in the vicinity of Catanduanes or Albay in the next 12 hours. [WEBSMS] | CVIS
9/1/2024 7:05:12 PM | [NSO Update] Luzon Grid-09/01/2024 19:05: The Luzon Grid is on "BLUE ALERT" due to Tropical Depression "ENTENG" is forecast to move generally northwestward until tomorrow (2 September) early morning and may make landfall in the vicinity of Catanduanes or Albay in the next 12 hours. [WEBSMS] | CLUZ
9/1/2024 5:40:59 PM | [NSO Update] Luzon Grid-09/01/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13801MW, PK=9914MW, RR=315MW, NetOpMargin: EVE=3572 Highest Unit O/L: GNPD 1&2 668MW Derated Plant: Masinloc 1 @300MW, Masinloc 2 @280MW, Masinloc 3 @305MW, SLTEC 2 @119MW, Calaca 1 @180MW, Calaca 2 @270MW [WEBSMS] | CLUZ
9/1/2024 5:37:54 PM | Mindanao Grid-09/01/2024 17:45: SMC (MCO) U2 on emergency shutdown at 1729H due to coal handling system problem. [WEBSMS] | CMIN
9/1/2024 5:27:39 PM | [NSO Update] Mindanao Grid-09/01/2024 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3199MW, PK=1991MW, RR=73MW, NetOpMargin: EVE=1135 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
9/1/2024 5:26:43 PM | [NSO Update] Visayas Grid-09/01/2024 17:26: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2647MW, PK=1956MW, RR=31MW, NetOpMargin: EVE=660 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @245MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PB104-3 @5MW, 08PDPP3_E @8MW, 08PDPP3_G @10MW, 08PDPP3_H @8MW [WEBSMS] | CVIS
9/1/2024 4:22:29 PM | Mindanao Grid-09/01/2024 16:29: San Francisco � Bislig 138kV L1 (7LI1SFN-BIS) energized at 1618H from Planned Outage. [WEBSMS] | CMIN
9/1/2024 4:02:54 PM | Mindanao Grid-09/01/2024 16:10: Kibawe -Agus 2 - 138kV L2 (7LI2 AG2-KIB ) energized back at 1556H from Forced Outage. [WEBSMS] | CMIN
9/1/2024 3:33:47 PM | Visayas Grid-09/01/2024 15:33: Colon SS 138 kV bus 1 energized at 1509H (Planned Outage) [WEBSMS] | CVIS
9/1/2024 2:24:20 PM | Luzon Grid-09/01/2024 14:24: San Jose-Taytay 230kV Line 2 restored at 1423H (Planned Outage) [WEBSMS] | CLUZ
9/1/2024 1:21:04 PM | Luzon Grid-09/01/2024 13:21: EERI 1 shutdown at 1318H (on commissioning) [WEBSMS] | CLUZ
9/1/2024 1:16:16 PM | Luzon Grid-09/01/2024 13:16: Sta Rita Module 30 online at 1313H (Unplanned Outage) [WEBSMS] | CLUZ
9/1/2024 1:08:02 PM | [NSO Update] Mindanao Grid-09/01/2024 13:15: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3381MW, PK=1813MW, RR=73MW, NetOpMargin: PM=1495, EVE=1289 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
9/1/2024 1:07:04 PM | [NSO Update] Visayas Grid-09/01/2024 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2795MW, PK=1791MW, RR=31MW, NetOpMargin: PM=972, EVE=689 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @245MW, CEDC U3 @75MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PB104-3 @5MW [WEBSMS] | CVIS
9/1/2024 1:04:49 PM | [NSO Update] Luzon Grid-09/01/2024 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14719MW, PK=10144MW, RR=346MW, NetOpMargin: PM=4229, EVE=2986 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @300MW, Masinloc 2 @270MW, Masinloc 3 @290MW, SLTEC 2 @119MW, Calaca 1 @180MW [WEBSMS] | CLUZ
9/1/2024 12:03:56 PM | [NSO Update] Mindanao Grid-09/01/2024 12:11: A Weather Disturbance Alert Notice (WDAN) was issued at 1100H today. The LPA located east of Eastern Visayas has developed into Tropical Depression ENTENG. Based on all available data, the center of the eye is estimated at 120 km north-northeast of Borongan City, Eastern Samar (12.6N, 126.0E). It has maximum sustained winds of 45 km/h, gustiness of 55 km/h, moving north-northwestward at 30 km/h. [WEBSMS] | CMIN
9/1/2024 12:03:30 PM | [NSO Update] Visayas Grid-09/01/2024 12:03: A Weather Disturbance Alert Notice (WDAN) was issued at 1100H today. The LPA located east of Eastern Visayas has developed into Tropical Depression ENTENG. Based on all available data, the center of the eye is estimated at 120 km north-northeast of Borongan City, Eastern Samar (12.6N, 126.0E). It has maximum sustained winds of 45 km/h, gustiness of 55 km/h, moving north-northwestward at 30 km/h. [WEBSMS] | CVIS
9/1/2024 12:03:15 PM | [NSO Update] Luzon Grid-09/01/2024 12:03: A Weather Disturbance Alert Notice (WDAN) was issued at 1100H today. The LPA located east of Eastern Visayas has developed into Tropical Depression ENTENG. Based on all available data, the center of the eye is estimated at 120 km north-northeast of Borongan City, Eastern Samar (12.6N, 126.0E). It has maximum sustained winds of 45 km/h, gustiness of 55 km/h, moving north-northwestward at 30 km/h. [WEBSMS] | CLUZ
9/1/2024 11:58:28 AM | Visayas Grid-09/01/2024 11:58: Dingle - PDPP3 138KV Line 2 energized at 1158H. (Planned Outage) [WEBSMS] | CVIS
9/1/2024 11:32:51 AM | Luzon Grid-09/01/2024 11:32: EERI 1 online at 1129H (on commissioning) [WEBSMS] | CLUZ
9/1/2024 10:06:43 AM | Visayas Grid-09/01/2024 10:06: Calbayog SS TR1 50MVA 138/69/13.8KV energized at 1000H. 0pened 69KV Secondary breaker side. (Planned Outage) [WEBSMS] | CVIS
9/1/2024 8:31:32 AM | Visayas Grid-09/01/2024 08:31: Dingle - PDPP3 138KV Line 2 de-energized at 0828H. (Planned Outage) [WEBSMS] | CVIS
9/1/2024 8:17:20 AM | Mindanao Grid-09/01/2024 08:24: San Frans - Bislig 138kV Line (7LI1SFN-BIS) deenergized at 0807H. (Planned Outage/Non-GOMP). Note: MD4 approved shutdown request. [WEBSMS] | CMIN
9/1/2024 7:55:03 AM | Mindanao Grid-09/01/2024 08:02: Tagoloan SS 100MVA Power Transformer No.1 (7XF01TAG) energized at 0750H. (Planned Outage/Non-GOMP). [WEBSMS] | CMIN
9/1/2024 7:34:04 AM | Visayas Grid-09/01/2024 07:34: Colon Substation 138kV Bus 1 de-energized at 0733H. (Planned Outage) [WEBSMS] | CVIS
9/1/2024 6:42:31 AM | Mindanao Grid-09/01/2024 06:49: Lala - Aurora 138kV L1 (7LI1LLA-AUR) deenergized at 0615H. (Planned Outage/GOMP). Note: Approved shutdown request by MTD-A and SPAR implementation. [WEBSMS] | CMIN
9/1/2024 6:03:27 AM | Mindanao Grid-09/01/2024 06:10: Tagoloan SS 100MVA Power Transformer No.1 (7XF01TAG) deenergized at 0414H. (Planned Outage/Non-GOMP). Note: MD3 Approved shutdown request. [WEBSMS] | CMIN
9/1/2024 5:47:28 AM | [NSO Update] Mindanao Grid-09/01/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3389MW, PK=1830MW, RR=73MW, NetOpMargin: AM=1486, PM=1417, EVE=1229 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
9/1/2024 5:46:42 AM | [NSO Update] Visayas Grid-09/01/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2866MW, PK=1806MW, RR=31MW, NetOpMargin: AM=1029, PM=852, EVE=577 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @250MW, CEDC U3 @75MW, PDPP3-H @8MW, PDPP3-E @8MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PB104-3 @5MW, PDPP3-G @10MW [WEBSMS] | CVIS
9/1/2024 5:45:42 AM | [NSO Update] Luzon Grid-09/01/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15131MW, PK=10375MW, RR=334MW, NetOpMargin: AM=4422, PM=4440, EVE=3102 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @310MW, Masinloc 2 @300MW, Masinloc 3 @200MW, SLTEC 2 @119MW [WEBSMS] | CLUZ
9/1/2024 5:06:04 AM | Luzon Grid-09/01/2024 05:06: SLTEC 1 online at 0500H (Planned Outage) [WEBSMS] | CLUZ
9/1/2024 5:00:54 AM | [NSO Update] Luzon Grid-09/01/2024 05:01: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 175 km East Northeast of Guiuan, Eastern Samar or 205 km East of Borongan City, Eastern Samar (11.5�N, 127.3�E). Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
9/1/2024 5:00:37 AM | [NSO Update] Mindanao Grid-09/01/2024 05:07: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 175 km East Northeast of Guiuan, Eastern Samar or 205 km East of Borongan City, Eastern Samar (11.5�N, 127.3�E). Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
9/1/2024 5:00:18 AM | [NSO Update] Visayas Grid-09/01/2024 05:00: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 175 km East Northeast of Guiuan, Eastern Samar or 205 km East of Borongan City, Eastern Samar (11.5�N, 127.3�E). Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
9/1/2024 4:06:17 AM | Luzon Grid-09/01/2024 04:06: San Jose-Taytay 230kV Line 2 de-energized at 0405H (Planned Outage) [WEBSMS] | CLUZ
9/1/2024 1:12:26 AM | Visayas Grid-09/01/2024 01:12: CEDC U2 cut-out at 0110H. (Planned Outage) [WEBSMS] | CVIS
9/1/2024 12:27:12 AM | Luzon Grid-09/01/2024 00:27: Sta Rita Module 30 shutdown at 0021H. (Maintenance Outage) [WEBSMS] | CLUZ
8/31/2024 10:29:23 PM | Mindanao Grid-08/31/2024 22:36: Agus 2 - Kibawe 138kV L1 (7LI1AG2-KIB of Kibawe side only) auto-tripped and auto-reclosed but failed, at 1909H. (Unplanned Outage). Advised for line patrol. Note: (7LI1AG2-KIB is energized up to Tower #103 only, for the Anti-pilferage Act of 1994) [WEBSMS] | CMIN
8/31/2024 10:04:27 PM | Luzon Grid-08/31/2024 22:04: San Jose PCB 8-05CB08SJO was restored at 2203H. (Unplanned Outage) [WEBSMS] | CLUZ
8/31/2024 9:33:29 PM | Luzon Grid-08/31/2024 21:33: San Juan-Calauan 230kV line 1 was restored at 2130H. (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 5:57:22 PM | Visayas Grid-08/31/2024 17:57: Calbayog SS 50MVA TR 2 energized at 1756H. (Planned Outage) [WEBSMS] | CVIS
8/31/2024 5:45:22 PM | Visayas Grid-08/31/2024 17:45: Concepcion SS 50MVA TR 1 energized at 1504H. (Planned Outage) [WEBSMS] | CVIS
8/31/2024 5:38:03 PM | Visayas Grid-08/31/2024 17:38: Calongcalong SS 50MVA TR 1 energized at 1737H. (Planned Outage) [WEBSMS] | CVIS
8/31/2024 5:36:52 PM | [NSO Update] Mindanao Grid-08/31/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3350MW, PK=2150MW, RR=73MW, NetOpMargin: EVE=1127 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
8/31/2024 5:36:49 PM | [NSO Update] Visayas Grid-08/31/2024 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2730MW, PK=2060MW, RR=31MW, NetOpMargin: EVE=639 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @245MW, CEDC U3 @75MW, PDPP3-H @8MW, PDPP3-E @8MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PB104-3 @5MW, PDPP3-G @10MW [WEBSMS] | CVIS
8/31/2024 5:36:41 PM | [NSO Update] Luzon Grid-08/31/2024 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14018MW, PK=11121MW, RR=358MW, NetOpMargin: EVE=2540 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @310MW, Masinloc 2 @300MW, Masinloc 3 @310MW [WEBSMS] | CLUZ
8/31/2024 5:30:58 PM | Visayas Grid-08/31/2024 17:31: Babatngon-Paranas 138 kV Line 1 energized at 1729H (Planned Outage) [WEBSMS] | CVIS
8/31/2024 5:02:09 PM | Visayas Grid-08/31/2024 17:02: Correction. Amlan-Mabinay 138 kV Line 1 energized at 1654H (Planned outage) [WEBSMS] | CVIS
8/31/2024 5:00:15 PM | Visayas Grid-08/31/2024 17:00: Colon SS. 138 kV bus 1 energized at 1700H (Planned Outage) [WEBSMS] | CVIS
8/31/2024 4:59:22 PM | Luzon Grid-08/31/2024 16:59: Olongapo-SBMA 230kV line was restored at 1658H. (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 4:54:54 PM | Visayas Grid-08/31/2024 16:54: Amlan-Mabinay 138 kV Line 1 energized at 1754H (Planned Outage) [WEBSMS] | CVIS
8/31/2024 4:01:11 PM | Mindanao Grid-08/31/2024 16:08: San Frans - Butuan 138kV Line (7LI1BUT-SFN) energized/restored at 1557H. From Unplanned Outage. [WEBSMS] | CMIN
8/31/2024 3:37:09 PM | Luzon Grid-08/31/2024 15:37: Tayabas PCB 9-05CB08TAY and 9-05CB24TAY were restored at 1527H and 1528H respectively. (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 1:28:56 PM | Mindanao Grid-08/31/2024 13:36: San Frans - Butuan 138kV Line auto-tripped at 1309H. (Unplanned Outage) Note: Advised for immediate line patrol. [WEBSMS] | CMIN
8/31/2024 1:24:41 PM | Luzon Grid-08/31/2024 13:24: Bolo PCB 9-02CB04BLZ restored at 1324H (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 12:50:23 PM | [NSO Update] Mindanao Grid-08/31/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3377MW, PK=2052MW, RR=73MW, NetOpMargin: PM=1252, EVE=1134 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
8/31/2024 12:48:09 PM | [NSO Update] Visayas Grid-08/31/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2886MW, PK=2015MW, RR=31MW, NetOpMargin: PM=840, EVE=577 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @245MW, CEDC U3 @75MW, PDPP3-H @8MW, PDPP3-E @8MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, PB104-3 @5MW, PDPP3-G @10MW [WEBSMS] | CVIS
8/31/2024 12:45:46 PM | [NSO Update] Luzon Grid-08/31/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15267MW, PK=11284MW, RR=389MW, NetOpMargin: PM=3594, EVE=2594 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @240MW, Masinloc 2 @300MW, Masinloc 3 @310MW [WEBSMS] | CLUZ
8/31/2024 11:06:45 AM | Luzon Grid-08/31/2024 11:06: Balsik PCB 9-06CB04BIK restored at 1106H (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 10:07:57 AM | Luzon Grid-08/31/2024 10:08: Balsik PCB 9-06CB04BIK de-energized at 1006H (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 10:06:19 AM | Luzon Grid-08/31/2024 10:06: Balsik PCB 9-02CB24BIK restored at 1005H (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 9:51:37 AM | Mindanao Grid-08/31/2024 09:58: Agus 5 - Aurora 138kV line energized/restored at 0948H. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/31/2024 9:04:42 AM | Luzon Grid-08/31/2024 09:04: Balsik PCB 9-02CB24BIK de-energized at 0903H (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 7:34:10 AM | Visayas Grid-08/31/2024 07:34: Amlan-Mabinay 138kV Line 1 de-energized at 0733H. (Planned Outage) [WEBSMS] | CVIS
8/31/2024 7:28:56 AM | Visayas Grid-08/31/2024 07:29: Calongcalong SS 50MVA TR 1 de-energized at 0727H. (Planned Outage) [WEBSMS] | CVIS
8/31/2024 7:13:44 AM | Luzon Grid-08/31/2024 07:13: San Juan-Calauan 230kV Line 1 de-energized at 0711H (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 7:09:26 AM | Visayas Grid-08/31/2024 07:09: Colon SS 138kV Bus 1 de-energized at 0709H. (Planned Outage) [WEBSMS] | CVIS
8/31/2024 7:08:57 AM | Luzon Grid-08/31/2024 07:09: Bolo PCB 9Z-02CB04BLZ de-energized at 0703H (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 6:55:57 AM | Visayas Grid-08/31/2024 06:56: Babatngon-Paranas 138kV Line 1 de-energized at 0655H. (Planned Outage) [WEBSMS] | CVIS
8/31/2024 6:52:37 AM | Luzon Grid-08/31/2024 06:52: SBMA-Olongapo 230kV Line de-energized at 0651H (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 6:39:52 AM | Visayas Grid-08/31/2024 06:39: Calbayog SS 50MVA TR 2 de-energized at 0637H. (Planned Outage) [WEBSMS] | CVIS
8/31/2024 6:35:38 AM | Luzon Grid-08/31/2024 06:35: Tayabas SS PCB 9-05CB08TAY restored at 0633H (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 6:34:21 AM | Luzon Grid-08/31/2024 06:34: Tayabas SS PCB 9-05CB24TAY de-energized at 0632H (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 6:26:24 AM | Mindanao Grid-08/31/2024 06:33: Agus 5 - Aurora 138kV line de-energized at 0616H. Planned Outage/Non-GOMP. (Note: P&E approved shutdown activities) [WEBSMS] | CMIN
8/31/2024 6:18:16 AM | Visayas Grid-08/31/2024 06:18: Concepcion SS 50MVA TR 1 de-energized at 0616H. (Planned Outage) [WEBSMS] | CVIS
8/31/2024 6:13:20 AM | Luzon Grid-08/31/2024 06:13: Concepcion-San Manuel 230kV Line 1 de-energized at 0612H (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 5:37:36 AM | [NSO Update] Luzon Grid-08/31/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14961MW, PK=10623MW, RR=382MW, NetOpMargin: AM=3956, PM=3262, EVE=2539 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @240MW, Masinloc 2 @300MW, Masinloc 3 @310MW, SLTEC 2 @120MW [WEBSMS] | CLUZ
8/31/2024 5:37:30 AM | [NSO Update] Visayas Grid-08/31/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2866MW, PK=2151MW, RR=31MW, NetOpMargin: AM=684, PM=661, EVE=506 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @247MW, CEDC U3 @75MW, PDPP3-H @8MW, PDPP3-E @8MW, GTEC @10MW, PB101-2 @5.5MW, PDPP1 U2 @4.5MW, PDPP1 U5 @4.5MW [WEBSMS] | CVIS
8/31/2024 5:37:25 AM | [NSO Update] Mindanao Grid-08/31/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3398MW, PK=2206MW, RR=73MW, NetOpMargin: AM=1119, PM=1075, EVE=1043 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
8/31/2024 4:15:40 AM | [NSO Update] Mindanao Grid-08/31/2024 04:22: Weather Advisory: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 695 km East of Butuan City, Agusan del Norte (8.5�N, 131.8�E). Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CMIN
8/31/2024 4:15:35 AM | [NSO Update] Visayas Grid-08/31/2024 04:15: Weather Advisory: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 695 km East of Butuan City, Agusan del Norte (8.5�N, 131.8�E). Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CVIS
8/31/2024 4:15:29 AM | [NSO Update] Luzon Grid-08/31/2024 04:15: Weather Advisory: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 695 km East of Butuan City, Agusan del Norte (8.5�N, 131.8�E). Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CLUZ
8/31/2024 12:48:38 AM | Luzon Grid-08/31/2024 00:48: For information: Commissioning and energization of San Manuel 230kV Bus 2 new main protection and BFR were completed at 0043H. [WEBSMS] | CLUZ
8/31/2024 12:37:45 AM | Luzon Grid-08/31/2024 00:37: San Manuel 230kV Bus 2 restored at 0030H (Planned Outage) [WEBSMS] | CLUZ
8/31/2024 12:15:43 AM | Luzon Grid-08/31/2024 00:15: Correction: QPPL shutdown at 0000H (Unplanned Outage) [WEBSMS] | CLUZ
8/31/2024 12:02:59 AM | Luzon Grid-08/31/2024 00:03: QPPL shutdown at 0000H (Planned Outage) [WEBSMS] | CLUZ
8/30/2024 7:22:31 PM | Mindanao Grid-08/30/2024 19:29: WMPC DG10 shutdown at 1916H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/30/2024 5:47:23 PM | [NSO Update] Visayas Grid-08/30/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2704MW, PK=2229MW, RR=31MW, NetOpMargin: EVE=443 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @245MW, CEDC U3 @75MW, PDPP3-C @10MW, PDPP3-E @8MW, GTEC @10MW, PB101-2 @5.5MW, PB104-3 @6MW [WEBSMS] | CVIS
8/30/2024 5:40:43 PM | [NSO Update] Luzon Grid-08/30/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14441MW, PK=11692MW, RR=398MW, NetOpMargin: EVE=2352 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @310MW, Masinloc 2 @300MW, Masinloc 3 @310MW, SLTEC 2 @120MW [WEBSMS] | CLUZ
8/30/2024 5:33:16 PM | [NSO Update] Mindanao Grid-08/30/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3353MW, PK=2207MW, RR=73MW, NetOpMargin: EVE=1074 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
8/30/2024 5:32:07 PM | Luzon Grid-08/30/2024 17:32: Balsik-Tayabas 500kV Line restored at 1731H (Unplanned Outage) [WEBSMS] | CLUZ
8/30/2024 5:13:04 PM | Luzon Grid-08/30/2024 17:13: Balsik-Tayabas 500kV Line autotripped at 1711H (Unplanned Outage) [WEBSMS] | CLUZ
8/30/2024 4:45:04 PM | Visayas Grid-08/30/2024 16:45: Calongcalong SS 138kV Bus 2 energized at 1643H. (Planned Outage) [WEBSMS] | CVIS
8/30/2024 3:22:22 PM | Luzon Grid-08/30/2024 15:22: Correction: Naga-Tiwi C 230kV Line 1 autotripped/auto-reclosed at 1414H (Unplanned Outage) [WEBSMS] | CLUZ
8/30/2024 2:20:54 PM | Luzon Grid-08/30/2024 14:20: Naga-Tiwi C 230kV Line 2 autotripped/auto-reclosed at 1414H (Unplanned Outage) [WEBSMS] | CLUZ
8/30/2024 12:46:21 PM | [NSO Update] Luzon Grid-08/30/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15568MW, PK=12085MW, RR=429MW, NetOpMargin: PM=3054, EVE=2767 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @305MW, Masinloc 2 @300MW, SLTEC 2 @119MW [WEBSMS] | CLUZ
8/30/2024 12:36:23 PM | [NSO Update] Mindanao Grid-08/30/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3388MW, PK=2350MW, RR=73MW, NetOpMargin: PM=965, EVE=1080 Highest Unit O/L: GNPK 1@ 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
8/30/2024 12:33:20 PM | [NSO Update] Visayas Grid-08/30/2024 12:33: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2832MW, PK=2394MW, RR=31MW, NetOpMargin: PM=407, EVE=409 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @245MW, CEDC U3 @75MW, PDPP3-H @8MW, PDPP3-E @8MW, GTEC @10MW, PDPP3-G @10MW, PDPP1-2 @4.3MW, PB101-2 @5.5MW, PB104-3 @6MW, PDPP1-5 @4.3MW [WEBSMS] | CVIS
8/30/2024 12:12:16 PM | [NSO Update] Luzon Grid-08/30/2024 12:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0955H with power going to Luzon [WEBSMS] | CLUZ
8/30/2024 11:22:49 AM | Mindanao Grid-08/30/2024 11:30: Sultan Kudarat SS 100MVA Transformer No. 3 energized at 1120H. (Planned Outage) [WEBSMS] | CMIN
8/30/2024 10:41:55 AM | Mindanao Grid-08/30/2024 10:49: WMPC DG10 online at 1037H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/30/2024 9:56:23 AM | [NSO Update] Visayas Grid-08/30/2024 09:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0955H with power going to Luzon [WEBSMS] | CVIS
8/30/2024 9:47:25 AM | [NSO Update] Visayas Grid-08/30/2024 09:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0945H from reverse power direction [WEBSMS] | CVIS
8/30/2024 9:46:38 AM | [NSO Update] Luzon Grid-08/30/2024 09:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0945H from reverse power direction [WEBSMS] | CLUZ
8/30/2024 9:03:06 AM | [NSO Update] Visayas Grid-08/30/2024 09:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0855H with power going to Visayas [WEBSMS] | CVIS
8/30/2024 9:02:20 AM | [NSO Update] Luzon Grid-08/30/2024 09:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0855H with power going to Visayas [WEBSMS] | CLUZ
8/30/2024 8:48:04 AM | [NSO Update] Luzon Grid-08/30/2024 08:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0845H from forward power direction [WEBSMS] | CLUZ
8/30/2024 8:47:32 AM | [NSO Update] Visayas Grid-08/30/2024 08:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0845H from forward power direction [WEBSMS] | CVIS
8/30/2024 8:20:05 AM | Visayas Grid-08/30/2024 08:20: Calongcalong SS 138kV Bus 2 de-energized at 0817H. (Planned Outage) [WEBSMS] | CVIS
8/30/2024 5:42:29 AM | Visayas Grid-08/30/2024 05:42: PGPP2 SOG U1 emergency shutdown at 0004H due to heavy steam leak at gland sealing supply header. (Unplanned Outage) [WEBSMS] | CVIS
8/30/2024 5:34:49 AM | [NSO Update] Luzon Grid-08/30/2024 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15652MW, PK=11469MW, RR=422MW, NetOpMargin: AM=3761, PM=2566, EVE=2507 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @305MW, Masinloc 2 @300MW, SLTEC 2 @119MW [WEBSMS] | CLUZ
8/30/2024 5:34:30 AM | [NSO Update] Visayas Grid-08/30/2024 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2867MW, PK=2362MW, RR=31MW, NetOpMargin: AM=475, PM=378, EVE=386 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @245MW, CEDC U3 @75MW, PDPP3-H @8MW, PDPP3-C @10MW, GTEC @10MW, PDPP3-G @10MW, PDPP1-2 @4.3MW, PB101-2 @5.5MW, PB104-3 @6MW, PDPP1-5 @4.3MW [WEBSMS] | CVIS
8/30/2024 5:34:26 AM | [NSO Update] Mindanao Grid-08/30/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3400MW, PK=2293MW, RR=73MW, NetOpMargin: AM=1034, PM=859, EVE=1007 Highest Unit O/L: GNPK 1@ 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @23.5MW [WEBSMS] | CMIN
8/30/2024 4:41:39 AM | Mindanao Grid-08/30/2024 04:48: Baloi-IDPP (Mapalad) 138kV Line restored/energized at 0438H. Unplanned Outage. [WEBSMS] | CMIN
8/30/2024 4:32:04 AM | Mindanao Grid-08/30/2024 04:39: Baloi-IDPP (Mapalad) 138kV Line auto-tripped at 0420H. Unplanned Outage. [WEBSMS] | CMIN
8/30/2024 4:18:35 AM | [NSO Update] Luzon Grid-08/30/2024 04:18: Weather Advisory: Southwest Monsoon affecting the western sections of Luzon and Visayas. [WEBSMS] | CLUZ
8/30/2024 4:18:16 AM | [NSO Update] Visayas Grid-08/30/2024 04:18: Weather Advisory: Southwest Monsoon affecting the western sections of Luzon and Visayas. [WEBSMS] | CVIS
8/30/2024 4:18:09 AM | [NSO Update] Mindanao Grid-08/30/2024 04:25: Weather Advisory: Southwest Monsoon affecting the western sections of Luzon and Visayas. [WEBSMS] | CMIN
8/29/2024 11:53:24 PM | Luzon Grid-08/29/2024 23:53: Balsik-San Marcelino 230kV Line 2 restored at 2352H (Planned Outage) [WEBSMS] | CLUZ
8/29/2024 10:44:18 PM | Luzon Grid-08/29/2024 22:44: San Jose PCB 8-05CB08SJO de-energized at 2243H (Unplanned Outage) [WEBSMS] | CLUZ
8/29/2024 10:00:18 PM | Luzon Grid-08/29/2024 22:00: Balsik-San Marcelino 230kV Line 2 de-energized at 2159H (Planned Outage) [WEBSMS] | CLUZ
8/29/2024 9:22:28 PM | Luzon Grid-08/29/2024 21:22: Balsik-San Marcelino 230kV Line 1 restored at 2122H (Planned Outage) [WEBSMS] | CLUZ
8/29/2024 6:57:04 PM | Luzon Grid-08/29/2024 18:57: Dasmarinas - Rosario 115kV line restored at 1856H (Unplanned Outage) [WEBSMS] | CLUZ
8/29/2024 6:35:51 PM | Luzon Grid-08/29/2024 18:35: Balsik-San Marcelino 230kV Line 1 de-energized at 1835H (Planned Outage) [WEBSMS] | CLUZ
8/29/2024 6:04:56 PM | Luzon Grid-08/29/2024 18:04: Pagbilao EHV SS 1000MVA T03 restored at 1804H (Planned Outage) [WEBSMS] | CLUZ
8/29/2024 5:54:27 PM | Visayas Grid-08/29/2024 17:54: Calongcalong 138 kV Bus 1 energized at 1753H (Planned Outage) [WEBSMS] | CVIS
8/29/2024 5:53:20 PM | Visayas Grid-08/29/2024 17:53: Calongcalong 138 kV Bus 1 energized ae 1753H (Planned Outage) [WEBSMS] | CVIS
8/29/2024 5:40:00 PM | [NSO Update] Mindanao Grid-08/29/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3264MW, PK=2174MW, RR=73MW, NetOpMargin: EVE=1017 Highest Unit O/L: GNPK 2&4 @151MW Derated Plant: GNPK U1 @68MW, MPC @40MW, MA1 @48.9MW, MA2 @21.5MW [WEBSMS] | CMIN
8/29/2024 5:39:03 PM | Mindanao Grid-08/29/2024 17:46: WMPC DG10 shutdown at 1736H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/29/2024 5:38:24 PM | [NSO Update] Visayas Grid-08/29/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2718MW, PK=2265MW, RR=31MW, NetOpMargin: EVE=422 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @240MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3-C @10MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-2 @5.5MW, PB104-3 @6MW, PDPP1-5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/29/2024 5:35:30 PM | [NSO Update] Luzon Grid-08/29/2024 17:35: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14376MW, PK=11108MW, RR=431MW, NetOpMargin: EVE=2837 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @300MW, Masinloc 2 @300MW, Masinloc 3 @320MW, SLTEC 2 @117MW [WEBSMS] | CLUZ
8/29/2024 2:19:53 PM | Luzon Grid-08/29/2024 14:19: Dasmarinas - Rosario 115kV line tripped at 1417H (Unplanned Outage) [WEBSMS] | CLUZ
8/29/2024 12:45:08 PM | [NSO Update] Mindanao Grid-08/29/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3296MW, PK=2349MW, RR=73MW, NetOpMargin: PM=874, EVE=950 Highest Unit O/L: GNPK 2&4 @151MW Derated Plant: GNPK U1 @68MW, MPC @40MW, MA1 @48.9MW, MA2 @21.5MW [WEBSMS] | CMIN
8/29/2024 12:42:16 PM | [NSO Update] Visayas Grid-08/29/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2813MW, PK=2386MW, RR=31MW, NetOpMargin: PM=396, EVE=400 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @240MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3-C @10MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-2 @5.5MW, PB104-3 @6MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/29/2024 12:40:29 PM | [NSO Update] Luzon Grid-08/29/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15368MW, PK=11863MW, RR=461MW, NetOpMargin: PM=3043, EVE=2681 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @295MW, Masinloc 2 @300MW, Masinloc 3 @320MW, SLTEC 2 @120MW [WEBSMS] | CLUZ
8/29/2024 11:54:35 AM | Mindanao Grid-08/29/2024 12:01: WMPC DG01 shutdown at 1146H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/29/2024 11:10:58 AM | Mindanao Grid-08/29/2024 11:18: Agus5-Aurora 138kV Line energized/restored at 1108H. Planned Outage. [WEBSMS] | CMIN
8/29/2024 9:02:29 AM | Visayas Grid-08/29/2024 09:02: Calongcalong 138 kV Bus 1 de-energized ae 0901H (Planned Outage) [WEBSMS] | CVIS
8/29/2024 8:11:17 AM | Mindanao Grid-08/29/2024 08:18: WMPC DG01 online at 0808H. RPS - System Voltage requirement. [WEBSMS] | CMIN
8/29/2024 8:10:31 AM | Mindanao Grid-08/29/2024 08:17: WMPC DG10 online at 0807H. RPS - System Voltage requirement. [WEBSMS] | CMIN
8/29/2024 7:57:56 AM | Mindanao Grid-08/29/2024 08:05: Agus5-Aurora 138kV Line de-energized at 0754H. Planned Outage. [WEBSMS] | CMIN
8/29/2024 6:08:00 AM | Luzon Grid-08/29/2024 06:08: San Manuel 230kV Bus 2 de-energized at 0604H (Planned Outage) [WEBSMS] | CLUZ
8/29/2024 5:50:15 AM | [NSO Update] Luzon Grid-08/29/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15429MW, PK=11152MW, RR=432MW, NetOpMargin: AM=3845, PM=3269, EVE=3077 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @295MW, Masinloc 2 @300MW, SLTEC @98MW [WEBSMS] | CLUZ
8/29/2024 5:36:32 AM | [NSO Update] Visayas Grid-08/29/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2878MW, PK=2325MW, RR=31MW, NetOpMargin: AM=522, PM=377, EVE=473 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @245MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3-C @10MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-2 @5.5MW, PB104-3 @6MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/29/2024 5:36:26 AM | [NSO Update] Mindanao Grid-08/29/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3396MW, PK=2357MW, RR=73MW, NetOpMargin: AM=967, PM=806, EVE=934 Highest Unit O/L: GNPK 1@ 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @21.5MW [WEBSMS] | CMIN
8/29/2024 3:59:51 AM | [NSO Update] Mindanao Grid-08/29/2024 04:07: Weather Advisory: Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CMIN
8/29/2024 3:59:47 AM | [NSO Update] Visayas Grid-08/29/2024 04:00: Weather Advisory: Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CVIS
8/29/2024 3:59:45 AM | [NSO Update] Luzon Grid-08/29/2024 04:00: Weather Advisory: Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CLUZ
8/28/2024 9:43:53 PM | Visayas Grid-08/28/2024 21:44: Cebu SS 69KV Veco line 3 auto-tripped at 2136H. (Unplanned Outage) [WEBSMS] | CVIS
8/28/2024 9:22:55 PM | Mindanao Grid-08/28/2024 21:30: WMPC DG10 shutdown at 2116H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/28/2024 7:14:18 PM | [NSO Update] Visayas Grid-08/28/2024 19:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1913H with power going to Luzon. [WEBSMS] | CVIS
8/28/2024 7:14:15 PM | [NSO Update] Luzon Grid-08/28/2024 19:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1913H with power going to Luzon. [WEBSMS] | CLUZ
8/28/2024 7:04:41 PM | [NSO Update] Visayas Grid-08/28/2024 19:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1903H from reverse power direction. [WEBSMS] | CVIS
8/28/2024 7:04:38 PM | [NSO Update] Luzon Grid-08/28/2024 19:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1903H from reverse power direction. [WEBSMS] | CLUZ
8/28/2024 5:42:56 PM | [NSO Update] Luzon Grid-08/28/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14218MW, PK=10251MW, RR=398MW, NetOpMargin: EVE=3569 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @305MW, Masinloc 2 @300MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
8/28/2024 5:33:15 PM | Mindanao Grid-08/28/2024 17:40: Baloi - Lugait 138kV Line energized/restored at 1732H. (Unplanned Outage) [WEBSMS] | CMIN
8/28/2024 5:24:58 PM | [NSO Update] Mindanao Grid-08/28/2024 17:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3346MW, PK=2291MW, RR=73MW, NetOpMargin: EVE=982 Highest Unit O/L: GNPK 1@ 151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @21.5MW [WEBSMS] | CMIN
8/28/2024 5:24:44 PM | [NSO Update] Visayas Grid-08/28/2024 17:25: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2762MW, PK=2258MW, RR=31MW, NetOpMargin: EVE=473 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @240MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3-C @10MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-2 @5.5MW, PB104-3 @6MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/28/2024 5:04:38 PM | Mindanao Grid-08/28/2024 17:12: WMPC DG1 shutdown at 1701H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/28/2024 4:57:33 PM | Mindanao Grid-08/28/2024 17:04: Agus6 SS 138/69kV 100MVA Power Transformer 1 energized/looped at 1648H. (Planned Outage) [WEBSMS] | CMIN
8/28/2024 3:16:47 PM | Mindanao Grid-08/28/2024 15:24: Baloi - Lugait 138kV Line de-energized at 1514H. (Unplanned Outage) [WEBSMS] | CMIN
8/28/2024 2:57:56 PM | Visayas Grid-08/28/2024 14:58: Toledo SS 138 kV Bus 2 energized at 1457H (Planned Outage) [WEBSMS] | CVIS
8/28/2024 1:25:29 PM | Mindanao Grid-08/28/2024 13:32: WMPC dg1 online at 1322H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/28/2024 12:37:19 PM | [NSO Update] Luzon Grid-08/28/2024 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14978MW, PK=11355MW, RR=429MW, NetOpMargin: PM=3194, EVE=2798 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @240MW, Masinloc 2 @300MW, Masinloc 3 @310MW [WEBSMS] | CLUZ
8/28/2024 12:35:29 PM | [NSO Update] Visayas Grid-08/28/2024 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2721MW, PK=2354MW, RR=31MW, NetOpMargin: PM=335, EVE=448 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @230MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3-C @10MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-2 @5.5MW, PB104-3 @6MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/28/2024 12:30:48 PM | [NSO Update] Mindanao Grid-08/28/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3391MW, PK=2410MW, RR=73MW, NetOpMargin: PM=908, EVE=951 Highest Unit O/L: GNPK 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @21.5MW [WEBSMS] | CMIN
8/28/2024 11:07:02 AM | Luzon Grid-08/28/2024 11:07: Correction: SLTEC 2 online at 1000H (Unplanned Outage) [WEBSMS] | CLUZ
8/28/2024 10:22:30 AM | [NSO Update] Visayas Grid-08/28/2024 10:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1020H with power going to Visayas. [WEBSMS] | CVIS
8/28/2024 10:21:48 AM | [NSO Update] Luzon Grid-08/28/2024 10:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1020H with power going to Visayas. [WEBSMS] | CLUZ
8/28/2024 10:09:38 AM | Luzon Grid-08/28/2024 10:09: SLTEC 2 online at 1000H (Planned Outage) [WEBSMS] | CLUZ
8/28/2024 10:06:39 AM | [NSO Update] Luzon Grid-08/28/2024 10:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1003H from forward power direction. [WEBSMS] | CLUZ
8/28/2024 10:06:20 AM | [NSO Update] Visayas Grid-08/28/2024 10:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1003H from forward power direction. [WEBSMS] | CVIS
8/28/2024 9:32:20 AM | Mindanao Grid-08/28/2024 09:39: WMPC DG10 online at 0930H. RPS - System Voltage requirement. [WEBSMS] | CMIN
8/28/2024 8:38:00 AM | Mindanao Grid-08/28/2024 08:45: Kauswagan - GNPK 230kV Line3 shutdown at 0806H. (Planned Outage) [WEBSMS] | CMIN
8/28/2024 8:23:03 AM | Visayas Grid-08/28/2024 08:23: Toledo SS 138 kV Bus 2 de-energized at 0822H (Planned Outage) [WEBSMS] | CVIS
8/28/2024 5:42:37 AM | [NSO Update] Mindanao Grid-08/28/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3400MW, PK=2317MW, RR=73MW, NetOpMargin: AM=1010, PM=807, EVE=930 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @21.5MW [WEBSMS] | CMIN
8/28/2024 5:41:19 AM | [NSO Update] Visayas Grid-08/28/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2932MW, PK=2374MW, RR=31MW, NetOpMargin: AM=526, PM=499, EVE=383 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @232MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3-C @10MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-2 @5.5MW, PB104-3 @6MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/28/2024 5:40:21 AM | [NSO Update] Luzon Grid-08/28/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15377MW, PK=11379MW, RR=422MW, NetOpMargin: AM=3577, PM=2471, EVE=2637 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @315MW, Masinloc 2 @300MW, Masinloc 3 @315MW, SLPGC 2 @145MW [WEBSMS] | CLUZ
8/28/2024 4:25:05 AM | [NSO Update] Luzon Grid-08/28/2024 04:25: Weather Advisory: Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CLUZ
8/28/2024 4:24:06 AM | [NSO Update] Mindanao Grid-08/28/2024 04:31: Weather Advisory: Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CMIN
8/28/2024 4:23:45 AM | [NSO Update] Visayas Grid-08/28/2024 04:24: Weather Advisory: Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CVIS
8/28/2024 12:07:35 AM | Mindanao Grid-08/28/2024 00:15: GNPK Unit 3 shutdown at 0004H for PMS (GOMP). [WEBSMS] | CMIN
8/28/2024 12:00:52 AM | Mindanao Grid-08/28/2024 00:08: JASAAN BESS online at 2359H from PMS(Non-GOMP). [WEBSMS] | CMIN
8/27/2024 10:42:31 PM | Luzon Grid-08/27/2024 22:42: MPGC4 at 57MW tripped at 2237H. On Commissioning Test (Unplanned Outage) [WEBSMS] | CLUZ
8/27/2024 9:33:58 PM | Mindanao Grid-08/27/2024 21:41: WMPC DG10 shutdown at 2122H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/27/2024 9:18:13 PM | Luzon Grid-08/27/2024 21:18: Nagsaag-Casecnan 230kV Line 2 restored at 2116H (Unplanned Outage) [WEBSMS] | CLUZ
8/27/2024 8:33:58 PM | Luzon Grid-08/27/2024 20:34: Tayabas-Naga 230kV Line 2 tripped/reclosed both side at 2030H. (Unplanned Outage) [WEBSMS] | CLUZ
8/27/2024 7:40:49 PM | Luzon Grid-08/27/2024 19:41: Nagsaag-Casecnan 230kV Line 2 tripped at 1938H. Reclosed at Nagsaag side. (Unplanned Outage) [WEBSMS] | CLUZ
8/27/2024 5:57:02 PM | Luzon Grid-08/27/2024 17:57: Pagbilao EHV 500kV Bus 1 restored at 1757H (Unplanned Outage) [WEBSMS] | CLUZ
8/27/2024 5:45:06 PM | [NSO Update] Mindanao Grid-08/27/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3468MW, PK=2280MW, RR=73MW, NetOpMargin: EVE=1115 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW, MA2 @26.5MW [WEBSMS] | CMIN
8/27/2024 5:44:17 PM | [NSO Update] Visayas Grid-08/27/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2738MW, PK=2217MW, RR=31MW, NetOpMargin: EVE=489 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @238MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3-C @10MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-2 @5.5MW, PB104-3 @6MW, PDPP1-2 @4.3MW, PDPP1-5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/27/2024 5:41:16 PM | [NSO Update] Luzon Grid-08/27/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14295MW, PK=11003MW, RR=357MW, NetOpMargin: EVE=2935 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @310MW, Masinloc 2 @300MW, Masinloc 3 @315MW [WEBSMS] | CLUZ
8/27/2024 4:48:05 PM | Luzon Grid-08/27/2024 16:48: Pagbilao EHV 500kV Bus 1 de-energized at 1646H (Unplanned Outage) [WEBSMS] | CLUZ
8/27/2024 3:27:06 PM | Visayas Grid-08/27/2024 15:27: PEDC unit No. 2 cut-in at 1518H. (Unplanned Outage) [WEBSMS] | CVIS
8/27/2024 12:38:39 PM | [NSO Update] Luzon Grid-08/27/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15099MW, PK=11868MW, RR=389MW, NetOpMargin: PM=2843, EVE=2845 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @305MW, Masinloc 2 @300MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
8/27/2024 12:31:00 PM | [NSO Update] Mindanao Grid-08/27/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3510MW, PK=2497MW, RR=73MW, NetOpMargin: PM=940, EVE=1038 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW, MA2 @26.5MW [WEBSMS] | CMIN
8/27/2024 12:29:49 PM | [NSO Update] Visayas Grid-08/27/2024 12:30: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2773MW, PK=2330MW, RR=31MW, NetOpMargin: PM=412, EVE=370 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @235MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3-C @10MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-2 @5.5MW, PB104-3 @6MW, PDPP1-2 @3.5MW, PDPP1-5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/27/2024 10:37:01 AM | Mindanao Grid-08/27/2024 10:44: WMPC DG10 online at 0951H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/27/2024 8:14:57 AM | Mindanao Grid-08/27/2024 08:22: Agus 6 SS Transformer No. 1 de-energized at 0807H. Planned Outage (GOMP) [WEBSMS] | CMIN
8/27/2024 7:52:26 AM | Mindanao Grid-08/27/2024 07:59: Lake Mainit HEP shutdown at 0701H. PMS(NON-GOMP) [WEBSMS] | CMIN
8/27/2024 6:13:13 AM | Mindanao Grid-08/27/2024 06:20: JASAAN BESS shutdown at 0603H (Non-GOMP) [WEBSMS] | CMIN
8/27/2024 5:46:49 AM | [NSO Update] Mindanao Grid-08/27/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3520MW, PK=2420MW, RR=73MW, NetOpMargin: AM=1027, PM=932, EVE=1000 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @26.5MW [WEBSMS] | CMIN
8/27/2024 5:45:43 AM | [NSO Update] Visayas Grid-08/27/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2796MW, PK=2220MW, RR=31MW, NetOpMargin: AM=546, PM=350, EVE=350 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @238MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3-C @10MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-2 @5.5MW, PB104-3 @6MW, PDPP1-2 @3.5MW, PDPP1-5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/27/2024 5:44:15 AM | [NSO Update] Luzon Grid-08/27/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15343MW, PK=11089MW, RR=422MW, NetOpMargin: AM=3832, PM=1999, EVE=2443 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @305MW, Masinloc 2 @300MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
8/27/2024 4:23:30 AM | [NSO Update] Mindanao Grid-08/27/2024 04:30: Weather Update: Southwest Monsoon affecting Southern Luzon and Visayas. [WEBSMS] | CMIN
8/27/2024 4:23:18 AM | [NSO Update] Visayas Grid-08/27/2024 04:23: Weather Update: Southwest Monsoon affecting Southern Luzon and Visayas. [WEBSMS] | CVIS
8/27/2024 4:23:04 AM | [NSO Update] Luzon Grid-08/27/2024 04:23: Weather Update: Southwest Monsoon affecting Southern Luzon and Visayas. [WEBSMS] | CLUZ
8/27/2024 1:22:55 AM | Visayas Grid-08/27/2024 01:23: PEDC U2 emergency shutdown at 0121H (Unplanned Outage) [WEBSMS] | CVIS
8/26/2024 9:05:55 PM | Luzon Grid-08/26/2024 21:06: San Lorenzo 60 online at 2104H (Unplanned Outage) [WEBSMS] | CLUZ
8/26/2024 8:59:36 PM | Luzon Grid-08/26/2024 20:59: Salong-SLTEC 230kV Lines 1 & 2 restored at 2056H and 2059H, respectively (Planned Outage) [WEBSMS] | CLUZ
8/26/2024 6:38:14 PM | Luzon Grid-08/26/2024 18:38: San Jose-Tayabas 500 kV Line 1 restored at 1838H (Unplanned Outage) [WEBSMS] | CLUZ
8/26/2024 5:46:22 PM | [NSO Update] Mindanao Grid-08/26/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3475MW, PK=2155MW, RR=73MW, NetOpMargin: EVE=1247 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @26.5MW, MA2 @47.5MW [WEBSMS] | CMIN
8/26/2024 5:45:43 PM | [NSO Update] Visayas Grid-08/26/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2727MW, PK=2076MW, RR=31MW, NetOpMargin: EVE=620 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @235MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP C @10MW, PDPP3 E @8MW, PDPP3 G @10MW, PDPP3 H @8MW, PB101 U2 @5.5MW, PB104 U3 @6MW, PDPP1 U2 @3.5MW, PDPP1 U5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/26/2024 5:44:09 PM | [NSO Update] Luzon Grid-08/26/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13504MW, PK=9880MW, RR=397MW, NetOpMargin: EVE=3227 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @305MW, Masinloc 2 @300MW, Masinloc 3 @315MW [WEBSMS] | CLUZ
8/26/2024 4:50:17 PM | Mindanao Grid-08/26/2024 16:57: Tagoloan - Villanueva 138kV L1 energized/restored at 1649H. (Planned Outage) [WEBSMS] | CMIN
8/26/2024 3:57:17 PM | Visayas Grid-08/26/2024 15:57: Babatngon-Paranas 138kV Line 1 energized at 1552H. (Planned Outage) [WEBSMS] | CVIS
8/26/2024 3:45:06 PM | Luzon Grid-08/26/2024 15:45: San Jose-Tayabas 500 kV line 1 de-energized at 1544H (Unplanned Outage) [WEBSMS] | CLUZ
8/26/2024 3:20:00 PM | Luzon Grid-08/26/2024 15:20: Manila-Muntinlupa 230kV Line restored at 1520H (Planned Outage) [WEBSMS] | CLUZ
8/26/2024 2:39:15 PM | Luzon Grid-08/26/2024 14:39: Tayabas 230kV Bus 1 restored at 1439H (Planned Outage) [WEBSMS] | CLUZ
8/26/2024 12:42:09 PM | [NSO Update] Mindanao Grid-08/26/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3516MW, PK=2146MW, RR=73MW, NetOpMargin: PM=1297, EVE=1239 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @26.5MW, MA2 @47.5MW [WEBSMS] | CMIN
8/26/2024 12:42:02 PM | [NSO Update] Visayas Grid-08/26/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2986MW, PK=2050MW, RR=31MW, NetOpMargin: PM=905, EVE=619 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @270MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3 E @8MW, PDPP3 G @10MW, PDPP3 H @8MW, PB101 U2 @5.5MW, PB104 U3 @6MW, PDPP1 U2 @3.5MW, PDPP1 U5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/26/2024 12:41:58 PM | [NSO Update] Luzon Grid-08/26/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14734MW, PK=10246MW, RR=429MW, NetOpMargin: PM=4059, EVE=3274 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @305MW, Masinloc 2 @280MW, Masinloc 3 @315MW [WEBSMS] | CLUZ
8/26/2024 11:51:10 AM | Luzon Grid-08/26/2024 11:51: Botolan-Subic 230kV Line autotripped at 1143H and auto-reclosed at Subic side. The line was looped and restored at 1146H. (Unplanned Outage) [WEBSMS] | CLUZ
8/26/2024 11:44:59 AM | Visayas Grid-08/26/2024 11:45: Lapulapu-Pajo 69 kV Line de-energized/energized at 0808H/1141H (Planned Outage) [WEBSMS] | CVIS
8/26/2024 6:54:40 AM | Luzon Grid-08/26/2024 06:54: Dasmarinas-Amadeo 230kV Line 1 and Calaca-Amadeo 230kV Line 2 restored at 0652H (Planned Outage) [WEBSMS] | CLUZ
8/26/2024 6:47:12 AM | Luzon Grid-08/26/2024 06:47: Manila-Muntinlupa 230kV Line de-energized at 0646H (Planned Outage) [WEBSMS] | CLUZ
8/26/2024 5:51:52 AM | [NSO Update] Mindanao Grid-08/26/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3528MW, PK=2088MW, RR=73MW, NetOpMargin: AM=1367, PM=1325, EVE=1331 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @26.5MW [WEBSMS] | CMIN
8/26/2024 5:50:10 AM | [NSO Update] Visayas Grid-08/26/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2501MW, PK=1914MW, RR=31MW, NetOpMargin: AM=556, PM=563, EVE=494 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @270MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3 C @10MW, PDPP3 E @8MW, PDPP3 G @10MW, PDPP3 H @8MW, PB101 U2 @5.5MW, PB104 U3 @6MW, PDPP1 U2 @3.5MW, PDPP1 U3 @4.5MW, PDPP1 U5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/26/2024 5:48:57 AM | [NSO Update] Luzon Grid-08/26/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14783MW, PK=9173MW, RR=408MW, NetOpMargin: AM=5203, PM=4796, EVE=3709 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @305MW, Masinloc 2 @280MW, Masinloc 3 @315MW, Calaca 2 @290MW [WEBSMS] | CLUZ
8/26/2024 5:14:51 AM | Mindanao Grid-08/26/2024 05:22: Tagoloan - Villanueva 138kV L1 (7LI1TAG-VLN) de-energized at 0504H. Planned Outage /Non-GOMP. [WEBSMS] | CMIN
8/26/2024 4:41:54 AM | Luzon Grid-08/26/2024 04:42: San Lorenzo 60 shutdown at 0440H (Unplanned Outage) [WEBSMS] | CLUZ
8/26/2024 4:15:48 AM | [NSO Update] Luzon Grid-08/26/2024 04:15: Weather Advisory: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/26/2024 4:15:04 AM | [NSO Update] Mindanao Grid-08/26/2024 04:22: Weather Advisory: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/26/2024 4:14:42 AM | [NSO Update] Visayas Grid-08/26/2024 04:14: Weather Advisory: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/26/2024 2:50:12 AM | Luzon Grid-08/26/2024 02:50: San Lorenzo 60 online at 0247H (Planned Outage) [WEBSMS] | CLUZ
8/26/2024 2:10:53 AM | Visayas Grid-08/26/2024 02:11: Isabel - Philphos 138 kV Line 1 energized at 0210H (Unplanned Outage) [WEBSMS] | CVIS
8/26/2024 2:03:12 AM | Visayas Grid-08/26/2024 02:03: PCPC cut-in at 0202H (Unplanned Outage) [WEBSMS] | CVIS
8/26/2024 1:46:02 AM | Luzon Grid-08/26/2024 01:46: Quezon-Mexico 230kV line restored at 0143H (Unplanned Outage) [WEBSMS] | CLUZ
8/26/2024 1:39:45 AM | Luzon Grid-08/26/2024 01:39: San Gabriel on reserve shutdown at 0138H (Unplanned Outage) [WEBSMS] | CLUZ
8/26/2024 1:35:35 AM | Luzon Grid-08/26/2024 01:35: Quezon-Mexico 230kV Line tripped again at 0133H (Unplanned Outage) [WEBSMS] | CLUZ
8/26/2024 1:33:30 AM | Luzon Grid-08/26/2024 01:33: Quezon-Mexico 230kV Line restored at 0132H (Unplanned Outage) [WEBSMS] | CLUZ
8/26/2024 1:28:53 AM | Luzon Grid-08/26/2024 01:29: Quezon-Mexico 230kV L tripped at 0122H (Unplanned Outage) [WEBSMS] | CLUZ
8/26/2024 12:43:22 AM | Luzon Grid-08/26/2024 00:43: Dasmarinas-Amadeo 230kV Line 1 de-energized at 0041H (Planned Outage) [WEBSMS] | CLUZ
8/26/2024 12:41:27 AM | Luzon Grid-08/26/2024 00:41: Calaca-Amadeo 230kV Line 2 de-energized at 0040H (Planned Outage) [WEBSMS] | CLUZ
8/26/2024 12:33:20 AM | Luzon Grid-08/26/2024 00:33: Tayabas 230kV Bus 1 de-energized at 0032H (Planned Outage) [WEBSMS] | CLUZ
8/26/2024 12:15:20 AM | Mindanao Grid-08/26/2024 00:22: FDC Unit 1 shutdown at 0011H (Planned Outage) [WEBSMS] | CMIN
8/25/2024 10:57:31 PM | Visayas Grid-08/25/2024 22:57: Isabel - Philphos 138 kV Line 1 tripped at 2252H (Unplanned Outage) [WEBSMS] | CVIS
8/25/2024 9:19:17 PM | Luzon Grid-08/25/2024 21:19: San Manuel-UPSI San Manuel BESS 69kV Line (CO) restored at 2115H (Planned Outage) [WEBSMS] | CLUZ
8/25/2024 7:30:34 PM | Visayas Grid-08/25/2024 19:30: Colon - Naga 138 kV Line 1 energized at 1928H. (Planned Outage) [WEBSMS] | CVIS
8/25/2024 6:35:15 PM | Mindanao Grid-08/25/2024 18:42: LAMSAN BIOMASS online at 1826H (Unplanned Outage, outside management control) [WEBSMS] | CMIN
8/25/2024 5:45:55 PM | Mindanao Grid-08/25/2024 17:53: Marawi SS 50MVA 138/69kV (7XF01MRW) energized at 1727H. Planned Outage /Non-GOMP [WEBSMS] | CMIN
8/25/2024 5:41:25 PM | [NSO Update] Mindanao Grid-08/25/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3576MW, PK=2082MW, RR=73MW, NetOpMargin: EVE=1422 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @26.5MW [WEBSMS] | CMIN
8/25/2024 5:39:47 PM | [NSO Update] Visayas Grid-08/25/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2630MW, PK=2046MW, RR=31MW, NetOpMargin: EVE=552 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @270MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3 C @10MW, PDPP3 G @10MW, PDPP3 E @8MW, PDPP3 H @8MW, PB101 U2 @5.5MW, PB104 U2 @5MW, PB104 U3 @6MW, PDPP1 U2 @3.5MW, PDPP1 U5 @4.3MW, GTEC @10MW, PDPP1 U3 @4.5MW [WEBSMS] | CVIS
8/25/2024 5:38:48 PM | [NSO Update] Luzon Grid-08/25/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13602MW, PK=10023MW, RR=260MW, NetOpMargin: EVE=3318 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @305MW, Masinloc 2 @280MW, Masinloc 3 @315MW, GNPD 1 @370MW, Calaca 2 @270MW, SLPGC 2 @75MW [WEBSMS] | CLUZ
8/25/2024 5:04:10 PM | Luzon Grid-08/25/2024 17:04: San Gabriel online at 1700H (Reserve Shutdown) [WEBSMS] | CLUZ
8/25/2024 5:03:02 PM | Visayas Grid-08/25/2024 17:03: Colon SS 138 kV Bus 1 energized at 1700H. (Planned Outage) [WEBSMS] | CVIS
8/25/2024 5:01:22 PM | Mindanao Grid-08/25/2024 17:08: PULANGI 4 Unit 1 online at 1700H (Unplanned Outage) [WEBSMS] | CMIN
8/25/2024 4:56:27 PM | Mindanao Grid-08/25/2024 17:03: JASAAN BESS online at 1653H (Maintenance Outage) [WEBSMS] | CMIN
8/25/2024 4:38:03 PM | Mindanao Grid-08/25/2024 16:45: PULANGI 4 Unit 1 failed to synchronize at 1609H due to excitation failure (Unplanned Outage) [WEBSMS] | CMIN
8/25/2024 4:31:35 PM | Luzon Grid-08/25/2024 16:31: San Jose-Hermosa 230kV Line restored at 1631H (Planned Outage) [WEBSMS] | CLUZ
8/25/2024 4:26:03 PM | Mindanao Grid-08/25/2024 16:33: PULANGI 4 Unit 2 online at 1623H (Planned Outage) [WEBSMS] | CMIN
8/25/2024 4:16:52 PM | Mindanao Grid-08/25/2024 16:24: Maramag - Kibawe 138kV Line 1 (7LI1MRM-KIB) energized at 1605H . Planned Outage [WEBSMS] | CMIN
8/25/2024 4:15:33 PM | Mindanao Grid-08/25/2024 16:22: Maramag - Kibawe 138kV Line 2 (7LI2MRM-KIB) energized at 1607H . Planned Outage. [WEBSMS] | CMIN
8/25/2024 4:13:53 PM | Mindanao Grid-08/25/2024 16:21: Maramag - Kibawe 138kV Line 2 (7LI2MRM-KIB) energized at 1605H . Planned Outage. [WEBSMS] | CMIN
8/25/2024 4:03:55 PM | Visayas Grid-08/25/2024 16:04: PCPC cut-out at 1559H to facilitate placing turbine on turning gear operation due to high turbine bearing vibration. (Unplanned outage) [WEBSMS] | CVIS
8/25/2024 3:43:00 PM | Mindanao Grid-08/25/2024 15:50: Jasaan- UPSI- Jasaan BESS 69 kV Line energized at 1538H. Planned Outage [WEBSMS] | CMIN
8/25/2024 3:41:50 PM | Visayas Grid-08/25/2024 15:41: Panit-an - Nabas 138 kV Line 2 energized at 1539H. (Planned Outage) [WEBSMS] | CVIS
8/25/2024 3:28:00 PM | Visayas Grid-08/25/2024 15:28: Cebu SS 138 kV Bus 2 energized at 1527H. (Planned Outage) [WEBSMS] | CVIS
8/25/2024 3:22:52 PM | Luzon Grid-08/25/2024 15:22: Tayabas-San Jose 500kV Line 1 restored at 1522H (Unplanned Outage) [WEBSMS] | CLUZ
8/25/2024 3:21:47 PM | Visayas Grid-08/25/2024 15:21: Colon-Nay 69kV line restored at 1518H. (Unplanned Outage) [WEBSMS] | CVIS
8/25/2024 3:09:22 PM | Luzon Grid-08/25/2024 15:09: Tayabas-San Jose 500kV Line 1 tripped at 1507H (Unplanned Outage) [WEBSMS] | CLUZ
8/25/2024 2:53:05 PM | Visayas Grid-08/25/2024 14:53: Colon-Nay 69kV line tripped at 1448H. (Unplanned Outage) [WEBSMS] | CVIS
8/25/2024 2:47:38 PM | Luzon Grid-08/25/2024 14:47: Binga-La Trinidad 230kV Line 2 restored at 1445H (Planned Outage) [WEBSMS] | CLUZ
8/25/2024 2:28:05 PM | Mindanao Grid-08/25/2024 14:35: Bunawan-Nabunturan 138kV Line (7LI1BUN-NAB) energized/restored at 1425H. Planned Outage [WEBSMS] | CMIN
8/25/2024 1:46:54 PM | Mindanao Grid-08/25/2024 13:54: Sultan Kudarat SS 100 MVA Power Transformer No. 2 (7XF02SKU) energized /restored at 1335H. Planned Outage [WEBSMS] | CMIN
8/25/2024 1:44:59 PM | Mindanao Grid-08/25/2024 13:52: Kibawe - Sultan Kudarat 138kV Line (7LI1KIB-SKU) energized /restored at 1332H . Planned Outage. [WEBSMS] | CMIN
8/25/2024 1:14:37 PM | Visayas Grid-08/25/2024 13:14: Correction: Dumanjug - Samboan 138 kV Line 1 tripped/reclosed at Dumanjug SS at 1228H and looped at Samboan SS at 1241H. (Unplanned Outage) [WEBSMS] | CVIS
8/25/2024 1:02:02 PM | [NSO Update] Visayas Grid-08/25/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2854MW, PK=1980MW, RR=31MW, NetOpMargin: PM=843, EVE=502 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @261MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3 C @10MW, PDPP3 G @10MW, PDPP3 E @8MW, PDPP3 H @8MW, PB101 U2 @5.5MW, PB104 U2 @5MW, PB104 U3 @6MW, PDPP1 U2 @3.5MW, PDPP1 U5 @4.3MW, GTEC @10MW, PDPP1 U3 @4.5MW, PCPC @50MW [WEBSMS] | CVIS
8/25/2024 12:56:07 PM | [NSO Update] Luzon Grid-08/25/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14809MW, PK=9944MW, RR=260MW, NetOpMargin: PM=4605, EVE=3069 Highest Unit O/L: GNPD 2 @668MW Derated Plant: Masinloc 1 @305MW, Masinloc 2 @280MW, Masinloc 3 @320MW, GNPD 1 @370MW, Calaca 2 @270MW [WEBSMS] | CLUZ
8/25/2024 12:54:14 PM | [NSO Update] Mindanao Grid-08/25/2024 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3494MW, PK=1931MW, RR=73MW, NetOpMargin: PM=1490, EVE=1400 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @26.5MW, MA2 @47.5MW [WEBSMS] | CMIN
8/25/2024 12:48:32 PM | Visayas Grid-08/25/2024 12:48: Dumanjug - Samboan 138 kV Line 1 tripped/reclosed at Samboan SS at 1228H and looped at Dumanjug SS at 1241H. (Unplanned Outage) [WEBSMS] | CVIS
8/25/2024 12:26:04 PM | Visayas Grid-08/25/2024 12:26: Babatngon-Paranas 138 kV Line 2 and Sta. Rita SS 50 MVA 138/69/13.8 kV TR1 tripped at 1218H. (Unplanned Outage) [WEBSMS] | CVIS
8/25/2024 12:18:31 PM | Mindanao Grid-08/25/2024 12:25: LAKE MAINIT online at 1200H (Unplanned Outage) [WEBSMS] | CMIN
8/25/2024 10:19:54 AM | Mindanao Grid-08/25/2024 10:27: (Correction) MINERGY COAL Unit 2 online at 0843H (from Reserve Shutdown) [WEBSMS] | CMIN
8/25/2024 10:15:56 AM | Mindanao Grid-08/25/2024 10:23: Maramag - Kibawe 138kV Line 2 (7LI2MRM-KIB) de-energized at 1013H . Planned Outage. [WEBSMS] | CMIN
8/25/2024 10:13:27 AM | Mindanao Grid-08/25/2024 10:20: PULANGI 4 Unit 2 shutdown at 1012H (Planned Outage) [WEBSMS] | CMIN
8/25/2024 10:09:34 AM | Mindanao Grid-08/25/2024 10:16: PULANGI 4 Unit 1 shutdown at 1003H (Planned Outage) [WEBSMS] | CMIN
8/25/2024 10:09:30 AM | Mindanao Grid-08/25/2024 10:16: Maramag - Kibawe 138kV Line 1 (7LI1MRM-KIB) de-energized at 10107H . Planned Outage. [WEBSMS] | CMIN
8/25/2024 9:57:22 AM | Mindanao Grid-08/25/2024 10:04: MINERGY COAL online at 0843H (from Reserve Shutdown) [WEBSMS] | CMIN
8/25/2024 9:19:22 AM | Mindanao Grid-08/25/2024 09:26: Jasaan- UPSI- Jasaan BESS 69 kV Line de-energized at 0900H. Planned Outage [WEBSMS] | CMIN
8/25/2024 9:17:41 AM | Luzon Grid-08/25/2024 09:17: Pagbilao EHV SS 500kV Bus 1 restored at 0917H (Unplanned Outage) [WEBSMS] | CLUZ
8/25/2024 8:58:16 AM | Visayas Grid-08/25/2024 08:58: Colon - Naga 138 kV Line 1 de-energized at 0858H. (Planned Outage) [WEBSMS] | CVIS
8/25/2024 8:43:30 AM | Mindanao Grid-08/25/2024 08:50: Kibawe - Sultan Kudarat 138kV Line (7LI1KIB-SKU) de-energized at 0801H . Planned Outage. [WEBSMS] | CMIN
8/25/2024 8:42:00 AM | Mindanao Grid-08/25/2024 08:49: Sultan Kudarat SS 100 MVA Power Transformer No. 2 (7XF02SKU) de-energized at 0758H. Planned Outage [WEBSMS] | CMIN
8/25/2024 8:30:09 AM | Luzon Grid-08/25/2024 08:30: Pagbilao EHV SS 500kV Bus 1 emergency shutdown at 0829H (Unplanned Outage) [WEBSMS] | CLUZ
8/25/2024 8:26:38 AM | Mindanao Grid-08/25/2024 08:33: JASAAN BESS shutdown at 0815H (Non-GOMP) [WEBSMS] | CMIN
8/25/2024 8:17:05 AM | Luzon Grid-08/25/2024 08:17: Pagbilao EHV SS 1000MVA T03 de-energized at 0817H (Planned Outage) [WEBSMS] | CLUZ
8/25/2024 8:06:35 AM | Luzon Grid-08/25/2024 08:06: Binga-La Trinidad 230kV Line 2 de-energized at 0806H (Planned Outage) [WEBSMS] | CLUZ
8/25/2024 7:41:49 AM | Mindanao Grid-08/25/2024 07:49: (Correction) LAMSAN BIOMASS with 13.2MW load shutdown at 0707H due to shutdown of 5BS01SKU (outside management control outage). [WEBSMS] | CMIN
8/25/2024 7:12:19 AM | Mindanao Grid-08/25/2024 07:19: LAMSAN BIOMASS with 13.2MW load shutdown at 0709H due to shutdown of 5BS01SKU (outside management control outage). [WEBSMS] | CMIN
8/25/2024 7:06:37 AM | Mindanao Grid-08/25/2024 07:13: Bunawan-Nabunturan 138kV Line (7LI1BUN-NAB) de-energized at 0702H. Planned Outage [WEBSMS] | CMIN
8/25/2024 7:06:31 AM | Mindanao Grid-08/25/2024 07:13: LAKE MAINIT with 7.2MW load shutdown at 0701H due to critical water level (Unplanned Outage) [WEBSMS] | CMIN
8/25/2024 7:05:25 AM | Visayas Grid-08/25/2024 07:05: Colon SS 138 kV Bus 1 de-energized at 0705H. (Planned Outage) [WEBSMS] | CVIS
8/25/2024 6:49:17 AM | Visayas Grid-08/25/2024 06:49: Cebu SS 138 kV Bus 2 de-energized at 0649H. (Planned Outage) [WEBSMS] | CVIS
8/25/2024 6:22:40 AM | Visayas Grid-08/25/2024 06:22: Panit-an - Nabas 138 kV Line 2 de-energized at 0622H. (Planned Outage) [WEBSMS] | CVIS
8/25/2024 6:22:37 AM | Mindanao Grid-08/25/2024 06:29: Marawi SS 50MVA 138/69kV (7XF01MRW) de-energized at 0607H. Planned Outage .Non-GOMP [WEBSMS] | CMIN
8/25/2024 6:14:11 AM | Luzon Grid-08/25/2024 06:14: San Jose-Hermosa 230kV Line de-energized at 0613H. (Planned Outage) [WEBSMS] | CLUZ
8/25/2024 5:52:05 AM | [NSO Update] Mindanao Grid-08/25/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3506MW, PK=1863MW, RR=73MW, NetOpMargin: AM=1570, PM=1463, EVE=1387 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @26.5MW, MA2 @47.5MW [WEBSMS] | CMIN
8/25/2024 5:51:03 AM | [NSO Update] Visayas Grid-08/25/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3017MW, PK=1969MW, RR=31MW, NetOpMargin: AM=1017, PM=1000, EVE=671 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @273MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3 C @10MW, PDPP3 G @10MW, PDPP3 E @8MW, PDPP3 H @8MW, PB101 U2 @5.5MW, PB104 U2 @5MW, PB104 U3 @6MW, PDPP1 U2 @3.5MW, PDPP1 U5 @4.3MW, GTEC @10MW, PDPP1 U3 @4.5MW [WEBSMS] | CVIS
8/25/2024 5:49:42 AM | [NSO Update] Luzon Grid-08/25/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15007MW, PK=9485MW, RR=260MW, NetOpMargin: AM=5262, PM=3974, EVE=2771 Highest Unit O/L: GNPD 2 @668MW Derated Plant: Calaca 1 @180MW, Masinloc 1 @305MW, Masinloc 2 @250MW, Masinloc 3 @300MW, GNPD 1 @370MW, Calaca 2 @260MW [WEBSMS] | CLUZ
8/25/2024 5:32:10 AM | Luzon Grid-08/25/2024 05:32: San Gabriel shutdown at 0526H (Reserve Shutdown) [WEBSMS] | CLUZ
8/25/2024 4:35:58 AM | [NSO Update] Mindanao Grid-08/25/2024 04:43: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/25/2024 4:35:44 AM | [NSO Update] Visayas Grid-08/25/2024 04:35: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/25/2024 4:35:28 AM | [NSO Update] Luzon Grid-08/25/2024 04:35: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/25/2024 1:43:31 AM | Luzon Grid-08/25/2024 01:43: Tayabas SS 600MVA T02 restored at 0143H (Planned Outage) [WEBSMS] | CLUZ
8/25/2024 1:05:27 AM | Luzon Grid-08/25/2024 01:05: Salong-SLTEC 230kV Lines 1 & 2 de-energized at 0102H and 0104H, respectively. (Planned Outage) [WEBSMS] | CLUZ
8/24/2024 10:58:35 PM | Luzon Grid-08/24/2024 22:58: Tayabas SS 600MVA T02 de-energized at 2258H (Planned Outage) [WEBSMS] | CLUZ
8/24/2024 8:54:18 PM | Luzon Grid-08/24/2024 20:54: Correction: Muntinlupa-Binan 230kV line 2 restored at 1732H (Planned Outage) [WEBSMS] | CLUZ
8/24/2024 7:28:43 PM | Luzon Grid-08/24/2024 19:28: Calaca-Amadeo 230kV Line 2 autotripped/autoreclosed at 1924H (Unplanned Outage) [WEBSMS] | CLUZ
8/24/2024 6:47:54 PM | Visayas Grid-08/24/2024 18:48: Mabinay - Kabankalan 138 kV Line 1 unlooped at Mabinay SS side at 1847H [WEBSMS] | CVIS
8/24/2024 6:36:27 PM | Visayas Grid-08/24/2024 18:36: Mabinay-Kabankalan 138 kV Line 2 unlooped at Kabankalan SS side at 1834H [WEBSMS] | CVIS
8/24/2024 6:19:42 PM | Luzon Grid-08/24/2024 18:19: Binga-La Trinidad 230 kV Line 1 restored at 1819H (Planned Outage) [WEBSMS] | CLUZ
8/24/2024 6:15:36 PM | Luzon Grid-08/24/2024 18:15: Correction: MPGC Unit 3 online at 1757H (Unplanned Outage) [WEBSMS] | CLUZ
8/24/2024 6:01:51 PM | Visayas Grid-08/24/2024 18:01: Samboan SS 138 kV Bus 2 energized at 1759H (Planned Outage) [WEBSMS] | CVIS
8/24/2024 6:01:09 PM | Luzon Grid-08/24/2024 18:01: MPGC Unit 3 online at 1757H (On Commissioning) [WEBSMS] | CLUZ
8/24/2024 6:00:53 PM | Visayas Grid-08/24/2024 18:00: Dumanjug - Samboan 138 kV Line 2 energized at 1759H (Planned Outage) [WEBSMS] | CVIS
8/24/2024 5:57:01 PM | [NSO Update] Mindanao Grid-08/24/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3591MW, PK=2199MW, RR=73MW, NetOpMargin: EVE=1319 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
8/24/2024 5:55:47 PM | [NSO Update] Visayas Grid-08/24/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2766MW, PK=2218MW, RR=31MW, NetOpMargin: EVE=517 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @270MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3 G @10MW, PDPP3 E @8MW, PDPP3 H @8MW, PB101 U2 @5.5MW, PB104 U2 @5MW, PB104 U3 @6MW, PDPP1 U2 @3.5MW, PDPP1 U5 @4.3MW, GTEC @10MW, PDPP1 U3 @4.5MW [WEBSMS] | CVIS
8/24/2024 5:53:23 PM | Visayas Grid-08/24/2024 17:53: Panit-an - Nabas 138 kV Line 1 energized at 1753H (Planned Outage) [WEBSMS] | CVIS
8/24/2024 5:51:01 PM | [NSO Update] Luzon Grid-08/24/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13453MW, PK=10589MW, RR=350MW, NetOpMargin: EVE=2513 Highest Unit O/L: GNPD 2 @668MW Derated Plant: Calaca 1 @160MW, Masinloc 1 @305MW, Masinloc 2 @250MW, Masinloc 3 @315MW, GNPD 1 @370MW, Calaca 2 @250MW [WEBSMS] | CLUZ
8/24/2024 5:50:21 PM | Mindanao Grid-08/24/2024 17:57: General Santos SS 138kV Bus 2 energized at 1748H. (Planned Outage) [WEBSMS] | CMIN
8/24/2024 5:38:34 PM | Visayas Grid-08/24/2024 17:38: Cadiz - Helios 138 kV Line de-energized at 1737H (Planned Outage) [WEBSMS] | CVIS
8/24/2024 5:33:51 PM | Luzon Grid-08/24/2024 17:33: Muntinlupa-Binan 230kV line 2 restored at 1732H (Unplanned Outage) [WEBSMS] | CLUZ
8/24/2024 5:01:10 PM | Visayas Grid-08/24/2024 17:01: Colon SS 138 kV Bus 1 energized at 1650H (Planned Outage) [WEBSMS] | CVIS
8/24/2024 4:29:45 PM | Mindanao Grid-08/24/2024 16:37: Manolo - Maramag 138kV L1 energized/restored at 1629H. (Planned Outage) [WEBSMS] | CMIN
8/24/2024 4:20:38 PM | Mindanao Grid-08/24/2024 16:27: WMPC DG10 shutdown at 1617H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/24/2024 4:16:28 PM | Luzon Grid-08/24/2024 16:16: La Trinidad - Bauang 230kV Line 1 autotripped/auto-reclosed at 1606H (Unplanned Outage) [WEBSMS] | CLUZ
8/24/2024 4:12:41 PM | Visayas Grid-08/24/2024 16:12: Samboan - Ginatilan 69 kV Line energized at 1610H. (Planned Outage) [WEBSMS] | CVIS
8/24/2024 4:10:26 PM | Visayas Grid-08/24/2024 16:10: Samboan SS 138/69/13.8 kV 30 MVA TR1 and 50 MVA TR2 energized at 1607H and 1606H [WEBSMS] | CVIS
8/24/2024 4:02:07 PM | Luzon Grid-08/24/2024 16:02: San Gabriel online at 1600H (Reserve Shutdown) [WEBSMS] | CLUZ
8/24/2024 3:06:27 PM | Mindanao Grid-08/24/2024 15:13: AGUS 5 Unit 2 online at 1457H. (Planned Outage) [WEBSMS] | CMIN
8/24/2024 2:57:57 PM | Luzon Grid-08/24/2024 14:58: Naga-Daraga 230kV Line autotripped/auto-reclosed at 1445H (Unplanned Outage) [WEBSMS] | CLUZ
8/24/2024 2:39:30 PM | Luzon Grid-08/24/2024 14:39: Salong SS 230kV Bus 2 restored at 1438H (Planned Outage) [WEBSMS] | CLUZ
8/24/2024 2:33:10 PM | Visayas Grid-08/24/2024 14:33: Gahit - Barotac Viejo 230 kV Line 1 energized at 1432H (Planned Outage) [WEBSMS] | CVIS
8/24/2024 2:19:23 PM | Mindanao Grid-08/24/2024 14:26: Agus 5 SY - Agus 5 HEP Line 2 energized/restored at 1417H. (Planned Outage) [WEBSMS] | CMIN
8/24/2024 2:11:50 PM | Visayas Grid-08/24/2024 14:11: Sangi SS 34.5 kV Bus 1 energized at 1407H. (Unplanned Outage) [WEBSMS] | CVIS
8/24/2024 1:25:52 PM | Mindanao Grid-08/24/2024 13:33: WMPC DG10 online at 1323H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/24/2024 12:57:20 PM | Visayas Grid-08/24/2024 12:57: Dumanjug-Samboan 138 kV Line 1 and Samboan SS 138 kV Bus 1 energized at 1255H and 1250H, respectively. (Unplanned Outage) [WEBSMS] | CVIS
8/24/2024 12:43:48 PM | [NSO Update] Mindanao Grid-08/24/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3609MW, PK=2209MW, RR=73MW, NetOpMargin: PM=1327, EVE=1281 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @26.5MW [WEBSMS] | CMIN
8/24/2024 12:38:41 PM | [NSO Update] Visayas Grid-08/24/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2919MW, PK=2166MW, RR=31MW, NetOpMargin: PM=722, EVE=541 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @270MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3 E @8MW, PDPP3 H @8MW, PB101 U2 @5.5MW, PB104 U2 @5MW, PB104 U3 @6MW, PDPP1 U2 @3.5MW, PDPP1 U5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/24/2024 12:37:39 PM | [NSO Update] Luzon Grid-08/24/2024 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14731MW, PK=10568MW, RR=350MW, NetOpMargin: PM=3813, EVE=2511 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: Calaca 1 @200MW, Masinloc 1 @305MW, Masinloc 2 @250MW, GNPD 1 @334MW [WEBSMS] | CLUZ
8/24/2024 12:36:38 PM | Visayas Grid-08/24/2024 12:36: Amlan-Palinpinon 138 kV Line 2 energized at 1232H. (Planned Outage) [WEBSMS] | CVIS
8/24/2024 9:12:33 AM | Mindanao Grid-08/24/2024 09:19: General Santos SS 138kV Bus 2 de-energized at 0911H. (Planned Outage) [WEBSMS] | CMIN
8/24/2024 9:03:12 AM | Visayas Grid-08/24/2024 09:03: Sangi SS 34.5 kV Bus 1 de-energized at 0900H. (Unplanned Outage) [WEBSMS] | CVIS
8/24/2024 8:45:36 AM | Visayas Grid-08/24/2024 08:45: Amlan-Palinpinon 138 kV Line 2 de-energized at 0845H. (Planned Outage) [WEBSMS] | CVIS
8/24/2024 8:21:06 AM | Mindanao Grid-08/24/2024 08:28: Manolo Fortich - Maramag 138kV L1 shutdown at 0807H. (Planned Outage) [WEBSMS] | CMIN
8/24/2024 8:19:17 AM | Luzon Grid-08/24/2024 08:19: Muntinlupa SS 230kV Bus 1 & Bus Coupler 8-10CB04MUN restored at 0816H (Planned Outage) [WEBSMS] | CLUZ
8/24/2024 8:14:39 AM | Luzon Grid-08/24/2024 08:14: Binga-La Trinidad 230 kV Line 1 de-energized at 0814H (Planned Outage) [WEBSMS] | CLUZ
8/24/2024 8:02:13 AM | Visayas Grid-08/24/2024 08:02: Dumanjug-Samboan 138 kV Line 1 and Samboan SS 138 kV Bus 1 de-energized at 0800H. (Unplanned Outage) [WEBSMS] | CVIS
8/24/2024 7:45:00 AM | Visayas Grid-08/24/2024 07:45: Samboan SS 138 kV Bus 2 de-energized at 0709H. (Planned Outage) [WEBSMS] | CVIS
8/24/2024 7:41:51 AM | Visayas Grid-08/24/2024 07:41: Samboan SS 138/69/13.8 kV 30 MVA TR1 & 50 MVA TR2 de-energized at 0739H. (Planned Outage) [WEBSMS] | CVIS
8/24/2024 7:39:32 AM | Visayas Grid-08/24/2024 07:39: Samboan SS 69 kV Bus 1 de-energized at 0738H. (Planned Outage) [WEBSMS] | CVIS
8/24/2024 7:38:40 AM | Visayas Grid-08/24/2024 07:38: Samboan-Ginatilan 69 kV Line de-energized at 0736H. (Planned Outage) [WEBSMS] | CVIS
8/24/2024 7:28:16 AM | Luzon Grid-08/24/2024 07:28: Salong SS 230kV Bus 2 de-energized at 0724H (Planned Outage) [WEBSMS] | CLUZ
8/24/2024 7:27:04 AM | Visayas Grid-08/24/2024 07:27: Colon SS 138 kV Bus 1 de-energized at 0725H. (Planned Outage) [WEBSMS] | CVIS
8/24/2024 7:10:59 AM | Visayas Grid-08/24/2024 07:11: Dumanjug-Samboan 138 kV Line 2 de-energized at 0709H. (Planned Outage) [WEBSMS] | CVIS
8/24/2024 7:08:07 AM | Mindanao Grid-08/24/2024 07:15: LAKE MAINIT shutdown at 0701H due to critical water level. (Unplanned Outage) [WEBSMS] | CMIN
8/24/2024 6:56:02 AM | Visayas Grid-08/24/2024 06:56: Mabinay-Kabankalan 138 kV Line 1 looped at Kabankalan SS side at 0654H. [WEBSMS] | CVIS
8/24/2024 6:29:28 AM | Luzon Grid-08/24/2024 06:29: San Gabriel shutdown at 0627H (Reserved Shutdown) [WEBSMS] | CLUZ
8/24/2024 6:21:23 AM | Visayas Grid-08/24/2024 06:21: Mabinay-Kabankalan 138 kV Line 2 looped at Mabinay SS side at 0549H. [WEBSMS] | CVIS
8/24/2024 6:19:50 AM | Visayas Grid-08/24/2024 06:19: Panit-an-Nabas 138 kV Line 1 de-energized at 0617H. (Planned Outage) [WEBSMS] | CVIS
8/24/2024 6:18:57 AM | Mindanao Grid-08/24/2024 06:26: Agus 5 SY - Agus 5 HEP Line 2 de-energized at 0612H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/24/2024 6:10:32 AM | Mindanao Grid-08/24/2024 06:17: AGUS 5 Unit 2 shutdown at 0608H (Planned Outage) [WEBSMS] | CMIN
8/24/2024 5:41:42 AM | [NSO Update] Luzon Grid-08/24/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15153MW, PK=10724MW, RR=440MW, NetOpMargin: AM=3990, PM=3563, EVE=2802 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 1 @200MW, Masinloc 1 @305MW, Masinloc 2 @250MW [WEBSMS] | CLUZ
8/24/2024 5:31:47 AM | [NSO Update] Mindanao Grid-08/24/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3625MW, PK=2195MW, RR=73MW, NetOpMargin: AM=1357, PM=1268, EVE=1259 Highest Unit O/L: GNPK 151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
8/24/2024 5:29:57 AM | [NSO Update] Visayas Grid-08/24/2024 05:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2881MW, PK=2077MW, RR=31MW, NetOpMargin: AM=774, PM=740, EVE=536 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @276MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PDPP3 C @10MW, PDPP3 E @8MW, PDPP3 H @8MW, PB101 U2 @5.5MW, PB104 U2 @5MW, PB104 U3 @6MW, PDPP1 U2 @3.5MW, PDPP1 U5 @4.3MW, GTEC @10MW [WEBSMS] | CVIS
8/24/2024 4:21:37 AM | [NSO Update] Luzon Grid-08/24/2024 04:21: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/24/2024 4:17:15 AM | [NSO Update] Mindanao Grid-08/24/2024 04:24: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/24/2024 4:16:55 AM | [NSO Update] Visayas Grid-08/24/2024 04:17: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/24/2024 3:15:53 AM | Luzon Grid-08/24/2024 03:15: Tayabas 600MVA T01 restored at 0312H (Planned Outage) [WEBSMS] | CLUZ
8/24/2024 2:46:53 AM | Mindanao Grid-08/24/2024 02:54: ASIGA Hydro online at 0047H (Unplanned Outage) [WEBSMS] | CMIN
8/24/2024 2:35:27 AM | Mindanao Grid-08/24/2024 02:42: ASIGA Hydro with 4.5MW load tripped at 0022H. Indication: Earth Fault (Unplanned Outage) [WEBSMS] | CMIN
8/24/2024 1:20:26 AM | Luzon Grid-08/24/2024 01:20: Muntinlupa 230kV Bus 1 was de-energized at 0118H. (Planned Outage) [WEBSMS] | CLUZ
8/24/2024 1:09:14 AM | Luzon Grid-08/24/2024 01:09: Muntinlupa-Binan 230kV line 2 was de-energized at 0107H. (Planned Outage) [WEBSMS] | CLUZ
8/24/2024 12:56:31 AM | Luzon Grid-08/24/2024 00:56: Tayabas 600MVA T01 was de-energized at 0053H. (Planned Outage) [WEBSMS] | CLUZ
8/23/2024 11:45:22 PM | Luzon Grid-08/23/2024 23:45: San Lorenzo Module 60 shutdown at 2343H. (Planned Outage) [WEBSMS] | CLUZ
8/23/2024 9:47:24 PM | Visayas Grid-08/23/2024 21:47: TVI unit 2 cut-in 2145H, initial load 10MW. [WEBSMS] | CVIS
8/23/2024 9:40:46 PM | Visayas Grid-08/23/2024 21:40: Colon-Naga 138 kV Line 2 energized at 2138H. (Planned Outage) [WEBSMS] | CVIS
8/23/2024 8:26:48 PM | Visayas Grid-08/23/2024 20:26: Calatrava SS 230 kV Bus 1 energized at 2025H (Planned Outage) [WEBSMS] | CVIS
8/23/2024 7:21:23 PM | Mindanao Grid-08/23/2024 19:28: WMPC DG10 shutdown at 1919H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/23/2024 7:05:54 PM | Luzon Grid-08/23/2024 19:05: Concepcion-Concepcion Solar 69kV line was restored at 1904H. (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2024 6:19:59 PM | Luzon Grid-08/23/2024 18:20: Lal-lo-Magapit BESS 69kV line, Lal-lo-Cagayan North Solar 69kV line 1, and Lal-lo-Cagayan North Solar 69kV line 2 were energized at 1811H, 1812, and 1814H respectively. (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2024 6:04:05 PM | Luzon Grid-08/23/2024 18:04: San Gabriel online at 1800H. (From Reserve Shutdown) [WEBSMS] | CLUZ
8/23/2024 6:02:32 PM | Luzon Grid-08/23/2024 18:02: Concepcion-Concepcion Solar 69kV line was de-energized at 1756H. (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2024 6:00:32 PM | Luzon Grid-08/23/2024 18:00: Bolo-Sual 230kV line 2 was restored at 1759H. (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2024 5:44:03 PM | [NSO Update] Luzon Grid-08/23/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13850MW, PK=11186MW, RR=350MW, NetOpMargin: EVE=2314 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 1 @210MW, Calaca 2 @270MW, Masinloc 1 @305MW, Masinloc 2 @250MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
8/23/2024 5:41:53 PM | [NSO Update] Visayas Grid-08/23/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2563MW, PK=2215MW, RR=31MW, NetOpMargin: EVE=316 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @255MW, GTEC @10MW, PDPP3 H @8MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PB104 U2 @5MW, PB101 U2 @5.5MW, PDPP1 U5 @4MW, PDPP3 C @10MW, PDPP3 E @8MW, PB104 U3 @6MW [WEBSMS] | CVIS
8/23/2024 5:41:50 PM | Luzon Grid-08/23/2024 17:41: Bolo-Sual 230kV line 2 auto-tripped at 1737H. (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2024 5:39:43 PM | [NSO Update] Mindanao Grid-08/23/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3598MW, PK=2259MW, RR=73MW, NetOpMargin: EVE=1267 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW, MA2 @26.5MW [WEBSMS] | CMIN
8/23/2024 5:38:23 PM | [NSO Update] Visayas Grid-08/23/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2563MW, PK=2215MW, RR=31MW, NetOpMargin: EVE=316 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Leyte A @255MW, GTEC @10MW, PDPP3 H @8MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PB104 U2 @5MW, PB101 U2 @5.5MW, PDPP1 U5 @4MW, PDPP3 C @10MW, PDPP3 E @8MW, PB104 U3 @6MW [WEBSMS] | CVIS
8/23/2024 5:14:40 PM | Mindanao Grid-08/23/2024 17:21: Agus5 SS 138 kV Bus 1 (7BS01AG5 23) energized/restored at 1711H. Planned Outage/Non-GOMP [WEBSMS] | CMIN
8/23/2024 4:16:54 PM | Mindanao Grid-08/23/2024 16:24: Villanueva-SBPI Villanueva BESS 138kV L energized /restored at 1607H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/23/2024 3:09:44 PM | Luzon Grid-08/23/2024 15:09: Calaca 8-03CB04CLC energized at 1506H (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2024 3:09:32 PM | Visayas Grid-08/23/2024 15:09: Colon SS 138KV Bus 2 tripped at 1447H / restored at 1454H, affecting TR1 & TR2 138KV High side of the transformer. (Unplanned Outage) [WEBSMS] | CVIS
8/23/2024 1:38:14 PM | Mindanao Grid-08/23/2024 13:45: WMPC DG10 online at 1336H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/23/2024 12:49:13 PM | [NSO Update] Mindanao Grid-08/23/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3639MW, PK=2342MW, RR=73MW, NetOpMargin: PM=1224, EVE=1193 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @26.5MW [WEBSMS] | CMIN
8/23/2024 12:47:45 PM | [NSO Update] Visayas Grid-08/23/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2728MW, PK=2244MW, RR=31MW, NetOpMargin: PM=453, EVE=264 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: Leyte A @261MW, GTEC @10MW, PDPP3 H @8MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PB104 U2 @5MW, PB101 U2 @5.5MW, PDPP1 U5 @4MW, PDPP3 C @10MW, PDPP3 E @8MW, PB104 U3 @6MW [WEBSMS] | CVIS
8/23/2024 12:46:44 PM | Visayas Grid-08/23/2024 12:46: TAREC online at 1240H. (Unplanned Outage) [WEBSMS] | CVIS
8/23/2024 12:46:36 PM | [NSO Update] Luzon Grid-08/23/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15101MW, PK=11389MW, RR=310MW, NetOpMargin: PM=3402, EVE=2672 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @220MW, Masinloc 1 @310MW, Masinloc 2 @250MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
8/23/2024 12:33:48 PM | Mindanao Grid-08/23/2024 12:41: WMPC DG10 shutdown at 1231H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/23/2024 12:10:23 PM | Mindanao Grid-08/23/2024 12:17: LAKE MAINIT online at 1200H (Unplanned Outage) [WEBSMS] | CMIN
8/23/2024 11:50:08 AM | Mindanao Grid-08/23/2024 11:57: Aurora - NagaMin 138 kV L1 (7LI1AUR-NAA) energized/looped at 1147H. Planned Outage [WEBSMS] | CMIN
8/23/2024 11:39:04 AM | Luzon Grid-08/23/2024 11:39: Lal-lo-Magapit BESS 69kV line restored at 1137H. (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2024 11:27:36 AM | Luzon Grid-08/23/2024 11:27: Lal-lo-Cagayan North Solar 69kV lines 1 and 2 were energized at 1121H and 1127H respectively. (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2024 11:14:53 AM | Luzon Grid-08/23/2024 11:14: San Gabriel shutdown at 1112H (Reserve Shutdown) [WEBSMS] | CLUZ
8/23/2024 9:36:37 AM | Luzon Grid-08/23/2024 09:36: Laoag SS 300MVA T02 restored at 0936H (Planned Outage) [WEBSMS] | CLUZ
8/23/2024 9:27:04 AM | Luzon Grid-08/23/2024 09:27: Calaca PCB 8-03CB04CLC de-energized at 0926H (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2024 9:13:05 AM | Mindanao Grid-08/23/2024 09:20: Agus5 SS 138 kV Bus 1 (7BS01AG5 23) de-energized at 0604H. Planned Outage/Non-GOMP [WEBSMS] | CMIN
8/23/2024 8:07:09 AM | Mindanao Grid-08/23/2024 08:14: LAKE MAINIT shutdown at 0802H due to critical water level. (Unplanned Outage) [WEBSMS] | CMIN
8/23/2024 7:27:23 AM | Mindanao Grid-08/23/2024 07:34: Aurora - NagaMin 138 kV L1 (7LI1AUR-NAA) de-energized at 0726H. Planned Outage [WEBSMS] | CMIN
8/23/2024 7:18:13 AM | Mindanao Grid-08/23/2024 07:25: WMPC DG10 online at 0717H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/23/2024 7:05:19 AM | Visayas Grid-08/23/2024 07:05: Colon-Naga 138 kV Line 2 de-energized at 0704H. (Planned Outage) [WEBSMS] | CVIS
8/23/2024 5:51:38 AM | [NSO Update] Mindanao Grid-08/23/2024 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3650MW, PK=2144MW, RR=73MW, NetOpMargin: AM=1434, PM=1324, EVE=1224 Highest Unit O/L: GNPK 1@151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @26.5MW [WEBSMS] | CMIN
8/23/2024 5:51:35 AM | [NSO Update] Visayas Grid-08/23/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2812MW, PK=2214MW, RR=31MW, NetOpMargin: AM=567, PM=567, EVE=342 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @276MW, GTEC @10MW, PDPP3 H @8MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PB104 U2 @5MW, PB101 U2 @5.5MW, PDPP1 U5 @4MW, PDPP3 C @10MW [WEBSMS] | CVIS
8/23/2024 5:51:29 AM | [NSO Update] Luzon Grid-08/23/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15284MW, PK=11371MW, RR=310MW, NetOpMargin: AM=3603, PM=3449, EVE=3214 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 1 @220MW, Masinloc 1 @310MW, Masinloc 2 @250MW, Masinloc 3 @280MW [WEBSMS] | CLUZ
8/23/2024 5:17:01 AM | Luzon Grid-08/23/2024 05:17: Laoag SS 300MVA T02 de-energized at 0515H (Planned Outage) [WEBSMS] | CLUZ
8/23/2024 4:04:29 AM | [NSO Update] Mindanao Grid-08/23/2024 04:11: Weather Advisory: Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CMIN
8/23/2024 4:04:26 AM | [NSO Update] Visayas Grid-08/23/2024 04:04: Weather Advisory: Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CVIS
8/23/2024 4:04:23 AM | [NSO Update] Luzon Grid-08/23/2024 04:04: Weather Advisory: Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CLUZ
8/23/2024 12:07:48 AM | Luzon Grid-08/23/2024 00:07: SLTEC Unit 2 shutdown at 0006H (Unplanned Outage) [WEBSMS] | CLUZ
8/22/2024 9:36:15 PM | Visayas Grid-08/22/2024 21:36: Calatrava SS 230 kV Bus 1 energized at 2133H (Planned Outage) [WEBSMS] | CVIS
8/22/2024 9:26:35 PM | Luzon Grid-08/22/2024 21:26: Pagbilao EHV 1000MVA T02 restored at 2125H (Planned Outage) [WEBSMS] | CLUZ
8/22/2024 9:15:49 PM | Visayas Grid-08/22/2024 21:15: Colon - Naga 138 kV Line 1 energized at 2114H (Planned Outage) [WEBSMS] | CVIS
8/22/2024 9:13:47 PM | Mindanao Grid-08/22/2024 21:20: Maramag - Kibawe 138kV L2 energized/looped at 2110H. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2024 9:11:48 PM | Mindanao Grid-08/22/2024 21:18: Pulangi 4 Unit 2 online at 2107H. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2024 9:10:51 PM | [NSO Update] Visayas Grid-08/22/2024 21:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2109H with power going to Luzon. [WEBSMS] | CVIS
8/22/2024 9:10:48 PM | [NSO Update] Luzon Grid-08/22/2024 21:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2109H with power going to Luzon. [WEBSMS] | CLUZ
8/22/2024 9:08:49 PM | [NSO Update] Luzon Grid-08/22/2024 21:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2059H from reverse power direction. [WEBSMS] | CLUZ
8/22/2024 9:07:54 PM | [NSO Update] Visayas Grid-08/22/2024 21:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2059H from reverse power direction. [WEBSMS] | CVIS
8/22/2024 8:51:32 PM | Mindanao Grid-08/22/2024 20:57: WMPC DG10 shutdown at 2046H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/22/2024 8:41:38 PM | Visayas Grid-08/22/2024 20:41: Magdugo - Calatrava 230 kV Line 1 Calatrava SS side isolated at 2025H due to the tripping Calatrava - Cadiz 230 kV Line 2, restored at 2033H (Unplanned Outage) [WEBSMS] | CVIS
8/22/2024 8:34:36 PM | Visayas Grid-08/22/2024 20:34: Calatrava - Cadiz 230 kV Line 2 tripped/reclosed at 2025H (Unplanned Outage) [WEBSMS] | CVIS
8/22/2024 8:21:14 PM | Luzon Grid-08/22/2024 20:21: Hermosa - San Jose 230kV Line restored at 2021H (Unplanned Outage) [WEBSMS] | CLUZ
8/22/2024 8:20:15 PM | Mindanao Grid-08/22/2024 20:26: Pulangi 4 Unit 2 with 63.7MW load tripped at 2008H. Indication: Excitation trip. No ALD activation, lowest frequency recorded at 59.65Hz. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2024 8:17:38 PM | Mindanao Grid-08/22/2024 20:23: Maramag - Kibawe 138kV Line2 tripped/open at Maramag side at 2008H. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2024 8:14:29 PM | Luzon Grid-08/22/2024 20:14: Hermosa - San Jose 230kV Line autotripped at 2010H (Unplanned Outage) [WEBSMS] | CLUZ
8/22/2024 7:56:10 PM | Mindanao Grid-08/22/2024 20:02: WMPC DG1 shutdown at 1946H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/22/2024 7:47:51 PM | Mindanao Grid-08/22/2024 19:54: WMPC DG01 shutdown at 1946H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/22/2024 5:56:04 PM | [NSO Update] Luzon Grid-08/22/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14080MW, PK=11649MW, RR=440MW, NetOpMargin: EVE=1992 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @117MW, Masinloc 1 @310MW, Masinloc 2 @250MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
8/22/2024 5:55:59 PM | [NSO Update] Visayas Grid-08/22/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2689MW, PK=2318MW, RR=31MW, NetOpMargin: EVE=340 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @273MW, GTEC @10MW, TGPP @115MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PB104 U2 @5MW, PB101 U2 @5.5MW, PDPP1 U5 @4MW, PDPP3 C @10MW, PDPP3 H @8MW [WEBSMS] | CVIS
8/22/2024 5:55:54 PM | [NSO Update] Mindanao Grid-08/22/2024 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3590MW, PK=2244MW, RR=73MW, NetOpMargin: EVE=1273 Highest Unit O/L: GNPK 1@151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @49MW, MA2 @26.5MW [WEBSMS] | CMIN
8/22/2024 5:15:19 PM | Mindanao Grid-08/22/2024 17:21: Butuan - Placer 138KV Line 2 auto tripped and successfully auto reclosed at 1703H (single-pole auto-reclosing (SPAR)). (Unplanned Outage) [WEBSMS] | CMIN
8/22/2024 2:24:12 PM | Visayas Grid-08/22/2024 14:24: Babatngon - Paranas 138 kV Line 1 energized at 1421H (Unplanned Outage) [WEBSMS] | CVIS
8/22/2024 2:17:50 PM | Visayas Grid-08/22/2024 14:17: Calatrava SS 230 kV Bus 1 de-energized at 1415H (Planned Outage) [WEBSMS] | CVIS
8/22/2024 2:11:39 PM | Mindanao Grid-08/22/2024 14:17: Mt Apo Unit 2 online at 1407H. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2024 2:04:40 PM | Visayas Grid-08/22/2024 14:04: Paranas-Calbayog 138kV Line 2 energized at 1354H. (Unplanned outage) [WEBSMS] | CVIS
8/22/2024 2:00:03 PM | Mindanao Grid-08/22/2024 14:06: WMPC DG01 online at 1355H. Replacement Unit. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/22/2024 1:56:03 PM | Visayas Grid-08/22/2024 13:56: Paranas 30MVA TR 1 energized at 1340H (Unplanned Outage) [WEBSMS] | CVIS
8/22/2024 1:55:19 PM | Mindanao Grid-08/22/2024 14:01: WMPC DG07 with 10MW running as RPS tripped at 1350H (Unplanned Outage) [WEBSMS] | CMIN
8/22/2024 1:51:55 PM | Visayas Grid-08/22/2024 13:51: Paranas 50MVA TR 2 energized at 1339H (Unplanned Outage) [WEBSMS] | CVIS
8/22/2024 1:48:29 PM | Visayas Grid-08/22/2024 13:48: Sta. Rita 50MVA TR energized at 1336H (Unplanned Outage) [WEBSMS] | CVIS
8/22/2024 1:46:12 PM | Visayas Grid-08/22/2024 13:46: Paranas-Calbayog 138kV Line 1 energized at 1331H (Unplanned Outage) [WEBSMS] | CVIS
8/22/2024 1:34:28 PM | Visayas Grid-08/22/2024 13:34: Babatngon-Paranas Line 2 energized at 1331H (Unplanned Outage) [WEBSMS] | CVIS
8/22/2024 1:03:24 PM | Mindanao Grid-08/22/2024 13:09: Mt Apo Unit 1 online at 1259H. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2024 1:01:55 PM | Mindanao Grid-08/22/2024 13:08: WMPC DG07 online at 1300H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/22/2024 12:58:47 PM | Visayas Grid-08/22/2024 12:58: Babatngon-Paranas 138kV Lines 1 and 2 tripped at 1251H. (Unplanned Outage) [WEBSMS] | CVIS
8/22/2024 12:45:37 PM | Mindanao Grid-08/22/2024 12:51: Mt Apo Unit 1 on emergency shutdown (with gradual de-loading) at 1239H to facilitate energization of Station Transformer for Mt Apo Unit 2. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2024 12:39:50 PM | [NSO Update] Luzon Grid-08/22/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15333MW, PK=12812MW, RR=400MW, NetOpMargin: PM=2121, EVE=1762 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @119MW, Masinloc 1 @310MW, Masinloc 2 @250MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
8/22/2024 12:36:26 PM | [NSO Update] Mindanao Grid-08/22/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3606MW, PK=2432MW, RR=73MW, NetOpMargin: PM=1101, EVE=1212 Highest Unit O/L: GNPK 151.9MW Derated Plant: MPC @40MW, MA1 @49MW [WEBSMS] | CMIN
8/22/2024 12:35:19 PM | [NSO Update] Visayas Grid-08/22/2024 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2905MW, PK=2478MW, RR=31MW, NetOpMargin: PM=396, EVE=302 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @273MW, GTEC @10MW, TGPP @115MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PB104 U2 @5MW, PB101 U2 @5.5MW, PDPP1 U5 @4MW, PDPP3 C @10MW, PDPP3 E @8MW, PDPP3 H @8MW [WEBSMS] | CVIS
8/22/2024 12:15:58 PM | Luzon Grid-08/22/2024 12:15: San Juan-Calauan 230kV Line 1 restored/looped at 1214H (Unplanned Outage) [WEBSMS] | CLUZ
8/22/2024 11:58:03 AM | Luzon Grid-08/22/2024 11:58: San Juan-Calauan 230kV Line 1 unloop at 1002H (San Juan side) due to air leak at PCB 8-02CB08SJU (Unplanned Outage) [WEBSMS] | CLUZ
8/22/2024 11:55:51 AM | [NSO Update] Luzon Grid-08/22/2024 11:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1154H with power going to Visayas. [WEBSMS] | CLUZ
8/22/2024 11:55:12 AM | [NSO Update] Visayas Grid-08/22/2024 11:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1154H with power going to Visayas. [WEBSMS] | CVIS
8/22/2024 11:47:49 AM | [NSO Update] Visayas Grid-08/22/2024 11:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1144H from forward power direction. [WEBSMS] | CVIS
8/22/2024 11:47:46 AM | [NSO Update] Luzon Grid-08/22/2024 11:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1144H from forward power direction. [WEBSMS] | CLUZ
8/22/2024 11:44:44 AM | [NSO Update] Visayas Grid-08/22/2024 11:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1136H with power going to Luzon. [WEBSMS] | CVIS
8/22/2024 11:44:08 AM | [NSO Update] Luzon Grid-08/22/2024 11:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1136H with power going to Luzon. [WEBSMS] | CLUZ
8/22/2024 11:28:10 AM | [NSO Update] Luzon Grid-08/22/2024 11:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1124H from forward power direction. [WEBSMS] | CLUZ
8/22/2024 11:27:45 AM | [NSO Update] Visayas Grid-08/22/2024 11:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1124H from forward power direction. [WEBSMS] | CVIS
8/22/2024 9:32:07 AM | Mindanao Grid-08/22/2024 09:38: WMPC DG10 online at 0929H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/22/2024 6:54:55 AM | Visayas Grid-08/22/2024 06:54: UMPP U4 cut in at 0621H (Unplanned Outage) [WEBSMS] | CVIS
8/22/2024 6:51:41 AM | Visayas Grid-08/22/2024 06:51: Colon-Naga 138kV Line 1 de-energized at 0647H. (Planned Outage) [WEBSMS] | CVIS
8/22/2024 5:59:26 AM | [NSO Update] Mindanao Grid-08/22/2024 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3614MW, PK=2361MW, RR=73MW, NetOpMargin: AM=1181, PM=1115, EVE=1193 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @150MW, MPC @40MW [WEBSMS] | CMIN
8/22/2024 5:57:24 AM | [NSO Update] Visayas Grid-08/22/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2817MW, PK=2415MW, RR=31MW, NetOpMargin: AM=371, PM=380, EVE=280 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: Leyte A @250MW, GTEC @10MW, TGPP @110MW, CEDC U3 @75MW, PGPP2_SOG 1 @18.5MW, PB104 U2 @5MW, PB104U3 @6MW, PDPP1 U5 @4MW, PDPP3 C @10MW, PDPP3 E @8MW, PDPP3 H @8MW, PEDC U3 @130MW, PB101 U2 @5.5MW [WEBSMS] | CVIS
8/22/2024 5:55:55 AM | [NSO Update] Luzon Grid-08/22/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15378MW, PK=11963MW, RR=440MW, NetOpMargin: AM=2975, PM=2351, EVE=2320 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: SLTEC 2 @119MW, Masinloc 1 @315MW, Masinloc 2 @220MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
8/22/2024 5:04:19 AM | Mindanao Grid-08/22/2024 05:10: LIBERTAD POWER online at 0220H (Unplanned Outage) [WEBSMS] | CMIN
8/22/2024 5:03:39 AM | Mindanao Grid-08/22/2024 05:10: LIBERTAD POWER with 6MW load tripped at 0216H. Indication: Vector surge protection trip, metering PT fuse failure alarm (Unplanned Outage) [WEBSMS] | CMIN
8/22/2024 4:33:46 AM | Visayas Grid-08/22/2024 04:34: TAREC online at 0431H. (Unplanned Outage) [WEBSMS] | CVIS
8/22/2024 4:15:11 AM | [NSO Update] Luzon Grid-08/22/2024 04:15: Weather Advisory: Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CLUZ
8/22/2024 4:13:51 AM | [NSO Update] Mindanao Grid-08/22/2024 04:20: Weather Advisory: Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CMIN
8/22/2024 4:13:35 AM | [NSO Update] Visayas Grid-08/22/2024 04:13: Weather Advisory: Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CVIS
8/22/2024 12:44:05 AM | Visayas Grid-08/22/2024 00:44: LGPP U2 cut-in at 0043H. (Unplanned Outage) [WEBSMS] | CVIS
8/22/2024 12:31:53 AM | Mindanao Grid-08/22/2024 00:38: (Correction) MT. APO 2 declared available at 0024H (houseload operation). From Maintenance Outage. [WEBSMS] | CMIN
8/22/2024 12:30:08 AM | Mindanao Grid-08/22/2024 00:36: MT. APO 2 declared available at 0024H (houseload operation). From Unplanned Outage. [WEBSMS] | CMIN
8/21/2024 10:17:14 PM | Mindanao Grid-08/21/2024 22:23: WMPC DG10 shutdown at 2216H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/21/2024 10:06:12 PM | [NSO Update] Luzon Grid-08/21/2024 22:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2205H with power going to Luzon. [WEBSMS] | CLUZ
8/21/2024 10:06:04 PM | [NSO Update] Visayas Grid-08/21/2024 22:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2205H with power going to Luzon. [WEBSMS] | CVIS
8/21/2024 10:00:10 PM | Visayas Grid-08/21/2024 22:00: TAREC was isolated from the grid due to the tripping of 60 MVA TR1 at 2149H. (Unplanned Outage) [WEBSMS] | CVIS
8/21/2024 9:56:35 PM | [NSO Update] Luzon Grid-08/21/2024 21:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2155H from reverse power direction. [WEBSMS] | CLUZ
8/21/2024 9:56:19 PM | [NSO Update] Visayas Grid-08/21/2024 21:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2155H from reverse power direction. [WEBSMS] | CVIS
8/21/2024 7:49:13 PM | Mindanao Grid-08/21/2024 19:55: WMPC DG01 shutdown at 1948H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/21/2024 7:18:05 PM | Visayas Grid-08/21/2024 19:18: Pal 1 U2 cut-in at 1917H. (Unplanned Outage) [WEBSMS] | CVIS
8/21/2024 6:35:00 PM | Mindanao Grid-08/21/2024 18:41: WMPC DG01 online at 1832H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/21/2024 6:34:01 PM | Mindanao Grid-08/21/2024 18:40: LIANGAN Hydro completed GUCT for the day at 1745H. Resumes commercial operation test. [WEBSMS] | CMIN
8/21/2024 5:43:08 PM | [NSO Update] Mindanao Grid-08/21/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3564MW, PK=2367MW, RR=73MW, NetOpMargin: EVE=1124 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @150MW, MPC @40MW [WEBSMS] | CMIN
8/21/2024 5:41:48 PM | [NSO Update] Visayas Grid-08/21/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2610MW, PK=2351MW, RR=31MW, NetOpMargin: EVE=228 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: LEYTE_A @250MW, LGPP_G01 @81.2MW, PGPP1 @75MW, CEDC_U3 @75MW, PDPP3_C @10MW, PDPP3_E @8MW, PDPP3_H @8MW, PGPP2_SOG 1 @18.5MW, GTEC @10MW, PB104_2 @5MW, PB104_3 @6MW, PB101_2 @5.5MW, PDPP1_U3 @4.5MW, PDPP1_U5 @4MW [WEBSMS] | CVIS
8/21/2024 5:40:15 PM | [NSO Update] Luzon Grid-08/21/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13961MW, PK=11768MW, RR=310MW, NetOpMargin: EVE=1883 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: SLTEC 2 @119MW, Masinloc 1 @310MW, Masinloc 2 @100MW, Masinloc 3 @310MW [WEBSMS] | CLUZ
8/21/2024 5:26:53 PM | Mindanao Grid-08/21/2024 17:33: WMPC DG01 shutdown at 1716H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/21/2024 5:00:53 PM | Mindanao Grid-08/21/2024 17:07: SBPI MACO BESS online at 1659H (Unplanned Outage) [WEBSMS] | CMIN
8/21/2024 4:57:16 PM | Mindanao Grid-08/21/2024 17:03: LIANGAN Hydro Unit 2 online at 1646H. Testing/GUCT. [WEBSMS] | CMIN
8/21/2024 4:03:59 PM | Luzon Grid-08/21/2024 16:04: Lumban-Malaya 230kV line 2 restored at 1603H (Planned Outage) [WEBSMS] | CLUZ
8/21/2024 3:57:25 PM | Luzon Grid-08/21/2024 15:57: San Jose-Angat 230kV L1 tripped/reclosed at 1545H (Unplanned Outage) [WEBSMS] | CLUZ
8/21/2024 3:07:54 PM | Mindanao Grid-08/21/2024 15:14: SBPI MACO BESS tripped at 1459H. Indication: Overvoltage (Unplanned Outage) [WEBSMS] | CMIN
8/21/2024 2:28:50 PM | Visayas Grid-08/21/2024 14:29: TAREC online at 1427H. (Unplanned Outage) [WEBSMS] | CVIS
8/21/2024 2:17:35 PM | Mindanao Grid-08/21/2024 14:24: LAKE MAINIT Hydro online at 1406H (Unplanned Outage) [WEBSMS] | CMIN
8/21/2024 2:17:00 PM | Mindanao Grid-08/21/2024 14:23: ASIGA Hydro online at 1400H (Unplanned Outage) [WEBSMS] | CMIN
8/21/2024 1:54:19 PM | Luzon Grid-08/21/2024 13:54: Kalayaan Unit 2 online as generator at 1353H (Unplanned Outage) [WEBSMS] | CLUZ
8/21/2024 1:54:17 PM | Mindanao Grid-08/21/2024 14:00: LIANGAN Hydro Unit 1 online at 1353H. Testing/GUCT. [WEBSMS] | CMIN
8/21/2024 1:34:11 PM | Mindanao Grid-08/21/2024 13:40: LIANGAN Hydro shutdown at 1331H. Testing/GUCT. [WEBSMS] | CMIN
8/21/2024 1:29:35 PM | Mindanao Grid-08/21/2024 13:36: (Correction) WMPC DG01 online at 1326H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/21/2024 1:28:26 PM | Mindanao Grid-08/21/2024 13:34: WMPC DG01 at 1326H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/21/2024 1:18:51 PM | Luzon Grid-08/21/2024 13:19: Kalayaan Unit 2 tripped as generator at 1309H (Unplanned Outage) [WEBSMS] | CLUZ
8/21/2024 1:17:27 PM | Luzon Grid-08/21/2024 13:17: undefined at 1309H Kalayaan Unit 2 tripped as generator at 1309H (Unplanned Outage) [WEBSMS] | CLUZ
8/21/2024 1:12:47 PM | Luzon Grid-08/21/2024 13:13: Kalayan Unit 2 tripped as generator at 1309H (Unplanned Outage) [WEBSMS] | CLUZ
8/21/2024 12:41:48 PM | [NSO Update] Luzon Grid-08/21/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15137MW, PK=12719MW, RR=310MW, NetOpMargin: PM=2107, EVE=1770 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @119MW, Masinloc 1 @310MW, Masinloc 2 @100MW, Masinloc 3 @310MW [WEBSMS] | CLUZ
8/21/2024 12:32:06 PM | Mindanao Grid-08/21/2024 12:38: LAKE MAINIT Hydro (load=7MW) and ASIGA Hydro (load=4.7MW) isolated at 1206H due to tripping of Butuan-Santiago 69 kV feeder (Unplanned Outage) [WEBSMS] | CMIN
8/21/2024 12:31:25 PM | [NSO Update] Mindanao Grid-08/21/2024 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3624MW, PK=2483MW, RR=73MW, NetOpMargin: PM=1068, EVE=1160 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @48.9MW [WEBSMS] | CMIN
8/21/2024 12:29:41 PM | [NSO Update] Visayas Grid-08/21/2024 12:29: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2824MW, PK=2480MW, RR=31MW, NetOpMargin: PM=313, EVE=225 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE_A @250MW, LGPP_G01 @81.2MW, PGPP1 @75MW, CEDC_U3 @75MW, PDPP3_C @9MW, PDPP3_E @8MW, PDPP3_H @8MW, PGPP2_SOG 1 @18.5MW, GTEC @10MW, PB104_2 @5MW, PB104_3 @6MW, PB101_2 @5.5MW, PDPP1_U3 @4.5MW, PDPP1_U5 @4MW [WEBSMS] | CVIS
8/21/2024 12:08:56 PM | Mindanao Grid-08/21/2024 12:15: LAKE MAINIT Hydro online at 1203H (Unplanned Outage) [WEBSMS] | CMIN
8/21/2024 12:03:06 PM | Visayas Grid-08/21/2024 12:03: TAREC tripped at 0942H. (Unplanned Outage) [WEBSMS] | CVIS
8/21/2024 10:28:58 AM | Visayas Grid-08/21/2024 10:29: Pal 1 U2 tripped at 1025H. (Unplanned Outage) [WEBSMS] | CVIS
8/21/2024 10:04:15 AM | Visayas Grid-08/21/2024 10:04: UMPP U3 cut-in at 0945H. (Unplanned Outage) [WEBSMS] | CVIS
8/21/2024 10:01:13 AM | Mindanao Grid-08/21/2024 10:07: LIANGAN Hydro online at 0958H for GUCT. [WEBSMS] | CMIN
8/21/2024 9:58:26 AM | Mindanao Grid-08/21/2024 10:04: WMPC DG10 online at 0955H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/21/2024 9:55:23 AM | [NSO Update] Luzon Grid-08/21/2024 09:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0954H with power going to Visayas. [WEBSMS] | CLUZ
8/21/2024 9:55:04 AM | [NSO Update] Visayas Grid-08/21/2024 09:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0954H with power going to Visayas. [WEBSMS] | CVIS
8/21/2024 9:53:31 AM | [NSO Update] Visayas Grid-08/21/2024 09:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0944H from forward power direction. [WEBSMS] | CVIS
8/21/2024 9:53:12 AM | [NSO Update] Luzon Grid-08/21/2024 09:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0944H from forward power direction. [WEBSMS] | CLUZ
8/21/2024 9:33:48 AM | Mindanao Grid-08/21/2024 09:40: LIANGAN Hydro shutdown at 0931H in preparation for GUCT. [WEBSMS] | CMIN
8/21/2024 8:13:48 AM | Mindanao Grid-08/21/2024 08:20: MT. APO 1 online at 0811H (Unplanned Outage) [WEBSMS] | CMIN
8/21/2024 7:19:41 AM | Mindanao Grid-08/21/2024 07:26: LAKE MAINIT Hydro shutdown at 0701H due to critical lake level. OMC Outage (Unplanned Outage) [WEBSMS] | CMIN
8/21/2024 7:13:56 AM | Mindanao Grid-08/21/2024 07:20: Kidapawan - Mt. Apo 2 138kV L energized at 0706H. (Planned Outage) [WEBSMS] | CMIN
8/21/2024 6:07:05 AM | Luzon Grid-08/21/2024 06:07: Lumban-Malaya 230kV line 2 was de-energized at 0606H. (Planned Outage) [WEBSMS] | CLUZ
8/21/2024 6:03:32 AM | [NSO Update] Mindanao Grid-08/21/2024 06:10: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3572MW, PK=2334MW, RR=73MW, NetOpMargin: AM=1165, PM=974, EVE=1046 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW [WEBSMS] | CMIN
8/21/2024 6:01:49 AM | [NSO Update] Visayas Grid-08/21/2024 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2793MW, PK=2420MW, RR=31MW, NetOpMargin: AM=342, PM=349, EVE=275 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE_A @227MW, LGPP_G01 @81.2MW, CEDC_U3 @75MW, PDPP3_C @9MW, PDPP3_E @8MW, PDPP1_U3 @4.5MW, PDPP1_U5 @4MW, PGPP2_SOG 1 @18.5MW, PDPP3_H @8MW, PB104_2 @5MW, PB104_3 @6MW, GTEC @10MW [WEBSMS] | CVIS
8/21/2024 5:58:43 AM | [NSO Update] Luzon Grid-08/21/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15234MW, PK=11886MW, RR=350MW, NetOpMargin: AM=2998, PM=2295, EVE=1935 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @119MW, Masinloc 1 @315MW, Masinloc 2 @100MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
8/21/2024 5:42:52 AM | Mindanao Grid-08/21/2024 05:49: Matanao-Kidapawan 138kV L1 restored at 0530H. (Unplanned Outage) [WEBSMS] | CMIN
8/21/2024 5:33:03 AM | Mindanao Grid-08/21/2024 05:39: Matanao-Kidapawan 138kV L1 tripped at 0411H. (Unplanned Outage) [WEBSMS] | CMIN
8/21/2024 4:42:07 AM | [NSO Update] Mindanao Grid-08/21/2024 04:48: Weather Update: Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CMIN
8/21/2024 4:41:52 AM | [NSO Update] Visayas Grid-08/21/2024 04:42: Weather Update: Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CVIS
8/21/2024 4:41:39 AM | [NSO Update] Luzon Grid-08/21/2024 04:41: Weather Update: Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CLUZ
8/21/2024 4:24:29 AM | Mindanao Grid-08/21/2024 04:31: MAGPP1 with 36MW load tripped at 0412H. Lowest frequency recorded was 59.79Hz. (Unplanned Outage). Indication: For verification [WEBSMS] | CMIN
8/21/2024 3:46:01 AM | Visayas Grid-08/21/2024 03:46: Leyte-A UMPP U3 & U4 simultaneously tripped at 0335H. (Unplanned Outage) [WEBSMS] | CVIS
8/20/2024 10:46:28 PM | [NSO Update] Visayas Grid-08/20/2024 22:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2244H with power going to Luzon [WEBSMS] | CVIS
8/20/2024 10:46:16 PM | [NSO Update] Luzon Grid-08/20/2024 22:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2244H with power going to Luzon [WEBSMS] | CLUZ
8/20/2024 10:37:07 PM | [NSO Update] Visayas Grid-08/20/2024 22:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2232H from reverse power direction [WEBSMS] | CVIS
8/20/2024 10:36:50 PM | [NSO Update] Luzon Grid-08/20/2024 22:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2232H from reverse power direction [WEBSMS] | CLUZ
8/20/2024 9:53:17 PM | Mindanao Grid-08/20/2024 21:59: WMPC DG10 shutdown at 2146H, end of RPS - System Voltage Requirement [WEBSMS] | CMIN
8/20/2024 9:25:15 PM | Mindanao Grid-08/20/2024 21:31: AGUS 1 Unit 2 online at 2117H. (Unplanned Outage) [WEBSMS] | CMIN
8/20/2024 9:07:29 PM | Mindanao Grid-08/20/2024 21:14: Agus 1 Unit 2 with 32MW load tripped at 2047H. Lowest frequency recorded was 59.785Hz. (Unplanned Outage). Indication: For verification [WEBSMS] | CMIN
8/20/2024 7:32:34 PM | Mindanao Grid-08/20/2024 19:39: WMPC DG01 shutdown at 1931H, end of RPS - System Voltage Requirement [WEBSMS] | CMIN
8/20/2024 5:56:14 PM | Luzon Grid-08/20/2024 17:56: Lumban-Malaya 230kV line 1 was restored at 1755H. (Planned Outage) [WEBSMS] | CLUZ
8/20/2024 5:46:28 PM | [NSO Update] Mindanao Grid-08/20/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3554MW, PK=2417MW, RR=73MW, NetOpMargin: EVE=1064 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW [WEBSMS] | CMIN
8/20/2024 5:46:13 PM | [NSO Update] Visayas Grid-08/20/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2660MW, PK=2400MW, RR=31MW, NetOpMargin: EVE=229 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE_A @273MW, LGPP_G01 @81.2MW, CEDC_U3 @75MW, PDPP3_C @9MW, PDPP3_E @8MW, PDPP1_U3 @4.5MW, PDPP1_U5 @4MW, PGPP2_SOG 1 @18.5MW, PDPP3_H @8MW [WEBSMS] | CVIS
8/20/2024 5:46:01 PM | [NSO Update] Luzon Grid-08/20/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13751MW, PK=11487MW, RR=350MW, NetOpMargin: EVE=1915 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @119MW, Masinloc 1 @260MW, Masinloc 2 @100MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
8/20/2024 5:17:22 PM | Luzon Grid-08/20/2024 17:17: Limay-Batangas II (BPC) 230kV Line 2 was restored at 1716H. (Planned Outage) [WEBSMS] | CLUZ
8/20/2024 4:07:18 PM | Luzon Grid-08/20/2024 16:07: Masinloc Unit 3 runback from 320MW to 94MW due to IDF 3A trouble. The unit recovered and is now stabilizing. [WEBSMS] | CLUZ
8/20/2024 2:35:02 PM | Luzon Grid-08/20/2024 14:35: Malaya PCB 8-02CB08MAL was closed at 1422H but tripped upon closing of PCB 8-02CB24MAL. (Unplanned Outage) [WEBSMS] | CLUZ
8/20/2024 1:43:27 PM | Luzon Grid-08/20/2024 13:43: Malaya SS PCB 8-02CB24MAL and 8-02CB08MAL tripped at 1337H. (Unplanned Outage) [WEBSMS] | CLUZ
8/20/2024 1:19:40 PM | Mindanao Grid-08/20/2024 13:26: WMPC DG01 online at 1255H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/20/2024 1:03:37 PM | [NSO Update] Mindanao Grid-08/20/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3598MW, PK=2485MW, RR=73MW, NetOpMargin: PM=1040, EVE=1125 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW [WEBSMS] | CMIN
8/20/2024 1:01:33 PM | [NSO Update] Visayas Grid-08/20/2024 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2862MW, PK=2478MW, RR=354MW, NetOpMargin: PM=354, EVE=255 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE_A @270MW, LGPP_G01 @81.2MW, CEDC_U3 @75MW, PDPP3_C @9MW, PDPP3_H @8MW, PDPP1_U3 @4.5MW, PDPP1_U5 @4MW, PGPP2_SOG 1 @18.5MW, PDPP3_E @8MW [WEBSMS] | CVIS
8/20/2024 12:56:26 PM | [NSO Update] Luzon Grid-08/20/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14865MW, PK=12482MW, RR=310MW, NetOpMargin: PM=2073, EVE=1580 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @119MW, Masinloc 1 @315MW, Masinloc 2 @100MW, Masinloc 3 @325MW, Calaca 1 @220MW [WEBSMS] | CLUZ
8/20/2024 12:26:28 PM | Luzon Grid-08/20/2024 12:26: San Gabriel online at 1200H (Reserve shutdown) [WEBSMS] | CLUZ
8/20/2024 10:44:18 AM | [NSO Update] Visayas Grid-08/20/2024 10:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1040H with power going to Visayas [WEBSMS] | CVIS
8/20/2024 10:43:30 AM | [NSO Update] Luzon Grid-08/20/2024 10:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1040H with power going to Visayas [WEBSMS] | CLUZ
8/20/2024 10:41:28 AM | [NSO Update] Visayas Grid-08/20/2024 10:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1030H from forward power direction [WEBSMS] | CVIS
8/20/2024 10:40:48 AM | [NSO Update] Luzon Grid-08/20/2024 10:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1030H from forward power direction [WEBSMS] | CLUZ
8/20/2024 9:13:42 AM | Mindanao Grid-08/20/2024 09:20: WMPC DG10 online at 0859H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/20/2024 7:22:58 AM | Luzon Grid-08/20/2024 07:23: Limay-Batangas II (BPC) 230kV Line 2 de-energized at 0723H (Planned Outage) [WEBSMS] | CLUZ
8/20/2024 6:46:12 AM | Luzon Grid-08/20/2024 06:46: San Manuel-UPSI San Manuel BESS 69kV Line (CO) de-energized at 0645H (Planned Outage) [WEBSMS] | CLUZ
8/20/2024 6:37:51 AM | Luzon Grid-08/20/2024 06:38: Lumban-Malaya 230kV Line 1 de-energized at 0637H (Planned Outage) [WEBSMS] | CLUZ
8/20/2024 6:04:14 AM | [NSO Update] Mindanao Grid-08/20/2024 06:10: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3609MW, PK=2389MW, RR=73MW, NetOpMargin: AM=1146, PM=1058, EVE=1140 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW [WEBSMS] | CMIN
8/20/2024 6:02:04 AM | [NSO Update] Luzon Grid-08/20/2024 06:02: Correction: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14884MW, PK=11549MW, RR=310MW, NetOpMargin: AM=3025, PM=1769, EVE=1275 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @119MW, Masinloc 1 @320MW, Masinloc 2 @100MW, Masinloc 3 @320MW, Calaca 1 @220MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/20/2024 5:59:29 AM | [NSO Update] Visayas Grid-08/20/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2820MW, PK=2337MW, RR=31MW, NetOpMargin: AM=452, PM=378, EVE=297 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE_A @273MW, LGPP_G01 @81.2MW, CEDC_U3 @75MW, PDPP3_C @9MW, PDPP3_H @8MW, PDPP1_U3 @4.5MW, PDPP1_U4 @3.5MW, PGPP2_SOG 1 @18.5MW [WEBSMS] | CVIS
8/20/2024 5:52:25 AM | [NSO Update] Luzon Grid-08/20/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14884MW, PK=11549MW, RR=310MW, NetOpMargin: AM=3025, PM=1769, EVE=1275 Highest Unit O/L: GNPD 1 @151.9MW Derated Plant: SLTEC 2 @119MW, Masinloc 1 @320MW, Masinloc 2 @100MW, Masinloc 3 @320MW, Calaca 1 @220MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/20/2024 4:44:37 AM | [NSO Update] Mindanao Grid-08/20/2024 04:51: Weather Update: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 1,030 km East Northeast of Extreme Northern Luzon (22.7 N, 131.6 E). Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CMIN
8/20/2024 4:44:05 AM | [NSO Update] Visayas Grid-08/20/2024 04:44: Weather Update: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 1,030 km East Northeast of Extreme Northern Luzon (22.7 N, 131.6 E). Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CVIS
8/20/2024 4:43:11 AM | [NSO Update] Luzon Grid-08/20/2024 04:43: Weather Update: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 1,030 km East Northeast of Extreme Northern Luzon (22.7 N, 131.6 E). Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
8/20/2024 3:57:19 AM | Luzon Grid-08/20/2024 03:57: Gardner - Taguig 115kV Line restored at 0354H (Unplanned Outage) [WEBSMS] | CLUZ
8/20/2024 3:07:34 AM | Luzon Grid-08/20/2024 03:07: For info: Commissioning of Muntinlupa 50MVAR Capacitor Bank No. 1 (New Main 1 Protection) completed at 0259H [WEBSMS] | CLUZ
8/20/2024 2:37:52 AM | Luzon Grid-08/20/2024 02:38: San Gabriel shutdown at 0229H (Reserved Shutdown) [WEBSMS] | CLUZ
8/20/2024 1:10:45 AM | Luzon Grid-08/20/2024 01:11: Gardner-Taguig 115kV Line de-energized at 0108H (Unplanned Outage) [WEBSMS] | CLUZ
8/19/2024 11:59:00 PM | Visayas Grid-08/19/2024 23:59: Toledo - Carmen 34.5 kV Line 2 energized at 2314H (Planned Outage) [WEBSMS] | CVIS
8/19/2024 11:24:16 PM | Luzon Grid-08/19/2024 23:24: Bacman-Palayan Binary Plant 230kV Tie Line energized at 2321H (Planned Outage) [WEBSMS] | CLUZ
8/19/2024 9:59:59 PM | [NSO Update] Visayas Grid-08/19/2024 22:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2153H with power going to Luzon. [WEBSMS] | CVIS
8/19/2024 9:59:54 PM | [NSO Update] Luzon Grid-08/19/2024 22:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2153H with power going to Luzon. [WEBSMS] | CLUZ
8/19/2024 9:47:50 PM | Mindanao Grid-08/19/2024 21:54: WMPC DG01 shutdown at 2146H, end of RPS - System Voltage Requirement [WEBSMS] | CMIN
8/19/2024 9:44:42 PM | [NSO Update] Visayas Grid-08/19/2024 21:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2143H from reverse power direction. [WEBSMS] | CVIS
8/19/2024 9:44:39 PM | [NSO Update] Luzon Grid-08/19/2024 21:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2143H from reverse power direction. [WEBSMS] | CLUZ
8/19/2024 5:51:16 PM | [NSO Update] Luzon Grid-08/19/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13738MW, PK=10925MW, RR=397MW, NetOpMargin: EVE=2416 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: SLTEC 2 @119MW, Masinloc 1 @315MW, Masinloc 2 @150MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
8/19/2024 5:51:10 PM | [NSO Update] Mindanao Grid-08/19/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3502MW, PK=2416MW, RR=73MW, NetOpMargin: EVE=1013 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW [WEBSMS] | CMIN
8/19/2024 5:51:03 PM | [NSO Update] Visayas Grid-08/19/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2635MW, PK=2307MW, RR=31MW, NetOpMargin: EVE=297 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: LEYTE_A @273MW, LGPP_G01 @81.2MW, CEDC_U3 @75MW, PDPP3_C @9MW, PDPP3_H @8MW [WEBSMS] | CVIS
8/19/2024 5:18:39 PM | Mindanao Grid-08/19/2024 17:25: WMPC DG01 shutdown at 1716H end of RPS - System Voltage Requirement [WEBSMS] | CMIN
8/19/2024 3:45:08 PM | Luzon Grid-08/19/2024 15:45: Mexico-San Rafael 230kV L1 restored at 1544H (Unplanned Outage) [WEBSMS] | CLUZ
8/19/2024 3:32:36 PM | Luzon Grid-08/19/2024 15:32: Mexico-San Rafael 230kV L1 tripped at 1529H (Unplanned Outage) [WEBSMS] | CLUZ
8/19/2024 3:29:43 PM | Visayas Grid-08/19/2024 15:29: Amlan-Palinpinon 1 138kV Line 1 energized at 1528H. (Unplanned Outage) [WEBSMS] | CVIS
8/19/2024 12:59:44 PM | Mindanao Grid-08/19/2024 13:06: WMPC DG01 online at 1256H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/19/2024 12:56:15 PM | [NSO Update] Luzon Grid-08/19/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14744MW, PK=12584MW, RR=389MW, NetOpMargin: PM=1771, EVE=1541 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: SLTEC 2 @119MW, Masinloc 1 @315MW, Masinloc 2 @150MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
8/19/2024 12:53:43 PM | [NSO Update] Mindanao Grid-08/19/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3461MW, PK=2596MW, RR=73MW, NetOpMargin: PM=792, EVE=874 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW [WEBSMS] | CMIN
8/19/2024 12:51:48 PM | [NSO Update] Visayas Grid-08/19/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2747MW, PK=2468MW, RR=31MW, NetOpMargin: PM=247, EVE=233 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: CLBYBNK_G01 @10MW, LEYTE_A @273MW, LGPP_G01 @81.2MW, CEDC_U03 @75MW, PAL2A_U01 @18.5MW, TPLPB4_U02 @5MW, TPLPB4_U03 @6MW, PDPP1_U02 @3.5MW, PDPP1_U03 @4.5MW, PDPP1_U05 @3.5MW, PDPP3_C @9MW, PDPP3_H @8MW, STBPB1_U02 @5.5MW [WEBSMS] | CVIS
8/19/2024 12:27:52 PM | Visayas Grid-08/19/2024 12:28: Cadiz - Gahit 230 kV Line 2 tripped/reclosed at 1218H (Unplanned Outage) [WEBSMS] | CVIS
8/19/2024 11:37:02 AM | Mindanao Grid-08/19/2024 11:43: TSI Unit 2 online at 1121H. (Unplanned Outage) [WEBSMS] | CMIN
8/19/2024 11:20:06 AM | [NSO Update] Mindanao Grid-08/19/2024 11:26: Weather Disturbance Alert Notice (WDAN) for Tropical Depression now Tropical Storm DINDO has been lifted today, August 19, 2024, at 1100H, as it is now outside the Philippine Area of Responsibility (PAR). The center of Tropical Storm DINDO was estimated based on all available data at 670 km Northeast of Itbayat, Batanes (OUTSIDE PAR) (25.3 �N, 126.2 �E ). [WEBSMS] | CMIN
8/19/2024 11:19:16 AM | [NSO Update] Luzon Grid-08/19/2024 11:19: Weather Disturbance Alert Notice (WDAN) for Tropical Depression now Tropical Storm DINDO has been lifted today, August 19, 2024, at 1100H, as it is now outside the Philippine Area of Responsibility (PAR). The center of Tropical Storm DINDO was estimated based on all available data at 670 km Northeast of Itbayat, Batanes (OUTSIDE PAR) (25.3 �N, 126.2 �E ). [WEBSMS] | CLUZ
8/19/2024 11:18:46 AM | [NSO Update] Visayas Grid-08/19/2024 11:18: Weather Disturbance Alert Notice (WDAN) for Tropical Depression now Tropical Storm DINDO has been lifted today, August 19, 2024, at 1100H, as it is now outside the Philippine Area of Responsibility (PAR). The center of Tropical Storm DINDO was estimated based on all available data at 670 km Northeast of Itbayat, Batanes (OUTSIDE PAR) (25.3 �N, 126.2 �E ). [WEBSMS] | CVIS
8/19/2024 11:15:08 AM | [NSO Update] Luzon Grid-08/19/2024 11:15: Weather Disturbance Alert Notice (WDAN) for Torpical Depression now Tropical Storm DINDO has been lifted today, August 19, 2024, at 1100H, as it is now outside the Philippine Area of Responsibility (PAR). The center of Tropical Storm DINDO was estimated based on all available data at 670 km Northeast of Itbayat, Batanes (OUTSIDE PAR) (25.3 �N, 126.2 �E ). [WEBSMS] | CLUZ
8/19/2024 11:00:13 AM | Luzon Grid-08/19/2024 11:00: San Gabriel online at 1059H. (From Reserve Shutdown) [WEBSMS] | CLUZ
8/19/2024 10:57:54 AM | Luzon Grid-08/19/2024 10:58: San Jose-Taytay 230kV line 1 auto-tripped/auto-reclosed at 1050H. (Unplanned Outage) [WEBSMS] | CLUZ
8/19/2024 10:55:06 AM | [NSO Update] Visayas Grid-08/19/2024 10:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1052H with power going to Visayas. [WEBSMS] | CVIS
8/19/2024 10:54:53 AM | [NSO Update] Luzon Grid-08/19/2024 10:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1052H with power going to Visayas. [WEBSMS] | CLUZ
8/19/2024 10:43:58 AM | [NSO Update] Visayas Grid-08/19/2024 10:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1042H from forward power direction. [WEBSMS] | CVIS
8/19/2024 10:43:07 AM | [NSO Update] Luzon Grid-08/19/2024 10:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1042H from forward power direction. [WEBSMS] | CLUZ
8/19/2024 9:54:07 AM | Mindanao Grid-08/19/2024 10:00: WMPC DG10 online at 0950H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/19/2024 8:38:46 AM | Visayas Grid-08/19/2024 08:38: Toledo - Carmen 34.5 kV Line 2 de-energized at 0836H (Planned Outage) [WEBSMS] | CVIS
8/19/2024 8:26:48 AM | Visayas Grid-08/19/2024 08:27: Kabankalan SS 30 MVA 138/69/13.8 kV TR1 de-energized at 0826H (Planned Outage) [WEBSMS] | CVIS
8/19/2024 6:17:19 AM | Visayas Grid-08/19/2024 06:17: Gahit - Barotac Viejo 230 kV Line 1 de-energized at 0616H (Planned Outage) [WEBSMS] | CVIS
8/19/2024 5:53:19 AM | [NSO Update] Mindanao Grid-08/19/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3409MW, PK=2340MW, RR=73MW, NetOpMargin: AM=996, PM=920, EVE=983 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW [WEBSMS] | CMIN
8/19/2024 5:52:02 AM | [NSO Update] Visayas Grid-08/19/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2799MW, PK=2415MW, RR=31MW, NetOpMargin: AM=353, PM=352, EVE=229 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: LEYTE_A @270MW, LGPP_G01 @81.2MW, CEDC_U03 @75MW, PDPP3_C @9MW, PDPP3_H @8MW [WEBSMS] | CVIS
8/19/2024 5:50:07 AM | [NSO Update] Luzon Grid-08/19/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15022MW, PK=11997MW, RR=382MW, NetOpMargin: AM=2642, PM=2082, EVE=1647 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: SLTEC 2 @119MW, Masinloc 1 @315MW, Masinloc 2 @150MW, Masinloc 3 @315MW [WEBSMS] | CLUZ
8/19/2024 4:46:16 AM | [NSO Update] Luzon Grid-08/19/2024 04:46: Weather Advisory: At 3:00 AM today, the center of Tropical Storm "DINDO" {JONGDARI} was estimated based on all available data at 635 km Northeast of Itbayat, Batanes (24.9�N, 126.1�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving Northeastward at 10 km/h. Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
8/19/2024 4:45:47 AM | [NSO Update] Luzon Grid-08/19/2024 04:45: Weather Advisory: At 3:00 AM today, the center of Tropical Storm "DINDO" {JONGDARI} was estimated based on all available data at 635 km Northeast of Itbayat, Batanes (24.9�N, 126.1�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving Northeastward at 10 km/h. Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
8/19/2024 4:21:59 AM | Mindanao Grid-08/19/2024 04:28: Nasipit-Therma Marine 2 138kV Line 2 (7LI2NAS-TM2) energized/restored at 0411H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/19/2024 4:20:18 AM | Mindanao Grid-08/19/2024 04:26: Nasipit SS Power Transformer No. ,100 MVA (7XF01NAS) energized/restored at 0410H. Planned Outage /Non-GOMP. [WEBSMS] | CMIN
8/19/2024 4:19:39 AM | [NSO Update] Mindanao Grid-08/19/2024 04:26: Weather Advisory: At 3:00 AM today, the center of Tropical Storm "DINDO" {JONGDARI} was estimated based on all available data at 635 km Northeast of Itbayat, Batanes (24.9�N, 126.1�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving Northeastward at 10 km/h. Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CMIN
8/19/2024 4:19:25 AM | [NSO Update] Visayas Grid-08/19/2024 04:19: Weather Advisory: At 3:00 AM today, the center of Tropical Storm "DINDO" {JONGDARI} was estimated based on all available data at 635 km Northeast of Itbayat, Batanes (24.9�N, 126.1�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving Northeastward at 10 km/h. Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CVIS
8/19/2024 4:18:41 AM | Mindanao Grid-08/19/2024 04:25: Nasipit SS 138 kV Bus 1(7BS01NAS) energized/restored at 0408H. Planned Outage/Non-GOMP [WEBSMS] | CMIN
8/19/2024 3:30:04 AM | Luzon Grid-08/19/2024 03:30: San Gabriel shutdown at 0328H. (Reserve Shutdown) [WEBSMS] | CLUZ
8/19/2024 2:30:56 AM | Visayas Grid-08/19/2024 02:31: Pal 1 U2 cut-in at 0229H. (Unplanned Outage) [WEBSMS] | CVIS
8/19/2024 2:29:43 AM | Visayas Grid-08/19/2024 02:29: Pal 1 U3 cut-in at 0227H. (Unplanned Outage) [WEBSMS] | CVIS
8/19/2024 2:10:28 AM | Visayas Grid-08/19/2024 02:10: Pal 1 U1 cut-in at 0208H. (Unplanned Outage) [WEBSMS] | CVIS
8/19/2024 1:22:20 AM | Mindanao Grid-08/19/2024 01:28: Nasipit SS 138 kV Bus 1(7BS01NAS) de-energized at 0117H. Planned Outage/Non-GOMP [WEBSMS] | CMIN
8/19/2024 1:20:51 AM | Mindanao Grid-08/19/2024 01:27: Nasipit SS Power Transformer No. , 100 MVA (7XF01NAS) de-energized at 0116H. Planned Outage /Non-GOMP. [WEBSMS] | CMIN
8/19/2024 12:36:36 AM | [NSO Update] Mindanao Grid-08/19/2024 00:43: Weather Disturbance Alert Notice (WDAN) is issued at 2300H. The Low-Pressure Area East of Taiwan has developed into Tropical Depression "DINDO". The center was estimated based on all available data 560 km Northeast of Itbayat, Batanes (24.7 �N, 125.3 �E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving Westward at 20 km/h. [WEBSMS] | CMIN
8/19/2024 12:36:21 AM | [NSO Update] Visayas Grid-08/19/2024 00:36: Weather Disturbance Alert Notice (WDAN) is issued at 2300H. The Low-Pressure Area East of Taiwan has developed into Tropical Depression "DINDO". The center was estimated based on all available data 560 km Northeast of Itbayat, Batanes (24.7 �N, 125.3 �E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving Westward at 20 km/h. [WEBSMS] | CVIS
8/19/2024 12:36:00 AM | [NSO Update] Luzon Grid-08/19/2024 00:36: Weather Disturbance Alert Notice (WDAN) is issued at 2300H. The Low-Pressure Area East of Taiwan has developed into Tropical Depression "DINDO". The center was estimated based on all available data 560 km Northeast of Itbayat, Batanes (24.7 �N, 125.3 �E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving Westward at 20 km/h. [WEBSMS] | CLUZ
8/19/2024 12:07:35 AM | Visayas Grid-08/19/2024 00:07: Amlan-Palinpinon 1 138kV Line 1 tripped at 2352H. (Unplanned Outage) [WEBSMS] | CVIS
8/19/2024 12:04:40 AM | Visayas Grid-08/19/2024 00:04: Pal 1 Units 1, 2 and 3 tripped at 2352H. (Unplanned Outage) [WEBSMS] | CVIS
8/19/2024 12:00:30 AM | Visayas Grid-08/19/2024 00:00: Amlan-Palinpinon 1 Line 1 tripped at 2352H. (Unplanned Outage) [WEBSMS] | CVIS
8/18/2024 10:06:20 PM | Luzon Grid-08/18/2024 22:06: For info: Energization of Tugegarao 8-03CB04TUG & 8-03CB24TUG stub protection completed at 2203H [WEBSMS] | CLUZ
8/18/2024 8:28:17 PM | Luzon Grid-08/18/2024 20:28: Binan-Balibago 115kV line restored at 2027H (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 6:07:58 PM | Luzon Grid-08/18/2024 18:07: Muntinlupa 115kV Bus 2 restored at 1807H (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 5:58:01 PM | [NSO Update] Mindanao Grid-08/18/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3334MW, PK=2185MW, RR=73MW, NetOpMargin: EVE=1076 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW [WEBSMS] | CMIN
8/18/2024 5:54:50 PM | [NSO Update] Visayas Grid-08/18/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2526MW, PK=2176MW, RR=31MW, NetOpMargin: EVE=319 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: PAL2A_U01 @18.5MW, LEYTE_A @258MW, LGPP_G01 @81.2MW, CEDC_U03 @75MW, PDPP1_U02 @3.5MW, PDPP1_U03 @4.5MW, PDPP1_U05 @4MW, PDPP3_C @9MW, PDPP3_H @8MW, STBPB1_U02 @5.5MW, CLBYBNK_G01 @10MW, TPLPB4_U02 @5MW, TPLPB4_U03 @6MW [WEBSMS] | CVIS
8/18/2024 5:52:00 PM | [NSO Update] Luzon Grid-08/18/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13887MW, PK=11292MW, RR=310MW, NetOpMargin: EVE=2285 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: SLTEC 2 @119MW, Masinloc 1 @315MW, Masinloc 2 @150MW, Masinloc 3 @305MW, Calaca 1 @180MW [WEBSMS] | CLUZ
8/18/2024 5:41:31 PM | Mindanao Grid-08/18/2024 17:47: TM2 Unit 1 shutdown at 1725H. End of MRU-Thermal Limit. [WEBSMS] | CMIN
8/18/2024 5:25:58 PM | Luzon Grid-08/18/2024 17:26: Tuguegarao 230kV Bus 1 restored at 1725H (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 5:19:45 PM | Visayas Grid-08/18/2024 17:19: TVI unit 2 tripped at 1713H. (Unplanned Outage) [WEBSMS] | CVIS
8/18/2024 5:12:35 PM | Mindanao Grid-08/18/2024 17:19: Villanueva-Jasaan 138 kV L2 energized/restored at 1707H. Planned Outage/GOMP [WEBSMS] | CMIN
8/18/2024 5:00:18 PM | Luzon Grid-08/18/2024 17:00: San Gabriel online at 1659H (Reserve Shutdown) [WEBSMS] | CLUZ
8/18/2024 4:48:47 PM | Visayas Grid-08/18/2024 16:48: Colon SS 138 kV Bus 1 energized at 1642H (Planned Outage) [WEBSMS] | CVIS
8/18/2024 4:48:04 PM | Luzon Grid-08/18/2024 16:48: San Jose-Tayabas 500kV Line 1 restored at 1647H (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 4:21:03 PM | Luzon Grid-08/18/2024 16:21: Binga-La Trinidad 230kV line 2 restored at 1620H (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 3:30:14 PM | [NSO Update] Visayas Grid-08/18/2024 15:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1529H with power going to Luzon. (Planned outage) [WEBSMS] | CVIS
8/18/2024 3:30:08 PM | [NSO Update] Luzon Grid-08/18/2024 15:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1529H with power going to Luzon. (Planned outage) [WEBSMS] | CLUZ
8/18/2024 2:21:48 PM | Luzon Grid-08/18/2024 14:21: Muntinlupa 115kV Bus 2 de-energized at 1420H (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 2:15:32 PM | Luzon Grid-08/18/2024 14:15: Muntinlupa 115kV Bus 1 restored at 1413H (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 12:48:42 PM | [NSO Update] Luzon Grid-08/18/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14616MW, PK=10708MW, RR=333MW, NetOpMargin: PM=3575, EVE=2420 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Masinloc 1 @315MW, Masinloc 2 @150MW, Masinloc 3 @315MW [WEBSMS] | CLUZ
8/18/2024 12:48:17 PM | [NSO Update] Visayas Grid-08/18/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2611MW, PK=1964MW, RR=31MW, NetOpMargin: PM=615, EVE=306 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: PAL2A_U01 @18.5MW, LEYTE_A @258MW, LGPP_G01 @81.2MW, CEDC_U03 @75MW, TPC 1A (Thermal) @45MW, PDPP1_U02 @3.5MW, PDPP1_U05 @4MW, PDPP3_C @9MW, PDPP3_H @8MW, STBPB1_U02 @5.5MW, CLBYBNK_G01 @10MW, TPLPB4_U02 @5MW, TPLPB4_U03 @6MW [WEBSMS] | CVIS
8/18/2024 12:48:09 PM | [NSO Update] Mindanao Grid-08/18/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3381MW, PK=1979MW, RR=73MW, NetOpMargin: PM=1329, EVE=1101 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW [WEBSMS] | CMIN
8/18/2024 9:24:20 AM | Mindanao Grid-08/18/2024 09:30: TM2 Unit 1 online at 0916H. MRU-Thermal Limit. [WEBSMS] | CMIN
8/18/2024 9:04:46 AM | Luzon Grid-08/18/2024 09:04: Marilao 300MVA T01(CO) was de-energized at 0849H. (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 8:43:59 AM | Visayas Grid-08/18/2024 08:44: TPC1-A cut-in at 0840H (Unplanned Outage) [WEBSMS] | CVIS
8/18/2024 8:27:03 AM | Luzon Grid-08/18/2024 08:27: Pagbilao EHV 1000MVA T02 was de-energized at 0825H. (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 8:17:59 AM | Luzon Grid-08/18/2024 08:18: Muntinlupa 115kV Bus 1 was de-energized at 0816H. (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 8:06:25 AM | Luzon Grid-08/18/2024 08:06: Binga-La Trinidad 230kV line 2 was de-energized at 0806H. (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 7:47:47 AM | Luzon Grid-08/18/2024 07:47: Binan-Balibago 115kV line was de-energized at 0747H. (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 7:31:09 AM | Luzon Grid-08/18/2024 07:31: San Gabriel shutdown at 0729H. (Reserve Shutdown) [WEBSMS] | CLUZ
8/18/2024 7:13:16 AM | Visayas Grid-08/18/2024 07:13: Colon SS 138 kV Bus 1 de-energized at 0658H (Planned Outage) [WEBSMS] | CVIS
8/18/2024 7:00:58 AM | [NSO Update] Luzon Grid-08/18/2024 07:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0647H from forward power direction. [WEBSMS] | CLUZ
8/18/2024 7:00:46 AM | [NSO Update] Visayas Grid-08/18/2024 07:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0647H from forward power direction. [WEBSMS] | CVIS
8/18/2024 6:35:16 AM | Mindanao Grid-08/18/2024 06:41: Villanueva-Jasaan 138 kV L2 de-energized at 0632H. Planned Outage/GOMP [WEBSMS] | CMIN
8/18/2024 5:48:41 AM | [NSO Update] Mindanao Grid-08/18/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3387MW, PK=1891MW, RR=73MW, NetOpMargin: AM=1423, PM=1281, EVE=1068 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW [WEBSMS] | CMIN
8/18/2024 5:46:15 AM | [NSO Update] Visayas Grid-08/18/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2624MW, PK=1937MW, RR=31MW, NetOpMargin: AM=656, PM=608, EVE=238 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: PAL2A_U01 @18.5MW, LEYTE_A @258MW, LGPP_G01 @81.2MW, CEDC_U03 @75MW, KSPC_G02 @70MW, PDPP1_U02 @3.5MW, PDPP1_U05 @4MW, PDPP3_C @9MW, PDPP3_H @8MW, STBPB1_U02 @5.5MW, CLBYBNK_G01 @10MW, TPLPB4_U02 @5MW, TPLPB4_U03 @6MW [WEBSMS] | CVIS
8/18/2024 5:44:05 AM | [NSO Update] Luzon Grid-08/18/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14807MW, PK=10334MW, RR=325MW, NetOpMargin: AM=4147, PM=4012, EVE=2922 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @118MW, Masinloc 1 @315MW, Masinloc 2 @150MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
8/18/2024 5:34:51 AM | Luzon Grid-08/18/2024 05:34: Tuguegarao SS 230kV Bus 1 de-energized at 0534H (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 5:06:58 AM | Luzon Grid-08/18/2024 05:06: San Jose-Tayabas 500kV Line 1 de-energized at 0506H (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 4:52:42 AM | [NSO Update] Mindanao Grid-08/18/2024 04:59: Weather Update: Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CMIN
8/18/2024 4:52:29 AM | [NSO Update] Visayas Grid-08/18/2024 04:52: Weather Update: Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CVIS
8/18/2024 4:52:21 AM | [NSO Update] Luzon Grid-08/18/2024 04:52: Weather Update: Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
8/18/2024 2:11:49 AM | Visayas Grid-08/18/2024 02:11: Compostela-Consolacion 69kV line tripped/auto-reclosed at 0209H. (Unplanned Outage) [WEBSMS] | CVIS
8/18/2024 1:16:47 AM | Luzon Grid-08/18/2024 01:16: Tayabas SS 500kV Bus 1 restored at 0115H (Planned Outage) [WEBSMS] | CLUZ
8/18/2024 1:14:50 AM | Visayas Grid-08/18/2024 01:14: Daanbantayan-Lanao 69kV line tripped/auto-reclosed at 0104H (Unplanned Outage) [WEBSMS] | CVIS
8/18/2024 12:28:23 AM | Luzon Grid-08/18/2024 00:28: Binan SS 300MVA T02 restored at 0028H (Planned Outage) [WEBSMS] | CLUZ
8/17/2024 11:31:11 PM | Mindanao Grid-08/17/2024 23:37: Matanao-Kidapawan 138kV Line 1 energized 2328H (Planned Outage). [WEBSMS] | CMIN
8/17/2024 11:01:31 PM | Visayas Grid-08/17/2024 23:01: Malitbog U1 tripped at 2256H. (Unplanned Outage) [WEBSMS] | CVIS
8/17/2024 10:48:53 PM | [NSO Update] Visayas Grid-08/17/2024 22:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2245H with power going to Luzon [WEBSMS] | CVIS
8/17/2024 10:48:13 PM | [NSO Update] Luzon Grid-08/17/2024 22:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2245H with power going to Luzon [WEBSMS] | CLUZ
8/17/2024 10:32:33 PM | [NSO Update] Visayas Grid-08/17/2024 22:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2231H from reverse power direction [WEBSMS] | CVIS
8/17/2024 10:32:08 PM | [NSO Update] Luzon Grid-08/17/2024 22:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2231H from reverse power direction [WEBSMS] | CLUZ
8/17/2024 9:43:09 PM | Mindanao Grid-08/17/2024 21:49: WMPC DG10 shutdown at 2141H end of RPS - System Voltage Requirement [WEBSMS] | CMIN
8/17/2024 8:35:14 PM | Luzon Grid-08/17/2024 20:35: Tayabas SS 500kV Bus 1 de-energized at 2034H (Planned Outage) [WEBSMS] | CLUZ
8/17/2024 6:15:02 PM | Mindanao Grid-08/17/2024 18:21: Lamsan Biomass with 13.7MW gross generation, isolated/tripped at 1718H. Affected by the tripping of Kibawe-Sultan Kudarat 138kV Line. Restored at 1804H. Unplanned Outage. [WEBSMS] | CMIN
8/17/2024 6:14:04 PM | [NSO Update] Visayas Grid-08/17/2024 18:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1759H with power going to Visayas [WEBSMS] | CVIS
8/17/2024 6:13:52 PM | [NSO Update] Luzon Grid-08/17/2024 18:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1759H with power going to Visayas [WEBSMS] | CLUZ
8/17/2024 6:13:10 PM | [NSO Update] Visayas Grid-08/17/2024 18:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1749H from forward power direction [WEBSMS] | CVIS
8/17/2024 6:12:55 PM | [NSO Update] Luzon Grid-08/17/2024 18:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1749H from forward power direction [WEBSMS] | CLUZ
8/17/2024 6:12:19 PM | [NSO Update] Mindanao Grid-08/17/2024 18:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3258MW, PK=2324MW, RR=73MW, NetOpMargin: EVE=861 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW [WEBSMS] | CMIN
8/17/2024 6:11:25 PM | [NSO Update] Visayas Grid-08/17/2024 18:11: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2576MW, PK=2238MW, RR=89MW, NetOpMargin: EVE=249 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: PAL2A_U01 @18.5MW, LEYTE_A @333MW, LGPP_G01 @66.5MW, CEDC_U03 @75MW, PDPP1_U02 @3.5MW, PDPP1_U05 @4MW, PDPP3_C @9MW, PDPP3_E @8MW, PDPP3_H @8MW, PB101-U2 @5.5MW, GTEC @10MW, PB104-U2 @5MW, PB104-U3 @6MW [WEBSMS] | CVIS
8/17/2024 6:08:45 PM | [NSO Update] Luzon Grid-08/17/2024 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13518MW, PK=11478MW, RR=397MW, NetOpMargin: EVE=1643 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @118MW, Masinloc 1 @315MW, Masinloc 2 @150MW [WEBSMS] | CLUZ
8/17/2024 6:05:44 PM | Mindanao Grid-08/17/2024 18:12: Davao-Kibawe 138kV Line energized/restored at 1753H. Planned Outage. [WEBSMS] | CMIN
8/17/2024 5:59:31 PM | Mindanao Grid-08/17/2024 18:05: Sultan Kudarat SS was isolated/Loss of Power at 1718H due to Forced Outage of Kibawe-Sultan Kudarat 138kV Line. Restored/Normalized at 1727H. Unplanned Outage. [WEBSMS] | CMIN
8/17/2024 5:53:16 PM | Mindanao Grid-08/17/2024 17:59: Kibawe-Sultan Kudarat 138kV Line tripped at 1718H. Auto-reclosed at Kibawe SS side only at 1718H also. Indications: Kibawe SS (M1) Ph.C, Dist=45.4Km. (M2) ZONE 1: A,N, Dist=None. Sultan Kudarat SS (M1) DTT Operate. Line restored at 1727H. Unplanned Outage. [WEBSMS] | CMIN
8/17/2024 5:11:05 PM | Luzon Grid-08/17/2024 17:11: For info: BFR Protection for Tayabas PCB 9-05CB04TAY and 9-05CB24TAY successfully commissioned at 1706H. [WEBSMS] | CLUZ
8/17/2024 5:09:17 PM | Visayas Grid-08/17/2024 17:09: Colon SS 138 kV bus 1 energized at 1635H (Planned Outage) [WEBSMS] | CVIS
8/17/2024 5:05:04 PM | Visayas Grid-08/17/2024 17:05: Cebu SS 100 MVA TR2 energized at 1644H (Planned Outage) [WEBSMS] | CVIS
8/17/2024 5:02:18 PM | Luzon Grid-08/17/2024 17:02: Tayabas-Pagbilao EHV 500kV Line 2 restored at 1700H (Planned Outage) [WEBSMS] | CLUZ
8/17/2024 4:16:17 PM | Luzon Grid-08/17/2024 16:16: Salong 230kV Bus 1 energized at 1615H (Planned Outage) [WEBSMS] | CLUZ
8/17/2024 4:11:43 PM | Mindanao Grid-08/17/2024 16:18: Libertad Power (LPE) online at 1604H (Unplanned Outage) [WEBSMS] | CMIN
8/17/2024 4:01:29 PM | Luzon Grid-08/17/2024 16:01: San Gabriel online at 1559H (Reserve Shutdown) [WEBSMS] | CLUZ
8/17/2024 3:12:37 PM | Visayas Grid-08/17/2024 15:12: DaanLungsod SS bus 1 energized at 1501H (Planned Outage) [WEBSMS] | CVIS
8/17/2024 12:54:59 PM | Mindanao Grid-08/17/2024 13:01: Nasipit SS 138kV 100MVA Transformer No.1 energized/restored at 1251H. Planned Outage. [WEBSMS] | CMIN
8/17/2024 12:53:29 PM | Mindanao Grid-08/17/2024 12:59: Nasipit SS 138kV Bus No.1 energized/restored at 1250H. Planned Outage. [WEBSMS] | CMIN
8/17/2024 12:40:39 PM | [NSO Update] Mindanao Grid-08/17/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3299MW, PK=2262MW, RR=73MW, NetOpMargin: PM=964, EVE=881 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW [WEBSMS] | CMIN
8/17/2024 12:39:19 PM | [NSO Update] Visayas Grid-08/17/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2701MW, PK=2204MW, RR=86MW, NetOpMargin: PM=411, EVE=257 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: PAL2A_U01 @18.5MW, LEYTE_A @333MW, LGPP_G01 @66.5MW, CEDC_U03 @75MW, PDPP1_U02 @3.5MW, PDPP1_U05 @4MW, PDPP3_E @8MW, PDPP3_H @8MW, PB101-U2 @5.5MW, GTEC @10MW, PB104-U2 @5MW, PB104-U3 @6MW, PB104-U4 @7MW [WEBSMS] | CVIS
8/17/2024 12:36:02 PM | [NSO Update] Luzon Grid-08/17/2024 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14712MW, PK=11528MW, RR=429MW, NetOpMargin: PM=2755, EVE=1924 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: SLTEC 2 @118MW, Ilijan B @450MW, Masinloc 1 @315MW, Masinloc 2 @150MW [WEBSMS] | CLUZ
8/17/2024 12:34:26 PM | Visayas Grid-08/17/2024 12:34: Colon-CVC 69 kV Line energized at 1231H (Unplanned Outage) [WEBSMS] | CVIS
8/17/2024 11:58:09 AM | Visayas Grid-08/17/2024 11:58: Colon-CVC 69 kV Line tripped at 1153H (Unplanned Outage) [WEBSMS] | CVIS
8/17/2024 11:27:26 AM | Luzon Grid-08/17/2024 11:27: Nagsaag-Binga 230kV Line 1 restored at 1127H (Planned Outage) [WEBSMS] | CLUZ
8/17/2024 10:50:08 AM | [NSO Update] Visayas Grid-08/17/2024 10:50: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1044H with power going to Luzon. [WEBSMS] | CVIS
8/17/2024 10:49:53 AM | [NSO Update] Luzon Grid-08/17/2024 10:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1044H with power going to Luzon. [WEBSMS] | CLUZ
8/17/2024 10:35:49 AM | [NSO Update] Visayas Grid-08/17/2024 10:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1034H from reverse power direction. [WEBSMS] | CVIS
8/17/2024 10:35:31 AM | [NSO Update] Luzon Grid-08/17/2024 10:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1034H from reverse power direction. [WEBSMS] | CLUZ
8/17/2024 10:23:42 AM | Mindanao Grid-08/17/2024 10:30: online at 1019H WMPC DG10 online at 1019H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/17/2024 9:46:35 AM | Mindanao Grid-08/17/2024 09:52: Kidapawan-Mt. Apo 2 138kV Line de-energized at 0946H. Planned Outage. [WEBSMS] | CMIN
8/17/2024 9:30:20 AM | Luzon Grid-08/17/2024 09:30: Angat HEPP Auxiliary Transformer A de-energized at 0929H (Planned Outage) [WEBSMS] | CLUZ
8/17/2024 9:16:41 AM | Luzon Grid-08/17/2024 09:16: Ambuklao-Ambuklao HEPP 230kV Tie Line restored at 0916H (Unplanned Outage) [WEBSMS] | CLUZ
8/17/2024 9:16:13 AM | [NSO Update] Visayas Grid-08/17/2024 09:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0913H with power going to Visayas. [WEBSMS] | CVIS
8/17/2024 9:16:00 AM | [NSO Update] Luzon Grid-08/17/2024 09:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0913H with power going to Visayas. [WEBSMS] | CLUZ
8/17/2024 9:03:31 AM | Mindanao Grid-08/17/2024 09:09: Matanao-Kidapawan 138kV Line 1 de-energized 0857H (Planned Outage). [WEBSMS] | CMIN
8/17/2024 8:50:19 AM | [NSO Update] Visayas Grid-08/17/2024 08:50: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0849H from forward power direction. [WEBSMS] | CVIS
8/17/2024 8:50:05 AM | [NSO Update] Luzon Grid-08/17/2024 08:50: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0849H from forward power direction. [WEBSMS] | CLUZ
8/17/2024 8:31:08 AM | Mindanao Grid-08/17/2024 08:37: Nasipit SS 138kV Bus No.1 de-energized at 0822H. Planned Outage. [WEBSMS] | CMIN
8/17/2024 8:29:40 AM | Mindanao Grid-08/17/2024 08:36: Nasipit SS 138kV 100MVA Transformer No.1 de-energized at 0821H. Planned Outage. [WEBSMS] | CMIN
8/17/2024 8:29:14 AM | Luzon Grid-08/17/2024 08:29: San Gabriel shutdown at 0827H (Reserve Shutdown) [WEBSMS] | CLUZ
8/17/2024 8:24:10 AM | Mindanao Grid-08/17/2024 08:30: Nasipit-Therma Marine 2 138kV Line 2 de-energized at 0819H. Planned Outage. [WEBSMS] | CMIN
8/17/2024 8:22:09 AM | Visayas Grid-08/17/2024 08:22: Colon SS 138 kV bus 1 de-energized at 0821H (Planned Outage) [WEBSMS] | CVIS
8/17/2024 8:15:44 AM | [NSO Update] Luzon Grid-08/17/2024 08:15: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 0815H. Market operations will resume starting interval 0820H. [WEBSMS] | CLUZ
8/17/2024 8:15:42 AM | [NSO Update] Visayas Grid-08/17/2024 08:15: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 0815H. Market operations will resume starting interval 0820H. [WEBSMS] | CVIS
8/17/2024 8:15:41 AM | [NSO Update] Mindanao Grid-08/17/2024 08:22: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 0815H. Market operations will resume starting interval 0820H. [WEBSMS] | CMIN
8/17/2024 8:13:47 AM | Visayas Grid-08/17/2024 08:13: Cebu SS 100 MVA TR2 de-energized at 0808H (Planned Outage) [WEBSMS] | CVIS
8/17/2024 8:11:51 AM | [NSO Update] Luzon Grid-08/17/2024 08:11: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 0815H due to failure to generate RTD schedule. [WEBSMS] | CLUZ
8/17/2024 8:11:47 AM | [NSO Update] Visayas Grid-08/17/2024 08:11: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 0815H due to failure to generate RTD schedule. [WEBSMS] | CVIS
8/17/2024 8:11:45 AM | [NSO Update] Mindanao Grid-08/17/2024 08:18: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 0815H due to failure to generate RTD schedule. [WEBSMS] | CMIN
8/17/2024 8:06:27 AM | Luzon Grid-08/17/2024 08:06: Salong SS 230kV Bus 1 de-energized at 0806H (Planned Outage) [WEBSMS] | CLUZ
8/17/2024 7:43:15 AM | Luzon Grid-08/17/2024 07:43: Binan SS 300MVA T02 1 de-energized at 0742H (Planned Outage) [WEBSMS] | CLUZ
8/17/2024 7:26:40 AM | Visayas Grid-08/17/2024 07:26: DaanLungsod SS bus 1 de-energized at 0726H (Planned Outage) [WEBSMS] | CVIS
8/17/2024 6:53:02 AM | Mindanao Grid-08/17/2024 06:59: Kibawe-Davao 138kV Line 2 de-energized at 0651H. Planned Outage. [WEBSMS] | CMIN
8/17/2024 6:27:30 AM | Visayas Grid-08/17/2024 06:27: Dingle-Panit an 138 kV Line 1 de-energized at 0626H (Planned Outage) [WEBSMS] | CVIS
8/17/2024 6:04:41 AM | Luzon Grid-08/17/2024 06:04: Ambuklao-Ambuklao HEPP 230kV Tie Line de-energized at 0604H (Planned Outage) [WEBSMS] | CLUZ
8/17/2024 6:01:57 AM | Luzon Grid-08/17/2024 06:02: SCPC 1 shutdown at 0601H (Planned Outage) [WEBSMS] | CLUZ
8/17/2024 5:46:30 AM | [NSO Update] Luzon Grid-08/17/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14753MW, PK=11361MW, RR=422MW, NetOpMargin: AM=2970, PM=2940, EVE=2497 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @118MW, Ilijan B @450MW, Masinloc 1 @315MW, Masinloc 2 @150MW [WEBSMS] | CLUZ
8/17/2024 5:31:28 AM | [NSO Update] Mindanao Grid-08/17/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3310MW, PK=2080MW, RR=73MW, NetOpMargin: AM=1157, PM=986, EVE=888 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW [WEBSMS] | CMIN
8/17/2024 5:30:08 AM | [NSO Update] Visayas Grid-08/17/2024 05:30: GRID UPDATE AS OF 6:00 AM System Condition: CAP=2731MW, PK=2715MW, RR=2573MW, NetOpMargin: AM=396, PM=401, EVE=301 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @66.5MW, LEYTE A @333MW, CEDC 3 @75MW [WEBSMS] | CVIS
8/17/2024 5:14:25 AM | Luzon Grid-08/17/2024 05:14: Nagsaag-Binga 230kV Line 1 de-energized at 0514H (Planned Outage) [WEBSMS] | CLUZ
8/17/2024 5:05:23 AM | Mindanao Grid-08/17/2024 05:11: Mt Apo U2 shutdown at 0501H (Planned Outage) [WEBSMS] | CMIN
8/17/2024 4:41:28 AM | Luzon Grid-08/17/2024 04:41: Las Pinas 300MVA T05 restored at 0441H (Planned Outage) [WEBSMS] | CLUZ
8/17/2024 4:04:03 AM | [NSO Update] Mindanao Grid-08/17/2024 04:10: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 375 km North Northeast of Itbayat, Batanes (24.0�N, 122.9�E). Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CMIN
8/17/2024 4:03:17 AM | [NSO Update] Visayas Grid-08/17/2024 04:03: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 375 km North Northeast of Itbayat, Batanes (24.0�N, 122.9�E). Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CVIS
8/17/2024 4:02:51 AM | [NSO Update] Luzon Grid-08/17/2024 04:02: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 375 km North Northeast of Itbayat, Batanes (24.0�N, 122.9�E). Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
8/17/2024 3:57:01 AM | Luzon Grid-08/17/2024 03:57: Las Pinas 300MVA TO3 restored at 0356H (Unplanned Outage) [WEBSMS] | CLUZ
8/17/2024 3:31:24 AM | Luzon Grid-08/17/2024 03:31: Las Pinas 300MVA TO3 tripped at 0321H at low side only (Unplanned Outage) [WEBSMS] | CLUZ
8/17/2024 3:16:14 AM | Luzon Grid-08/17/2024 03:16: Dasmarinas-Amadeo 230kV Line 2 restored at 0315H. Dasmarinas-Las Pinas 230kV Line 1 looped/normalize at 0313H (Unplanned Outage) [WEBSMS] | CLUZ
8/17/2024 2:48:31 AM | Luzon Grid-08/17/2024 02:48: Dasmarinas-Amadeo 230kV Line 2 emergency shutdown at 0246H. Dasmarinas-Las Pinas 230kV Line 1 unlooped at 0244H at Dasmarinas side (Unplanned Outage) [WEBSMS] | CLUZ
8/17/2024 12:57:26 AM | Luzon Grid-08/17/2024 00:57: Las Pinas 300MVA T05 de-energized at 0054H (Planned Outage) [WEBSMS] | CLUZ
8/17/2024 12:08:48 AM | Luzon Grid-08/17/2024 00:08: Tayabas-Pagbilao EHV 500kV Line 2 de-energized at 0008H (Planned Outage) [WEBSMS] | CLUZ
8/16/2024 11:09:29 PM | [NSO Update] Visayas Grid-08/16/2024 23:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2306H with power going to Luzon. [WEBSMS] | CVIS
8/16/2024 11:09:10 PM | [NSO Update] Luzon Grid-08/16/2024 23:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2306H with power going to Luzon. [WEBSMS] | CLUZ
8/16/2024 10:55:45 PM | [NSO Update] Luzon Grid-08/16/2024 22:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2252H from reverse power direction. [WEBSMS] | CLUZ
8/16/2024 10:55:06 PM | [NSO Update] Visayas Grid-08/16/2024 22:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2252H from reverse power direction. [WEBSMS] | CVIS
8/16/2024 10:24:33 PM | Luzon Grid-08/16/2024 22:24: Pagbilao EHV 1000MVA T01 restored at 2223H (Planned Outage) [WEBSMS] | CLUZ
8/16/2024 9:48:37 PM | Mindanao Grid-08/16/2024 21:54: WMPC DG10 shutdown at 2148H end of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2024 7:28:18 PM | Mindanao Grid-08/16/2024 19:34: Maramag - Kibawe 138kV L2 energized at 1925H. (Planned Outage) [WEBSMS] | CMIN
8/16/2024 6:49:42 PM | Mindanao Grid-08/16/2024 18:56: Kidapawan 138kV Bus No. 1 energized at 1847H. (Planned Outage) [WEBSMS] | CMIN
8/16/2024 6:22:39 PM | Mindanao Grid-08/16/2024 18:29: WMPC DG01 shutdown at 1821H end of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2024 6:18:26 PM | [NSO Update] Visayas Grid-08/16/2024 18:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1807H with power going to Visayas. [WEBSMS] | CVIS
8/16/2024 6:18:13 PM | [NSO Update] Luzon Grid-08/16/2024 18:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1807H with power going to Visayas. [WEBSMS] | CLUZ
8/16/2024 6:15:32 PM | [NSO Update] Luzon Grid-08/16/2024 18:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1757H from forward power direction. [WEBSMS] | CLUZ
8/16/2024 6:15:07 PM | [NSO Update] Visayas Grid-08/16/2024 18:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1757H from forward power direction. [WEBSMS] | CVIS
8/16/2024 6:14:04 PM | [NSO Update] Luzon Grid-08/16/2024 18:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1757H from forward power direction. [WEBSMS] | CLUZ
8/16/2024 5:34:35 PM | [NSO Update] Luzon Grid-08/16/2024 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13738MW, PK=11846MW, RR=398MW, NetOpMargin: EVE=1494 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @116MW, SCPC 1 @135MW, Ilijan B @450MW, Masinloc 1 @265MW, Masinloc 2 @210MW, Masinloc 3 @315MW [WEBSMS] | CLUZ
8/16/2024 5:27:30 PM | [NSO Update] Mindanao Grid-08/16/2024 17:33: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3298MW, PK=2249MW, RR=73MW, NetOpMargin: EVE=3298 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @28.5MW [WEBSMS] | CMIN
8/16/2024 5:26:15 PM | [NSO Update] Visayas Grid-08/16/2024 17:26: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2760MW, PK=2373MW, RR=91MW, NetOpMargin: EVE=296 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @66.5MW, LEYTE A @333MW, CEDC 3 @75MW [WEBSMS] | CVIS
8/16/2024 2:03:31 PM | Mindanao Grid-08/16/2024 14:09: Agusan Lake HEP online at 1401H from OMC outage. (Unplanned Outage) [WEBSMS] | CMIN
8/16/2024 1:10:23 PM | Mindanao Grid-08/16/2024 13:16: Kidapawan 138kV Bus No. 1 de-energized at 1303H. (Planned Outage) [WEBSMS] | CMIN
8/16/2024 12:40:14 PM | [NSO Update] Luzon Grid-08/16/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14825MW, PK=12659MW, RR=429MW, NetOpMargin: PM=1737, EVE=1363 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @115MW, SCPC 1 @135MW, Ilijan B @450MW, Masinloc 1 @265MW, Masinloc 2 @210MW, Masinloc 3 @315MW [WEBSMS] | CLUZ
8/16/2024 12:40:10 PM | [NSO Update] Visayas Grid-08/16/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2865MW, PK=2464MW, RR=91MW, NetOpMargin: PM=309, EVE=276 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @66.5MW, LEYTE A @333MW, CEDC 3 @75MW [WEBSMS] | CVIS
8/16/2024 12:40:03 PM | [NSO Update] Mindanao Grid-08/16/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3332MW, PK=2472MW, RR=73MW, NetOpMargin: PM=787, EVE=872 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @28.5MW [WEBSMS] | CMIN
8/16/2024 12:12:40 PM | Mindanao Grid-08/16/2024 12:19: Agusan Lake HEP shutdown at 1201H. (Unplanned Outage) [WEBSMS] | CMIN
8/16/2024 11:53:28 AM | Mindanao Grid-08/16/2024 11:59: Agus 5 U2 online at 1147H (Planned Outage) [WEBSMS] | CMIN
8/16/2024 11:40:22 AM | Mindanao Grid-08/16/2024 11:46: Agus 5 SY - Agus 5 HEP 138kV L2 energized at 1139H. (Planned Outage) [WEBSMS] | CMIN
8/16/2024 11:30:00 AM | Luzon Grid-08/16/2024 11:30: SLPGC-Calaca 230kV Line 1 restored at 1128H (Planned Outage) [WEBSMS] | CLUZ
8/16/2024 10:29:09 AM | Mindanao Grid-08/16/2024 10:35: Manolo F1 U3 online at 1020H from Forced outage. (Unplanned Outage) [WEBSMS] | CMIN
8/16/2024 10:27:38 AM | Mindanao Grid-08/16/2024 10:33: WMPC DG01 online at 1016H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2024 9:55:05 AM | Mindanao Grid-08/16/2024 10:01: Manolo Fortich 1 U1 online at 0952H from Forced outage. (Unplanned Outage) [WEBSMS] | CMIN
8/16/2024 9:39:49 AM | Mindanao Grid-08/16/2024 09:46: WMPC DG10 online at 0935H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2024 7:20:35 AM | Mindanao Grid-08/16/2024 07:26: Tagoloan - Villanueva 138kV L1 energized at 0717H. (Planned Outage) [WEBSMS] | CMIN
8/16/2024 6:47:50 AM | Mindanao Grid-08/16/2024 06:54: Maramag - Kibawe 138kV L2 de-energized at 0643H. (Planned Outage) [WEBSMS] | CMIN
8/16/2024 6:43:11 AM | Mindanao Grid-08/16/2024 06:49: Agus 5 SY - Agus 5 HEP 138kV L2 de-energized at 0620H. (Planned Outage) [WEBSMS] | CMIN
8/16/2024 5:44:51 AM | [NSO Update] Mindanao Grid-08/16/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3342MW, PK=2333MW, RR=73MW, NetOpMargin: AM=935, PM=813, EVE=907 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @28.5MW [WEBSMS] | CMIN
8/16/2024 5:44:00 AM | [NSO Update] Visayas Grid-08/16/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2963MW, PK=2408MW, RR=86MW, NetOpMargin: AM=469, PM=299, EVE=312 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @66.5MW, LEYTE A @333MW, CEDC 3 @75MW [WEBSMS] | CVIS
8/16/2024 5:41:36 AM | [NSO Update] Luzon Grid-08/16/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15061MW, PK=12240MW, RR=422MW, NetOpMargin: AM=2399, PM=2165, EVE=2022 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @115MW, Limay 8 @60MW, SCPC 1 @135MW, Ilijan B @450MW, Masinloc 1 @315MW, Masinloc 2 @210MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
8/16/2024 5:14:27 AM | Mindanao Grid-08/16/2024 05:20: Tagoloan-Villanueva 138kV Line 1 de-energized at 0507H. Planned Outage. [WEBSMS] | CMIN
8/16/2024 4:43:53 AM | [NSO Update] Mindanao Grid-08/16/2024 04:50: Weather Update: Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CMIN
8/16/2024 4:43:40 AM | [NSO Update] Visayas Grid-08/16/2024 04:43: Weather Update: Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CVIS
8/16/2024 4:43:24 AM | [NSO Update] Luzon Grid-08/16/2024 04:43: Weather Update: Southwest Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
8/16/2024 4:16:25 AM | Luzon Grid-08/16/2024 04:16: San Jose-Taytay 230kV Line 2 restored at 0416H (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2024 1:05:46 AM | Luzon Grid-08/16/2024 01:05: San Jose-Taytay 230kV Line 2 de-energized at 0105H (Unplanned Outage) [WEBSMS] | CLUZ
8/15/2024 11:13:35 PM | Visayas Grid-08/15/2024 23:13: TPC1-A emergency shutdown at 2312H (Unplanned Outage) [WEBSMS] | CVIS
8/15/2024 9:22:25 PM | Mindanao Grid-08/15/2024 21:28: WMPC (DG10) shutdown at 2115H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/15/2024 6:11:22 PM | [NSO Update] Mindanao Grid-08/15/2024 18:17: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3280MW, PK=2389MW, RR=73MW, NetOpMargin: EVE=818 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29.5MW [WEBSMS] | CMIN
8/15/2024 6:04:14 PM | [NSO Update] Visayas Grid-08/15/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2707MW, PK=2342MW, RR=91MW, NetOpMargin: EVE=274 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @329MW, CEDC 3 @75MW, TGPP @65MW [WEBSMS] | CVIS
8/15/2024 6:01:51 PM | [NSO Update] Luzon Grid-08/15/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13475MW, PK=11754MW, RR=398MW, NetOpMargin: EVE=1323 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @115MW, Limay 8 @60MW, SCPC 1 @135MW, Ilijan B @450MW, Masinloc 1 @315MW, Masinloc 2 @210MW, Calaca 2 @290MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
8/15/2024 5:38:36 PM | Mindanao Grid-08/15/2024 17:44: Agus 5 HEPP Unit 2 online at 1734H (Unplanned Outage) [WEBSMS] | CMIN
8/15/2024 5:36:04 PM | Mindanao Grid-08/15/2024 17:42: Maco-Therma Marine 1 138kV Line 1 energized/restored at 1733H. Planned Outage. [WEBSMS] | CMIN
8/15/2024 5:28:15 PM | Mindanao Grid-08/15/2024 17:34: AGUS 5 HEP Unit 2 on emergency shutdown at 1721H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2024 5:21:49 PM | Mindanao Grid-08/15/2024 17:28: WMPC (DG01) shutdown at 1717H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/15/2024 4:16:14 PM | Mindanao Grid-08/15/2024 16:22: WMPC (DG08) cut-out/shutdown at 1614H from RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/15/2024 1:29:26 PM | [NSO Update] Luzon Grid-08/15/2024 13:29: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14497MW, PK=12500MW, RR=429MW, NetOpMargin: PM=1568, EVE=1379 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, SCPC 1 @135MW, Ilijan B @450MW, Masinloc 1 @315MW, Masinloc 2 @210MW, Calaca 1 @180MW, Calaca 2 @280MW [WEBSMS] | CLUZ
8/15/2024 1:14:59 PM | Mindanao Grid-08/15/2024 13:21: Update: WMPC (DG08) cut-in/online at 1308H as RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/15/2024 1:12:59 PM | Mindanao Grid-08/15/2024 13:19: WMPC (DG08) cut-in/online at 1308 H as RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/15/2024 12:54:08 PM | [NSO Update] Mindanao Grid-08/15/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3327MW, PK=2495MW, RR=73MW, NetOpMargin: PM=759, EVE=843 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29.5MW [WEBSMS] | CMIN
8/15/2024 12:52:12 PM | [NSO Update] Visayas Grid-08/15/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2866MW, PK=2460MW, RR=86MW, NetOpMargin: PM=320, EVE=287 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @323MW, CEDC 3 @75MW, TGPP @64.2MW [WEBSMS] | CVIS
8/15/2024 12:06:38 PM | Mindanao Grid-08/15/2024 12:12: Manolo Fortich 2 HEPP U4 online at 1155H. PMS Non-GOMP [WEBSMS] | CMIN
8/15/2024 12:04:40 PM | [NSO Update] Mindanao Grid-08/15/2024 12:11: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 1200H. Market operations will resume starting interval 1205H. [WEBSMS] | CMIN
8/15/2024 12:04:26 PM | [NSO Update] Visayas Grid-08/15/2024 12:04: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 1200H. Market operations will resume starting interval 1205H. [WEBSMS] | CVIS
8/15/2024 12:04:07 PM | [NSO Update] Luzon Grid-08/15/2024 12:04: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 1200H. Market operations will resume starting interval 1205H. [WEBSMS] | CLUZ
8/15/2024 12:02:48 PM | [NSO Update] Mindanao Grid-08/15/2024 12:09: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 1150H due to failure to transfer RTD schedule to SO [WEBSMS] | CMIN
8/15/2024 12:02:30 PM | [NSO Update] Visayas Grid-08/15/2024 12:02: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 1150H due to failure to transfer RTD schedule to SO [WEBSMS] | CVIS
8/15/2024 12:01:37 PM | [NSO Update] Luzon Grid-08/15/2024 12:01: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 1150H due to failure to transfer RTD schedule to SO [WEBSMS] | CLUZ
8/15/2024 10:03:37 AM | Mindanao Grid-08/15/2024 10:09: WMPC (DG01) online at 1000H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/15/2024 9:07:24 AM | Mindanao Grid-08/15/2024 09:13: WMPC (DG10) online at 0902H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/15/2024 8:21:07 AM | Mindanao Grid-08/15/2024 08:27: Manolo Fortich 2 U4 shutdown at 0801H. PMS Non-GOMP [WEBSMS] | CMIN
8/15/2024 8:09:54 AM | Mindanao Grid-08/15/2024 08:16: Liangan Unit 1 online at 0800H. Commercial Testing. [WEBSMS] | CMIN
8/15/2024 6:54:00 AM | Mindanao Grid-08/15/2024 07:00: Maco-Therma Marine 1 138kV Line 1 de-energized at 0649H. Planned Outage. [WEBSMS] | CMIN
8/15/2024 5:53:05 AM | [NSO Update] Luzon Grid-08/15/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14776MW, PK=11829MW, RR=422MW, NetOpMargin: AM=2525, PM=1767, EVE=1555 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, SCPC 1 @135MW, Ilijan B @450MW, Masinloc 1 @320MW, Masinloc 2 @210MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
8/15/2024 5:51:59 AM | [NSO Update] Mindanao Grid-08/15/2024 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3334MW, PK=2383MW, RR=73MW, NetOpMargin: AM=878, PM=721, EVE=833 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29.5MW [WEBSMS] | CMIN
8/15/2024 5:51:56 AM | [NSO Update] Visayas Grid-08/15/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2956MW, PK=2441MW, RR=86MW, NetOpMargin: AM=430, PM=296, EVE=292 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @329MW, CEDC 3 @75MW, TGPP @63.2MW [WEBSMS] | CVIS
8/15/2024 4:01:21 AM | [NSO Update] Mindanao Grid-08/15/2024 04:07: Weather Advisory: Southwest Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
8/15/2024 4:01:06 AM | [NSO Update] Visayas Grid-08/15/2024 04:01: Weather Advisory: Southwest Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
8/15/2024 4:00:50 AM | [NSO Update] Luzon Grid-08/15/2024 04:00: Weather Advisory: Southwest Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
8/15/2024 3:05:36 AM | Mindanao Grid-08/15/2024 03:11: Lala SS 230kV 150MVA Power Transformer No. 3 energized at 0255H. Planned Outage. [WEBSMS] | CMIN
8/15/2024 1:33:48 AM | Mindanao Grid-08/15/2024 01:40: Lala SS 230kV 150MVA Power Transformer No. 3 de-energized at 0129H (Planned Outage) [WEBSMS] | CMIN
8/15/2024 1:17:21 AM | Mindanao Grid-08/15/2024 01:23: Lala SS 230kV 150MVA Power Transformer No.2 energized at 0110H (Planned Outage) [WEBSMS] | CMIN
8/15/2024 12:22:08 AM | Mindanao Grid-08/15/2024 00:28: Manolo Fortich 1 U1 & U3 with total load of 18.6MW load tripped at 0004H (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 11:55:30 PM | Mindanao Grid-08/15/2024 00:01: Manolo F1 U1 & U3 online at 1143H & 1144H respectively. (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 10:35:24 PM | Mindanao Grid-08/14/2024 22:41: Lala SS 230kV 150MVA Power Transformer No. 2 de-energized at 2230H. (Planned Outage) [WEBSMS] | CMIN
8/14/2024 10:12:40 PM | Mindanao Grid-08/14/2024 22:18: WMPC DG10 shutdown at 2156H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/14/2024 9:16:15 PM | Mindanao Grid-08/14/2024 21:22: Mt Apo U3 with 2.2MW load tripped again at 2106H (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 9:00:25 PM | Mindanao Grid-08/14/2024 21:06: Mt Apo U3 online at 2053H (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 7:46:02 PM | Mindanao Grid-08/14/2024 19:52: Manolo Fortich 1 U1 & U3 with total load of 21MW load tripped at 1931H (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 7:17:47 PM | Mindanao Grid-08/14/2024 19:24: Therma South (TSI) emergency shutdown at 1913H. Implemented gradual unloading from 110 to 0MW thru RTD. (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 7:08:20 PM | Luzon Grid-08/14/2024 19:08: Duhat 300MVA TO3(Customer Owned) was restored at 1847H. (Planned Outage) [WEBSMS] | CLUZ
8/14/2024 5:56:15 PM | [NSO Update] Luzon Grid-08/14/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13643MW, PK=11707MW, RR=397MW, NetOpMargin: EVE=1539 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, SCPC 1 @135MW, Ilijan B @450MW, Masinloc 1 @320MW, Masinloc 2 @210MW, Masinloc 3 @310MW [WEBSMS] | CLUZ
8/14/2024 5:43:07 PM | [NSO Update] Mindanao Grid-08/14/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3461MW, PK=2396MW, RR=73MW, NetOpMargin: EVE=992 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/14/2024 5:41:58 PM | [NSO Update] Visayas Grid-08/14/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2795MW, PK=2421MW, RR=91MW, NetOpMargin: EVE=282 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @324MW, CEDC 3 @75MW, TGPP @63.2MW [WEBSMS] | CVIS
8/14/2024 5:24:08 PM | Mindanao Grid-08/14/2024 17:30: WMPC DG08 shutdown at 1716H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/14/2024 5:21:00 PM | Mindanao Grid-08/14/2024 17:27: Agus 6 U1 online at 1718H. (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 5:20:12 PM | Mindanao Grid-08/14/2024 17:26: online at 1718H [WEBSMS] | CMIN
8/14/2024 5:03:17 PM | Luzon Grid-08/14/2024 17:03: San Roque Unit 3 conducted Load Rejection Test(LRT) at 1659H from 145MW load. [WEBSMS] | CLUZ
8/14/2024 4:49:42 PM | Mindanao Grid-08/14/2024 16:56: Polanco SS 100MVA 138kV Power Transformer No. 3 energized/restored at 1646H. (Planned Outage) [WEBSMS] | CMIN
8/14/2024 4:42:13 PM | Mindanao Grid-08/14/2024 16:48: Liangan Hydro Plant online at 1636H (Test & Commissioning) [WEBSMS] | CMIN
8/14/2024 4:06:34 PM | Mindanao Grid-08/14/2024 16:12: Mt Apo U3 with 2.6MW load tripped at 1555H. (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 3:57:17 PM | Mindanao Grid-08/14/2024 16:03: Liangan Hydro Plant shutdown at 1555H (Test & Commissioning) [WEBSMS] | CMIN
8/14/2024 3:42:17 PM | Luzon Grid-08/14/2024 15:42: San Roque Unit 3 conducted Load Rejection Test(LRT) at 1541H from 128MW load. [WEBSMS] | CLUZ
8/14/2024 3:32:16 PM | Luzon Grid-08/14/2024 15:32: Lumban-Gumaca 230kV line 2 was restored at 1531H. (Planned Outage) [WEBSMS] | CLUZ
8/14/2024 3:16:50 PM | Mindanao Grid-08/14/2024 15:23: WMPC (DG08) online at 1508H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/14/2024 3:09:46 PM | Mindanao Grid-08/14/2024 15:16: WMPC DG04 with 10MW running as RPS tripped at 1457H (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 3:08:20 PM | Mindanao Grid-08/14/2024 15:14: Liangan Hydro Plant shutdown at 1500H (Test & Commissioning) [WEBSMS] | CMIN
8/14/2024 3:04:54 PM | Mindanao Grid-08/14/2024 15:11: Manolo Fortich 2 U3 online at 1457H (Planned Outage) [WEBSMS] | CMIN
8/14/2024 2:36:23 PM | Mindanao Grid-08/14/2024 14:42: Liangan Hydro Plant online at 1434H (Test & Commissioning) [WEBSMS] | CMIN
8/14/2024 2:16:44 PM | Mindanao Grid-08/14/2024 14:23: Liangan Hydro Plant shutdown at 1412H (Test & Commissioning) [WEBSMS] | CMIN
8/14/2024 2:15:03 PM | Luzon Grid-08/14/2024 14:14: San Roque Unit 3 conducted Load Rejection Test(LRT) at 1411H from 128MW load. [WEBSMS] | CLUZ
8/14/2024 1:43:56 PM | Mindanao Grid-08/14/2024 13:50: Liangan Hydro Plant online at 1341H (Test & Commissioning) [WEBSMS] | CMIN
8/14/2024 1:24:34 PM | Mindanao Grid-08/14/2024 13:30: Liangan Hydro Plant shutdown at 1321H (Test & Commissioning) [WEBSMS] | CMIN
8/14/2024 1:06:00 PM | [NSO Update] Mindanao Grid-08/14/2024 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3484MW, PK=2441MW, RR=73MW, NetOpMargin: PM=970, EVE=1042 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/14/2024 1:03:59 PM | [NSO Update] Visayas Grid-08/14/2024 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2947MW, PK=2473MW, RR=91MW, NetOpMargin: PM=382, EVE=264 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, CEDC 3 @75MW, TGPP @63.2MW [WEBSMS] | CVIS
8/14/2024 12:56:23 PM | Mindanao Grid-08/14/2024 13:02: Liangan Hydro Plant online at 1254H (Test & Commissioning) [WEBSMS] | CMIN
8/14/2024 12:53:57 PM | [NSO Update] Luzon Grid-08/14/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14569MW, PK=12317MW, RR=429MW, NetOpMargin: PM=1823, EVE=1278 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, SCPC 1 @135MW, Ilijan B @450MW, Masinloc 1 @320MW, Masinloc 2 @210MW, Masinloc 3 @310MW [WEBSMS] | CLUZ
8/14/2024 12:26:40 PM | Luzon Grid-08/14/2024 12:26: Sual 2 online at 1224H (Planned Outage) [WEBSMS] | CLUZ
8/14/2024 11:56:03 AM | Mindanao Grid-08/14/2024 12:02: Agus 6 U3 online at 1150H. (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 11:49:36 AM | Mindanao Grid-08/14/2024 11:55: Liangan Hydro Plant at 1149H load rejection test of 4.5MW (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 11:30:15 AM | Mindanao Grid-08/14/2024 11:36: Agus 6 SY - Agus 6 HEP 69kV L3 (5LI3AG6-AP6) energized at 1121H. (Planned Outage) [WEBSMS] | CMIN
8/14/2024 11:24:48 AM | Mindanao Grid-08/14/2024 11:31: Liangan Hydro Plant online at 1116H (Test & Commissioning) [WEBSMS] | CMIN
8/14/2024 11:15:01 AM | Mindanao Grid-08/14/2024 11:21: Manolo-Maramag 138kV L1 energized at 1112H. (Planned Outage) [WEBSMS] | CMIN
8/14/2024 11:13:57 AM | Mindanao Grid-08/14/2024 11:20: Maramag SS 138kV Bus 2 energized at 1109H. (Planned Outage) [WEBSMS] | CMIN
8/14/2024 11:08:20 AM | Mindanao Grid-08/14/2024 11:14: WMPC (DG04) online at 1106H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/14/2024 10:59:42 AM | Mindanao Grid-08/14/2024 11:06: Liangan Hydro Plant emergency stop at 1055H (Test & commissioning) [WEBSMS] | CMIN
8/14/2024 10:02:34 AM | Mindanao Grid-08/14/2024 10:08: WMPC (DG10) online at 0955H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/14/2024 9:48:17 AM | Mindanao Grid-08/14/2024 09:54: Agus 6 SY - Agus 6 HEP 69kV L3 (5LI3AG6-AP6) deenergized at 0930H. (Planned Outage) [WEBSMS] | CMIN
8/14/2024 9:42:21 AM | Mindanao Grid-08/14/2024 09:48: Agus 6 U2 online at 0932H. (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 9:36:31 AM | Mindanao Grid-08/14/2024 09:42: Agus 6 U2 with 34MW load tripped at 0916H. Details to follow. (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 9:13:32 AM | Luzon Grid-08/14/2024 09:13: Duhat 300MVA TO3 de-energized at 0911H (Planned Outage) [WEBSMS] | CLUZ
8/14/2024 9:08:50 AM | Mindanao Grid-08/14/2024 09:15: Agus 6 Unit 3 shutdown at 0906H (Unplanned Outage) [WEBSMS] | CMIN
8/14/2024 8:39:37 AM | Mindanao Grid-08/14/2024 08:45: Maramag SS 138kV Bus 2 de-energized at 0828H. (Planned Outage) [WEBSMS] | CMIN
8/14/2024 8:19:36 AM | Mindanao Grid-08/14/2024 08:25: Manolo-Maramag 138kV L1 de-energized at 0817H. (Planned Outage) [WEBSMS] | CMIN
8/14/2024 8:07:58 AM | Mindanao Grid-08/14/2024 08:14: Manolo Fortich 2 U3 shutdown at 0804H (Planned Outage) PMS Non-GOMP [WEBSMS] | CMIN
8/14/2024 6:12:08 AM | Luzon Grid-08/14/2024 06:12: Lumban-Gumaca 230kV Line 2 de-energized at 0603H (Planned Outage) [WEBSMS] | CLUZ
8/14/2024 5:39:39 AM | [NSO Update] Mindanao Grid-08/14/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3529MW, PK=2275MW, RR=73MW, NetOpMargin: AM=1181, PM=971, EVE=1081 Highest Unit O/L: GNPK 1@151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/14/2024 5:39:28 AM | [NSO Update] Visayas Grid-08/14/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3034MW, PK=2339MW, RR=91MW, NetOpMargin: AM=604, PM=589, EVE=560 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @321MW, CEDC 3 @75MW, TGPP @80.2MW [WEBSMS] | CVIS
8/14/2024 5:39:15 AM | [NSO Update] Luzon Grid-08/14/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14545MW, PK=12105MW, RR=422MW, NetOpMargin: AM=2017, PM=1893, EVE=1517 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, SCPC 1 @135MW, Ilijan B @450MW, Masinloc 1 @320MW, Masinloc 2 @210MW, Calaca U1 @180MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
8/14/2024 4:09:25 AM | [NSO Update] Mindanao Grid-08/14/2024 04:15: Weather Advisory: Southwest Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
8/14/2024 4:09:02 AM | [NSO Update] Visayas Grid-08/14/2024 04:09: Weather Advisory: Southwest Monsoon affecting Northern and Central Luzon. [WEBSMS] | CVIS
8/14/2024 4:08:59 AM | [NSO Update] Luzon Grid-08/14/2024 04:08: Weather Advisory: Southwest Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
8/14/2024 12:31:46 AM | Visayas Grid-08/14/2024 00:32: LGPP U2 cut out at 0016H (Unplanned Outage) [WEBSMS] | CVIS
8/14/2024 12:22:59 AM | Visayas Grid-08/14/2024 00:23: LGPP U2 cut out at 0016H (Planned Outage) [WEBSMS] | CVIS
8/13/2024 8:24:06 PM | Mindanao Grid-08/13/2024 20:30: WMPC DG10 shutdown at 2021H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/13/2024 6:56:42 PM | Visayas Grid-08/13/2024 18:56: LGPP U3 cut-in at 1855H (Unplanned Outage) [WEBSMS] | CVIS
8/13/2024 5:43:59 PM | Luzon Grid-08/13/2024 17:44: Lumban-Gumaca 230kV Line 1 restored at 1744H (Planned Outage) [WEBSMS] | CLUZ
8/13/2024 5:35:24 PM | Mindanao Grid-08/13/2024 17:41: AGUS2 HEP U3 online at 1719H. Planned Outage (GOMP) [WEBSMS] | CMIN
8/13/2024 5:32:13 PM | [NSO Update] Mindanao Grid-08/13/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3436MW, PK=2247MW, RR=73MW, NetOpMargin: EVE=1116 Highest Unit O/L: GNPK 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29.5MW [WEBSMS] | CMIN
8/13/2024 5:30:28 PM | [NSO Update] Visayas Grid-08/13/2024 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2730MW, PK=2284MW, RR=89MW, NetOpMargin: EVE=357 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @290MW, CEDC 3 @75MW, TGPP @80.3MW [WEBSMS] | CVIS
8/13/2024 5:28:08 PM | [NSO Update] Luzon Grid-08/13/2024 17:28: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13050MW, PK=11934MW, RR=398MW, NetOpMargin: EVE=718 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, SCPC 1 @135MW, Ilijan B @450MW, Masinloc 1 @320MW, Masinloc 2 @200MW, Calaca U1 @200MW [WEBSMS] | CLUZ
8/13/2024 5:20:14 PM | Luzon Grid-08/13/2024 17:20: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1719H (Planned Outage) [WEBSMS] | CLUZ
8/13/2024 4:51:57 PM | Mindanao Grid-08/13/2024 16:58: WMPC DG04 shutdown at 1637H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/13/2024 4:29:51 PM | Luzon Grid-08/13/2024 16:30: Labo SS 230kV Bus 2 restored at 1630H (Planned Outage) [WEBSMS] | CLUZ
8/13/2024 3:44:42 PM | Mindanao Grid-08/13/2024 15:51: Mt Apo Unit 3 (MA3) tripped at 1532H (Unplanned Outage). [WEBSMS] | CMIN
8/13/2024 3:27:12 PM | Mindanao Grid-08/13/2024 15:33: Agus 6 SY - Agus 6 HEP U1 69kV L (5LI1AG6-AP6) energized/restored at 1523H. From PO/Others. (Note: Agus 6 HEPP Management approved shutdown request) [WEBSMS] | CMIN
8/13/2024 3:01:08 PM | Visayas Grid-08/13/2024 15:01: Carcon - Sangi 34.5 kV Line 2 re-energized at 1459H (Unplanned Outage) [WEBSMS] | CVIS
8/13/2024 2:50:45 PM | Visayas Grid-08/13/2024 14:51: Carcon - Sangi 34.5 kV Line 1 re-energized at 1448H (Unplanned Outage) [WEBSMS] | CVIS
8/13/2024 2:33:26 PM | Visayas Grid-08/13/2024 14:33: Carcon - Sangi 34.5 kV L1 and L2 tripped at 1428H (Unplanned Outage) [WEBSMS] | CVIS
8/13/2024 2:15:28 PM | Mindanao Grid-08/13/2024 14:22: WMPC (DG04) online at 1321H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/13/2024 1:13:53 PM | [NSO Update] Mindanao Grid-08/13/2024 13:20: GRID UPDATE AS OF 1:00 PM System Condition: CAP=3481MW, PK=2461MW, RR=73MW, NetOpMargin: PM=947, EVE=1043 Highest Unit O/L: GNPK 1@151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29.5MW [WEBSMS] | CMIN
8/13/2024 1:12:34 PM | [NSO Update] Visayas Grid-08/13/2024 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2964MW, PK=2438MW, RR=91MW, NetOpMargin: PM=435, EVE=310 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @282MW, CEDC 3 @75MW, TGPP @80.3MW [WEBSMS] | CVIS
8/13/2024 1:08:21 PM | [NSO Update] Luzon Grid-08/13/2024 13:08: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14107MW, PK=12387MW, RR=429MW, NetOpMargin: PM=1291, EVE=918 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, SCPC 1 @135MW, Ilijan B @450MW, Masinloc 1 @320MW, Masinloc 2 @200MW, Calaca 1 @200MW [WEBSMS] | CLUZ
8/13/2024 12:40:33 PM | Visayas Grid-08/13/2024 12:40: Colon - Sibonga 69 kV Line re-energized at 1238H (Unplanned Outage) [WEBSMS] | CVIS
8/13/2024 12:35:53 PM | Visayas Grid-08/13/2024 12:36: Colon - Sibonga 69 kV Line tripped at 1222H (Unplanned Outage) [WEBSMS] | CVIS
8/13/2024 12:00:39 PM | Luzon Grid-08/13/2024 12:00: San Gabriel online at 1159H (Reserve Shutdown) [WEBSMS] | CLUZ
8/13/2024 9:49:50 AM | Luzon Grid-08/13/2024 09:49: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0947H (Planned Outage) [WEBSMS] | CLUZ
8/13/2024 9:26:04 AM | Mindanao Grid-08/13/2024 09:32: WMPC (DG10) online at 0909H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/13/2024 8:49:52 AM | Visayas Grid-08/13/2024 08:50: LGPP U2 cut-in at 0845H (Unplanned Outage) [WEBSMS] | CVIS
8/13/2024 8:39:27 AM | Mindanao Grid-08/13/2024 08:45: Agus 6 SY - Agus 6 HEP U1 69kV L (5LI1AG6-AP6) deenergized at 0830H. Planned Outage/Others. (Note: Customers approved request shutdown) [WEBSMS] | CMIN
8/13/2024 8:24:59 AM | Mindanao Grid-08/13/2024 08:31: Agus6 U1 shutdown at 0803H (Planned Outage). [WEBSMS] | CMIN
8/13/2024 8:14:12 AM | Mindanao Grid-08/13/2024 08:20: Polanco SS 100MVA Power Transformer No.3 (7XF03POZ) deenergized at 0803H. Planned Outage/Non-GOMP. (Note: P&E approved shutdown request) [WEBSMS] | CMIN
8/13/2024 7:29:53 AM | Visayas Grid-08/13/2024 07:30: KSPC U1 cut-in 0726H (Unplanned Outage) [WEBSMS] | CVIS
8/13/2024 6:22:33 AM | Luzon Grid-08/13/2024 06:22: Labo SS 230kV Bus 2 de-energized at 0621H (Planned Outage) [WEBSMS] | CLUZ
8/13/2024 6:16:03 AM | Luzon Grid-08/13/2024 06:16: Lumban-Gumaca 230kV Line 1 de-energized at 0615H (Planned Outage) [WEBSMS] | CLUZ
8/13/2024 5:52:37 AM | [NSO Update] Mindanao Grid-08/13/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3486MW, PK=2400MW, RR=73MW, NetOpMargin: AM=1013, PM=919, EVE=1019 Highest Unit O/L: GNPK 1@151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29.5MW [WEBSMS] | CMIN
8/13/2024 5:50:42 AM | [NSO Update] Visayas Grid-08/13/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2869MW, PK=2383MW, RR=90MW, NetOpMargin: AM=396, PM=227, EVE=225 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @290MW, CEDC 3 @75MW, TGPP @41MW [WEBSMS] | CVIS
8/13/2024 5:47:15 AM | [NSO Update] Luzon Grid-08/13/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14298MW, PK=11862MW, RR=422MW, NetOpMargin: AM=2015, PM=902, EVE=731 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @117MW, Limay 8 @60MW, SCPC 1 @130MW, Ilijan B @450MW, Masinloc 1 @320MW, Masinloc 2 @200MW, Masinloc 3 @315MW [WEBSMS] | CLUZ
8/13/2024 4:33:06 AM | Luzon Grid-08/13/2024 04:33: San Gabriel shutdown at 0426H (Reserve Shutdown) [WEBSMS] | CLUZ
8/13/2024 4:01:15 AM | [NSO Update] Visayas Grid-08/13/2024 04:01: Weather Advisory: Southwest Monsoon affecting Luzon and the western section of Visayas. [WEBSMS] | CVIS
8/13/2024 4:01:11 AM | [NSO Update] Mindanao Grid-08/13/2024 04:07: Weather Advisory: Southwest Monsoon affecting Luzon and the western section of Visayas. [WEBSMS] | CMIN
8/13/2024 4:00:31 AM | [NSO Update] Luzon Grid-08/13/2024 04:00: Weather Advisory: Southwest Monsoon affecting Luzon and the western section of Visayas. [WEBSMS] | CLUZ
8/13/2024 1:33:04 AM | Luzon Grid-08/13/2024 01:33: San Jose PCB 9-05CB04SJO energized at 0132H (Planned Outage) [WEBSMS] | CLUZ
8/13/2024 1:25:31 AM | Visayas Grid-08/13/2024 01:25: LGPP U3 tripped at 0122H. (Unplanned Outage) [WEBSMS] | CVIS
8/13/2024 12:10:40 AM | Visayas Grid-08/13/2024 00:10: Dumanjug-Corella 230 kV Line 1 (CBIP) successfully looped at 0006H in Corella SS. (Under test and commissioning) [WEBSMS] | CVIS
8/12/2024 11:39:28 PM | Visayas Grid-08/12/2024 23:39: Corella SS 300 MVA 230/138/13.8 kV TR1 energized at 2337H from Dumanjug SS. (Under test and commissioning) [WEBSMS] | CVIS
8/12/2024 11:13:09 PM | Visayas Grid-08/12/2024 23:13: Dumanjug-Corella 230 kV Line 1 energized at 2309H from Dumanjug SS. (Under test and commissioning) [WEBSMS] | CVIS
8/12/2024 10:18:39 PM | Visayas Grid-08/12/2024 22:18: LGPP U2 emergency shutdown at 2209H (Unplanned Outage) [WEBSMS] | CVIS
8/12/2024 10:10:27 PM | Luzon Grid-08/12/2024 22:10: San Jose PCB 9-05CB04SJO was de-energized at 2208H. (Planned Outage) [WEBSMS] | CLUZ
8/12/2024 9:58:42 PM | Mindanao Grid-08/12/2024 22:05: WMPC DG10 shutdown at 2146H as RPS - System Voltage Requirement [WEBSMS] | CMIN
8/12/2024 8:53:11 PM | Visayas Grid-08/12/2024 20:53: TGPP U3 cut in at 2050H (Planned Outage) [WEBSMS] | CVIS
8/12/2024 8:34:11 PM | [NSO Update] Visayas Grid-08/12/2024 20:34: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2033H with power going to Luzon. [WEBSMS] | CVIS
8/12/2024 8:34:09 PM | [NSO Update] Luzon Grid-08/12/2024 20:34: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2033H with power going to Luzon. [WEBSMS] | CLUZ
8/12/2024 8:21:08 PM | [NSO Update] Luzon Grid-08/12/2024 20:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2018H from reverse power direction. [WEBSMS] | CLUZ
8/12/2024 8:19:38 PM | [NSO Update] Visayas Grid-08/12/2024 20:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2018H from reverse power direction. [WEBSMS] | CVIS
8/12/2024 6:40:53 PM | Mindanao Grid-08/12/2024 18:47: Maco - Therma Marine 1 138kV L2 energized at 1839H. (Planned Outage) [WEBSMS] | CMIN
8/12/2024 5:53:34 PM | Mindanao Grid-08/12/2024 18:00: WMPC DG01 shutdown at 1746H as RPS - System Voltage Requirement [WEBSMS] | CMIN
8/12/2024 5:48:02 PM | [NSO Update] Mindanao Grid-08/12/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3437MW, PK=2322MW, RR=73MW, NetOpMargin: EVE=1042 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/12/2024 5:47:53 PM | [NSO Update] Visayas Grid-08/12/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2680MW, PK=2362MW, RR=91MW, NetOpMargin: EVE=227 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @280MW, CEDC 3 @75MW, TGPP @80.3MW, PCPC @110MW [WEBSMS] | CVIS
8/12/2024 5:47:43 PM | [NSO Update] Luzon Grid-08/12/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12923MW, PK=11512MW, RR=398MW, NetOpMargin: EVE=1013 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, SCPC 1 @135MW, Calaca 1 @180MW, Masinloc 1 @320MW, Masinloc 2 @200MW, Masinloc 3 @315MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/12/2024 4:38:40 PM | Luzon Grid-08/12/2024 16:38: Currimao-Paguludan 69kV line, and Paguludan-Currimao Solar I 69kV line were restored at 1630H. Paguludan-Currimao Solar II 69kV line was energized at 1631H. (Planned Outage) [WEBSMS] | CLUZ
8/12/2024 3:49:04 PM | [NSO Update] Visayas Grid-08/12/2024 15:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1546H with power going to Visayas. [WEBSMS] | CVIS
8/12/2024 3:49:01 PM | [NSO Update] Luzon Grid-08/12/2024 15:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1546H with power going to Visayas. [WEBSMS] | CLUZ
8/12/2024 3:26:30 PM | Luzon Grid-08/12/2024 15:26: Bantay-Currimao 115kV line and Currimao-Laoag 115kV line were restored at 1524H. (Planned Outage) [WEBSMS] | CLUZ
8/12/2024 3:14:00 PM | [NSO Update] Luzon Grid-08/12/2024 15:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1512H from forward power direction. [WEBSMS] | CLUZ
8/12/2024 3:13:52 PM | [NSO Update] Visayas Grid-08/12/2024 15:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1512H from forward power direction. [WEBSMS] | CVIS
8/12/2024 12:58:30 PM | [NSO Update] Mindanao Grid-08/12/2024 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3479MW, PK=2453MW, RR=73MW, NetOpMargin: PM=953, EVE=1011 Highest Unit O/L: GNPK 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/12/2024 12:52:26 PM | [NSO Update] Visayas Grid-08/12/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2754MW, PK=2411MW, RR=91MW, NetOpMargin: PM=252, EVE=231 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @282MW, CEDC 3 @75MW, TGPP @80.3MW, PCPC @67MW [WEBSMS] | CVIS
8/12/2024 12:49:25 PM | [NSO Update] Luzon Grid-08/12/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13715MW, PK=12038MW, RR=429MW, NetOpMargin: PM=1247, EVE=871 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, SCPC 1 @135MW, Calaca 1 @180MW, Masinloc 1 @320MW, Masinloc 2 @200MW, Masinloc 3 @315MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/12/2024 11:02:53 AM | Luzon Grid-08/12/2024 11:03: San Gabriel online at 1100H (Reserve Shutdown) [WEBSMS] | CLUZ
8/12/2024 10:49:47 AM | Mindanao Grid-08/12/2024 10:56: WMPC (DG01) online at 1045H as RPS - System Voltage Requirement [WEBSMS] | CMIN
8/12/2024 9:58:32 AM | Luzon Grid-08/12/2024 09:58: For info: Sta Rita-San Lorenzo 230kV Bus 1 and Bus 2 Tie Breakers were unlooped at 0954H. Batangas 300MVA T04 and T05 are in parallel configuration at 0956H. This is in preparation for the synchronization of San Gabriel. [WEBSMS] | CLUZ
8/12/2024 9:36:38 AM | Mindanao Grid-08/12/2024 09:43: WMPC (DG10) online at 0929H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/12/2024 8:35:11 AM | Mindanao Grid-08/12/2024 08:41: Maco - Therma Marine 1 138kV L2 de-energized at 0828H. (Planned Outage) [WEBSMS] | CMIN
8/12/2024 6:31:53 AM | Luzon Grid-08/12/2024 06:32: Currimao SS 115kV Bus 1 de-energized at 0619H (Planned Outage) [WEBSMS] | CLUZ
8/12/2024 6:30:20 AM | Luzon Grid-08/12/2024 06:30: Bantay-Currimao 115kV Line and Currimao-Laoag 115kV Line de-energized at 0618H and 0621H, respectively. (Planned Outage) [WEBSMS] | CLUZ
8/12/2024 6:20:21 AM | Luzon Grid-08/12/2024 06:20: Currimao-Paguludan 69kV Line (CO) de-energized at 0556H (Planned Outage) [WEBSMS] | CLUZ
8/12/2024 6:02:44 AM | [NSO Update] Luzon Grid-08/12/2024 06:02: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,375 km East of Extreme Northern Luzon (22.5�N, 135.0�E). Southwest Monsoon affecting Luzon and the western section of Visayas. [WEBSMS] | CLUZ
8/12/2024 5:58:57 AM | Luzon Grid-08/12/2024 05:59: Paguludan-Currimao Solar 69kV Line (CO) de-energized at 0552H (Planned Outage) [WEBSMS] | CLUZ
8/12/2024 5:57:28 AM | Luzon Grid-08/12/2024 05:57: Paguludan-Currimao II Solar 69kV Line (CO) de-energized at 0553H (Planned Outage) [WEBSMS] | CLUZ
8/12/2024 5:46:09 AM | [NSO Update] Luzon Grid-08/12/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14152MW, PK=11406MW, RR=422MW, NetOpMargin: AM=2325, PM=2037, EVE=1645 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: SLTEC 2 @117MW, Limay 8 @60MW, SCPC 1 @130MW, Calaca 1 @160MW, Masinloc 1 @320MW, Masinloc 2 @170MW, Masinloc 3 @315MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/12/2024 5:44:55 AM | [NSO Update] Visayas Grid-08/12/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2903MW, PK=2323MW, RR=86MW, NetOpMargin: AM=494, PM=390, EVE=320 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @290MW, CEDC 3 @75MW, TGPP @80.3MW [WEBSMS] | CVIS
8/12/2024 5:43:14 AM | [NSO Update] Mindanao Grid-08/12/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3518MW, PK=2319MW, RR=73MW, NetOpMargin: AM=1126, PM=921, EVE=979 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/12/2024 5:16:09 AM | Luzon Grid-08/12/2024 05:16: Sta Rita 10 online at 0513H (Planned Outage) [WEBSMS] | CLUZ
8/12/2024 4:29:38 AM | [NSO Update] Mindanao Grid-08/12/2024 04:36: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,375 km East of Extreme Northern Luzon (22.5�N, 135.0�E). Southwest Monsoon affecting Luzon and the western section of Visayas. [WEBSMS] | CMIN
8/12/2024 4:29:03 AM | [NSO Update] Visayas Grid-08/12/2024 04:29: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,375 km East of Extreme Northern Luzon (22.5�N, 135.0�E). Southwest Monsoon affecting Luzon and the western section of Visayas. [WEBSMS] | CVIS
8/12/2024 2:49:27 AM | Visayas Grid-08/12/2024 02:49: Maha B U1 cut-in at 0245H (Unplanned Outage) [WEBSMS] | CVIS
8/12/2024 1:29:43 AM | Luzon Grid-08/12/2024 01:29: San Gabriel shutdown at 0128H (Reserve Shutdown) [WEBSMS] | CLUZ
8/12/2024 12:16:41 AM | Luzon Grid-08/12/2024 00:16: Muntinlupa 115kV Bus 2 restored at 0015H (Planned Outage) [WEBSMS] | CLUZ
8/11/2024 9:04:46 PM | Mindanao Grid-08/11/2024 21:11: WMPC DG10 shutdown at 2101H. End of RPS-System Voltage Requirement [WEBSMS] | CMIN
8/11/2024 8:52:19 PM | Luzon Grid-08/11/2024 20:52: Muntinlupa 115kV Bus 2 de-energized at 2051H (Planned Outage) [WEBSMS] | CLUZ
8/11/2024 8:37:44 PM | Luzon Grid-08/11/2024 20:37: Muntinlupa 115kV Bus 1 restored at 2037H (Planned Outage) [WEBSMS] | CLUZ
8/11/2024 7:06:51 PM | [NSO Update] Visayas Grid-08/11/2024 19:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1750H with power going to Luzon. [WEBSMS] | CVIS
8/11/2024 7:06:36 PM | [NSO Update] Luzon Grid-08/11/2024 19:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1750H with power going to Luzon. [WEBSMS] | CLUZ
8/11/2024 7:00:35 PM | Visayas Grid-08/11/2024 19:00: THVI U2 cut in at 1857H (Unplanned Outage) [WEBSMS] | CVIS
8/11/2024 6:34:13 PM | Mindanao Grid-08/11/2024 18:40: WMPC (DG10) online at 1828H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/11/2024 6:00:58 PM | Mindanao Grid-08/11/2024 18:07: Mt Apo U3 online at 1745H (Planned Outage-GOMP) [WEBSMS] | CMIN
8/11/2024 5:57:49 PM | Visayas Grid-08/11/2024 17:58: Ubay-Corella 138 kV line energized at 1753H (Planned Outage) [WEBSMS] | CVIS
8/11/2024 5:43:07 PM | [NSO Update] Mindanao Grid-08/11/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3515MW, PK=2185MW, RR=73MW, NetOpMargin: EVE=1256 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/11/2024 5:41:58 PM | [NSO Update] Visayas Grid-08/11/2024 17:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1740H from reverse power direction. [WEBSMS] | CVIS
8/11/2024 5:41:42 PM | [NSO Update] Luzon Grid-08/11/2024 17:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1740H from reverse power direction. [WEBSMS] | CLUZ
8/11/2024 5:40:58 PM | [NSO Update] Visayas Grid-08/11/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2415MW, PK=2069MW, RR=85MW, NetOpMargin: EVE=260 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: Leyte A @235MW, CEDC 3 @75MW, TGPP @80.3MW [WEBSMS] | CVIS
8/11/2024 5:39:36 PM | [NSO Update] Luzon Grid-08/11/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12566MW, PK=10393MW, RR=310MW, NetOpMargin: EVE=1863 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: SLTEC 2 @118MW, Limay 8 @60MW, SCPC 1 @130MW, Calaca 1 @180MW, GNPD 2 @600MW, Masinloc 1 @320MW, Masinloc 2 @150MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/11/2024 5:08:36 PM | Visayas Grid-08/11/2024 17:08: Maha A U2 cut in at 1703H, EDC-LeyteA cap increase to 235MW (Unplanned Outage) [WEBSMS] | CVIS
8/11/2024 4:51:37 PM | Visayas Grid-08/11/2024 16:51: Maha A U1 cut in at 1626H (Unplanned Outage) [WEBSMS] | CVIS
8/11/2024 4:13:27 PM | Visayas Grid-08/11/2024 16:13: Colon SS 138 kV bus 1 energized at 1611H (Planned Outage) [WEBSMS] | CVIS
8/11/2024 4:00:46 PM | Luzon Grid-08/11/2024 16:00: San Gabriel online at 1559H (Reserve Shutdown) [WEBSMS] | CLUZ
8/11/2024 3:25:41 PM | Luzon Grid-08/11/2024 15:25: Gamu 230kV Bus 2 restored at 1524H (Planned Outage) [WEBSMS] | CLUZ
8/11/2024 2:34:31 PM | [NSO Update] Luzon Grid-08/11/2024 14:34: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1433H with power going to Visayas. [WEBSMS] | CLUZ
8/11/2024 2:34:16 PM | [NSO Update] Visayas Grid-08/11/2024 14:34: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1433H with power going to Visayas. [WEBSMS] | CVIS
8/11/2024 2:25:14 PM | [NSO Update] Visayas Grid-08/11/2024 14:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1423H from forward power direction. [WEBSMS] | CVIS
8/11/2024 2:24:57 PM | [NSO Update] Luzon Grid-08/11/2024 14:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1423H from forward power direction. [WEBSMS] | CLUZ
8/11/2024 12:53:31 PM | Mindanao Grid-08/11/2024 13:00: Tagoloan - Manolo 138kV L2 (7LI2TAG-MNO) energized/restored at 1248H. From Planned Outage/Non-GOMP. (Note: P&E approved request shutdown) [WEBSMS] | CMIN
8/11/2024 12:35:27 PM | [NSO Update] Mindanao Grid-08/11/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3557MW, PK=2028MW, RR=73MW, NetOpMargin: PM=1456, EVE=1221 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/11/2024 12:32:05 PM | [NSO Update] Visayas Grid-08/11/2024 12:32: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2624MW, PK=1990MW, RR=82MW, NetOpMargin: PM=553, EVE=247 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @210MW, CEDC 3 @75MW, TGPP @80.3MW [WEBSMS] | CVIS
8/11/2024 12:29:35 PM | [NSO Update] Luzon Grid-08/11/2024 12:29: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13509MW, PK=10097MW, RR=339MW, NetOpMargin: PM=3073, EVE=1885 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @118MW, Limay 8 @60MW, SCPC 1 @130MW, Calaca 1 @160MW, GNPD 2 @600MW, Masinloc 1 @320MW, Masinloc 2 @150MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/11/2024 11:49:25 AM | Mindanao Grid-08/11/2024 11:55: Tagoloan SS 100MVA Power Transformer No.2 (7XF02TAG) energized/restored at 1141H. From Planned Outage/Non-GOMP. (Note: P&E approved request shutdown) [WEBSMS] | CMIN
8/11/2024 11:45:40 AM | Mindanao Grid-08/11/2024 11:52: Tagoloan SS 138 kV Bus 2 energized/restored at 1140H. From Planned Outage/Non-GOMP. (Note: P&E approved request shutdown) [WEBSMS] | CMIN
8/11/2024 10:47:30 AM | [NSO Update] Visayas Grid-08/11/2024 10:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1045H with power going to Luzon. [WEBSMS] | CVIS
8/11/2024 10:47:05 AM | [NSO Update] Luzon Grid-08/11/2024 10:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1045H with power going to Luzon. [WEBSMS] | CLUZ
8/11/2024 10:37:56 AM | [NSO Update] Visayas Grid-08/11/2024 10:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1035H from reverse power direction. [WEBSMS] | CVIS
8/11/2024 10:37:40 AM | [NSO Update] Luzon Grid-08/11/2024 10:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1035H from reverse power direction. [WEBSMS] | CLUZ
8/11/2024 10:03:25 AM | Visayas Grid-08/11/2024 10:03: Daanbantayan SS 230kV Bus 2 energized at 0959H. (Planned Outage) [WEBSMS] | CVIS
8/11/2024 8:47:10 AM | [NSO Update] Visayas Grid-08/11/2024 08:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0846H with power going to Visayas. [WEBSMS] | CVIS
8/11/2024 8:46:55 AM | [NSO Update] Luzon Grid-08/11/2024 08:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0846H with power going to Visayas. [WEBSMS] | CLUZ
8/11/2024 8:38:28 AM | [NSO Update] Visayas Grid-08/11/2024 08:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0836H from forward power direction. [WEBSMS] | CVIS
8/11/2024 8:37:57 AM | [NSO Update] Luzon Grid-08/11/2024 08:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0836H from forward power direction. [WEBSMS] | CLUZ
8/11/2024 8:29:34 AM | Visayas Grid-08/11/2024 08:29: Daanbantayan SS 230kV Bus 2 de-energized at 0828H. (Planned Outage) [WEBSMS] | CVIS
8/11/2024 8:14:43 AM | Luzon Grid-08/11/2024 08:14: Muntinlupa 115kV Bus 1 was de-energized at 0813H. (Planned Outage) [WEBSMS] | CLUZ
8/11/2024 6:58:36 AM | Visayas Grid-08/11/2024 06:58: Colon SS 138kV Bus 1 de-energized at 0656H. (Unplanned Outage) [WEBSMS] | CVIS
8/11/2024 6:34:17 AM | Luzon Grid-08/11/2024 06:34: Gamu 230kV Bus 2 was de-energized at 0633H. (Planned Outage) [WEBSMS] | CLUZ
8/11/2024 6:20:32 AM | Luzon Grid-08/11/2024 06:20: Daraga-Bacman 230kV line 2 was de-energized at 0616H. (Planned Outage) [WEBSMS] | CLUZ
8/11/2024 5:43:14 AM | [NSO Update] Mindanao Grid-08/11/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3566MW, PK=1974MW, RR=73MW, NetOpMargin: AM=1520, PM=1492, EVE=1365 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/11/2024 5:39:26 AM | [NSO Update] Visayas Grid-08/11/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2554MW, PK=1849MW, RR=80MW, NetOpMargin: AM=626, PM=639, EVE=323 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @218MW, CEDC 3 @75MW, TGPP @80.3MW [WEBSMS] | CVIS
8/11/2024 5:37:43 AM | [NSO Update] Luzon Grid-08/11/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13295MW, PK=9274MW, RR=332MW, NetOpMargin: AM=3689, PM=3056, EVE=1664 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @118MW, Limay 8 @60MW, SCPC 1 @130MW, Calaca 1 @160MW, GNPD 2 @600MW, Masinloc 1 @320MW, Masinloc 2 @150MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/11/2024 5:35:20 AM | Mindanao Grid-08/11/2024 05:41: Tagoloan SS 138 kV Bus 2 de-energized at 0526H (Planned Outage) [WEBSMS] | CMIN
8/11/2024 5:32:27 AM | Mindanao Grid-08/11/2024 05:38: Tagoloan SS 100MVA Transformer (T2 ) de-energized at 0524H (Planned Outage) [WEBSMS] | CMIN
8/11/2024 5:30:41 AM | Luzon Grid-08/11/2024 05:30: San Gabriel shutdown at 0529H (Reserve Shutdown) [WEBSMS] | CLUZ
8/11/2024 5:29:41 AM | Mindanao Grid-08/11/2024 05:36: Tagoloan Manolo 138 kV L2 de-energized at 0522H (Planned Outage) [WEBSMS] | CMIN
8/11/2024 4:44:24 AM | [NSO Update] Mindanao Grid-08/11/2024 04:50: Weather Update: Southwest Monsoon affecting Luzon and the western section of Visayas. [WEBSMS] | CMIN
8/11/2024 4:44:10 AM | [NSO Update] Visayas Grid-08/11/2024 04:44: Weather Update: Southwest Monsoon affecting Luzon and the western section of Visayas. [WEBSMS] | CVIS
8/11/2024 4:44:08 AM | [NSO Update] Luzon Grid-08/11/2024 04:44: Weather Update: Southwest Monsoon affecting Luzon and the western section of Visayas. [WEBSMS] | CLUZ
8/11/2024 4:37:39 AM | Luzon Grid-08/11/2024 04:37: San Jose SS 750MVA T01 restored at 0432H (Planned Outage) [WEBSMS] | CLUZ
8/11/2024 1:49:54 AM | Luzon Grid-08/11/2024 01:49: Balsik-San Marcelino 230kV Line 1 restored at 0149H (Planned Outage) [WEBSMS] | CLUZ
8/11/2024 12:12:06 AM | Mindanao Grid-08/11/2024 00:18: MCC U2 shutdown at 2359H. PMS NON-GOMP. [WEBSMS] | CMIN
8/10/2024 10:39:12 PM | [NSO Update] Visayas Grid-08/10/2024 22:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2236H with power going to Luzon [WEBSMS] | CVIS
8/10/2024 10:38:33 PM | [NSO Update] Luzon Grid-08/10/2024 22:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2236H with power going to Luzon [WEBSMS] | CLUZ
8/10/2024 10:33:53 PM | Luzon Grid-08/10/2024 22:33: Balsik-San Marcelino 230kV Line 1 de-energized at 2233H (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 10:32:46 PM | Mindanao Grid-08/10/2024 22:39: Power Source (PPEI) online at 2215H. Unplanned Outage. [WEBSMS] | CMIN
8/10/2024 10:30:37 PM | [NSO Update] Visayas Grid-08/10/2024 22:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2226H from reverse power direction [WEBSMS] | CVIS
8/10/2024 10:29:53 PM | [NSO Update] Luzon Grid-08/10/2024 22:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2226H from reverse power direction [WEBSMS] | CLUZ
8/10/2024 10:20:34 PM | Luzon Grid-08/10/2024 22:20: Balsik-San Marcelino 230kV Line 2 restored at 2220H (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 10:18:48 PM | Luzon Grid-08/10/2024 22:18: Daraga-Bacman 230kV line 1 restored at 2218H (Unplanned Outage) [WEBSMS] | CLUZ
8/10/2024 9:28:33 PM | Luzon Grid-08/10/2024 21:28: San Jose SS 750MVA T01 de-energized at 2128H (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 8:10:04 PM | Mindanao Grid-08/10/2024 20:16: Matanao- Kidapawan 138 kV L1 energized at 1958H (Planned Outage) [WEBSMS] | CMIN
8/10/2024 7:33:28 PM | Mindanao Grid-08/10/2024 19:39: Power Source (PPEI) emergency shutdown at 1927H. Unplanned Outage. [WEBSMS] | CMIN
8/10/2024 6:40:20 PM | [NSO Update] Mindanao Grid-08/10/2024 18:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3557MW, PK=2284MW, RR=73MW, NetOpMargin: EVE=1200 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/10/2024 6:36:39 PM | Luzon Grid-08/10/2024 18:36: Balsik-San Marcelino 230kV Line 2 de-energized at 1836H (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 6:06:27 PM | [NSO Update] Visayas Grid-08/10/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2487MW, PK=2141MW, RR=88MW, NetOpMargin: EVE=258 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @218MW, CEDC 3 @75MW, TGPP @80.3MW [WEBSMS] | CVIS
8/10/2024 6:04:45 PM | [NSO Update] Luzon Grid-08/10/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12737MW, PK=10419MW, RR=397MW, NetOpMargin: EVE=1921 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @118MW, Limay 8 @60MW, SCPC 1 @130MW, Calaca 1 @180MW, GNPD 2 @600MW, Masinloc 1 @320MW, Masinloc 2 @150MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/10/2024 5:46:29 PM | Visayas Grid-08/10/2024 17:46: Compostela-Carmen 69kV Line energized at 1744H. (Planned Outage) [WEBSMS] | CVIS
8/10/2024 5:31:51 PM | Luzon Grid-08/10/2024 17:31: Gamu 230kV Bus 1 restored at 1731H (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 5:07:33 PM | Luzon Grid-08/10/2024 17:07: Pagbilao EHV-Pagbilao CFTPP 230kV line 1 restored at 1706H (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 5:04:45 PM | Visayas Grid-08/10/2024 17:04: Colon SS 138kV Bus 1 energized 1703H. (Planned Outage) [WEBSMS] | CVIS
8/10/2024 5:01:12 PM | Luzon Grid-08/10/2024 17:01: San Gabriel online at 1659H (Reserve Shutdown) [WEBSMS] | CLUZ
8/10/2024 4:42:36 PM | Mindanao Grid-08/10/2024 16:49: Tagoloan-Villanueva 138 kV L2 energized/ restored at 1637H from Planned Outage. [WEBSMS] | CMIN
8/10/2024 4:20:11 PM | Luzon Grid-08/10/2024 16:20: Bay-Lumban 230kV line 2 restored at 1620H (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 3:50:23 PM | Mindanao Grid-08/10/2024 15:56: Polanco SS 138 kV Bus 1 energized at 1548H from Planned Outage) [WEBSMS] | CMIN
8/10/2024 3:32:57 PM | Mindanao Grid-08/10/2024 15:39: Aurora-NagaMin 138 kV L2 auto-tripped at NagaMin SS side only at 1509H , NagaMin SVC also tripped at 1510H. An estimated of 50 MW customers voltage sensitive load activated. Highest frequency recorded was 60.47 Hz. Line restored at 1519H and SVC energized back at 1525H.( Unplanned Outages) [WEBSMS] | CMIN
8/10/2024 2:34:37 PM | Visayas Grid-08/10/2024 14:34: Compostela SS 50 MVA TR4 energized at 1433H. (Planned Outage) [WEBSMS] | CVIS
8/10/2024 1:05:35 PM | [NSO Update] Luzon Grid-08/10/2024 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13622MW, PK=10771MW, RR=429MW, NetOpMargin: PM=2422, EVE=1190 Highest Unit O/L: GNPD 1@668MW Derated Plant: SLTEC 2 @118MW, Limay 8 @60MW, SCPC 1 @130MW, Calaca 1 @180MW, GNPD 2 @600MW, Masinloc 1 @320MW, Masinloc 2 @150MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/10/2024 1:01:24 PM | [NSO Update] Mindanao Grid-08/10/2024 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3600MW, PK=2195MW, RR=73MW, NetOpMargin: PM=1332, EVE=1265 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/10/2024 12:59:00 PM | [NSO Update] Visayas Grid-08/10/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2614MW, PK=2140MW, RR=85MW, NetOpMargin: PM=389, EVE=244 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: Leyte A @218MW, CEDC 3 @75MW, TGPP @80.3MW, PDPP3-E @8MW, PDPP3-H @8MW, PB104 U3 @5MW [WEBSMS] | CVIS
8/10/2024 12:00:50 PM | Luzon Grid-08/10/2024 12:00: Las Pinas SS 230kV Tie Line was restored at 1200H. (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 11:49:08 AM | Mindanao Grid-08/10/2024 11:55: NagaMin SS 50MVA Transformer (T2 ) de-energized at 0912H (Planned Outage) [WEBSMS] | CMIN
8/10/2024 11:46:34 AM | Mindanao Grid-08/10/2024 11:53: NagaMin SS 50MVA Transformer (T2 ) energized at 1139H (Planned Outage) [WEBSMS] | CMIN
8/10/2024 10:12:37 AM | Mindanao Grid-08/10/2024 10:19: Baloi SS 50MVA Power Transformer No.1 (7XF01BLO) energized at 1002H. ( Planned Outage) [WEBSMS] | CMIN
8/10/2024 10:11:37 AM | Mindanao Grid-08/10/2024 10:18: Baloi SS 50MVA Power Transformer No.1 (7XF01BLO) de-energized at 0756H. ( Planned Outage) [WEBSMS] | CMIN
8/10/2024 9:31:59 AM | Mindanao Grid-08/10/2024 09:38: Toril - Bunawan 230kV Line 2 auto-tripped and successfully auto reclosed at 0923H (single-pole auto-reclosing (SPAR)). Unplanned Outage. Indication: Phase C, 16.7 km. [WEBSMS] | CMIN
8/10/2024 9:18:29 AM | Mindanao Grid-08/10/2024 09:24: Zamboanga SS 50MVA Transformer (T2 ) de-energized at 0912H (Planned Outage) [WEBSMS] | CMIN
8/10/2024 9:06:33 AM | Luzon Grid-08/10/2024 09:06: Pagbilao EHV 1000MVA T01 was de-energized at 0903H. (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 8:48:00 AM | Mindanao Grid-08/10/2024 08:54: Matanao- Kidapawan 138 kV L1 de-energized at 0814H (Planned Outage) [WEBSMS] | CMIN
8/10/2024 8:24:15 AM | [NSO Update] Luzon Grid-08/10/2024 08:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0822H with power going to Visayas. [WEBSMS] | CLUZ
8/10/2024 8:24:12 AM | [NSO Update] Visayas Grid-08/10/2024 08:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0822H with power going to Visayas. [WEBSMS] | CVIS
8/10/2024 8:19:41 AM | Visayas Grid-08/10/2024 08:19: Compostela SS 100MVA TR 4 de-energized at 0813H. (Planned Outage) [WEBSMS] | CVIS
8/10/2024 8:14:43 AM | Luzon Grid-08/10/2024 08:14: Pagbilao EHV-Pagbilao CFTPP 230kV line 1 was de-energized at 0813H. (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 8:12:20 AM | [NSO Update] Luzon Grid-08/10/2024 08:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0811H from forward power direction. [WEBSMS] | CLUZ
8/10/2024 8:12:17 AM | [NSO Update] Visayas Grid-08/10/2024 08:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0811H from forward power direction. [WEBSMS] | CVIS
8/10/2024 8:00:23 AM | Luzon Grid-08/10/2024 08:00: Bay-Lumban 230kV line 2 was de-energized at 0759H. (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 7:49:19 AM | Visayas Grid-08/10/2024 07:49: Colon SS 138kV Bus 1 de-energized 0743H. (Planned Outage) [WEBSMS] | CVIS
8/10/2024 7:44:24 AM | Mindanao Grid-08/10/2024 07:50: Polanco SS 138 kV Bus 1 de-energized at 0631H (Planned Outage) [WEBSMS] | CMIN
8/10/2024 6:43:52 AM | Mindanao Grid-08/10/2024 06:50: Tagoloan-Villanueva 138 kV L2 de-energized at 0631H (Planned Outage) [WEBSMS] | CMIN
8/10/2024 6:34:10 AM | Luzon Grid-08/10/2024 06:34: Gamu 230kV Bus 1 was de-energized at 0633H. (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 6:26:23 AM | Visayas Grid-08/10/2024 06:26: Consolacion-MRI 69kV Line de-energized at 0611H. (Planned Outage) [WEBSMS] | CVIS
8/10/2024 6:15:33 AM | Luzon Grid-08/10/2024 06:15: Daraga-Bacman 230kV line 1 was de-energized at 0614H. (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 5:58:51 AM | [NSO Update] Mindanao Grid-08/10/2024 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3630MW, PK=2128MW, RR=73MW, NetOpMargin: AM=1428, PM=1389, EVE=1328 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/10/2024 5:53:52 AM | [NSO Update] Visayas Grid-08/10/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2461MW, PK=2095MW, RR=84MW, NetOpMargin: AM=282, PM=246, EVE=231 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: Leyte A @218MW, CEDC 3 @75MW, TGPP @80.3MW, PDPP3-E @8MW, PDPP3-H @8MW, PB104 U3 @5MW [WEBSMS] | CVIS
8/10/2024 5:52:09 AM | [NSO Update] Luzon Grid-08/10/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13819MW, PK=10968MW, RR=422MW, NetOpMargin: AM=2429, PM=1875, EVE=1309 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: SLTEC 2 @117MW, Limay 8 @60MW, SCPC 1 @130MW, Calaca 1 @190MW, GNPD 2 @600MW, Masinloc 1 @320MW, Masinloc 2 @150MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/10/2024 5:24:48 AM | Visayas Grid-08/10/2024 05:24: THVI unit no, 2 cut-out from the system at 0521H. (Unplanned Outage) [WEBSMS] | CVIS
8/10/2024 4:23:27 AM | [NSO Update] Mindanao Grid-08/10/2024 04:29: Weather Advisory: Southwest Monsoon affecting Luzon and the western sections of Visayas and Mindanao. [WEBSMS] | CMIN
8/10/2024 4:23:12 AM | [NSO Update] Visayas Grid-08/10/2024 04:23: Weather Advisory: Southwest Monsoon affecting Luzon and the western sections of Visayas and Mindanao. [WEBSMS] | CVIS
8/10/2024 4:22:57 AM | [NSO Update] Luzon Grid-08/10/2024 04:22: Weather Advisory: Southwest Monsoon affecting Luzon and the western sections of Visayas and Mindanao. [WEBSMS] | CLUZ
8/10/2024 3:40:45 AM | Luzon Grid-08/10/2024 03:40: San Gabriel shutdown at 0337H (Reserve Shutdown) [WEBSMS] | CLUZ
8/10/2024 3:25:34 AM | Luzon Grid-08/10/2024 03:25: Tayabas SS 230kV Bus 1 restored at 0319H (Planned Outage) [WEBSMS] | CLUZ
8/10/2024 1:08:45 AM | Luzon Grid-08/10/2024 01:08: Tayabas SS 230kV Bus 1 de-energized at 0108H (Planned Outage) [WEBSMS] | CLUZ
8/9/2024 11:44:46 PM | Luzon Grid-08/09/2024 23:44: Sual 2 shutdown at 2343H (Planned Outage) [WEBSMS] | CLUZ
8/9/2024 10:12:34 PM | Luzon Grid-08/09/2024 22:12: Las Pinas SS 230kV Tie Line de-energized at 2212H (Planned Outage) [WEBSMS] | CLUZ
8/9/2024 9:57:54 PM | [NSO Update] Luzon Grid-08/09/2024 21:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2143H with power going to Luzon. [WEBSMS] | CLUZ
8/9/2024 9:57:36 PM | [NSO Update] Visayas Grid-08/09/2024 21:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2143H with power going to Luzon. [WEBSMS] | CVIS
8/9/2024 9:34:23 PM | [NSO Update] Visayas Grid-08/09/2024 21:34: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2133H from reverse power direction. [WEBSMS] | CVIS
8/9/2024 9:34:04 PM | [NSO Update] Luzon Grid-08/09/2024 21:34: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2133H from reverse power direction. [WEBSMS] | CLUZ
8/9/2024 9:31:18 PM | Mindanao Grid-08/09/2024 21:37: Marawi SS 50MVA Power Transformer (7XF01MRW) energized/restored at 2119H. (Unplanned Outage) [WEBSMS] | CMIN
8/9/2024 8:41:13 PM | Mindanao Grid-08/09/2024 20:47: Mindanao Spot Peak for August 09, 2024, is 2,251.77 MW at 1325H. The highest peak to date is 2,577.02 MW at 1333H on May 22, 2024. [WEBSMS] | CMIN
8/9/2024 6:33:27 PM | Mindanao Grid-08/09/2024 18:39: Marawi SS 50MVA Power Transformer (7XF01MRW) auto-tripped at 1814H. Unplanned Outage. [WEBSMS] | CMIN
8/9/2024 5:46:25 PM | [NSO Update] Mindanao Grid-08/09/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3580MW, PK=2208MW, RR=73MW, NetOpMargin: EVE=1299 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/9/2024 5:44:46 PM | [NSO Update] Visayas Grid-08/09/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2627MW, PK=2268MW, RR=91MW, NetOpMargin: EVE=268 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @197MW, CEDC 3 @75MW, TGPP @80.3MW, PDPP3-E @8MW, PDPP3-H @8MW, PB104 U3 @5MW [WEBSMS] | CVIS
8/9/2024 5:42:37 PM | [NSO Update] Luzon Grid-08/09/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13200MW, PK=11106MW, RR=398MW, NetOpMargin: EVE=1696 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: SLTEC 2 @117MW, Limay 8 @60MW, SCPC 1 @130MW, Calaca 1 @200MW, GNPD 2 @600MW, Masinloc 1 @315MW, Masinloc 2 @150MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/9/2024 4:53:58 PM | Luzon Grid-08/09/2024 16:53: Bay SS 230kV Bus 1 restored at 1653H (Planned Outage) [WEBSMS] | CLUZ
8/9/2024 3:15:36 PM | Visayas Grid-08/09/2024 15:15: Colon-KSPC 138 kV Line 1 energized at 1514H (Planned Outage) [WEBSMS] | CVIS
8/9/2024 2:27:04 PM | [NSO Update] Luzon Grid-08/09/2024 14:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1425H with power going to Visayas. [WEBSMS] | CLUZ
8/9/2024 2:26:52 PM | [NSO Update] Visayas Grid-08/09/2024 14:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1425H with power going to Visayas. [WEBSMS] | CVIS
8/9/2024 2:22:30 PM | [NSO Update] Visayas Grid-08/09/2024 14:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1407H from forward power direction. [WEBSMS] | CVIS
8/9/2024 2:22:18 PM | [NSO Update] Luzon Grid-08/09/2024 14:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1407H from forward power direction. [WEBSMS] | CLUZ
8/9/2024 12:56:24 PM | [NSO Update] Mindanao Grid-08/09/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3603MW, PK=2422MW, RR=73MW, NetOpMargin: PM=1108, EVE=1165 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/9/2024 12:54:31 PM | [NSO Update] Visayas Grid-08/09/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2776MW, PK=2391MW, RR=91MW, NetOpMargin: PM=294, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @189MW, CEDC 3 @75MW, TGPP @80.3MW, PDPP3-E @8MW, PDPP3-H @8MW [WEBSMS] | CVIS
8/9/2024 12:50:10 PM | [NSO Update] Luzon Grid-08/09/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14121MW, PK=12079MW, RR=429MW, NetOpMargin: PM=1613, EVE=1233 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, SCPC 1 @130MW, Calaca 1 @180MW, Calaca 2 @284MW, GNPD 2 @550MW, Masinloc 1 @310MW, Masinloc 2 @150MW, Masinloc 3 @315MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/9/2024 12:20:01 PM | Luzon Grid-08/09/2024 12:20: San Gabriel online at 1159H (Reserve Shutdown) [WEBSMS] | CLUZ
8/9/2024 12:14:31 PM | Visayas Grid-08/09/2024 12:14: PGPP1 U2 cut-in at 1210H. (Unplanned Outage) [WEBSMS] | CVIS
8/9/2024 10:47:05 AM | Mindanao Grid-08/09/2024 10:53: Agus 4 - Baloi 138kV L2 energized/restored at 1043H. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/9/2024 10:38:55 AM | Mindanao Grid-08/09/2024 10:45: WMPC DG10 online at 1036H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/9/2024 9:36:19 AM | [NSO Update] Luzon Grid-08/09/2024 09:36: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0928H with power going to Luzon. [WEBSMS] | CLUZ
8/9/2024 9:35:38 AM | [NSO Update] Visayas Grid-08/09/2024 09:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0928H with power going to Luzon. [WEBSMS] | CVIS
8/9/2024 9:16:16 AM | [NSO Update] Visayas Grid-08/09/2024 09:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0910H from forward power direction. [WEBSMS] | CVIS
8/9/2024 9:13:52 AM | [NSO Update] Luzon Grid-08/09/2024 09:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0910H from forward power direction. [WEBSMS] | CLUZ
8/9/2024 8:19:21 AM | Mindanao Grid-08/09/2024 08:25: Toril - Bunawan 230kV Line 2 auto-tripped and auto reclosed at 0734H (single-pole auto-reclosing). Unplanned Outage. [WEBSMS] | CMIN
8/9/2024 8:10:12 AM | Mindanao Grid-08/09/2024 08:16: Baloi - Agus4 138kV line 2 de-energized 0756H (Planned Outage). [WEBSMS] | CMIN
8/9/2024 7:12:38 AM | Luzon Grid-08/09/2024 07:12: Bay SS 230kV Bus 1 de-energized at 0709H (Planned Outage) [WEBSMS] | CLUZ
8/9/2024 6:22:19 AM | Visayas Grid-08/09/2024 06:22: PGPP1 U2 shutdown at 0610H for VFD adjustment. (Unplanned Outage) [WEBSMS] | CVIS
8/9/2024 6:05:28 AM | Mindanao Grid-08/09/2024 06:11: Power Source (PPEI) emergency shutdown at 0600H. Unplanned Outage. [WEBSMS] | CMIN
8/9/2024 5:58:41 AM | Mindanao Grid-08/09/2024 06:05: TSI Unit 2 online at 0555H (Unplanned Outage) [WEBSMS] | CMIN
8/9/2024 5:42:54 AM | [NSO Update] Luzon Grid-08/09/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14308MW, PK=11721MW, RR=422MW, NetOpMargin: AM=2164, PM=1815, EVE=1733 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, SCPC 1 @130MW, Calaca 1 @180MW, Calaca 2 @200MW, GNPD 2 @550MW, Masinloc 1 @310MW, Masinloc 2 @150MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/9/2024 5:28:35 AM | [NSO Update] Mindanao Grid-08/09/2024 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3479MW, PK=2339MW, RR=73MW, NetOpMargin: AM=1067, PM=954, EVE=1078 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/9/2024 5:26:48 AM | [NSO Update] Visayas Grid-08/09/2024 05:26: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2850MW, PK=2352MW, RR=91MW, NetOpMargin: AM=407, PM=405, EVE=272 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @197MW, CEDC 3 @75MW, TGPP @80.3MW, PDPP3-E @8MW, PB104 U4 @5MW, PDPP3-H @8MW [WEBSMS] | CVIS
8/9/2024 4:37:54 AM | [NSO Update] Mindanao Grid-08/09/2024 04:44: Weather Update: Southwest Monsoon affecting Luzon and the western section of Visayas. [WEBSMS] | CMIN
8/9/2024 4:37:31 AM | [NSO Update] Visayas Grid-08/09/2024 04:37: Weather Update: Southwest Monsoon affecting Luzon and the western section of Visayas. [WEBSMS] | CVIS
8/9/2024 4:37:17 AM | [NSO Update] Luzon Grid-08/09/2024 04:37: Weather Update: Southwest Monsoon affecting Luzon and the western section of Visayas. [WEBSMS] | CLUZ
8/9/2024 2:28:50 AM | Luzon Grid-08/09/2024 02:28: San Gabriel shutdown at 0228H (Reserve Shutdown) [WEBSMS] | CLUZ
8/8/2024 9:44:26 PM | [NSO Update] Luzon Grid-08/08/2024 21:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2135H with power going to Luzon [WEBSMS] | CLUZ
8/8/2024 9:43:41 PM | [NSO Update] Visayas Grid-08/08/2024 21:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2135H with power going to Luzon [WEBSMS] | CVIS
8/8/2024 9:42:20 PM | [NSO Update] Luzon Grid-08/08/2024 21:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2125H from reverse power direction [WEBSMS] | CLUZ
8/8/2024 9:38:59 PM | [NSO Update] Visayas Grid-08/08/2024 21:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2125H from reverse power direction [WEBSMS] | CVIS
8/8/2024 9:27:22 PM | Mindanao Grid-08/08/2024 21:33: WMPC DG10 shutdown at 2116H. End of RPS-System Voltage Requirement [WEBSMS] | CMIN
8/8/2024 5:53:21 PM | [NSO Update] Luzon Grid-08/08/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13032MW, PK=11150MW, RR=398MW, NetOpMargin: EVE=1484 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, SCPC 1 @130MW, Calaca 1 @150MW, Calaca 2 @200MW, GNPD 2 @550MW, Masinloc 1 @310MW, Masinloc 2 @150MW, Masinloc 3 @320MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/8/2024 5:40:52 PM | [NSO Update] Mindanao Grid-08/08/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3425MW, PK=2370MW, RR=73MW, NetOpMargin: EVE=982 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/8/2024 5:37:13 PM | [NSO Update] Visayas Grid-08/08/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2672MW, PK=2317MW, RR=91MW, NetOpMargin: EVE=263 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @210MW, CEDC 3 @75MW, TGPP @80MW, PDPP3-E @8MW, PB104 U4 @5MW, PDPP3-H @8MW [WEBSMS] | CVIS
8/8/2024 5:36:21 PM | Luzon Grid-08/08/2024 17:36: Naga-Tiwi C 230kV L3 restored at 1729H (Planned Outage) [WEBSMS] | CLUZ
8/8/2024 5:18:36 PM | Mindanao Grid-08/08/2024 17:24: WMPC DG08 shutdown at 1716H. End of RPS-System Voltage Requirement [WEBSMS] | CMIN
8/8/2024 1:35:38 PM | [NSO Update] Luzon Grid-08/08/2024 13:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1334H with power going to Visayas. [WEBSMS] | CLUZ
8/8/2024 1:35:17 PM | [NSO Update] Visayas Grid-08/08/2024 13:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1334H with power going to Visayas. [WEBSMS] | CVIS
8/8/2024 1:31:15 PM | [NSO Update] Visayas Grid-08/08/2024 13:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1324H from forward power direction. [WEBSMS] | CVIS
8/8/2024 1:25:25 PM | [NSO Update] Luzon Grid-08/08/2024 13:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1324H from forward power direction. [WEBSMS] | CLUZ
8/8/2024 1:01:31 PM | [NSO Update] Visayas Grid-08/08/2024 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2695MW, PK=2382MW, RR=91MW, NetOpMargin: PM=221, EVE=231 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @195MW, CEDC 3 @75MW, TGPP @80.3MW, PB104 U3 @5MW, PB104 U4 @7MW [WEBSMS] | CVIS
8/8/2024 12:56:25 PM | [NSO Update] Mindanao Grid-08/08/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3466MW, PK=2494MW, RR=73MW, NetOpMargin: PM=898, EVE=963 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/8/2024 12:53:58 PM | [NSO Update] Luzon Grid-08/08/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14343MW, PK=11817MW, RR=389MW, NetOpMargin: PM=2137, EVE=1315 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, SCPC 1 @130MW, Calaca 1 @150MW, Calaca 2 @180MW, GNPD 2 @550MW, Masinloc 1 @315MW, Masinloc 2 @310MW [WEBSMS] | CLUZ
8/8/2024 12:36:46 PM | Visayas Grid-08/08/2024 12:36: PGPP1 U1 re-online at 1231H (Unplanned Outage) [WEBSMS] | CVIS
8/8/2024 12:08:13 PM | Luzon Grid-08/08/2024 12:08: San Gabriel online at 1203H (Reserve shutdown) [WEBSMS] | CLUZ
8/8/2024 11:14:24 AM | Mindanao Grid-08/08/2024 11:20: WMPC DG08 online at 1113H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/8/2024 10:14:00 AM | Mindanao Grid-08/08/2024 10:13: WMPC DG10 online at 1004H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/8/2024 10:07:37 AM | Mindanao Grid-08/08/2024 10:13: WMPC DG10 online at 1004H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/8/2024 5:29:30 AM | [NSO Update] Mindanao Grid-08/08/2024 05:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3474MW, PK=2431MW, RR=73MW, NetOpMargin: AM=970, PM=922, EVE=982 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/8/2024 4:23:32 AM | [NSO Update] Mindanao Grid-08/08/2024 04:23: Weather Update: Southwest Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
8/7/2024 9:55:05 PM | Mindanao Grid-08/07/2024 21:55: WMPC DG10 shutdown at 2146H. End of RPS-System Voltage Requirement [WEBSMS] | CMIN
8/7/2024 9:25:45 PM | [NSO Update] Visayas Grid-08/07/2024 21:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2056H with power going to Luzon [WEBSMS] | CVIS
8/7/2024 9:25:03 PM | [NSO Update] Luzon Grid-08/07/2024 21:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2056H with power going to Luzon [WEBSMS] | CLUZ
8/7/2024 9:23:18 PM | [NSO Update] Visayas Grid-08/07/2024 21:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2046H from reverse power direction [WEBSMS] | CVIS
8/7/2024 9:22:57 PM | [NSO Update] Luzon Grid-08/07/2024 21:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2046H from reverse power direction [WEBSMS] | CLUZ
8/7/2024 9:09:32 PM | Mindanao Grid-08/07/2024 21:15: WMPC DG01 shutdown at 2101H. End of RPS-System Voltage Requirement [WEBSMS] | CMIN
8/7/2024 6:06:52 PM | [NSO Update] Mindanao Grid-08/07/2024 18:13: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3432MW, PK=2372MW, RR=73MW, NetOpMargin: EVE=987 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/7/2024 5:59:02 PM | [NSO Update] Visayas Grid-08/07/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2600MW, PK=2272MW, RR=90MW, NetOpMargin: EVE=238 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @200MW, CEDC 3 @75MW, TGPP @80.3MW [WEBSMS] | CVIS
8/7/2024 5:57:03 PM | [NSO Update] Luzon Grid-08/07/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13185MW, PK=11519MW, RR=278MW, NetOpMargin: EVE=1388 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, Masinloc 1 @310MW, Masinloc 3 @325MW, SCPC 1 @130MW, Calaca 2 @258MW [WEBSMS] | CLUZ
8/7/2024 5:01:16 PM | Luzon Grid-08/07/2024 17:01: Naga-Tiwi C 230kV Line 2 restored at 1701H (Planned Outage) [WEBSMS] | CLUZ
8/7/2024 3:30:42 PM | Luzon Grid-08/07/2024 15:30: EERI 2 online at 1525H. (On test and commissioning) [WEBSMS] | CLUZ
8/7/2024 1:53:09 PM | [NSO Update] Visayas Grid-08/07/2024 13:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1350H with power going to Visayas [WEBSMS] | CVIS
8/7/2024 1:52:25 PM | [NSO Update] Luzon Grid-08/07/2024 13:52: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1350H with power going to Visayas [WEBSMS] | CLUZ
8/7/2024 1:46:20 PM | [NSO Update] Luzon Grid-08/07/2024 13:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1339H from forward power direction [WEBSMS] | CLUZ
8/7/2024 1:45:43 PM | [NSO Update] Visayas Grid-08/07/2024 13:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1339H from forward power direction [WEBSMS] | CVIS
8/7/2024 1:04:55 PM | [NSO Update] Mindanao Grid-08/07/2024 13:11: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3476MW, PK=2454MW, RR=73MW, NetOpMargin: PM=948, EVE=1014 Highest Unit O/L: GNPK 151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/7/2024 1:01:34 PM | [NSO Update] Visayas Grid-08/07/2024 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2707MW, PK=2362MW, RR=89MW, NetOpMargin: PM=256, EVE=229 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @190MW, CEDC 3 @75MW, TGPP @80.3MW, PCPC @67.5MW, PDPP1 U2 @3.5MW [WEBSMS] | CVIS
8/7/2024 12:51:48 PM | [NSO Update] Luzon Grid-08/07/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13558MW, PK=12032MW, RR=309MW, NetOpMargin: PM=1217, EVE=815 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, Masinloc 1 @310MW, Masinloc 3 @300MW, SCPC 1 @130MW, Calaca 2 @270MW, Masinloc 2 @130MW [WEBSMS] | CLUZ
8/7/2024 12:32:42 PM | Luzon Grid-08/07/2024 12:32: Pagbilao 2 online at 1231H (Unplanned Outage) [WEBSMS] | CLUZ
8/7/2024 12:04:58 PM | Mindanao Grid-08/07/2024 12:11: Asiga Hydro online at 1131H (Unplanned Outage) [WEBSMS] | CMIN
8/7/2024 11:57:47 AM | Luzon Grid-08/07/2024 11:57: GNPD 2 online at 1156H (Unplanned Outage) [WEBSMS] | CLUZ
8/7/2024 11:19:44 AM | Mindanao Grid-08/07/2024 11:26: LAKE MAINIT hydro online at 1118H (Unplanned Outage) [WEBSMS] | CMIN
8/7/2024 10:20:30 AM | Mindanao Grid-08/07/2024 10:26: WMPC DG01 online at 1018H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/7/2024 10:06:33 AM | Mindanao Grid-08/07/2024 10:12: ASIGA Hydro with 4.7MW load isolated at 0941H due to tripping of Butuan-Santiago 69 kV feeder (Unplanned Outage) [WEBSMS] | CMIN
8/7/2024 10:05:51 AM | Mindanao Grid-08/07/2024 10:12: LAKE MAINIT Hydro with 8.5MW load isolated at 0941H due to tripping of Butuan-Santiago 69 kV feeder (Unplanned Outage) [WEBSMS] | CMIN
8/7/2024 9:22:48 AM | Mindanao Grid-08/07/2024 09:29: WMPC DG10 online at 0913H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/7/2024 6:18:28 AM | Luzon Grid-08/07/2024 06:18: Naga-Tiwi C 230kV Line 2 de-energized at 0618H (Planned Outage) [WEBSMS] | CLUZ
8/7/2024 5:46:55 AM | [NSO Update] Mindanao Grid-08/07/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3485MW, PK=2396MW, RR=73MW, NetOpMargin: AM=1017, PM=924, EVE=1067 Highest Unit O/L: GNPK 151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/7/2024 5:45:27 AM | [NSO Update] Visayas Grid-08/07/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2791MW, PK=2302MW, RR=91MW, NetOpMargin: AM=398, PM=398, EVE=334 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @195MW, CEDC 3 @75MW, TGPP @80.3MW, PCPC @67.5MW [WEBSMS] | CVIS
8/7/2024 5:40:22 AM | [NSO Update] Luzon Grid-08/07/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13702MW, PK=11696MW, RR=342MW, NetOpMargin: AM=1664, PM=1458, EVE=1241 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, Masinloc 1 @270MW, Masinloc 3 @300MW, SCPC 1 @130MW, Calaca 2 @258MW [WEBSMS] | CLUZ
8/7/2024 5:02:09 AM | Luzon Grid-08/07/2024 05:02: Masinloc Unit 2 online at 0500H (Unplanned Outage) [WEBSMS] | CLUZ
8/7/2024 4:13:14 AM | [NSO Update] Mindanao Grid-08/07/2024 04:19: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 575 km Northeast of Itbayat, Batanes (24.6�N, 125.6�E). Southwest Monsoon affecting Central and Southern Luzon, and Visayas. [WEBSMS] | CMIN
8/7/2024 4:12:49 AM | [NSO Update] Visayas Grid-08/07/2024 04:12: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 575 km Northeast of Itbayat, Batanes (24.6�N, 125.6�E). Southwest Monsoon affecting Central and Southern Luzon, and Visayas. [WEBSMS] | CVIS
8/7/2024 4:12:25 AM | [NSO Update] Luzon Grid-08/07/2024 04:12: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 575 km Northeast of Itbayat, Batanes (24.6�N, 125.6�E). Southwest Monsoon affecting Central and Southern Luzon, and Visayas. [WEBSMS] | CLUZ
8/7/2024 1:11:35 AM | Luzon Grid-08/07/2024 01:12: Masinloc Unit 2 tripped at 0107H from 76MW load. (Unplanned Outage) [WEBSMS] | CLUZ
8/6/2024 8:50:08 PM | Mindanao Grid-08/06/2024 20:56: WMPC DG10 shutdown at 2047H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/6/2024 7:22:48 PM | Luzon Grid-08/06/2024 19:23: Masinloc 2 online at 1922H (Planned Outage) [WEBSMS] | CLUZ
8/6/2024 5:41:52 PM | [NSO Update] Luzon Grid-08/06/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12096MW, PK=10782MW, RR=398MW, NetOpMargin: EVE=916 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, Masinloc 1 @310MW, Masinloc 3 @295MW, SCPC 1 @130MW, Ilijan B @450MW, Calaca 1 @193MW [WEBSMS] | CLUZ
8/6/2024 5:38:27 PM | [NSO Update] Mindanao Grid-08/06/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3422MW, PK=2374MW, RR=73MW, NetOpMargin: EVE=975 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/6/2024 5:34:36 PM | [NSO Update] Visayas Grid-08/06/2024 17:35: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2509MW, PK=2169MW, RR=90MW, NetOpMargin: EVE=250 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @183MW, CEDC 3 @75MW, TGPP @80.3MW, PGPP1 @71MW [WEBSMS] | CVIS
8/6/2024 4:54:03 PM | Mindanao Grid-08/06/2024 17:00: WMPC DG8 shutdown at 1648H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/6/2024 4:47:56 PM | Mindanao Grid-08/06/2024 16:54: Lala SS AC Filter No.5 declared available at 1638H. (Unplanned Outage) [WEBSMS] | CMIN
8/6/2024 3:57:07 PM | Visayas Grid-08/06/2024 15:57: SCBP cut-in at 1553H. (Unplanned Outage) [WEBSMS] | CVIS
8/6/2024 3:36:56 PM | Luzon Grid-08/06/2024 15:37: EERI Unit 2 tripped at 1524H (On Testing and Commissioning). [WEBSMS] | CLUZ
8/6/2024 3:12:19 PM | Visayas Grid-08/06/2024 15:12: SCBP tripped at 1507H. (Unplanned Outage) [WEBSMS] | CVIS
8/6/2024 2:22:44 PM | Mindanao Grid-08/06/2024 14:29: Kibawe-Sultan Kudarat 138kVL auto-tripped and auto-reclosed at Kibawe SS side only, at 1359H. Said TL successfully restored/looped at 1407H. From Unplanned Outage. [WEBSMS] | CMIN
8/6/2024 2:15:40 PM | Mindanao Grid-08/06/2024 14:22: Update: Kibawe-Sultan Kudarat 138kV Line auto-tripped, and auto-reclosed at Kibawe SS side only at 1359H. Said TL is restored/completely looped at 1407H. From Unplanned Outage. [WEBSMS] | CMIN
8/6/2024 2:07:37 PM | Mindanao Grid-08/06/2024 14:14: Kibawe-Sultan Kudarat (Kibawe-Nuling 138kVL) 138kV L auto-tripped at 1359H. Unplanned Outage. [WEBSMS] | CMIN
8/6/2024 1:02:14 PM | [NSO Update] Mindanao Grid-08/06/2024 13:09: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3464MW, PK=2476MW, RR=73MW, NetOpMargin: PM=915, EVE=1021 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/6/2024 12:57:42 PM | [NSO Update] Visayas Grid-08/06/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2731MW, PK=2248MW, RR=89MW, NetOpMargin: PM=394, EVE=287 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @170MW, CEDC 3 @75MW, TGPP @80.3MW, PGPP1 @71MW [WEBSMS] | CVIS
8/6/2024 12:54:17 PM | [NSO Update] Luzon Grid-08/06/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13018MW, PK=11717MW, RR=389MW, NetOpMargin: PM=913, EVE=813 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @295MW, SCPC 1 @130MW, Ilijan B @450MW, Calaca 1 @184MW [WEBSMS] | CLUZ
8/6/2024 11:30:48 AM | Mindanao Grid-08/06/2024 11:37: WMPC DG10 online at 1124H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/6/2024 11:20:48 AM | Mindanao Grid-08/06/2024 11:27: WMPC DG4 tripped at 1115H while running as RPS due to Turbo Charger Trip indication. (Unplanned Outage) [WEBSMS] | CMIN
8/6/2024 10:52:33 AM | Mindanao Grid-08/06/2024 10:59: WMPC DG8 online at 1044H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/6/2024 10:29:51 AM | Luzon Grid-08/06/2024 10:30: Pagbilao 2 with 377MW tripped at 1023H. Lowest system frequency was 59.405Hz. (Unplanned Outage) [WEBSMS] | CLUZ
8/6/2024 9:59:29 AM | Mindanao Grid-08/06/2024 10:06: WMPC DG4 online at 0956H. RPS - System Voltage Requirement. Replacement Unit. [WEBSMS] | CMIN
8/6/2024 9:53:57 AM | Visayas Grid-08/06/2024 09:54: PGPP2 Sogongon U2 cut-in at 0953H. (Unplanned Outage) [WEBSMS] | CVIS
8/6/2024 9:37:58 AM | Mindanao Grid-08/06/2024 09:44: WMPC DG10 tripped at 0935H. (Unplanned Outage) [WEBSMS] | CMIN
8/6/2024 9:25:46 AM | Mindanao Grid-08/06/2024 09:32: WMPC DG10 online at 0924H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/6/2024 6:08:06 AM | Visayas Grid-08/06/2024 06:08: PGPP2 Sogongon U2 emergency shutdown at 0605H. (Unplanned Outage) [WEBSMS] | CVIS
8/6/2024 6:06:06 AM | [NSO Update] Luzon Grid-08/06/2024 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13642MW, PK=11469MW, RR=382MW, NetOpMargin: AM=1792, PM=1150, EVE=755 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @300MW, SCPC 1 @130MW, Ilijan B @450MW, Calaca 1 @150MW [WEBSMS] | CLUZ
8/6/2024 5:39:29 AM | [NSO Update] Visayas Grid-08/06/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2791MW, PK=2181MW, RR=86MW, NetOpMargin: AM=524, PM=337, EVE=248 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @200MW, CEDC 3 @75MW, TGPP @80.3MW, PGPP1 @71MW [WEBSMS] | CVIS
8/6/2024 5:39:26 AM | [NSO Update] Mindanao Grid-08/06/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3472MW, PK=2347MW, RR=73MW, NetOpMargin: AM=1052, PM=967, EVE=1064 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/6/2024 4:28:47 AM | [NSO Update] Mindanao Grid-08/06/2024 04:35: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 835 km East Northeast of Extreme Northern Luzon (24.8�N, 128.7�E). Southwest Monsoon affecting Southern Luzon and Visayas. [WEBSMS] | CMIN
8/6/2024 4:12:05 AM | [NSO Update] Visayas Grid-08/06/2024 04:12: Weather Advisory: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 835 km East Northeast of Extreme Northern Luzon (24.8�N, 128.7�E). Southwest Monsoon affecting Southern Luzon and Visayas. [WEBSMS] | CVIS
8/6/2024 4:12:01 AM | [NSO Update] Luzon Grid-08/06/2024 04:12: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 835 km East Northeast of Extreme Northern Luzon (24.8�N, 128.7�E). Southwest Monsoon affecting Southern Luzon and Visayas. [WEBSMS] | CLUZ
8/6/2024 4:09:16 AM | Mindanao Grid-08/06/2024 04:16: Kidapawan-Mt. Apo 3 69kV Line de-energized at 0406H. Planned Outage. [WEBSMS] | CMIN
8/6/2024 3:35:02 AM | Visayas Grid-08/06/2024 03:35: Compostela-Consolacion 69 kV Line auto reclosed at 0328H (Unplanned Outage) [WEBSMS] | CVIS
8/6/2024 12:49:31 AM | Luzon Grid-08/06/2024 00:49: Calaca Unit 2 online at 0048H (Unplanned Outage) [WEBSMS] | CLUZ
8/6/2024 12:09:21 AM | Mindanao Grid-08/06/2024 00:16: MT. APO 3 shutdown at 0002H (Planned Outage) [WEBSMS] | CMIN
8/5/2024 7:56:16 PM | Mindanao Grid-08/05/2024 20:03: WMPC DG10 shutdown at 1955H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/5/2024 5:41:29 PM | [NSO Update] Mindanao Grid-08/05/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3345MW, PK=2280MW, RR=73MW, NetOpMargin: EVE=992 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/5/2024 5:41:24 PM | [NSO Update] Visayas Grid-08/05/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2510MW, PK=2136MW, RR=88MW, NetOpMargin: EVE=285 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @192MW, CEDC 3 @75MW, TGPP @80.3MW, PGPP1 @71MW [WEBSMS] | CVIS
8/5/2024 5:41:19 PM | [NSO Update] Luzon Grid-08/05/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12203MW, PK=10840MW, RR=358MW, NetOpMargin: EVE=1005 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @300MW, SCPC 1 @130MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/5/2024 4:51:19 PM | Visayas Grid-08/05/2024 16:51: Daanbantayan SS 230 kV Bus 1 energized at 1648H. (Planned Outage) [WEBSMS] | CVIS
8/5/2024 4:06:31 PM | Mindanao Grid-08/05/2024 16:13: WMPC DG01 shutdown at 1601H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/5/2024 3:08:06 PM | Mindanao Grid-08/05/2024 15:14: MCC Unit 3 online at 1504H (Unplanned Outage) [WEBSMS] | CMIN
8/5/2024 1:16:04 PM | Mindanao Grid-08/05/2024 13:22: SPGI online at 1238H (Unplanned Outage) [WEBSMS] | CMIN
8/5/2024 1:15:47 PM | Mindanao Grid-08/05/2024 13:22: WMPC DG01 online at 1302H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/5/2024 12:45:26 PM | [NSO Update] Mindanao Grid-08/05/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3385MW, PK=2385MW, RR=73MW, NetOpMargin: PM=927, EVE=1039 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/5/2024 12:44:09 PM | [NSO Update] Visayas Grid-08/05/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2757MW, PK=2303MW, RR=86MW, NetOpMargin: PM=369, EVE=249 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @192MW, CEDC 3 @75MW, TGPP @80.3MW, PGPP1 @71MW [WEBSMS] | CVIS
8/5/2024 12:41:25 PM | [NSO Update] Luzon Grid-08/05/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13226MW, PK=11859MW, RR=389MW, NetOpMargin: PM=979, EVE=714 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @290MW, SCPC 1 @130MW, Ilijan B @450MW [WEBSMS] | CLUZ
8/5/2024 11:57:18 AM | Mindanao Grid-08/05/2024 12:04: Kibawe-Maramag 138kV Line 2 energized at 1155H. Planned Outage. [WEBSMS] | CMIN
8/5/2024 10:41:38 AM | Luzon Grid-08/05/2024 10:42: EERI Unit 2 online at 1035H (On Testing and Commissioning) [WEBSMS] | CLUZ
8/5/2024 10:26:47 AM | Luzon Grid-08/05/2024 10:27: San Gabriel online at 1025H (Reserve Shutdown) [WEBSMS] | CLUZ
8/5/2024 10:21:38 AM | Visayas Grid-08/05/2024 10:22: PGPP2 Sogongon U1 cut-in at 1017H. (Unplanned Outage) [WEBSMS] | CVIS
8/5/2024 9:44:23 AM | Mindanao Grid-08/05/2024 09:51: WMPC DG10 online at 0941H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/5/2024 9:30:29 AM | Luzon Grid-08/05/2024 09:30: Hermosa-Duhat 230kV Line restored at 0930H (Unplanned Outage) [WEBSMS] | CLUZ
8/5/2024 9:15:32 AM | Luzon Grid-08/05/2024 09:15: Hermosa-Duhat 230kV Line tripped at 0913H (Unplanned Outage) [WEBSMS] | CLUZ
8/5/2024 9:00:45 AM | Visayas Grid-08/05/2024 09:01: Daanbantayan SS 230 kV Bus 1 de-energized at 0858H. (Planned Outage) [WEBSMS] | CVIS
8/5/2024 8:59:32 AM | Mindanao Grid-08/05/2024 09:06: Kibawe-Maramag 138kV Line 2 de-energized at 0855H. Planned Outage. [WEBSMS] | CMIN
8/5/2024 8:04:47 AM | Mindanao Grid-08/05/2024 08:11: PULANGI 4 Unit 3 shutdown at 0803H (Planned Outage) [WEBSMS] | CMIN
8/5/2024 6:59:36 AM | Mindanao Grid-08/05/2024 07:06: LAMSAN Biomass online at 0600H (Unplanned Outage) [WEBSMS] | CMIN
8/5/2024 6:44:45 AM | Mindanao Grid-08/05/2024 06:51: LAMSAN Biomass with 13.5MW load (net) tripped at 0457H. Indication: Turbine Trip due to STG Inlet Temperature High High (Unplanned Outage) [WEBSMS] | CMIN
8/5/2024 6:12:11 AM | Visayas Grid-08/05/2024 06:12: PEDC U1 cut-in at 0610H. (Unplanned Outage) [WEBSMS] | CVIS
8/5/2024 6:10:00 AM | Visayas Grid-08/05/2024 06:10: PGPP2 Sogongon U1 emergency shutdown at 0604H. (Unplanned Outage) [WEBSMS] | CVIS
8/5/2024 5:55:01 AM | [NSO Update] Mindanao Grid-08/05/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3395MW, PK=2238MW, RR=73MW, NetOpMargin: AM=1084, PM=932, EVE=1022 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/5/2024 5:53:59 AM | [NSO Update] Visayas Grid-08/05/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2714MW, PK=2202MW, RR=86MW, NetOpMargin: AM=427, PM=252, EVE=231 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @200MW, CEDC 3 @75MW, TGPP @80.3MW, PDPP3-E @8MW, PGPP1 @71MW, PB101-2 @5.5MW, PB104-2 @4.5MW, PB104-3 @5MW, PDPP1-U2 @4MW, PDPP1-U3 @4MW, PDPP1-U5 @4MW, PDPP3-H @8MW, PB104-4 @5.5MW [WEBSMS] | CVIS
8/5/2024 5:52:50 AM | [NSO Update] Luzon Grid-08/05/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13471MW, PK=11100MW, RR=422MW, NetOpMargin: AM=1949, PM=1456, EVE=966 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @290MW, SCPC 1 @130MW, Ilijan B @490MW [WEBSMS] | CLUZ
8/5/2024 4:07:20 AM | [NSO Update] Luzon Grid-08/05/2024 04:07: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,155 km East Northeast of Extreme Northern Luzon (24.1�N, 132.5�E). Southwest Monsoon affecting Palawan, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/5/2024 4:06:13 AM | [NSO Update] Visayas Grid-08/05/2024 04:06: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,155 km East Northeast of Extreme Northern Luzon (24.1�N, 132.5�E). Southwest Monsoon affecting Palawan, Visayas, and Mindanao. [WEBSMS] | CVIS
8/5/2024 4:05:30 AM | [NSO Update] Mindanao Grid-08/05/2024 04:12: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,155 km East Northeast of Extreme Northern Luzon (24.1�N, 132.5�E). Southwest Monsoon affecting Palawan, Visayas, and Mindanao. [WEBSMS] | CMIN
8/5/2024 2:29:41 AM | Luzon Grid-08/05/2024 02:30: San Gabriel shutdown at 0228H (Reserve Shutdown) [WEBSMS] | CLUZ
8/5/2024 1:46:53 AM | Luzon Grid-08/05/2024 01:47: MPGC 3 shutdown at 0143H (Unplanned Outage) [WEBSMS] | CLUZ
8/5/2024 12:56:52 AM | Visayas Grid-08/05/2024 00:57: EDC-Mahanagdong total plant shutdown at 0042H (Planned Outage) [WEBSMS] | CVIS
8/4/2024 6:27:49 PM | Luzon Grid-08/04/2024 18:28: Botolan-Subic 230kV Line restored at 1827H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 6:16:42 PM | Mindanao Grid-08/04/2024 18:23: Nabunturan SS 100MVA Power Transformer No.1 energized/restored at 1813H. From Planned Outage/GOMP. [WEBSMS] | CMIN
8/4/2024 5:52:54 PM | Luzon Grid-08/04/2024 17:53: San Esteban-Bantay 115kV Line restored at 1752H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 5:51:31 PM | Luzon Grid-08/04/2024 17:51: San Esteban SS 100MVA T02 restored at 1751H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 5:44:53 PM | [NSO Update] Mindanao Grid-08/04/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3365MW, PK=2119MW, RR=73MW, NetOpMargin: EVE=1173 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/4/2024 5:43:52 PM | [NSO Update] Visayas Grid-08/04/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2512MW, PK=1996MW, RR=81MW, NetOpMargin: EVE=435 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @286MW, CEDC 3 @75MW, TGPP @80.3MW, PGPP2 SOG1 @18MW, PDPP3-E @8MW, PGPP1 @71MW, PB101-2 @5.5MW, PB104-2 @4.5MW, PB104-3 @5MW, PDPP1-U2 @4MW, PDPP1-U3 @4MW, PDPP1-U5 @4MW, PDPP3-H @8MW [WEBSMS] | CVIS
8/4/2024 5:42:03 PM | [NSO Update] Luzon Grid-08/04/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12249MW, PK=9982MW, RR=310MW, NetOpMargin: EVE=1957 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: SLTEC 2 @115MW, Limay 8 @60MW, Masinloc 1 @300MW, Masinloc 3 @290MW, SCPC 1 @130MW, Ilijan B @490MW [WEBSMS] | CLUZ
8/4/2024 5:28:51 PM | Visayas Grid-08/04/2024 17:29: Daanbantayan - Tabango 230 kV Line 2 energized at 1726H (Planned Outage) [WEBSMS] | CVIS
8/4/2024 5:01:52 PM | Luzon Grid-08/04/2024 17:02: San Gabriel online at 1659H (Reserved Shutdown) [WEBSMS] | CLUZ
8/4/2024 4:54:15 PM | Luzon Grid-08/04/2024 16:54: Taytay SS 300MVA T05 restored at 1653H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 4:51:24 PM | Luzon Grid-08/04/2024 16:51: Taytay SS 230kV Bus 2 restored at 1651H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 4:48:21 PM | Mindanao Grid-08/04/2024 16:55: Baloi-Tagoloan 138kV L energized/restored at 1643H. From Planned Outage/GOMP. [WEBSMS] | CMIN
8/4/2024 4:01:41 PM | Luzon Grid-08/04/2024 16:02: EERI 2 shutdown at 1559H (On commisssioning) [WEBSMS] | CLUZ
8/4/2024 3:14:50 PM | Visayas Grid-08/04/2024 15:15: PGPP1 U3 cut-in at 1513H (Unplanned Outage) [WEBSMS] | CVIS
8/4/2024 3:03:25 PM | Mindanao Grid-08/04/2024 15:10: Jasaan-Butuan 138kV L energized/restored at 1459H. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/4/2024 12:42:29 PM | [NSO Update] Mindanao Grid-08/04/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3406MW, PK=1912MW, RR=73MW, NetOpMargin: PM=1421, EVE=1215 Highest Unit O/L: GNPK 1 @151.MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/4/2024 12:32:11 PM | [NSO Update] Visayas Grid-08/04/2024 12:32: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2706MW, PK=1813MW, RR=79MW, NetOpMargin: PM=814, EVE=407 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @280MW, CEDC 3 @75MW, TGPP @80.3MW, PGPP2 SOG1 @18MW, PDPP3-E @8MW, PGPP1 @76MW, PB101-2 @5.5MW, PB104-2 @4.5MW, PB104-3 @5MW, PDPP1-U2 @4MW, PDPP1-U3 @4MW, PDPP1-U5 @4MW [WEBSMS] | CVIS
8/4/2024 12:29:18 PM | [NSO Update] Luzon Grid-08/04/2024 12:29: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13396MW, PK=10038MW, RR=299MW, NetOpMargin: PM=3058, EVE=1866 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @115MW, Limay 8 @60MW, Masinloc 1 @290MW, Masinloc 3 @290MW, SCPC 1 @130MW, Ilijan A @300MW [WEBSMS] | CLUZ
8/4/2024 12:19:52 PM | Luzon Grid-08/04/2024 12:20: Ilijan GT1-1 online at 1218H (Reserve Shutdown) [WEBSMS] | CLUZ
8/4/2024 11:14:08 AM | Luzon Grid-08/04/2024 11:14: Quezon 300MVA T03 restored at 1112H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 9:05:20 AM | Mindanao Grid-08/04/2024 09:12: Jasaan-Butuan 138kV L deenergized/shutdown at 0859H. Planned Outage/Non-GOMP. (Note: MD4 approved request shutdown) [WEBSMS] | CMIN
8/4/2024 9:01:13 AM | Visayas Grid-08/04/2024 09:01: Mandaue GIS 69 kV Feeders 1 and 4 energized at 0900H and 0859H, respectively (Unplanned Outage) [WEBSMS] | CVIS
8/4/2024 8:34:25 AM | Mindanao Grid-08/04/2024 08:41: Baloi-Tagoloan 138kV L deenergized/shutdown at 0818H. Planned Outage/GOMP. [WEBSMS] | CMIN
8/4/2024 8:02:52 AM | Mindanao Grid-08/04/2024 08:09: Baloi - Agus 6 138kV L2 energized/restored at 0759H. From Planned Outage /Non-GOMP. (Note: P&E approved shutdown activities) [WEBSMS] | CMIN
8/4/2024 7:33:18 AM | Mindanao Grid-08/04/2024 07:40: Nabunturan SS 100MVA Power Transformer No.1 deenergized at 0721H. Planned Outage/GOMP. [WEBSMS] | CMIN
8/4/2024 7:09:00 AM | Luzon Grid-08/04/2024 07:09: Taytay SS 230kV Bus 2 de-energized at 0708H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 7:07:45 AM | Luzon Grid-08/04/2024 07:08: Taytay SS 300MVA T05 de-energized at 0706H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 7:01:05 AM | Visayas Grid-08/04/2024 07:01: Daanbantayan - Tabango 230 kV Line 2 de-energized at 0700H (Planned Outage) [WEBSMS] | CVIS
8/4/2024 6:35:58 AM | Luzon Grid-08/04/2024 06:36: San Esteban SS 100MVA T02 de-energized at 0635H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 6:33:57 AM | Luzon Grid-08/04/2024 06:34: San Esteban-Bantay 115kV Line de-energized at 0633H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 6:07:42 AM | Luzon Grid-08/04/2024 06:08: Botolan-Subic 230kV Line de-energized at 0606H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 5:48:57 AM | Luzon Grid-08/04/2024 05:49: San Gabriel shutdown at 0529H (Reserve Shutdown) [WEBSMS] | CLUZ
8/4/2024 5:44:35 AM | [NSO Update] Mindanao Grid-08/04/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3415MW, PK=1874MW, RR=73MW, NetOpMargin: AM=1468, PM=1390, EVE=1234 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/4/2024 5:44:03 AM | [NSO Update] Visayas Grid-08/04/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2594MW, PK=1803MW, RR=80MW, NetOpMargin: AM=711, PM=682, EVE=378 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @287MW, CEDC 3 @75MW, TGPP @80.3MW, PGPP2 SOG1 @18MW, PDPP3-E @8MW, PGPP1 @76MW, PB101-2 @5.5MW, PB104-2 @4.5MW, PB104-3 @5MW, PDPP1-U2 @4MW, PDPP1-U3 @4MW, PDPP1-U5 @4MW [WEBSMS] | CVIS
8/4/2024 5:43:40 AM | [NSO Update] Luzon Grid-08/04/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13286MW, PK=9153MW, RR=285MW, NetOpMargin: AM=3848, PM=3241, EVE=1638 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @115MW, Limay 8 @60MW, Masinloc 1 @290MW, Masinloc 3 @290MW, SCPC 1 @130MW, Ilijan A @300MW, Calaca 1 @160MW [WEBSMS] | CLUZ
8/4/2024 5:02:56 AM | Luzon Grid-08/04/2024 05:03: Quezon 300MVA T07 and TO8 restored at 0502H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 4:58:38 AM | Luzon Grid-08/04/2024 04:58: Quezon 230kV Bus 2 restored at 0458H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 4:39:28 AM | Mindanao Grid-08/04/2024 04:46: Baloi SS 138kV Bus 1 energized at 0437H. (Planned Outage) [WEBSMS] | CMIN
8/4/2024 4:30:20 AM | [NSO Update] Mindanao Grid-08/04/2024 04:37: Weather Advisory: Southwest Monsoon affecting Visayas and Mindanao. [WEBSMS] | CMIN
8/4/2024 4:30:01 AM | [NSO Update] Visayas Grid-08/04/2024 04:30: Weather Advisory: Southwest Monsoon affecting Visayas and Mindanao. [WEBSMS] | CVIS
8/4/2024 4:29:58 AM | [NSO Update] Luzon Grid-08/04/2024 04:30: Weather Advisory: Southwest Monsoon affecting Visayas and Mindanao. [WEBSMS] | CLUZ
8/4/2024 12:19:19 AM | Luzon Grid-08/04/2024 00:19: Quezon 230kV Bus 2 and Quezon 300MVA T08 (CO) de-energized at 0016H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 12:17:30 AM | Luzon Grid-08/04/2024 00:17: Quezon 300MVA T07 (CO) de-energized at 0014H (Planned Outage) [WEBSMS] | CLUZ
8/4/2024 12:16:16 AM | Luzon Grid-08/04/2024 00:16: Quezon (Balintawak) 300MVA T03 (CO) de-energized at 0013H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 10:56:09 PM | Luzon Grid-08/03/2024 22:56: Ilijan GT 1-1 shutdown at 2253H (Unplanned Outage) [WEBSMS] | CLUZ
8/3/2024 10:46:15 PM | Mindanao Grid-08/03/2024 22:53: Baloi SS 138kV Bus 1 de-energized at 2241H. (Planned Outage) [WEBSMS] | CMIN
8/3/2024 9:37:51 PM | Luzon Grid-08/03/2024 21:38: Concepcion-TERASU Solar PP 69kV Line (CO) restored at 2137H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 9:33:06 PM | Visayas Grid-08/03/2024 21:33: Mandaue GIS 69 kV Feeders 1 and 4 de-energized at 2132H (Unplanned Outage) [WEBSMS] | CVIS
8/3/2024 7:39:03 PM | Luzon Grid-08/03/2024 19:39: Concepcion-UPSI Concepcion BESS 69kV Line (CO) restored at 1938H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 7:24:13 PM | Luzon Grid-08/03/2024 19:24: Concepcion-Concepcion 1 Solar PP 69kV Line (CO) restored at 1924H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 6:53:52 PM | Luzon Grid-08/03/2024 18:54: Hermosa-Calaguiman restored at 1852H (Unplanned Outage) [WEBSMS] | CLUZ
8/3/2024 6:37:55 PM | Visayas Grid-08/03/2024 18:38: Daanbantayan - Tabango 230 kV Line 1 energized at 1837H (Planned Outage) [WEBSMS] | CVIS
8/3/2024 6:30:59 PM | Luzon Grid-08/03/2024 18:31: Paguludan-Currimao Solar Line 2 69kV restored at 1829H (Unplanned Outage) [WEBSMS] | CLUZ
8/3/2024 6:20:40 PM | Luzon Grid-08/03/2024 18:20: Taytay SS 230kV Bus 1 restored at 1819H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 6:01:34 PM | Mindanao Grid-08/03/2024 18:08: Agus 5 Unit 1 online at 1801H (Planned Outage) [WEBSMS] | CMIN
8/3/2024 5:48:03 PM | Mindanao Grid-08/03/2024 17:54: Agus 5 SY - Agus 5 HEP 138kV L1 energized at 1744H (Planned Outage) [WEBSMS] | CMIN
8/3/2024 5:39:03 PM | [NSO Update] Mindanao Grid-08/03/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3372MW, PK=2233MW, RR=73MW, NetOpMargin: EVE=1066 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/3/2024 5:39:00 PM | [NSO Update] Luzon Grid-08/03/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12227MW, PK=10328MW, RR=397MW, NetOpMargin: EVE=1502 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @117MW, Limay 8 @60MW, Masinloc 1 @280MW, Masinloc 3 @300MW, SCPC 1 @130MW, Ilijan A @490MW [WEBSMS] | CLUZ
8/3/2024 5:38:58 PM | [NSO Update] Visayas Grid-08/03/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2530MW, PK=2120MW, RR=90MW, NetOpMargin: EVE=320 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @316MW, CEDC 3 @75MW, TGPP @80.3MW, PGPP2 SOG1 @18MW, PDPP3-E @8MW, PCPC @125MW, PGPP1 @76MW, PB101-2 @5.5MW, PB104-2 @4.5MW, PB104-3 @5MW, PDPP1-U2 @4MW, PDPP1-U3 @4MW, PDPP1-U5 @4MW [WEBSMS] | CVIS
8/3/2024 5:19:33 PM | Luzon Grid-08/03/2024 17:19: La Trinidad SS 230kV Bus 2 restored at 1718H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 5:00:21 PM | Visayas Grid-08/03/2024 17:00: Colon SS 138 kV Bus 1 energized at 1659H. (Planned Outage) [WEBSMS] | CVIS
8/3/2024 4:02:08 PM | Luzon Grid-08/03/2024 16:02: San Gabriel online at 1600H (Reserve Shutdown) [WEBSMS] | CLUZ
8/3/2024 2:17:13 PM | Luzon Grid-08/03/2024 14:17: Correction: San Jose-Camarin 115kV Line restored at 1411H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 2:13:09 PM | Luzon Grid-08/03/2024 14:13: San Jose-Camarin 115kV Line de-energized at 1411H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 2:11:42 PM | Luzon Grid-08/03/2024 14:12: Paguludan-Curimmao Phase 2 69kV de-energized at 1405H (Unplanned Outage) [WEBSMS] | CLUZ
8/3/2024 2:09:03 PM | Mindanao Grid-08/03/2024 14:15: Baloi - Agus 6 138kV L2 de-energized at 1407H. (Planned Outage) [WEBSMS] | CMIN
8/3/2024 12:42:42 PM | [NSO Update] Luzon Grid-08/03/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13504MW, PK=10749MW, RR=427MW, NetOpMargin: PM=2327, EVE=1375 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @117MW, Limay 8 @60MW, Masinloc 1 @280MW, Masinloc 3 @300MW, SCPC 1 @130MW, Ilijan A @490MW [WEBSMS] | CLUZ
8/3/2024 12:34:49 PM | [NSO Update] Visayas Grid-08/03/2024 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2698MW, PK=2118MW, RR=84MW, NetOpMargin: PM=495, EVE=240 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, CEDC 3 @75MW, TGPP @80.3MW, PGPP2 SOG1 @18MW, PDPP3-E @8MW, PCPC @67.5MW, PGPP1 @76MW, PB101-2 @5.5MW, PB104-2 @4.5MW, PB104-3 @5MW, PDPP1-U2 @4MW, PDPP1-U3 @4MW, PDPP1-U5 @4MW [WEBSMS] | CVIS
8/3/2024 12:33:25 PM | [NSO Update] Mindanao Grid-08/03/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3412MW, PK=2249MW, RR=73MW, NetOpMargin: PM=1089, EVE=1013 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/3/2024 12:33:03 PM | Luzon Grid-08/03/2024 12:33: Balsik SS PCB 9Z-01CB24BIK restored at 1232H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 11:58:21 AM | Luzon Grid-08/03/2024 11:58: San Jose-Camarin 115kV Line de-energized at 1147H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 11:36:39 AM | Mindanao Grid-08/03/2024 11:43: AGUS 5 Unit 1 shutdown at 0603H (Planned Outage) [WEBSMS] | CMIN
8/3/2024 11:29:26 AM | Luzon Grid-08/03/2024 11:29: San Jose-North Caloocan 115kV Line restored at 1127H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 11:21:07 AM | Luzon Grid-08/03/2024 11:21: SLPGC-Calaca 230kV Line 1 de-energized at 1118H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 11:18:35 AM | Mindanao Grid-08/03/2024 11:25: Butuan - Placer 138kV L1 energized at 1116H. (Planned Outage) [WEBSMS] | CMIN
8/3/2024 10:52:13 AM | Visayas Grid-08/03/2024 10:52: Amlan-Palinpinon 138KV Line 2 energized at 1047H. (Unplanned Outage) [WEBSMS] | CVIS
8/3/2024 10:25:32 AM | Luzon Grid-08/03/2024 10:25: Correction: San Gabriel shutdown at 0629H (Reserve Shutdown) [WEBSMS] | CLUZ
8/3/2024 10:03:16 AM | Luzon Grid-08/03/2024 10:03: Balsik SS PCB 9Z-01CB24BIK de-energized at 1002H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 10:01:59 AM | Luzon Grid-08/03/2024 10:02: Balsik SS PCB 9Z-01CB08BIK restored at 0952H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 9:41:35 AM | Luzon Grid-08/03/2024 09:41: Correction: San Gabriel shutdown at 0629H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 8:16:54 AM | Luzon Grid-08/03/2024 08:17: Concepcion-Concepcion 1 Solar PP 69kV Line (CO) de-energized at 0814H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 8:16:18 AM | Luzon Grid-08/03/2024 08:16: Concepcion-UPSI Concepcion BESS 69kV Line (CO) de-energized at 0809H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 8:10:59 AM | Mindanao Grid-08/03/2024 08:17: Butuan - Placer 138kV L1 de-energized at 0808H. (Planned Outage) [WEBSMS] | CMIN
8/3/2024 8:07:06 AM | Mindanao Grid-08/03/2024 08:13: PULANGI 4 Unit 2 online at 0803H (Planned Outage) [WEBSMS] | CMIN
8/3/2024 8:06:17 AM | Luzon Grid-08/03/2024 08:06: Balsik SS PCB 9Z-01CB08BIK de-energized at 0902H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 7:39:10 AM | Luzon Grid-08/03/2024 07:39: San Jose-North Caloocan 115kV Line de-energized at 0738H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 7:21:57 AM | Visayas Grid-08/03/2024 07:22: Daanbantayan-Tabango 230KV Line 1 de-energized at 0719H. (Planned Outage) [WEBSMS] | CVIS
8/3/2024 7:03:24 AM | Luzon Grid-08/03/2024 07:03: Taytay SS 230kV Bus 1 de-energized at 0702H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 6:48:13 AM | Visayas Grid-08/03/2024 06:48: Colon SS 138KV Bus 1 de-energized at 0646H. (Planned Outage) [WEBSMS] | CVIS
8/3/2024 6:33:29 AM | Luzon Grid-08/03/2024 06:33: La Trinidad SS 230kV Bus 2 de-energized at 0633H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 6:32:03 AM | Luzon Grid-08/03/2024 06:32: Concepcion-TERASU Solar PP 69kV Line (CO) de-energized at 0629H (Planned Outage) [WEBSMS] | CLUZ
8/3/2024 6:31:51 AM | Luzon Grid-08/03/2024 06:32: San Gabriel shutdown at 0209H (Reserve Shutdown) [WEBSMS] | CLUZ
8/3/2024 6:12:48 AM | Mindanao Grid-08/03/2024 06:19: Agus 5 SY - Agus 5 HEP 138kV L1 de-energized at 0611H. (Planned Outage) [WEBSMS] | CMIN
8/3/2024 5:54:59 AM | [NSO Update] Mindanao Grid-08/03/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3431MW, PK=2096MW, RR=73MW, NetOpMargin: AM=1261, PM=1160, EVE=1105 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/3/2024 5:53:41 AM | [NSO Update] Visayas Grid-08/03/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2742MW, PK=2007MW, RR=82MW, NetOpMargin: AM=652, PM=538, EVE=334 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @319MW, CEDC 3 @75MW, TGPP @80.3MW, PGPP2 SOG1 @18MW, PDPP3-E @8MW, PCPC @67.5MW, PGPP1 @76MW, PB101-2 @5.5MW, PB104-2 @4.5MW, PB104-3 @5MW, PDPP1-U2 @4MW, PDPP1-U3 @4MW, PDPP1-U5 @4MW [WEBSMS] | CVIS
8/3/2024 5:51:05 AM | [NSO Update] Luzon Grid-08/03/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13637MW, PK=10353MW, RR=418MW, NetOpMargin: AM=2867, PM=2320, EVE=1583 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: SLTEC 2 @116MW, Limay 8 @60MW, Masinloc 1 @280MW, Masinloc 3 @300MW, SCPC 1 @130MW, Ilijan A @490MW [WEBSMS] | CLUZ
8/3/2024 4:05:36 AM | [NSO Update] Luzon Grid-08/03/2024 04:05: Weather Advisory: Southwest Monsoon affecting the western sections of Visayas and Mindanao. [WEBSMS] | CLUZ
8/3/2024 4:05:08 AM | [NSO Update] Visayas Grid-08/03/2024 04:05: Weather Advisory: Southwest Monsoon affecting the western sections of Visayas and Mindanao. [WEBSMS] | CVIS
8/3/2024 4:04:52 AM | [NSO Update] Mindanao Grid-08/03/2024 04:11: Weather Advisory: Southwest Monsoon affecting the western sections of Visayas and Mindanao. [WEBSMS] | CMIN
8/3/2024 3:32:59 AM | Mindanao Grid-08/03/2024 03:39: Agus 6 Unit 5 online at 0330H (Planned Outage) [WEBSMS] | CMIN
8/3/2024 2:17:22 AM | Luzon Grid-08/03/2024 02:17: For info: Sta. Rita-San Lorenzo 230kV Bus A & B Tie Breakers were closed at 0215H, looping Sta. Rita CCPP and San Lorenzo CCPP. The splitting of Batangas 300MVA T04 and T05 was completed at 0211H. Sta. Rita Modules 10 and 20 are on shutdown. [WEBSMS] | CLUZ
8/2/2024 11:45:19 PM | Luzon Grid-08/02/2024 23:45: Sta. Rita Module 10 shutdown at 2344H (Planned Outage) [WEBSMS] | CLUZ
8/2/2024 11:32:11 PM | Visayas Grid-08/02/2024 23:32: PEDC U1 emergency shutdown at 2331H. (Unplanned Outage) [WEBSMS] | CVIS
8/2/2024 8:26:43 PM | Luzon Grid-08/02/2024 20:26: Limay-PAVI Green ORS 69kV Line (CO) restored at 2026H (Planned Outage) [WEBSMS] | CLUZ
8/2/2024 8:17:03 PM | Mindanao Grid-08/02/2024 20:23: WMPC DG10 shutdown at 2016H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/2/2024 7:48:46 PM | Luzon Grid-08/02/2024 19:49: Limay-PAVI Green ORS 69kV Line (CO) de-energized at 1940H (Planned Outage) [WEBSMS] | CLUZ
8/2/2024 6:25:18 PM | Visayas Grid-08/02/2024 18:25: DaanBantayan SS 230 kV bus 2 energized at 1820H (Planned Outage) [WEBSMS] | CVIS
8/2/2024 5:41:41 PM | [NSO Update] Mindanao Grid-08/02/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3318MW, PK=2193MW, RR=73MW, NetOpMargin: EVE=1052 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/2/2024 5:40:46 PM | [NSO Update] Visayas Grid-08/02/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2544MW, PK=2174MW, RR=90MW, NetOpMargin: EVE=279 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @314MW, CEDC 3 @75MW, TGPP @80.3MW, PGPP2 SOG1 @15MW, PDPP3-E @8MW, PCPC @67.5MW [WEBSMS] | CVIS
8/2/2024 5:39:24 PM | [NSO Update] Luzon Grid-08/02/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12501MW, PK=11000MW, RR=398MW, NetOpMargin: EVE=1103 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, Masinloc 1 @275MW, Masinloc 3 @305MW, SCPC 1 @130MW, Ilijan A @490MW, MPGC 3 @90MW, SCPC 3 @140MW [WEBSMS] | CLUZ
8/2/2024 4:57:42 PM | Mindanao Grid-08/02/2024 17:04: WMPC DG01 shutdown at 1657H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/2/2024 2:41:06 PM | Luzon Grid-08/02/2024 14:41: Calaca 1 online at 1440H (Unplanned Outage) [WEBSMS] | CLUZ
8/2/2024 1:23:26 PM | Mindanao Grid-08/02/2024 13:30: WMPC DG01 online at 1317H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/2/2024 1:17:02 PM | [NSO Update] Mindanao Grid-08/02/2024 13:23: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3358MW, PK=2458MW, RR=73MW, NetOpMargin: PM=827, EVE=913 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/2/2024 1:14:51 PM | [NSO Update] Visayas Grid-08/02/2024 13:15: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2674MW, PK=2355MW, RR=86MW, NetOpMargin: PM=233, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @314MW, CEDC 3 @75MW, TGPP @80.3MW [WEBSMS] | CVIS
8/2/2024 1:08:54 PM | Mindanao Grid-08/02/2024 13:15: WMPC DG10 online at 1305H. (Unplanned Outage) [WEBSMS] | CMIN
8/2/2024 1:07:41 PM | Mindanao Grid-08/02/2024 13:14: Update: WMPC DG10 with 10MW load running as RPS tripped at 1242H. Indication: PLC module fault. (Unplanned Outage) [WEBSMS] | CMIN
8/2/2024 1:02:36 PM | [NSO Update] Luzon Grid-08/02/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13424MW, PK=12117MW, RR=429MW, NetOpMargin: PM=878, EVE=707 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, Masinloc 1 @300MW, Masinloc 3 @300MW, SCPC 1 @130MW, Ilijan A @460MW, MPGC 3 @90MW, SCPC 3 @130MW [WEBSMS] | CLUZ
8/2/2024 12:46:34 PM | Mindanao Grid-08/02/2024 12:53: Correction: WMPC DG10 with 10MW load running as RPS tripped at 1242H (Unplanned Outage) [WEBSMS] | CMIN
8/2/2024 10:23:07 AM | Mindanao Grid-08/02/2024 10:29: WMPC DG10 online at 1021H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/2/2024 8:33:09 AM | Visayas Grid-08/02/2024 08:33: Daanbantayan SS 230KV Bus 2 de-energized at 0830H. (Planned Outage) [WEBSMS] | CVIS
8/2/2024 7:09:04 AM | Visayas Grid-08/02/2024 07:09: Carcon-Sangi 34.5 kV Line 1 restored at 0708H. (Unplanned Outage) [WEBSMS] | CVIS
8/2/2024 6:00:29 AM | [NSO Update] Mindanao Grid-08/02/2024 06:07: Weather Update: Southwest Monsoon affecting the western sections of Visayas and Mindanao. [WEBSMS] | CMIN
8/2/2024 6:00:08 AM | [NSO Update] Visayas Grid-08/02/2024 06:00: Weather Update: Southwest Monsoon affecting the western sections of Visayas and Mindanao. [WEBSMS] | CVIS
8/2/2024 5:59:51 AM | [NSO Update] Luzon Grid-08/02/2024 06:00: Weather Update: Southwest Monsoon affecting the western sections of Visayas and Mindanao. [WEBSMS] | CLUZ
8/2/2024 5:48:48 AM | [NSO Update] Mindanao Grid-08/02/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3368MW, PK=2263MW, RR=73MW, NetOpMargin: AM=1032, PM=837, EVE=946 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/2/2024 5:46:52 AM | [NSO Update] Visayas Grid-08/02/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2920MW, PK=2294MW, RR=86MW, NetOpMargin: AM=540, PM=394, EVE=285 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @317MW, CEDC 3 @75MW, TGPP @80.3MW, PGPP1 @76MW [WEBSMS] | CVIS
8/2/2024 5:43:01 AM | [NSO Update] Luzon Grid-08/02/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13851MW, PK=11393MW, RR=422MW, NetOpMargin: AM=2036, PM=1251, EVE=909 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, Masinloc 1 @300MW, Masinloc 3 @300MW, SCPC 1 @130MW, Ilijan A @460MW, MPGC 3 @90MW, SCPC 3 @130MW [WEBSMS] | CLUZ
8/2/2024 5:27:26 AM | Visayas Grid-08/02/2024 05:27: Carcon-Sangi 34.5 kV Line 1 tripped at 0227H. (Unplanned Outage) [WEBSMS] | CVIS
8/2/2024 12:26:49 AM | Mindanao Grid-08/02/2024 00:33: Jasaan-Nasipit 138kV line restored at 0024H. (Unplanned Outage) [WEBSMS] | CMIN
8/1/2024 10:15:14 PM | Visayas Grid-08/01/2024 22:15: Dumanjug SS 100 MVA 138/69/13.8 kV TR2 looped at the 69 kV side (with load) and in parallel operation with TR1 at 2203H (under Test and Commissioning) [WEBSMS] | CVIS
8/1/2024 9:59:22 PM | Mindanao Grid-08/01/2024 22:06: TM2 Unit 1 shutdown at 2156H. End of MRU-Thermal Limit. [WEBSMS] | CMIN
8/1/2024 9:14:36 PM | Luzon Grid-08/01/2024 21:14: Limay - Orion Solar 69kV Line restored at 2113H (Unplanned Outage) [WEBSMS] | CLUZ
8/1/2024 8:16:26 PM | Luzon Grid-08/01/2024 20:16: Limay - Orion Solar 69kV Line tripped at 2012H (Unplanned Outage) [WEBSMS] | CLUZ
8/1/2024 8:10:49 PM | Mindanao Grid-08/01/2024 20:17: WMPC DG10 shutdown at 2009H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/1/2024 5:40:47 PM | [NSO Update] Mindanao Grid-08/01/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3300MW, PK=2280MW, RR=73MW, NetOpMargin: EVE=948 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/1/2024 5:39:35 PM | [NSO Update] Visayas Grid-08/01/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2531MW, PK=2179MW, RR=89MW, NetOpMargin: EVE=263 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @310MW, CEDC 3 @75MW, TPC-Thermal @71MW, TGPP @80.3MW, PGPP1 @75MW, PDPP3-E @8MW, PDPP3-H @8MW [WEBSMS] | CVIS
8/1/2024 5:36:52 PM | [NSO Update] Luzon Grid-08/01/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12460MW, PK=11337MW, RR=397MW, NetOpMargin: EVE=725 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, Masinloc 1 @300MW, Masinloc 3 @315MW, SCPC 1 @130MW, Ilijan A @460MW, MPGC 3 @90MW, SCPC 3 @130MW [WEBSMS] | CLUZ
8/1/2024 5:33:17 PM | [NSO Update] Visayas Grid-08/01/2024 17:33: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1648H with power going to Luzon [WEBSMS] | CVIS
8/1/2024 5:33:01 PM | [NSO Update] Luzon Grid-08/01/2024 17:33: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1648H with power going to Luzon [WEBSMS] | CLUZ
8/1/2024 4:19:03 PM | [NSO Update] Visayas Grid-08/01/2024 16:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1617H from reverse power direction [WEBSMS] | CVIS
8/1/2024 4:18:48 PM | [NSO Update] Luzon Grid-08/01/2024 16:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1617H from reverse power direction [WEBSMS] | CLUZ
8/1/2024 4:14:44 PM | Mindanao Grid-08/01/2024 16:21: Peak Power San Francisco Unit 2 shutdown at 1613H. End of MRU-Thermal Limit. [WEBSMS] | CMIN
8/1/2024 4:14:13 PM | Mindanao Grid-08/01/2024 16:20: Peak Power San Francisco Unit 1 shutdown at 1613H. End of MRU-Thermal Limit. [WEBSMS] | CMIN
8/1/2024 4:12:08 PM | Mindanao Grid-08/01/2024 16:18: TM2 Unit 1 online at 1607H. MRU-Thermal Limit. [WEBSMS] | CMIN
8/1/2024 3:53:59 PM | Luzon Grid-08/01/2024 15:54: Dasmarinas-TMC II (Ternate) 115kV restored at 1548H (Planned Outage) [WEBSMS] | CLUZ
8/1/2024 3:43:17 PM | Mindanao Grid-08/01/2024 15:49: Peak Power San Francisco Unit 2 online at 1536H. MRU-Thermal Limit. [WEBSMS] | CMIN
8/1/2024 3:42:07 PM | Mindanao Grid-08/01/2024 15:48: Peak Power San Francisco Unit 1 online at 1535H. MRU-Thermal Limit. [WEBSMS] | CMIN
8/1/2024 3:39:24 PM | Mindanao Grid-08/01/2024 15:46: Jasaan-Nasipit 138kV line tripped at 1519H. (Unplanned Outage) [WEBSMS] | CMIN
8/1/2024 2:42:34 PM | Mindanao Grid-08/01/2024 14:49: LAMSAN Biomass online at 1409H (Unplanned Outage) [WEBSMS] | CMIN
8/1/2024 2:41:59 PM | Mindanao Grid-08/01/2024 14:48: LAMSAN Biomass with 13.5MW (net) tripped at 1404H. Indication: 50N non-directional earth fault, 50 non-directional overcurrent, 27-under voltage protecton. Affected by Simuay 69 kV line fault (Unplanned Outage) [WEBSMS] | CMIN
8/1/2024 2:39:37 PM | Mindanao Grid-08/01/2024 14:46: LAMSAN Bionass online at 1354H (Unplanned Outage) [WEBSMS] | CMIN
8/1/2024 2:39:02 PM | Mindanao Grid-08/01/2024 14:45: LAMSAN Biomass with 13.5MW (net) tripped at 1348H. Indication: 50N non-directional earth fault. Affected by Simuay 69 kV line fault (Unplanned Outage) [WEBSMS] | CMIN
8/1/2024 1:40:20 PM | [NSO Update] Luzon Grid-08/01/2024 13:40: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1338H with power going to Visayas [WEBSMS] | CLUZ
8/1/2024 1:40:04 PM | [NSO Update] Visayas Grid-08/01/2024 13:40: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1338H with power going to Visayas [WEBSMS] | CVIS
8/1/2024 1:29:56 PM | [NSO Update] Visayas Grid-08/01/2024 13:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1327H from forward power direction [WEBSMS] | CVIS
8/1/2024 1:29:40 PM | [NSO Update] Luzon Grid-08/01/2024 13:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1327H from forward power direction [WEBSMS] | CLUZ
8/1/2024 12:46:25 PM | [NSO Update] Mindanao Grid-08/01/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3334MW, PK=2450MW, RR=73MW, NetOpMargin: PM=811, EVE=925 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/1/2024 12:37:49 PM | [NSO Update] Visayas Grid-08/01/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2722MW, PK=2350MW, RR=91MW, NetOpMargin: PM=281, EVE=265 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @250MW, CEDC 3 @75MW, TPC-Thermal @71MW, TGPP @80.3MW, PGPP1 @75MW, PDPP3-E @8MW, PDPP3-H @8MW [WEBSMS] | CVIS
8/1/2024 12:31:01 PM | [NSO Update] Luzon Grid-08/01/2024 12:31: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13311MW, PK=11893MW, RR=429MW, NetOpMargin: PM=989, EVE=724 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @114MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @285MW, SCPC 1 @130MW, Ilijan A @560MW, MPGC 3 @90MW, SCPC 3 @130MW [WEBSMS] | CLUZ
8/1/2024 11:07:41 AM | Mindanao Grid-08/01/2024 11:14: WMPC DG10 online at 1106H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/1/2024 10:40:06 AM | Mindanao Grid-08/01/2024 10:46: AGUS 4 unit 1 online at 1033H (Unplanned Outage) [WEBSMS] | CMIN
8/1/2024 10:17:25 AM | Visayas Grid-08/01/2024 10:17: UMPP U2 tripped at 1001H (Unplanned Outage) [WEBSMS] | CVIS
8/1/2024 10:14:57 AM | Visayas Grid-08/01/2024 10:15: UMPP U3 & U4 tripped at 0959H (Unplanned Outage) [WEBSMS] | CVIS
8/1/2024 9:06:00 AM | Mindanao Grid-08/01/2024 09:12: AGUS 4 Unit 1 emergency shutdown at 0904H (Unplanned Outage/ Forced Outage) [WEBSMS] | CMIN
8/1/2024 8:05:29 AM | Mindanao Grid-08/01/2024 08:12: AGUS 2 Unit 3 shutdown at 0803H (Planned Outage) [WEBSMS] | CMIN
8/1/2024 6:23:32 AM | Visayas Grid-08/01/2024 06:23: PGPP1 U3 cut-out at 0604H (Unplanned Outage) [WEBSMS] | CVIS
8/1/2024 5:48:13 AM | [NSO Update] Mindanao Grid-08/01/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3344MW, PK=2374MW, RR=73MW, NetOpMargin: AM=896, PM=852, EVE=965 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
8/1/2024 5:46:32 AM | [NSO Update] Visayas Grid-08/01/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2835MW, PK=2358MW, RR=91MW, NetOpMargin: AM=386, PM=308, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @314MW, CEDC 3 @75MW, TPC-Thermal @71MW, TGPP @80.3MW, PGPP1 @95MW, PDPP3-E @8MW, PDPP3-H @8MW [WEBSMS] | CVIS
8/1/2024 5:44:06 AM | [NSO Update] Luzon Grid-08/01/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13630MW, PK=11520MW, RR=422MW, NetOpMargin: AM=1688, PM=1139, EVE=1080 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @113MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @285MW, SCPC 1 @130MW, Ilijan A @560MW, MPGC 3 @90MW [WEBSMS] | CLUZ
8/1/2024 4:45:56 AM | Mindanao Grid-08/01/2024 04:52: Steag U2 online at 0321H. (Planned Outage) [WEBSMS] | CMIN
8/1/2024 3:57:04 AM | [NSO Update] Luzon Grid-08/01/2024 03:57: Weather Update: Ridge of High Pressure Area (HPA) extending over Northern Luzon. [WEBSMS] | CLUZ
8/1/2024 3:57:01 AM | [NSO Update] Visayas Grid-08/01/2024 03:57: Weather Update: Ridge of High Pressure Area (HPA) extending over Northern Luzon. [WEBSMS] | CVIS
8/1/2024 3:56:54 AM | [NSO Update] Mindanao Grid-08/01/2024 04:03: Weather Update: Ridge of High Pressure Area (HPA) extending over Northern Luzon. [WEBSMS] | CMIN
8/1/2024 12:49:39 AM | Visayas Grid-08/01/2024 00:49: COL-CVC 69KV Feeder energized at 0047H. (Planned Outage) [WEBSMS] | CVIS
8/1/2024 12:10:47 AM | Visayas Grid-08/01/2024 00:11: COL-CVC 69KV Feeder de-energized at 0006H. (Planned Outage) [WEBSMS] | CVIS
7/31/2024 10:55:54 PM | Visayas Grid-07/31/2024 22:56: Dumanjug SS 69kV Bus 2 energized at 2252H (Unplanned Outage) [WEBSMS] | CVIS
7/31/2024 9:26:04 PM | Visayas Grid-07/31/2024 21:26: Dumanjug SS 100 MVA 138/69/13.8 kV TR2 energized at 2122H, under test and commissioning. [WEBSMS] | CVIS
7/31/2024 8:18:16 PM | [NSO Update] Visayas Grid-07/31/2024 20:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1914H from reverse power direction [WEBSMS] | CVIS
7/31/2024 8:18:00 PM | [NSO Update] Luzon Grid-07/31/2024 20:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1914H from reverse power direction [WEBSMS] | CLUZ
7/31/2024 8:13:44 PM | [NSO Update] Luzon Grid-07/31/2024 20:13: Update on System Advisory: The Luzon Grid Yellow Alert Notice issued today has been lifted effective 2000H. [WEBSMS] | CLUZ
7/31/2024 7:40:54 PM | Mindanao Grid-07/31/2024 19:47: WMPC DG10 shutdown at 1931H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/31/2024 6:32:24 PM | [NSO Update] Visayas Grid-07/31/2024 18:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1818H with power going to Visayas [WEBSMS] | CVIS
7/31/2024 6:32:07 PM | [NSO Update] Luzon Grid-07/31/2024 18:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1818H with power going to Visayas [WEBSMS] | CLUZ
7/31/2024 6:30:03 PM | [NSO Update] Visayas Grid-07/31/2024 18:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1804H from forward power direction [WEBSMS] | CVIS
7/31/2024 6:29:46 PM | [NSO Update] Luzon Grid-07/31/2024 18:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1804H from forward power direction [WEBSMS] | CLUZ
7/31/2024 5:58:30 PM | [NSO Update] Mindanao Grid-07/31/2024 18:05: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3185MW, PK=2251MW, RR=73MW, NetOpMargin: EVE=862 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/31/2024 5:56:37 PM | [NSO Update] Visayas Grid-07/31/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2568MW, PK=2248MW, RR=91MW, NetOpMargin: EVE=229 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, CEDC 3 @75MW, TPC-Thermal @71MW, TGPP @80.3MW, PGPP1 @95MW [WEBSMS] | CVIS
7/31/2024 5:53:48 PM | [NSO Update] Luzon Grid-07/31/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=11874MW, PK=11008MW, RR=404MW, NetOpMargin: EVE=462 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @113MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @300MW, SCPC 1 @130MW, Ilijan A @460MW, MPGC 3 @90MW [WEBSMS] | CLUZ
7/31/2024 5:19:39 PM | Mindanao Grid-07/31/2024 17:26: WMPC DG01 shutdown at 1717H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/31/2024 5:04:53 PM | Visayas Grid-07/31/2024 17:05: Dumanjug SS 69kV Bus 2 de-energized at 1703H (Unplanned Outage) [WEBSMS] | CVIS
7/31/2024 4:53:14 PM | Luzon Grid-07/31/2024 16:53: Labo-Naga 230kV Line 2 restored at 1652H (Planned Outage) [WEBSMS] | CLUZ
7/31/2024 4:47:16 PM | Mindanao Grid-07/31/2024 16:53: Baloi - Agus2 138kV L1 energized at 1645H. (Planned Outage) [WEBSMS] | CMIN
7/31/2024 4:22:58 PM | Visayas Grid-07/31/2024 16:23: Dumanjug SS 69kV Bus 1 energized at 1620H (Planned Outage) [WEBSMS] | CVIS
7/31/2024 1:47:52 PM | Luzon Grid-07/31/2024 13:48: Sual 2 online at 1345H (Unplanned Outage) [WEBSMS] | CLUZ
7/31/2024 1:35:46 PM | Mindanao Grid-07/31/2024 13:42: WMPC DG01 online at 1332H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2024 1:05:05 PM | Luzon Grid-07/31/2024 13:05: SCPC 3 online at 1303H (Unplanned Outage) [WEBSMS] | CLUZ
7/31/2024 12:59:58 PM | Mindanao Grid-07/31/2024 13:06: Baloi - Agus2 138kV L1 de-energized at 1258H. (Planned Outage) [WEBSMS] | CMIN
7/31/2024 12:59:17 PM | Luzon Grid-07/31/2024 12:59: GNPD 2 emergency shutdown at 1259H. (Unplanned Outage) [WEBSMS] | CLUZ
7/31/2024 12:50:06 PM | Mindanao Grid-07/31/2024 12:56: Baloi - Agus2 138kV L2 energized at 1246H. (Planned Outage) [WEBSMS] | CMIN
7/31/2024 12:47:27 PM | [NSO Update] Mindanao Grid-07/31/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3227MW, PK=2417MW, RR=73MW, NetOpMargin: PM=737, EVE=815 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/31/2024 12:45:01 PM | [NSO Update] Visayas Grid-07/31/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2721MW, PK=2367MW, RR=91MW, NetOpMargin: PM=264, EVE=258 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @310MW, CEDC 3 @75MW, TPC-Thermal @71MW, TGPP @80.3MW, PDPP3-E @8MW, PDPP3-H @8MW [WEBSMS] | CVIS
7/31/2024 12:42:45 PM | [NSO Update] Luzon Grid-07/31/2024 12:42: Luzon Grid is on YELLOW Alert for interval hours 1500H-1600H and 1800H-2100H. Total capacity on forced outage is 2897.9MW. Total of de-rated capacity is 120MW. [WEBSMS] | CLUZ
7/31/2024 12:38:38 PM | [NSO Update] Luzon Grid-07/31/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=12969MW, PK=11768MW, RR=424MW, NetOpMargin: PM=777, EVE=316 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @113MW, Limay 8 @60MW, Masinloc 1 @315MW, Masinloc 3 @300MW, SCPC 1 @135MW [WEBSMS] | CLUZ
7/31/2024 10:51:22 AM | Mindanao Grid-07/31/2024 10:58: TSI U2 with 150.18MW load tripped at 1026H. Lowest frequency at 59.116Hz with ALD activation Cause: Boiler tube leak. (Unplanned Outage) [WEBSMS] | CMIN
7/31/2024 9:59:39 AM | Mindanao Grid-07/31/2024 10:06: WMPC DG10 online at 0957H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2024 9:57:29 AM | Visayas Grid-07/31/2024 09:57: Dumanjug SS 69kV Bus 1 de-energized at 0930H (Planned Outage) [WEBSMS] | CVIS
7/31/2024 9:06:31 AM | Mindanao Grid-07/31/2024 09:13: Baloi - Agus2 138kV L2 de-energized at 0905H. (Planned Outage) [WEBSMS] | CMIN
7/31/2024 8:20:47 AM | Luzon Grid-07/31/2024 08:21: San Gabriel online at 0817H. (Reserve Shutdown) [WEBSMS] | CLUZ
7/31/2024 7:44:30 AM | Luzon Grid-07/31/2024 07:44: Sual 2 with 290MW tripped at 0741H. Lowest system frequency was 59.29Hz. (Unplanned Outage) [WEBSMS] | CLUZ
7/31/2024 6:16:33 AM | Luzon Grid-07/31/2024 06:16: Labo-Naga 230kV Line 2 de-energized at 0616H (Planned Outage) [WEBSMS] | CLUZ
7/31/2024 5:44:20 AM | [NSO Update] Mindanao Grid-07/31/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3384MW, PK=2403MW, RR=73MW, NetOpMargin: AM=908, PM=775, EVE=839 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/31/2024 5:41:31 AM | [NSO Update] Visayas Grid-07/31/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2722MW, PK=2285MW, RR=87MW, NetOpMargin: AM=350, PM=227, EVE=227 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, CEDC 3 @75MW, TPC-Thermal @71MW, TGPP @80.3MW [WEBSMS] | CVIS
7/31/2024 5:40:00 AM | [NSO Update] Luzon Grid-07/31/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14272MW, PK=11362MW, RR=424MW, NetOpMargin: AM=2486, PM=1536, EVE=1448 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @113MW, Limay 8 @60MW, Masinloc 1 @315MW, Masinloc 3 @300MW, SCPC 1 @125MW [WEBSMS] | CLUZ
7/31/2024 4:14:20 AM | [NSO Update] Mindanao Grid-07/31/2024 04:20: Weather Update: Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CMIN
7/31/2024 4:14:07 AM | [NSO Update] Visayas Grid-07/31/2024 04:14: Weather Update: Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CVIS
7/31/2024 4:13:29 AM | [NSO Update] Luzon Grid-07/31/2024 04:13: Weather Update: Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CLUZ
7/31/2024 2:02:30 AM | Visayas Grid-07/31/2024 02:02: PEDC Unit No. 2 cut-in at 0146H, initial load 8.0 (Planned Outage) [WEBSMS] | CVIS
7/31/2024 1:22:15 AM | Visayas Grid-07/31/2024 01:22: Calong-calong-Toledo Solar 69 kV Line energized at 0119H. (Planned Outage) [WEBSMS] | CVIS
7/30/2024 9:57:33 PM | [NSO Update] Visayas Grid-07/30/2024 21:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2155H with power going to Luzon [WEBSMS] | CVIS
7/30/2024 9:57:15 PM | [NSO Update] Luzon Grid-07/30/2024 21:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2155H with power going to Luzon [WEBSMS] | CLUZ
7/30/2024 9:45:57 PM | [NSO Update] Visayas Grid-07/30/2024 21:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2145H from reverse power direction [WEBSMS] | CVIS
7/30/2024 9:45:41 PM | [NSO Update] Luzon Grid-07/30/2024 21:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2145H from reverse power direction [WEBSMS] | CLUZ
7/30/2024 9:08:26 PM | Visayas Grid-07/30/2024 21:08: Corella SS 300 MVA 230/138/13.8 kV TR1 energized at 2107H, under test and commissioning. (Unplanned Outage) [WEBSMS] | CVIS
7/30/2024 8:19:53 PM | Mindanao Grid-07/30/2024 20:26: IDPP-Lugait 138kV Line and Lugait SS 75MVA Transformer No.2 energized simultaneously at 2014H. Planned Outage. [WEBSMS] | CMIN
7/30/2024 8:18:39 PM | Mindanao Grid-07/30/2024 20:25: WMPC DG10 shutdown at 2016H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/30/2024 8:13:10 PM | Visayas Grid-07/30/2024 20:13: Corella SS 300 MVA 230/138/13.8 kV TR1 tripped at 1953H, under test and commissioning. (Unplanned Outage) [WEBSMS] | CVIS
7/30/2024 8:06:39 PM | Mindanao Grid-07/30/2024 20:13: Lamsan (LSK) online at 1943H (Unplanned Outage) [WEBSMS] | CMIN
7/30/2024 7:39:57 PM | Visayas Grid-07/30/2024 19:40: Dumanjug SS 138 kV Bus 2 energized at 1939H (Unplanned Outage) [WEBSMS] | CVIS
7/30/2024 7:16:00 PM | Mindanao Grid-07/30/2024 19:22: Update: Lamsan (LSK) with 15.2MW load tripped at 1909H. Indication: Turbine vibration high high. [WEBSMS] | CMIN
7/30/2024 7:12:29 PM | Mindanao Grid-07/30/2024 19:19: Lamsan (LSK) with 15.2MW load tripped at 1909H. Cause: to be determined. (Unplanned Outage) [WEBSMS] | CMIN
7/30/2024 7:01:49 PM | Visayas Grid-07/30/2024 19:02: Calong-calong-Toledo Solar 69 kV Line de-energized at 1857H. (Planned Outage) [WEBSMS] | CVIS
7/30/2024 6:09:58 PM | [NSO Update] Luzon Grid-07/30/2024 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12824MW, PK=10928MW, RR=406MW, NetOpMargin: EVE=1490 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @113MW, Limay 8 @60MW, Masinloc 1 @315MW, Masinloc 3 @310MW, SCPC 1 @125MW [WEBSMS] | CLUZ
7/30/2024 5:37:20 PM | [NSO Update] Mindanao Grid-07/30/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3286MW, PK=2307MW, RR=73MW, NetOpMargin: EVE=905 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @32.5MW [WEBSMS] | CMIN
7/30/2024 5:36:24 PM | [NSO Update] Visayas Grid-07/30/2024 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2529MW, PK=2202MW, RR=90MW, NetOpMargin: EVE=237 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @310MW, CEDC 3 @75MW, TPC-Thermal @71MW, TGPP @80.3MW [WEBSMS] | CVIS
7/30/2024 5:21:40 PM | Luzon Grid-07/30/2024 17:21: EERI Unit 2 shutdown at 1717H (On Testing and Commissioning) [WEBSMS] | CLUZ
7/30/2024 4:49:44 PM | Mindanao Grid-07/30/2024 16:56: WMPC DG01 shutdown at 1647H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/30/2024 4:23:00 PM | Mindanao Grid-07/30/2024 16:29: Lamsan (LSK) online at 1540H (Unplanned Outage) [WEBSMS] | CMIN
7/30/2024 4:09:52 PM | Luzon Grid-07/30/2024 16:10: La Trinidad 230kV Bus 2 restored at 1606H (Planned Outage) [WEBSMS] | CLUZ
7/30/2024 3:56:19 PM | Visayas Grid-07/30/2024 15:56: Dumanjug SS 138 kV Bus 2 de-energized at 1554H (Unplanned Outage) [WEBSMS] | CVIS
7/30/2024 3:49:28 PM | Luzon Grid-07/30/2024 15:49: Bolo PCB 9-03CB24BLZ tripped at 1541H and was closed at 1549H. (Unplanned Outage) [WEBSMS] | CLUZ
7/30/2024 3:34:45 PM | Mindanao Grid-07/30/2024 15:41: Update: Lamsan (LSK) with 13MW load tripped at 1505H. Indication: Turbine exhaust pressure high high. (Unplanned Outage) [WEBSMS] | CMIN
7/30/2024 3:27:56 PM | Visayas Grid-07/30/2024 15:28: Dumanjug SS 138 kV Bus 1 energized at 1523H (Unplanned Outage) [WEBSMS] | CVIS
7/30/2024 3:10:52 PM | Mindanao Grid-07/30/2024 15:17: Lamsan (LSK) with 13MW load tripped at 1503H. Cause: to be determined. (Unplanned Outage) [WEBSMS] | CMIN
7/30/2024 2:59:59 PM | Luzon Grid-07/30/2024 15:00: Naga-Labo 230kV line 1 was restored at 1456H. (Planned Outage) [WEBSMS] | CLUZ
7/30/2024 2:39:25 PM | Mindanao Grid-07/30/2024 14:45: Tacurong - General Santos 138kV Line 1 energized at 1438H. (Planned Outage) [WEBSMS] | CMIN
7/30/2024 2:16:02 PM | Mindanao Grid-07/30/2024 14:22: WMPC DG01 online at 1021H. RPS - System Voltage Requirement [WEBSMS] | CMIN
7/30/2024 1:28:56 PM | [NSO Update] Visayas Grid-07/30/2024 13:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1315H with power going to Visayas [WEBSMS] | CVIS
7/30/2024 1:28:49 PM | [NSO Update] Luzon Grid-07/30/2024 13:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1315H with power going to Visayas [WEBSMS] | CLUZ
7/30/2024 1:09:03 PM | [NSO Update] Luzon Grid-07/30/2024 13:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1305H from forward power direction [WEBSMS] | CLUZ
7/30/2024 1:08:33 PM | [NSO Update] Visayas Grid-07/30/2024 13:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1305H from forward power direction [WEBSMS] | CVIS
7/30/2024 12:57:58 PM | [NSO Update] Luzon Grid-07/30/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13838MW, PK=11235MW, RR=424MW, NetOpMargin: PM=2179, EVE=1909 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @113MW, Limay 8 @60MW, Masinloc 1 @310MW, Masinloc 3 @290MW, SCPC 1 @125MW [WEBSMS] | CLUZ
7/30/2024 12:52:12 PM | [NSO Update] Mindanao Grid-07/30/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3330MW, PK=2515MW, RR=73MW, NetOpMargin: PM=742, EVE=873 Highest Unit O/L: GNPK 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW, MCO U2 (SMC U2) @90MW [WEBSMS] | CMIN
7/30/2024 12:45:13 PM | [NSO Update] Visayas Grid-07/30/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2730MW, PK=2386MW, RR=91MW, NetOpMargin: PM=253, EVE=255 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @302MW, CEDC 3 @75MW, TPC-Thermal @70MW, TGPP @80.3MW [WEBSMS] | CVIS
7/30/2024 11:56:22 AM | Luzon Grid-07/30/2024 11:56: EERI Unit 2 online at 1152H. (On Testing and Commissioning) [WEBSMS] | CLUZ
7/30/2024 9:11:04 AM | Mindanao Grid-07/30/2024 09:17: WMPC DG10 online at 0907H. RPS - System Voltage Requirement [WEBSMS] | CMIN
7/30/2024 8:55:00 AM | Visayas Grid-07/30/2024 08:55: Dumanjug SS 138 kV Bus 1 de-energized at 0848H (Unplanned Outage) [WEBSMS] | CVIS
7/30/2024 8:11:58 AM | Mindanao Grid-07/30/2024 08:18: Lamsan (LSK) online at 0751H from Forced outage. (Unplanned Outage) [WEBSMS] | CMIN
7/30/2024 8:09:48 AM | Mindanao Grid-07/30/2024 08:16: Tacurong - General Santos 138kV Line 1 de-energized at 0808H. (Planned Outage) [WEBSMS] | CMIN
7/30/2024 8:06:59 AM | Mindanao Grid-07/30/2024 08:13: Pulangi U2 shutdown at 0803H. (Planned outage- Non-GOMP) [WEBSMS] | CMIN
7/30/2024 8:04:34 AM | Mindanao Grid-07/30/2024 08:11: Update. (LSK) with 10.42MW load tripped at 0715H, newly sync at 0707H from Planned outage. Cause: Turbine exhaust pressure high high. (Unplanned Outage) [WEBSMS] | CMIN
7/30/2024 7:20:54 AM | Mindanao Grid-07/30/2024 07:27: Lamsan (LSK) with 10.42MW load tripped at 0715H, newly sync at 0707H from Planned outage. Cause: to be determined. (Unplanned Outage) [WEBSMS] | CMIN
7/30/2024 7:12:37 AM | Mindanao Grid-07/30/2024 07:19: Lamsan (LSK) online at 0707H. (Planned Outage) [WEBSMS] | CMIN
7/30/2024 6:22:36 AM | Luzon Grid-07/30/2024 06:22: Naga-Labo 230kV Line 1 de-energized at 0622H (Planned Outage) [WEBSMS] | CLUZ
7/30/2024 6:14:42 AM | Luzon Grid-07/30/2024 06:14: La Trinidad 230kV Bus 2 de-energized at 0610H (Planned Outage) [WEBSMS] | CLUZ
7/30/2024 5:48:08 AM | Luzon Grid-07/30/2024 05:48: San Jose-Taytay 230kV Line 1 restored at 0548H (Planned Outage) [WEBSMS] | CLUZ
7/30/2024 5:47:39 AM | [NSO Update] Visayas Grid-07/30/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2665MW, PK=2324MW, RR=87MW, NetOpMargin: AM=253, PM=227, EVE=233 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @307MW, CEDC 3 @75MW, TPC-Thermal @70MW, TGPP @80.3MW [WEBSMS] | CVIS
7/30/2024 5:47:12 AM | [NSO Update] Mindanao Grid-07/30/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3289MW, PK=2398MW, RR=73MW, NetOpMargin: AM=818, PM=794, EVE=848 Highest Unit O/L: GNPK 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @32.5MW [WEBSMS] | CMIN
7/30/2024 5:46:56 AM | [NSO Update] Luzon Grid-07/30/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13857MW, PK=11438MW, RR=424MW, NetOpMargin: AM=1995, PM=2167, EVE=2045 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @113MW, Limay 8 @60MW, Masinloc 1 @290MW, Masinloc 3 @295MW, SCPC 1 @125MW, SCPC 4 @75MW [WEBSMS] | CLUZ
7/30/2024 4:05:21 AM | [NSO Update] Luzon Grid-07/30/2024 04:05: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 480 km North Northwest of Itbayat, Batanes (24.9�N, 120.5�E). Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CLUZ
7/30/2024 4:05:15 AM | [NSO Update] Visayas Grid-07/30/2024 04:05: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 480 km North Northwest of Itbayat, Batanes (24.9�N, 120.5�E). Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CVIS
7/30/2024 4:05:12 AM | [NSO Update] Mindanao Grid-07/30/2024 04:11: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 480 km North Northwest of Itbayat, Batanes (24.9�N, 120.5�E). Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CMIN
7/30/2024 1:03:20 AM | Luzon Grid-07/30/2024 01:03: San Jose-Taytay 230kV Line 1 de-energized at 0103H (Planned Outage) [WEBSMS] | CLUZ
7/29/2024 10:25:47 PM | [NSO Update] Luzon Grid-07/29/2024 22:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2204H power to Luzon. [WEBSMS] | CLUZ
7/29/2024 10:25:44 PM | [NSO Update] Visayas Grid-07/29/2024 22:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2204H power to Luzon. [WEBSMS] | CVIS
7/29/2024 9:56:59 PM | [NSO Update] Visayas Grid-07/29/2024 21:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2154H from reverse power direction. [WEBSMS] | CVIS
7/29/2024 9:56:11 PM | [NSO Update] Luzon Grid-07/29/2024 21:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2154H from reverse power direction. [WEBSMS] | CLUZ
7/29/2024 9:23:01 PM | Mindanao Grid-07/29/2024 21:29: WMPC DG10 shutdown at 2116H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/29/2024 8:05:08 PM | Luzon Grid-07/29/2024 20:05: Laoag-Pasuquin Solar 115kV Line (CO) restored at 2004H (Planned Outage) [WEBSMS] | CLUZ
7/29/2024 6:03:48 PM | Luzon Grid-07/29/2024 18:03: Laoag-Pasuquin Solar 115kV Line (CO) de-energized at 1803H (Planned Outage) [WEBSMS] | CLUZ
7/29/2024 5:54:54 PM | [NSO Update] Mindanao Grid-07/29/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3359MW, PK=2295MW, RR=73MW, NetOpMargin: EVE=991 Highest Unit O/L: GNPK 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/29/2024 5:53:26 PM | [NSO Update] Visayas Grid-07/29/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2543MW, PK=2226MW, RR=87MW, NetOpMargin: EVE=231 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC 3 @75MW, TPC-Thermal @70MW, TGPP @80.3MW [WEBSMS] | CVIS
7/29/2024 5:45:21 PM | [NSO Update] Luzon Grid-07/29/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12604MW, PK=10208MW, RR=406MW, NetOpMargin: EVE=1990 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @109MW, Limay 8 @60MW, Masinloc 1 @290MW, Masinloc 3 @295MW, SCPC 1 @125MW [WEBSMS] | CLUZ
7/29/2024 5:27:35 PM | Mindanao Grid-07/29/2024 17:34: WMPC DG1 shutdown at 1716H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/29/2024 5:16:03 PM | Luzon Grid-07/29/2024 17:16: SCPC 4 online at 1713H (Unplanned Outage) [WEBSMS] | CLUZ
7/29/2024 4:00:54 PM | Luzon Grid-07/29/2024 16:01: EERI 2 shutdown at 1558H (on commissioning) [WEBSMS] | CLUZ
7/29/2024 1:23:35 PM | Mindanao Grid-07/29/2024 13:30: WMPC DG1 online at 1321H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/29/2024 1:03:15 PM | [NSO Update] Mindanao Grid-07/29/2024 13:09: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3401MW, PK=2366MW, RR=73MW, NetOpMargin: PM=962, EVE=1024 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/29/2024 1:01:59 PM | [NSO Update] Visayas Grid-07/29/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2667MW, PK=2247MW, RR=91MW, NetOpMargin: PM=328, EVE=304 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @307MW, CEDC 3 @75MW, TPC-Thermal @70MW, TGPP @80.3MW [WEBSMS] | CVIS
7/29/2024 12:58:39 PM | [NSO Update] Luzon Grid-07/29/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13804MW, PK=10780MW, RR=424MW, NetOpMargin: PM=2599, EVE=2419 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @109MW, Limay 8 @60MW, Masinloc 1 @280MW, Masinloc 3 @285MW, SCPC 1 @125MW [WEBSMS] | CLUZ
7/29/2024 12:43:24 PM | Visayas Grid-07/29/2024 12:43: Leyte-A Malitbog U3 cut-in at 1234H (Unplanned Outage) [WEBSMS] | CVIS
7/29/2024 12:24:27 PM | Mindanao Grid-07/29/2024 12:31: Agus5 HEPP U1 cut-in/online at 1223H. (Planned Outage) [WEBSMS] | CMIN
7/29/2024 12:11:35 PM | Mindanao Grid-07/29/2024 12:18: Agus SS - Agus5 HEPP U1 138kV L1 energized at 1208H. (Planned Outage) [WEBSMS] | CMIN
7/29/2024 11:33:24 AM | [NSO Update] Visayas Grid-07/29/2024 11:33: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1122H with power going to Visayas [WEBSMS] | CVIS
7/29/2024 11:33:05 AM | [NSO Update] Luzon Grid-07/29/2024 11:33: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1122H with power going to Visayas [WEBSMS] | CLUZ
7/29/2024 11:32:26 AM | [NSO Update] Visayas Grid-07/29/2024 11:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1112H from forward power direction [WEBSMS] | CVIS
7/29/2024 11:32:02 AM | [NSO Update] Luzon Grid-07/29/2024 11:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1112H from forward power direction [WEBSMS] | CLUZ
7/29/2024 11:31:18 AM | [NSO Update] Visayas Grid-07/29/2024 11:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1044H with power going to Luzon [WEBSMS] | CVIS
7/29/2024 11:31:01 AM | [NSO Update] Luzon Grid-07/29/2024 11:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1044H with power going to Luzon [WEBSMS] | CLUZ
7/29/2024 11:30:10 AM | [NSO Update] Visayas Grid-07/29/2024 11:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1034H from reverse power direction [WEBSMS] | CVIS
7/29/2024 11:29:41 AM | [NSO Update] Luzon Grid-07/29/2024 11:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1034H from reverse power direction [WEBSMS] | CLUZ
7/29/2024 9:56:42 AM | Mindanao Grid-07/29/2024 10:03: WMPC DG10 shutdown at 0953H. RPS-System Voltage Requirement [WEBSMS] | CMIN
7/29/2024 9:17:23 AM | [NSO Update] Visayas Grid-07/29/2024 09:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0907H with power going to Visayas [WEBSMS] | CVIS
7/29/2024 9:16:07 AM | [NSO Update] Luzon Grid-07/29/2024 09:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0907H with power going to Visayas [WEBSMS] | CLUZ
7/29/2024 9:12:27 AM | [NSO Update] Visayas Grid-07/29/2024 09:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0840H from forward power direction [WEBSMS] | CVIS
7/29/2024 9:12:11 AM | [NSO Update] Luzon Grid-07/29/2024 09:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0840H from forward power direction [WEBSMS] | CLUZ
7/29/2024 8:24:51 AM | Mindanao Grid-07/29/2024 08:31: Agus5 SS - Agus5 HEPP U1 138kV L1 de-energized/shutdown at 0821H.(Planned Outage) [WEBSMS] | CMIN
7/29/2024 8:19:20 AM | Mindanao Grid-07/29/2024 08:25: Agus5 HEPP U1 shutdown at 0818H. (Planned Outage) [WEBSMS] | CMIN
7/29/2024 7:34:43 AM | Mindanao Grid-07/29/2024 07:41: SEC 2 online/cut-in at 0732H. (Unplanned Outage) [WEBSMS] | CMIN
7/29/2024 6:34:04 AM | Luzon Grid-07/29/2024 06:34: Dona Imelda 300MVA T02 restored at 0630H (Planned Outage) [WEBSMS] | CLUZ
7/29/2024 5:42:52 AM | [NSO Update] Luzon Grid-07/29/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13660MW, PK=10503MW, RR=424MW, NetOpMargin: AM=2733, PM=1801, EVE=1943 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @109MW, Limay 8 @60MW, Masinloc 1 @230MW, Masinloc 3 @315MW, SCPC 1 @125MW [WEBSMS] | CLUZ
7/29/2024 5:42:48 AM | [NSO Update] Visayas Grid-07/29/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2555MW, PK=2197MW, RR=91MW, NetOpMargin: AM=267, PM=218, EVE=227 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @275MW, CEDC 3 @75MW, PB104-3 @5MW, PB104-4 @5MW, PDPP3-H @8MW, PDPP3-E @8MW, TGPP @80.3MW, PB104-2 @4.5MW [WEBSMS] | CVIS
7/29/2024 5:42:44 AM | [NSO Update] Mindanao Grid-07/29/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3412MW, PK=2369MW, RR=73MW, NetOpMargin: AM=970, PM=932, EVE=1109 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/29/2024 5:41:36 AM | Mindanao Grid-07/29/2024 05:48: Baloi SS 138kV Bus No.1 energized/restored at 0534H. From Planned Outage (PO00AC) / Non-GOMP. [WEBSMS] | CMIN
7/29/2024 5:15:56 AM | Luzon Grid-07/29/2024 05:16: Dasmarinas SS 300MVA T03 was restored at 0514H. (Planned Outage) [WEBSMS] | CLUZ
7/29/2024 4:54:03 AM | [NSO Update] Mindanao Grid-07/29/2024 05:00: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 220 km Northeast of Aparri, Cagayan (20.0�N, 122.8�E). Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CMIN
7/29/2024 4:53:59 AM | [NSO Update] Visayas Grid-07/29/2024 04:54: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 220 km Northeast of Aparri, Cagayan (20.0�N, 122.8�E). Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CVIS
7/29/2024 4:53:56 AM | [NSO Update] Luzon Grid-07/29/2024 04:54: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 220 km Northeast of Aparri, Cagayan (20.0�N, 122.8�E). Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CLUZ
7/29/2024 3:13:05 AM | Luzon Grid-07/29/2024 03:13: Dasmarinas SS 300MVA T03 de-energized at 0311H (Planned Outage) [WEBSMS] | CLUZ
7/29/2024 12:03:33 AM | Mindanao Grid-07/29/2024 00:10: Baloi SS 138kV Bus No.1 deenergized at 2352H. Planned Outage (PO00AC) / Non-GOMP. [WEBSMS] | CMIN
7/28/2024 11:14:26 PM | Luzon Grid-07/28/2024 23:14: Dona Imelda 300MVA T02 was de-energized at 2311H. (Planned Outage) [WEBSMS] | CLUZ
7/28/2024 10:34:09 PM | Visayas Grid-07/28/2024 22:34: PGPP2 Okoy cut in at 2227H (Unplanned Outage) [WEBSMS] | CVIS
7/28/2024 9:23:52 PM | Luzon Grid-07/28/2024 21:23: The commissioning and energization of Dasmarinas 600MVA T01 new Main Protections were completed at 2122H. [WEBSMS] | CLUZ
7/28/2024 9:15:45 PM | Luzon Grid-07/28/2024 21:15: Dasmarinas 600MVA T01 was restored at 2113H. (Planned Outage-On-going commissioning and energization of New Main Protections) [WEBSMS] | CLUZ
7/28/2024 8:45:42 PM | Luzon Grid-07/28/2024 20:45: Calaca Unit 2 shutdown at 2042H. (Unplanned Outage) [WEBSMS] | CLUZ
7/28/2024 8:44:30 PM | Luzon Grid-07/28/2024 20:44: The commissioning and energization of the new Batangas 300MVA T02 was completed at 2041H. [WEBSMS] | CLUZ
7/28/2024 7:14:15 PM | [NSO Update] Visayas Grid-07/28/2024 19:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1910H with power going to Luzon. [WEBSMS] | CVIS
7/28/2024 7:14:05 PM | [NSO Update] Luzon Grid-07/28/2024 19:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1910H with power going to Luzon. [WEBSMS] | CLUZ
7/28/2024 7:08:28 PM | [NSO Update] Luzon Grid-07/28/2024 19:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1900H from reverse power direction. [WEBSMS] | CLUZ
7/28/2024 7:07:11 PM | [NSO Update] Visayas Grid-07/28/2024 19:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1900H from reverse power direction. [WEBSMS] | CVIS
7/28/2024 6:55:23 PM | Luzon Grid-07/28/2024 18:55: Olongapo-Subic(Hanjin) 230kV line was restored at 1854H. (Planned Outage) [WEBSMS] | CLUZ
7/28/2024 6:09:17 PM | Luzon Grid-07/28/2024 18:09: EERI Unit 2 online at 1806H. (Under Testing and Commissioning) [WEBSMS] | CLUZ
7/28/2024 5:40:18 PM | [NSO Update] Mindanao Grid-07/28/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3248MW, PK=2049MW, RR=73MW, NetOpMargin: EVE=1127 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @34.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/28/2024 5:38:44 PM | [NSO Update] Visayas Grid-07/28/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2225MW, PK=1950MW, RR=86MW, NetOpMargin: EVE=189 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @276MW, CEDC 3 @75MW, PB104-3 @5MW, PB104-4 @5MW, PDPP3-H @8MW, PDPP3-E @8MW, TGPP @80.3MW, PB104-2 @4.5MW [WEBSMS] | CVIS
7/28/2024 5:37:16 PM | [NSO Update] Luzon Grid-07/28/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12684MW, PK=9115MW, RR=311MW, NetOpMargin: EVE=3258 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @109MW, Limay 8 @60MW, Masinloc 1 @290MW, Masinloc 3 @320MW, SCPC 1 @125MW, Calaca 2 @288MW [WEBSMS] | CLUZ
7/28/2024 5:30:20 PM | Mindanao Grid-07/28/2024 17:36: Kauswagan - Lala 230kV L2 (8LI2KSW-LLA) energized/restored at 1728H. From Planned Outage/ Non-GOMP. [WEBSMS] | CMIN
7/28/2024 5:21:48 PM | Luzon Grid-07/28/2024 17:21: Taytay-Malaya 230kV line 2 was restored at 1720H. (Planned Outage) [WEBSMS] | CLUZ
7/28/2024 5:13:44 PM | Luzon Grid-07/28/2024 17:13: The Commissioning and Energization of Ilijan CCPP 500kV Bus 2 New Main Protection was completed at 1711H. [WEBSMS] | CLUZ
7/28/2024 4:43:58 PM | Luzon Grid-07/28/2024 16:44: Ilijan CCPP 500kV Bus 2 was energized at 1641H. (On-going commissioning and energization of Ilijan 500kV Bus 2 New Main Protection) [WEBSMS] | CLUZ
7/28/2024 4:25:10 PM | Visayas Grid-07/28/2024 16:25: Cebu-Colon 138 kV L3 energized at 1618H (Planned Outage) [WEBSMS] | CVIS
7/28/2024 4:24:26 PM | [NSO Update] Visayas Grid-07/28/2024 16:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1622H with power going to Visayas. [WEBSMS] | CVIS
7/28/2024 4:23:40 PM | [NSO Update] Luzon Grid-07/28/2024 16:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1622H with power going to Visayas. [WEBSMS] | CLUZ
7/28/2024 4:15:05 PM | [NSO Update] Visayas Grid-07/28/2024 16:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1612H from forward power direction. [WEBSMS] | CVIS
7/28/2024 4:14:47 PM | [NSO Update] Luzon Grid-07/28/2024 16:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1612H from forward power direction. [WEBSMS] | CLUZ
7/28/2024 2:42:14 PM | Mindanao Grid-07/28/2024 14:48: Bislig-Nabunturan 138kV line energized/restored at 1440H. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
7/28/2024 12:43:24 PM | Luzon Grid-07/28/2024 12:43: Correction: Duhat 300MVA T03 energized and commissioned at 1233H (On Commissioning) [WEBSMS] | CLUZ
7/28/2024 12:40:10 PM | Luzon Grid-07/28/2024 12:40: Duhat 300MVA T02 energized and commissioned at 1233H (On Commissioning) [WEBSMS] | CLUZ
7/28/2024 12:38:00 PM | [NSO Update] Mindanao Grid-07/28/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3285MW, PK=1927MW, RR=73MW, NetOpMargin: PM=1285, EVE=1013 Highest Unit O/L: GNPK 1 @ 151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @37.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/28/2024 12:36:36 PM | [NSO Update] Visayas Grid-07/28/2024 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2438MW, PK=1856MW, RR=83MW, NetOpMargin: PM=499, EVE=182 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @315MW, CEDC 3 @75MW, PB104-3 @5MW, PB104-4 @5MW, PDPP3-H @8MW, PDPP3-E @8MW, TGPP @80.3MW, PB104-2 @4.5MW [WEBSMS] | CVIS
7/28/2024 12:35:12 PM | [NSO Update] Luzon Grid-07/28/2024 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13779MW, PK=9425MW, RR=334MW, NetOpMargin: PM=4020, EVE=2274 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: SLTEC 2 @109MW, Limay 8 @60MW, Masinloc 1 @290MW, SCPC 1 @125MW, Calaca 2 @270MW [WEBSMS] | CLUZ
7/28/2024 11:23:26 AM | Luzon Grid-07/28/2024 11:23: Duhat 300MVA T02 (Customer Owned) restored at 1120H (Planned Outage) [WEBSMS] | CLUZ
7/28/2024 10:38:27 AM | Visayas Grid-07/28/2024 10:38: Cebu SS 300 MVA TR1 energized at 1038H (Planned Outage) [WEBSMS] | CVIS
7/28/2024 8:39:33 AM | Visayas Grid-07/28/2024 08:39: Cebu SS 300 MVA TR1 de-energized at 0838H (Planned Outage) [WEBSMS] | CVIS
7/28/2024 7:23:35 AM | Luzon Grid-07/28/2024 07:23: Olongapo-Subic 230kV Line de-energized at 0723H (Planned Outage) [WEBSMS] | CLUZ
7/28/2024 7:11:06 AM | Mindanao Grid-07/28/2024 07:17: Bislig-Nabunturan 138kV line de-energized at 0706H. Planned Outage. [WEBSMS] | CMIN
7/28/2024 6:56:02 AM | Luzon Grid-07/28/2024 06:56: Taytay-Malaya 230kV Line 2 de-energized at 0653H (Planned Outage) [WEBSMS] | CLUZ
7/28/2024 6:44:42 AM | Mindanao Grid-07/28/2024 06:51: Lugait-IDPP 138kV line de-energized at 0642H. Planned Outage. [WEBSMS] | CMIN
7/28/2024 6:34:34 AM | Visayas Grid-07/28/2024 06:34: Cebu-Colon 138 kV L3 de-energized at 0634H (Planned Outage) [WEBSMS] | CVIS
7/28/2024 6:23:32 AM | Visayas Grid-07/28/2024 06:23: Kananga-Tabango 230 kV L2 de-energized at 0622H (Planned Outage) [WEBSMS] | CVIS
7/28/2024 6:13:14 AM | Luzon Grid-07/28/2024 06:13: Dasmarinas SS 600MVA T01 de-energized at 0611H (Planned Outage) [WEBSMS] | CLUZ
7/28/2024 5:40:41 AM | [NSO Update] Mindanao Grid-07/28/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3294MW, PK=1856MW, RR=73MW, NetOpMargin: AM=1365, PM=1206, EVE=969 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @34.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/28/2024 5:40:36 AM | [NSO Update] Visayas Grid-07/28/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2439MW, PK=1735MW, RR=80MW, NetOpMargin: AM=625, PM=502, EVE=186 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @315MW, CEDC 3 @75MW, PB104-3 @5MW, PB104-4 @5.5MW, PDPP3-H @8MW, PDPP3-E @8MW, TGPP @80.3MW, PB104-2 @4.5MW [WEBSMS] | CVIS
7/28/2024 5:40:33 AM | [NSO Update] Luzon Grid-07/28/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13864MW, PK=9171MW, RR=326MW, NetOpMargin: AM=4368, PM=3436, EVE=2108 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 2 @109MW, Limay 8 @60MW, Masinloc 1 @290MW, SCPC 1 @125MW, Masinloc 3 @305MW, Calaca 2 @200MW [WEBSMS] | CLUZ
7/28/2024 5:06:31 AM | Visayas Grid-07/28/2024 05:06: PGPP2-Okoy cut-in at 0503H (Unplanned Outage) [WEBSMS] | CVIS
7/28/2024 4:44:39 AM | Mindanao Grid-07/28/2024 04:51: Kauswagan SS 230kV Bus No.1 energized at 0442H. (Planned Outage) [WEBSMS] | CMIN
7/28/2024 4:09:08 AM | [NSO Update] Luzon Grid-07/28/2024 04:09: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 440 km East of Catarman, Northern Samar (12.5�N, 128.7�E). Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CLUZ
7/28/2024 4:09:04 AM | [NSO Update] Visayas Grid-07/28/2024 04:09: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 440 km East of Catarman, Northern Samar (12.5�N, 128.7�E). Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CVIS
7/28/2024 4:09:00 AM | [NSO Update] Mindanao Grid-07/28/2024 04:15: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 440 km East of Catarman, Northern Samar (12.5�N, 128.7�E). Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CMIN
7/28/2024 2:24:25 AM | Mindanao Grid-07/28/2024 02:30: Kauswagan SS 230kV Bus No.1 de-energized at 0222H. (Planned Outage) [WEBSMS] | CMIN
7/28/2024 1:07:50 AM | Mindanao Grid-07/28/2024 01:14: Kauswagan - Lala 230kV L2 de-energized at 0106H. (Planned Outage) [WEBSMS] | CMIN
7/28/2024 12:32:54 AM | Mindanao Grid-07/28/2024 00:39: SEC 2 shutdown at 2357H due to steam leak at the Steam Drum Sight Glass .(Unplanned Outage). [WEBSMS] | CMIN
7/28/2024 12:02:21 AM | Luzon Grid-07/28/2024 00:02: SLTEC 1 shutdown at 0002H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 11:58:50 PM | Luzon Grid-07/27/2024 23:58: SLPGC 1 shutdown at 2357H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 11:54:05 PM | Mindanao Grid-07/28/2024 00:00: Kauswagan - Lala 230kV L1 energized at 2351H. (Planned Outage) [WEBSMS] | CMIN
7/27/2024 11:20:50 PM | Mindanao Grid-07/27/2024 23:27: Matanao - Gen San 138kV L1 energized at 2319H (Planned Outage). [WEBSMS] | CMIN
7/27/2024 11:01:24 PM | Mindanao Grid-07/27/2024 23:07: Gen San SS 138kV Bus No. 1 energized at 2259H. (Planned Outage) [WEBSMS] | CMIN
7/27/2024 10:56:38 PM | Luzon Grid-07/27/2024 22:56: SCPC 4 with 150MW tripped at 2254H. Lowest system frequency was 59.50Hz. (Unplanned Outage) [WEBSMS] | CLUZ
7/27/2024 10:42:38 PM | Luzon Grid-07/27/2024 22:42: Duhat 300MVA T02 (Customer Owned) de-energized at 2242H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 10:13:43 PM | Mindanao Grid-07/27/2024 22:20: Kauswagan - Lala 230kV L1 de-energized at 2212H. (Planned Outage) [WEBSMS] | CMIN
7/27/2024 10:07:29 PM | Luzon Grid-07/27/2024 22:07: San Jose-Quezon 230kV Line 1 restored at 2205H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 9:52:14 PM | Luzon Grid-07/27/2024 21:52: Tayabas SS 9Z-02CB24TAY restored at 2151H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 8:02:01 PM | Visayas Grid-07/27/2024 20:02: PGPP2 Okoy emergency cut out at 1938H (Unplanned Outage) [WEBSMS] | CVIS
7/27/2024 7:57:09 PM | Luzon Grid-07/27/2024 19:57: Tayabas SS 9Z-02CB24TAY de-energized at 1953H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 7:37:38 PM | Luzon Grid-07/27/2024 19:37: Tayabas SS 9Z-02CB24TAY restored at 1937H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 7:27:26 PM | Luzon Grid-07/27/2024 19:27: Ilijan SS 500kV Bus 2 de-energized at 1927H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 7:19:06 PM | Mindanao Grid-07/27/2024 19:25: WMPC DG10 shutdown at 1916H. RPS-System Voltage Requirement [WEBSMS] | CMIN
7/27/2024 5:40:37 PM | [NSO Update] Mindanao Grid-07/27/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3353MW, PK=2157MW, RR=73MW, NetOpMargin: EVE=1123 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @37.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/27/2024 5:40:20 PM | [NSO Update] Luzon Grid-07/27/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13305MW, PK=10351MW, RR=401MW, NetOpMargin: EVE=2554 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 1 @49MW, Limay 8 @60MW, Masinloc 1 @290MW, SCPC 1 @125MW, Masinloc 3 @300MW, SLTEC 2 @90MW [WEBSMS] | CLUZ
7/27/2024 5:40:03 PM | [NSO Update] Visayas Grid-07/27/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2446MW, PK=2011MW, RR=86MW, NetOpMargin: EVE=350 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, CEDC 3 @75MW, PB104-3 @5MW, PB104-4 @5.5MW, PDPP3-H @8MW, PDPP3-E @8MW, TGPP @80.5MW, PB104-2 @4.5MW [WEBSMS] | CVIS
7/27/2024 5:04:58 PM | Luzon Grid-07/27/2024 17:05: EERI Unit 2 online at 1703H. (On Testing and Commissioning) [WEBSMS] | CLUZ
7/27/2024 4:04:47 PM | Visayas Grid-07/27/2024 16:04: Cebu SS 300 MVA TR3 energized at 1603H (Planned Outage) [WEBSMS] | CVIS
7/27/2024 3:42:56 PM | Visayas Grid-07/27/2024 15:43: Cebu-Colon 138 kV L2 energized at 1541H (Planned Outage) [WEBSMS] | CVIS
7/27/2024 3:41:32 PM | Mindanao Grid-07/27/2024 15:48: Agus 6 SS 69kV Bus no. 1 energized at 1540H. (Planned Outage) [WEBSMS] | CMIN
7/27/2024 3:30:31 PM | Luzon Grid-07/27/2024 15:30: Binan-Calamba 230kV Line 2 restored at 1529H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 2:56:46 PM | Luzon Grid-07/27/2024 14:56: Lumban - Gumaca 230kV Line 1 tripped/reclosed both side at 1451H (Unplanned Outage) [WEBSMS] | CLUZ
7/27/2024 2:49:04 PM | Luzon Grid-07/27/2024 14:49: Ilijan 500kV Bus 2 restored at 1448H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 12:40:47 PM | Mindanao Grid-07/27/2024 12:47: Gen San SS 138kV Bus No. 1 de-energized at 1239H. (Planned Outage) [WEBSMS] | CMIN
7/27/2024 12:39:56 PM | [NSO Update] Luzon Grid-07/27/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14201MW, PK=10741MW, RR=414MW, NetOpMargin: PM=3046, EVE=2122 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 1 @49MW, Limay 8 @60MW, Masinloc 1 @290MW, SCPC 1 @125MW, Masinloc 3 @300MW, SLTEC 2 @62MW [WEBSMS] | CLUZ
7/27/2024 12:37:55 PM | [NSO Update] Mindanao Grid-07/27/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3384MW, PK=2140MW, RR=73MW, NetOpMargin: PM=1171, EVE=1110 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @37.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/27/2024 12:36:12 PM | [NSO Update] Visayas Grid-07/27/2024 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2564MW, PK=2063MW, RR=83MW, NetOpMargin: PM=417, EVE=245 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @308MW, CEDC 3 @75MW, PB104-3 @5MW, PB104-4 @5.5MW, PDPP3-H @8MW, PDPP3-E @8MW, TGPP @80.5MW, PB104-2 @4.5MW [WEBSMS] | CVIS
7/27/2024 12:21:06 PM | Mindanao Grid-07/27/2024 12:27: Agus 6 SS 69kV Bus no. 1 de-energized at 1218H. (Planned Outage) [WEBSMS] | CMIN
7/27/2024 11:26:37 AM | Mindanao Grid-07/27/2024 11:33: Bunawan SS 50MVA Transformer No. 1 energized at 1121H. (Planned Outage) [WEBSMS] | CMIN
7/27/2024 10:19:07 AM | Luzon Grid-07/27/2024 10:19: Tayabas SS 9Z-02CB24TAY de-energized at 1015H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 10:16:51 AM | Visayas Grid-07/27/2024 10:16: KSPC-Colon 138 kV L1 de-energized at 1015H (Planned Outage) [WEBSMS] | CVIS
7/27/2024 10:07:42 AM | Mindanao Grid-07/27/2024 10:14: Matanao 138kV Bus No. 1 energized at 1006H. (Planned Outage) [WEBSMS] | CMIN
7/27/2024 9:54:21 AM | Mindanao Grid-07/27/2024 10:00: WMPC DG10 online at 0951H. RPS - System Voltage Requirement [WEBSMS] | CMIN
7/27/2024 9:38:38 AM | Luzon Grid-07/27/2024 09:38: San Jose 230kV Bus 1 restored at 0938H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 8:48:21 AM | Mindanao Grid-07/27/2024 08:54: Matanao 138kV Bus No. 1 de-energized at 0847H. (Planned Outage) [WEBSMS] | CMIN
7/27/2024 8:34:57 AM | Mindanao Grid-07/27/2024 08:41: Matanao - GenSan 138kV L1 de-energized at 0832H. (Planned Outage) [WEBSMS] | CMIN
7/27/2024 8:23:50 AM | Visayas Grid-07/27/2024 08:23: Cebu SS 300 MVA TR3 de-energized at 0822H (Planned Outage) [WEBSMS] | CVIS
7/27/2024 7:55:28 AM | Mindanao Grid-07/27/2024 08:01: Bunawan SS 50MVA Transformer No. 1 de-energized at 0754H. (Planned Outage) [WEBSMS] | CMIN
7/27/2024 6:53:06 AM | Luzon Grid-07/27/2024 06:53: Binan-Calamba 230kV Line 2 de-energized at 0640H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 6:43:28 AM | Visayas Grid-07/27/2024 06:43: Cebu-Colon 138 kV L2 de-energized at 0643H (Planned Outage) [WEBSMS] | CVIS
7/27/2024 6:38:27 AM | Visayas Grid-07/27/2024 06:38: Kananga-Tabango 230 kV L1 de-energized at 0625H (Planned Outage) [WEBSMS] | CVIS
7/27/2024 6:07:33 AM | Luzon Grid-07/27/2024 06:07: Ilijan 500kV Bus 2 de-energized at 0605H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 6:02:46 AM | [NSO Update] Luzon Grid-07/27/2024 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14142MW, PK=10085MW, RR=384MW, NetOpMargin: AM=3673, PM=3267, EVE=2309 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 1 @49MW, Limay 8 @60MW, Masinloc 1 @290MW, SCPC 1 @125MW, Masinloc 3 @300MW, Calaca U2 @280MW, SLTEC 2 @29MW [WEBSMS] | CLUZ
7/27/2024 5:54:51 AM | [NSO Update] Visayas Grid-07/27/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2572MW, PK=2090MW, RR=81MW, NetOpMargin: AM=401, PM=305, EVE=259 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, CEDC 3 @75MW, PGPP2 OKOY @14MW, PB104-3 @5MW, PB104-4 @5.5MW, PDPP3-H @8MW, PDPP3-E @8MW, TGPP @80.5MW, PB104-2 @4.5MW [WEBSMS] | CVIS
7/27/2024 5:44:59 AM | [NSO Update] Mindanao Grid-07/27/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3397MW, PK=2163MW, RR=73MW, NetOpMargin: AM=1161, PM=1095, EVE=1016 Highest Unit O/L: GNPK 1 @151.9MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @37.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/27/2024 4:08:35 AM | [NSO Update] Mindanao Grid-07/27/2024 04:15: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,035 km East of Southeastern Mindanao (6.5�N, 135.0�E). Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
7/27/2024 4:08:26 AM | [NSO Update] Visayas Grid-07/27/2024 04:08: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,035 km East of Southeastern Mindanao (6.5�N, 135.0�E). Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
7/27/2024 4:08:14 AM | [NSO Update] Luzon Grid-07/27/2024 04:08: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,035 km East of Southeastern Mindanao (6.5�N, 135.0�E). Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
7/27/2024 1:15:12 AM | Luzon Grid-07/27/2024 01:15: SLTEC 2 online at 0011H (Unplanned Outage) [WEBSMS] | CLUZ
7/27/2024 12:43:13 AM | Luzon Grid-07/27/2024 00:43: San Jose-Quezon 230kV Line 1 de-energized at 0040H (Planned Outage) [WEBSMS] | CLUZ
7/27/2024 12:08:13 AM | Visayas Grid-07/27/2024 00:08: KSPC U1 cut-out 0001H (Unplanned Outage) [WEBSMS] | CVIS
7/26/2024 11:54:34 PM | Luzon Grid-07/26/2024 23:54: Sta. Rita 20 shutdown at 2350H (Planned Outage) [WEBSMS] | CLUZ
7/26/2024 11:31:15 PM | Mindanao Grid-07/26/2024 23:37: SMC U2 online at 2326H (Unplanned Outage) [WEBSMS] | CMIN
7/26/2024 10:06:24 PM | Luzon Grid-07/26/2024 22:06: San Jose 230kV Bus 1 de-energized at 2205H (Planned Outage) [WEBSMS] | CLUZ
7/26/2024 9:05:06 PM | [NSO Update] Visayas Grid-07/26/2024 21:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2102H with power going to Luzon [WEBSMS] | CVIS
7/26/2024 9:04:35 PM | [NSO Update] Luzon Grid-07/26/2024 21:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2102H with power going to Luzon [WEBSMS] | CLUZ
7/26/2024 8:19:19 PM | Mindanao Grid-07/26/2024 20:25: WMPC DG10 shutdown at 2016H. RPS-System Voltage Requirement [WEBSMS] | CMIN
7/26/2024 8:13:27 PM | Luzon Grid-07/26/2024 20:13: Tayabas PCB 8-02CB04TAY and 8-02CB08TAY restored at 2011H & 2010H, respectively (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2024 8:07:35 PM | [NSO Update] Visayas Grid-07/26/2024 20:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2006H from reverse power direction [WEBSMS] | CVIS
7/26/2024 8:07:06 PM | [NSO Update] Luzon Grid-07/26/2024 20:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2006H from reverse power direction [WEBSMS] | CLUZ
7/26/2024 8:03:30 PM | Luzon Grid-07/26/2024 20:03: Tayabas PCB 8-02CB04TAY and 8-02CB08TAY de-energized at 2001H & 2002H, respectively (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2024 6:34:51 PM | Mindanao Grid-07/26/2024 18:41: Bislig -Nabunturan 138 kV Line auto-tripped at 1815H due to line -to- ground fault (CN) ( Unplanned Outage). Line restored at 1824H [WEBSMS] | CMIN
7/26/2024 5:49:44 PM | [NSO Update] Mindanao Grid-07/26/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3162MW, PK=2375MW, RR=73MW, NetOpMargin: EVE=715 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/26/2024 5:47:46 PM | [NSO Update] Visayas Grid-07/26/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2655MW, PK=2287MW, RR=86MW, NetOpMargin: EVE=281 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @308MW, CEDC 3 @75MW, PGPP2 OKOY @14MW, PB104-3 @5MW, PB104-4 @6.5MW, PDPP3-H @8MW, PDPP3-E @8MW, TGPP @80.5MW [WEBSMS] | CVIS
7/26/2024 5:45:27 PM | [NSO Update] Luzon Grid-07/26/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13561MW, PK=10408MW, RR=2801MW, NetOpMargin: EVE=2801 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 1 @49MW, Limay 8 @60MW, Masinloc 1 @290MW, SCPC 1 @125MW, Masinloc 3 @280MW [WEBSMS] | CLUZ
7/26/2024 5:23:25 PM | Luzon Grid-07/26/2024 17:23: Tayabas 230kV Bus 1 restored at 1658H (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2024 5:23:14 PM | Mindanao Grid-07/26/2024 17:29: WMPC DG08 shutdown at 1716H. RPS-System Voltage Requirement [WEBSMS] | CMIN
7/26/2024 5:10:52 PM | Luzon Grid-07/26/2024 17:10: For Info: Batangas new 300MVA TO2 energized (high side) at 1652H . On going commissioning test [WEBSMS] | CLUZ
7/26/2024 4:43:05 PM | [NSO Update] Visayas Grid-07/26/2024 16:43: SO-initiated Market Intervention for Visayas has been lifted today at 1639H. Market operations will resume starting interval 1645H. [WEBSMS] | CVIS
7/26/2024 3:58:04 PM | Mindanao Grid-07/26/2024 16:04: Butuan-San Francisco 138 kV line auto- tripped and successful single pole auto -reclosed at 1544H. [WEBSMS] | CMIN
7/26/2024 3:46:40 PM | Luzon Grid-07/26/2024 15:46: Tayabas 230kV Bus 1 de-energized at 1545H (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2024 2:54:28 PM | [NSO Update] Visayas Grid-07/26/2024 14:54: SO-initiated Market Intervention for Visayas is issued today starting interval 1455H due to MLD implementation to prevent the overloading of Ubay-Maasin 138kV Line. [WEBSMS] | CVIS
7/26/2024 2:10:31 PM | Mindanao Grid-07/26/2024 14:16: Davao -Bunawan 138 kV L2 auto tripped and auto reclosed at 1350H (Unplanned Outage) [WEBSMS] | CMIN
7/26/2024 1:46:36 PM | Luzon Grid-07/26/2024 13:46: EERI Unit 2 shutdown at 1343H. (Under test and commissioning) [WEBSMS] | CLUZ
7/26/2024 1:21:56 PM | Mindanao Grid-07/26/2024 13:28: SMC U2 with 33.66MW load tripped at 1314H. Indication: To be determined. (Unplanned outage) [WEBSMS] | CMIN
7/26/2024 1:18:18 PM | Mindanao Grid-07/26/2024 13:24: WMPC DG08 online at 1310H. RPS - System Voltage Requirement [WEBSMS] | CMIN
7/26/2024 1:13:25 PM | [NSO Update] Luzon Grid-07/26/2024 13:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1312H with power going to Visayas. [WEBSMS] | CLUZ
7/26/2024 1:12:57 PM | [NSO Update] Visayas Grid-07/26/2024 13:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1312H with power going to Visayas. [WEBSMS] | CVIS
7/26/2024 1:02:35 PM | [NSO Update] Visayas Grid-07/26/2024 13:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1258H from forward power direction. [WEBSMS] | CVIS
7/26/2024 1:01:38 PM | [NSO Update] Luzon Grid-07/26/2024 13:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1258H from forward power direction. [WEBSMS] | CLUZ
7/26/2024 12:51:37 PM | [NSO Update] Luzon Grid-07/26/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14288MW, PK=10977MW, RR=372MW, NetOpMargin: PM=2939, EVE=2820 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 1 @49MW, Limay 8 @60MW, Masinloc 1 @290MW, SCPC 1 @125MW, Masinloc 3 @285MW [WEBSMS] | CLUZ
7/26/2024 12:43:59 PM | [NSO Update] Mindanao Grid-07/26/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3337MW, PK=2546MW, RR=73MW, NetOpMargin: PM=719, EVE=813 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/26/2024 12:42:03 PM | [NSO Update] Visayas Grid-07/26/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2672MW, PK=2372MW, RR=90MW, NetOpMargin: PM=210, EVE=253 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @303MW, CEDC 3 @75MW, PB104-1 @4MW, PB104-3 @5MW, PB104-4 @6.5MW, PDPP3-H @8MW, PDPP3-E @8MW, TGPP @80.5MW [WEBSMS] | CVIS
7/26/2024 11:18:01 AM | Mindanao Grid-07/26/2024 11:24: SMC U2 online at 1111H (Planned Outage) [WEBSMS] | CMIN
7/26/2024 10:13:53 AM | Mindanao Grid-07/26/2024 10:20: FDC U3 online at 1004H (Unplanned Outage) [WEBSMS] | CMIN
7/26/2024 9:48:50 AM | Mindanao Grid-07/26/2024 09:55: WMPC DG10 online at 0933H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/26/2024 6:02:55 AM | [NSO Update] Mindanao Grid-07/26/2024 06:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3087MW, PK=2435MW, RR=73MW, NetOpMargin: AM=579, PM=516, EVE=608 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @30.5MW [WEBSMS] | CMIN
7/26/2024 6:01:07 AM | [NSO Update] Visayas Grid-07/26/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2651MW, PK=2361MW, RR=89MW, NetOpMargin: AM=201, PM=321, EVE=261 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC 3 @75MW, PB104-2 @4.5MW, PB104-3 @5MW, PB104-4 @6.5MW, PDPP3-H @8MW, PDPP3-E @8MW, TGPP @80.5MW [WEBSMS] | CVIS
7/26/2024 5:59:26 AM | [NSO Update] Luzon Grid-07/26/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14446MW, PK=10876MW, RR=379MW, NetOpMargin: AM=3191, PM=2681, EVE=3044 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 1 @49MW, Limay 8 @60MW, Masinloc 1 @300MW, SCPC 1 @125MW, Masinloc 3 @290MW [WEBSMS] | CLUZ
7/26/2024 5:15:34 AM | Luzon Grid-07/26/2024 05:15: Dolores - Masinag 115kV line energized at 0510H (Planned Outage) [WEBSMS] | CLUZ
7/26/2024 4:56:03 AM | [NSO Update] Mindanao Grid-07/26/2024 05:02: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,035 km East of Southeastern Mindanao (6.3 N, 135.0 E). Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
7/26/2024 4:55:36 AM | [NSO Update] Visayas Grid-07/26/2024 04:55: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,035 km East of Southeastern Mindanao (6.3 N, 135.0 E). Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
7/26/2024 4:55:19 AM | [NSO Update] Luzon Grid-07/26/2024 04:55: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 1,035 km East of Southeastern Mindanao (6.3 N, 135.0 E). Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
7/26/2024 3:48:05 AM | Luzon Grid-07/26/2024 03:48: Calaca 1 tripped at 0338H. (Unplanned Outage). [WEBSMS] | CLUZ
7/26/2024 1:06:41 AM | Luzon Grid-07/26/2024 01:06: Dolores - Masinag 115kV line de-energized at 0105H (Planned Outage) [WEBSMS] | CLUZ
7/25/2024 10:54:04 PM | [NSO Update] Luzon Grid-07/25/2024 22:54: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2250H with power going to Luzon [WEBSMS] | CLUZ
7/25/2024 10:53:40 PM | [NSO Update] Visayas Grid-07/25/2024 22:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2250H with power going to Luzon [WEBSMS] | CVIS
7/25/2024 10:52:41 PM | [NSO Update] Luzon Grid-07/25/2024 22:52: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2207H from reverse power direction [WEBSMS] | CLUZ
7/25/2024 10:52:23 PM | [NSO Update] Visayas Grid-07/25/2024 22:52: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2207H from reverse power direction [WEBSMS] | CVIS
7/25/2024 10:51:42 PM | Mindanao Grid-07/25/2024 22:58: Mt Apo U3 online at 2243H (Unplanned Outage) [WEBSMS] | CMIN
7/25/2024 9:12:36 PM | Visayas Grid-07/25/2024 21:12: TGPP U3 cut-out at 2112H (Planned Outage) [WEBSMS] | CVIS
7/25/2024 8:48:55 PM | Mindanao Grid-07/25/2024 20:55: WMPC DG10 shutdown at 2048H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/25/2024 8:47:56 PM | Luzon Grid-07/25/2024 20:47: Dona Imelda - Paco (Manila) restored at 2047H (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 8:45:52 PM | Mindanao Grid-07/25/2024 20:52: Liangan Hydro Plant shutdown at 2045H. Test & commissioning. [WEBSMS] | CMIN
7/25/2024 8:41:52 PM | Visayas Grid-07/25/2024 20:41: TGPP U1 cut-in at 2040H (Unplanned Outage) [WEBSMS] | CVIS
7/25/2024 8:24:35 PM | Visayas Grid-07/25/2024 20:24: PGPP1 U3 cut-in at 2023H (Unplanned Outage) [WEBSMS] | CVIS
7/25/2024 8:14:01 PM | Mindanao Grid-07/25/2024 20:20: Liangan Hydro Plant online at 2011H. Testing and commissioning. [WEBSMS] | CMIN
7/25/2024 6:33:17 PM | Luzon Grid-07/25/2024 18:33: Calaca Unit 1 online at 1829H (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 6:31:13 PM | Mindanao Grid-07/25/2024 18:37: Liangan Hydro Plant online at 1830H. Testing and commissioning. [WEBSMS] | CMIN
7/25/2024 6:26:21 PM | Visayas Grid-07/25/2024 18:26: PGPP1 U3 tripped at 1821H (Unplanned Outage) [WEBSMS] | CVIS
7/25/2024 6:18:30 PM | [NSO Update] Luzon Grid-07/25/2024 18:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13405MW, PK=9595MW, RR=344MW, NetOpMargin: EVE=3466 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 1 @59MW, Limay 8 @60MW, Masinloc 1 @240MW, SCPC 1 @125MW, Masinloc 3 @280MW, SLPGC 1 @140MW [WEBSMS] | CLUZ
7/25/2024 6:17:04 PM | Luzon Grid-07/25/2024 18:17: Laoag-Caparispisan (Pagudpud Wind Farm) 115kV Line looped at 1810H (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 6:11:37 PM | Mindanao Grid-07/25/2024 18:18: Liangan Hydro Plant shutdown at 1807H. Test & commissioning. [WEBSMS] | CMIN
7/25/2024 5:58:26 PM | Luzon Grid-07/25/2024 17:58: Dona Imelda - Paco (Manila) 230kV Line tripped at 1756H (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 5:53:26 PM | Luzon Grid-07/25/2024 17:53: Laoag-Caparispisan (Pagudpud Wind Farm) 115kV line auto-tripped at 1747H and auto-reclosed at Laoag side. (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 5:53:18 PM | [NSO Update] Mindanao Grid-07/25/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3031MW, PK=2367MW, RR=73MW, NetOpMargin: EVE=591 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/25/2024 5:48:36 PM | [NSO Update] Visayas Grid-07/25/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2607MW, PK=2242MW, RR=87MW, NetOpMargin: EVE=278 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @290MW, CEDC 3 @75MW, PB104-2 @4.5MW, PDPP3-E @8MW, PB104-3 @5MW, PB104-4 @6.5MW, TGPP @79.5MW [WEBSMS] | CVIS
7/25/2024 5:19:57 PM | Luzon Grid-07/25/2024 17:19: Dona Imelda 300MVA T01 restored at 1719H (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 5:03:32 PM | Mindanao Grid-07/25/2024 17:09: Liangan Hydro Plant online at 1645H. Testing and commissioning. [WEBSMS] | CMIN
7/25/2024 4:16:31 PM | Mindanao Grid-07/25/2024 16:22: WMPC DG01 shutdown at 1616H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/25/2024 3:39:37 PM | Visayas Grid-07/25/2024 15:39: TGPP U1 emergency shutdown at 1538H (Unplanned Outage) [WEBSMS] | CVIS
7/25/2024 2:55:33 PM | Luzon Grid-07/25/2024 14:55: Tayabas PCB 9-04CB24TAY restored at 1455H (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 2:24:54 PM | Visayas Grid-07/25/2024 14:24: EDC-Malitbog U3 cut-in at 1411H (Unplanned Outage) [WEBSMS] | CVIS
7/25/2024 2:17:21 PM | Luzon Grid-07/25/2024 14:17: Bacman-Palayan Binary Plant 230kV Tie Line de-energized at 1412H (Planned Outage) [WEBSMS] | CLUZ
7/25/2024 1:45:31 PM | Mindanao Grid-07/25/2024 13:51: WMPC DG1 online at 1342H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/25/2024 1:33:07 PM | Luzon Grid-07/25/2024 13:33: Bacnotan-CIP II 69kV line was restored at 1332H. (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 12:59:27 PM | [NSO Update] Luzon Grid-07/25/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13233MW, PK=9705MW, RR=358MW, NetOpMargin: PM=3170, EVE=3336 Highest Unit O/L: GNPD 1@668MW Derated Plant: SLTEC 1 @55MW, SLPGC 2 @125MW, Limay 8 @60MW, Masinloc 1 @250MW, SCPC 1 @125MW, Masinloc 3 @240MW, SLPGC 1 @110MW, Calaca U2 @150MW, GNPD U2 @334MW [WEBSMS] | CLUZ
7/25/2024 12:43:40 PM | [NSO Update] Visayas Grid-07/25/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2616MW, PK=2296MW, RR=87MW, NetOpMargin: PM=232, EVE=241 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @252MW, CEDC 3 @75MW, PB104-2 @4.5MW, PDPP3-E @8MW, PB104-3 @5MW, PDPP1-5 @4MW [WEBSMS] | CVIS
7/25/2024 12:43:12 PM | Luzon Grid-07/25/2024 12:43: Bacnotan-CIP II 69kV line auto-tripped at 1238H. (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 11:58:54 AM | Mindanao Grid-07/25/2024 12:05: Mt Apo U3 with 3MW load tripped at 1152H. Indication: To be determined. (Unplanned outage) [WEBSMS] | CMIN
7/25/2024 11:45:58 AM | Luzon Grid-07/25/2024 11:45: Dona Imelda 300MVA T03 was restored at 1144H. (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 11:35:48 AM | Luzon Grid-07/25/2024 11:35: Nagsaag-Pantabangan 230kV line was restored at 1134H. (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 11:09:19 AM | [NSO Update] Mindanao Grid-07/25/2024 11:15: Weather Disturbance Alert Notice (WDAN) for Super Typhoon CARINA has been lifted today, July 25, 2024, at 1100H, as it is now outside the Philippine Area of Responsibility (PAR). The center of Super Typhoon CARINA was estimated based on all available data at 515 km North Northwest of Itbayat, Batanes (OUTSIDE PAR) (25.1 �N, 120.0 �E ) [WEBSMS] | CMIN
7/25/2024 11:09:03 AM | [NSO Update] Visayas Grid-07/25/2024 11:09: Weather Disturbance Alert Notice (WDAN) for Super Typhoon CARINA has been lifted today, July 25, 2024, at 1100H, as it is now outside the Philippine Area of Responsibility (PAR). The center of Super Typhoon CARINA was estimated based on all available data at 515 km North Northwest of Itbayat, Batanes (OUTSIDE PAR) (25.1 �N, 120.0 �E ) [WEBSMS] | CVIS
7/25/2024 11:08:54 AM | [NSO Update] Luzon Grid-07/25/2024 11:08: Weather Disturbance Alert Notice (WDAN) for Super Typhoon CARINA has been lifted today, July 25, 2024, at 1100H, as it is now outside the Philippine Area of Responsibility (PAR). The center of Super Typhoon CARINA was estimated based on all available data at 515 km North Northwest of Itbayat, Batanes (OUTSIDE PAR) (25.1 �N, 120.0 �E ) [WEBSMS] | CLUZ
7/25/2024 10:22:32 AM | Mindanao Grid-07/25/2024 10:28: Balo-i - Lugait 138kV Line energized at 1020H. (Planned Outage) [WEBSMS] | CMIN
7/25/2024 10:12:30 AM | Mindanao Grid-07/25/2024 10:18: WMPC DG10 online at 1008H.RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/25/2024 9:10:50 AM | Luzon Grid-07/25/2024 09:10: Tayabas PCB 9-04CB24TAY was de-energized at 0906H. (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 8:38:38 AM | Luzon Grid-07/25/2024 08:38: Hermosa-Marilao 230kV line was restored at 0837H. (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 8:18:49 AM | Luzon Grid-07/25/2024 08:18: GNPD Unit 2 online at 0816H. (Planned Outage) [WEBSMS] | CLUZ
7/25/2024 8:16:30 AM | Mindanao Grid-07/25/2024 08:22: Balo-i - Lugait 138kV Line de-energized/shutdown at 0814H. (Planned Outage) [WEBSMS] | CMIN
7/25/2024 5:39:42 AM | [NSO Update] Mindanao Grid-07/25/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3080MW, PK=2325MW, RR=73MW, NetOpMargin: AM=682, PM=651, EVE=732 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/25/2024 5:37:38 AM | [NSO Update] Luzon Grid-07/25/2024 05:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0527H with power going to Visayas. [WEBSMS] | CLUZ
7/25/2024 5:35:14 AM | [NSO Update] Visayas Grid-07/25/2024 05:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0527H with power going to Visayas. [WEBSMS] | CVIS
7/25/2024 5:33:58 AM | [NSO Update] Visayas Grid-07/25/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2581MW, PK=2270MW, RR=88MW, NetOpMargin: AM=223, PM=255, EVE=191 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @260MW, CEDC 3 @75MW [WEBSMS] | CVIS
7/25/2024 5:33:47 AM | [NSO Update] Luzon Grid-07/25/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13053MW, PK=9277MW, RR=368MW, NetOpMargin: AM=3408, PM=3682, EVE=3479 Highest Unit O/L: GNPD 1@668MW Derated Plant: SLTEC 1 @49MW, SLPGC 2 @75MW, Limay 8 @60MW, Masinloc 1 @250MW, SCPC 1 @125MW, Masinloc 3 @240MW, SLPGC 1 @75MW, Calaca U2 @150MW [WEBSMS] | CLUZ
7/25/2024 4:51:54 AM | [NSO Update] Visayas Grid-07/25/2024 04:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0450H from forward power direction. [WEBSMS] | CVIS
7/25/2024 4:51:49 AM | [NSO Update] Luzon Grid-07/25/2024 04:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0450H from forward power direction. [WEBSMS] | CLUZ
7/25/2024 4:08:34 AM | [NSO Update] Luzon Grid-07/25/2024 04:08: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "CARINA" {GAEMI} was estimated based on all available data at 450 km North of Itbayat, Batanes (24.8�N, 121.3�E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 250 km/h. It is moving Northward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
7/25/2024 4:08:31 AM | [NSO Update] Visayas Grid-07/25/2024 04:08: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "CARINA" {GAEMI} was estimated based on all available data at 450 km North of Itbayat, Batanes (24.8�N, 121.3�E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 250 km/h. It is moving Northward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CVIS
7/25/2024 4:08:25 AM | [NSO Update] Mindanao Grid-07/25/2024 04:15: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "CARINA" {GAEMI} was estimated based on all available data at 450 km North of Itbayat, Batanes (24.8�N, 121.3�E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 250 km/h. It is moving Northward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CMIN
7/25/2024 4:02:31 AM | Luzon Grid-07/25/2024 04:02: Hermosa - Duhat 230kV Line tripped at 0401H (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 4:01:25 AM | Luzon Grid-07/25/2024 04:01: Hermosa - Duhat 230kV Line restored at 0400H (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2024 3:43:38 AM | Luzon Grid-07/25/2024 03:43: Hermosa - Duhat 230kV Line tripped at 0337H (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 11:20:28 PM | [NSO Update] Luzon Grid-07/24/2024 23:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2319H with power going to Luzon. [WEBSMS] | CLUZ
7/24/2024 11:20:25 PM | [NSO Update] Visayas Grid-07/24/2024 23:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2319H with power going to Luzon. [WEBSMS] | CVIS
7/24/2024 10:17:47 PM | Luzon Grid-07/24/2024 22:18: Limay - Batangas (BTG) 230kV Line 2 restored at 2217H (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 10:10:16 PM | [NSO Update] Visayas Grid-07/24/2024 22:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2209H from reverse power direction. [WEBSMS] | CVIS
7/24/2024 10:10:13 PM | [NSO Update] Luzon Grid-07/24/2024 22:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2209H from reverse power direction. [WEBSMS] | CLUZ
7/24/2024 9:26:40 PM | Luzon Grid-07/24/2024 21:26: Malaya 2 with 130MW tripped at 2124H. Lowest system frequency was 59.62Hz. (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 9:09:31 PM | Luzon Grid-07/24/2024 21:09: Limay - Batangas (BTG) 230kV Line 2 tripped at 2059H (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 8:20:42 PM | Mindanao Grid-07/24/2024 20:27: WMPC DG10 shutdown at 2016H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/24/2024 7:46:06 PM | [NSO Update] Luzon Grid-07/24/2024 19:46: Weather Update: At 3:00 PM today, the center of the eye of Super Typhoon "CARINA" {GAEMI} was estimated based on all available data at 395 km North of Itbayat, Batanes (24.3�N, 122.3�E) with maximum sustained winds of 185 km/h near the center and gustiness of up to 230 km/h. It is moving Northwestward at 20 km/h. [WEBSMS] | CLUZ
7/24/2024 7:45:34 PM | [NSO Update] Visayas Grid-07/24/2024 19:45: Weather Update: At 3:00 PM today, the center of the eye of Super Typhoon "CARINA" {GAEMI} was estimated based on all available data at 395 km North of Itbayat, Batanes (24.3�N, 122.3�E) with maximum sustained winds of 185 km/h near the center and gustiness of up to 230 km/h. It is moving Northwestward at 20 km/h. [WEBSMS] | CVIS
7/24/2024 7:44:55 PM | [NSO Update] Mindanao Grid-07/24/2024 19:51: Weather Update: At 3:00 PM today, the center of the eye of Super Typhoon "CARINA" {GAEMI} was estimated based on all available data at 395 km North of Itbayat, Batanes (24.3�N, 122.3�E) with maximum sustained winds of 185 km/h near the center and gustiness of up to 230 km/h. It is moving Northwestward at 20 km/h. [WEBSMS] | CMIN
7/24/2024 6:28:50 PM | Mindanao Grid-07/24/2024 18:35: WMPC DG10 online at 1826H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2024 6:25:44 PM | Luzon Grid-07/24/2024 18:26: Pantabangan - Nagsaag 230kV Line tripped at 1819H. (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 6:08:53 PM | [NSO Update] Mindanao Grid-07/24/2024 18:15: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3038MW, PK=2285MW, RR=73MW, NetOpMargin: EVE=680 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/24/2024 6:07:49 PM | Luzon Grid-07/24/2024 18:08: Dona Imelda 300MVA T01 tripped at 1805H (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 6:06:27 PM | [NSO Update] Visayas Grid-07/24/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2523MW, PK=2056MW, RR=84MW, NetOpMargin: EVE=383 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @255MW, CEDC 3 @75MW, PB104-2 @4.5MW, PB104-4 @6.5MW, PDPP1-5 @4MW, PB104-3 @5MW [WEBSMS] | CVIS
7/24/2024 6:04:15 PM | Luzon Grid-07/24/2024 18:04: Dona Imelda 300MVA T03 tripped at 1800H (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 6:00:28 PM | [NSO Update] Luzon Grid-07/24/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12579MW, PK=7787MW, RR=410MW, NetOpMargin: EVE=4382 Highest Unit O/L: GNPD 1@668MW Derated Plant: SLTEC 1 @49MW, SLPGC 2 @75MW, Limay 8 @60MW, Masinloc 1 @250MW, SCPC 1 @125MW, Masinloc 3 @280MW, SLPGC 1 @75MW [WEBSMS] | CLUZ
7/24/2024 5:35:16 PM | Luzon Grid-07/24/2024 17:35: Correction: San Jose 115kV - Angat Line 2 restored at 1735H (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 5:28:24 PM | Luzon Grid-07/24/2024 17:28: San Jose 115kV - Angat Line 2 restored at 1715H (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 5:15:03 PM | Mindanao Grid-07/24/2024 17:21: WMPC DG10 shutdown at 1713H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/24/2024 5:00:34 PM | Luzon Grid-07/24/2024 17:00: Tayabas PCB 9-04CB04TAY restored at 1659H (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 4:09:47 PM | Mindanao Grid-07/24/2024 16:16: WMPC DG4 online at 1605H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2024 3:52:04 PM | Mindanao Grid-07/24/2024 15:58: Lake Mainit HEP online at 1548H (Unplanned Outage). [WEBSMS] | CMIN
7/24/2024 3:45:26 PM | Luzon Grid-07/24/2024 15:45: MPGC Unit 4 online at 1543H. (On-going test and commissioning.) [WEBSMS] | CLUZ
7/24/2024 2:01:14 PM | Mindanao Grid-07/24/2024 14:07: ASIGA HEP tripped at 1323H (Unplanned Outage). [WEBSMS] | CMIN
7/24/2024 1:56:00 PM | Mindanao Grid-07/24/2024 14:02: Lake Mainit HEP tripped at 1323H (Unplanned Outage) [WEBSMS] | CMIN
7/24/2024 1:38:30 PM | Mindanao Grid-07/24/2024 13:45: MACO BESS tripped at 1318H (Unplanned Outage). [WEBSMS] | CMIN
7/24/2024 1:26:21 PM | Luzon Grid-07/24/2024 13:26: Tayabas-San Jose 500kV Line 1 looped at Tayabas side at 1326H. (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 1:11:30 PM | Luzon Grid-07/24/2024 13:11: Tayabas-San Jose 500kV Line 1 tripped (reclosed at San Jose only) at 1307H. (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 12:44:31 PM | [NSO Update] Mindanao Grid-07/24/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3060MW, PK=2387MW, RR=73MW, NetOpMargin: PM=600, EVE=674 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/24/2024 12:44:25 PM | [NSO Update] Visayas Grid-07/24/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2542MW, PK=2213MW, RR=88MW, NetOpMargin: PM=241, EVE=323 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @255MW, CEDC 3 @75MW [WEBSMS] | CVIS
7/24/2024 12:44:14 PM | [NSO Update] Luzon Grid-07/24/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13096MW, PK=8791MW, RR=440MW, NetOpMargin: PM=3865, EVE=2900 Highest Unit O/L: GNPD 1@668MW Derated Plant: SLTEC 1 @49MW, SLPGC 2 @75MW, Limay 8 @60MW, Masinloc 1 @300MW, SCPC 1 @125MW, Masinloc 3 @290MW, SLPGC 1 @40MW [WEBSMS] | CLUZ
7/24/2024 12:28:14 PM | Luzon Grid-07/24/2024 12:28: Correction: San Jose 115kV - Angat Line 2 tripped at 1209H (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 12:11:28 PM | Luzon Grid-07/24/2024 12:11: San Jose 115kV Line 2 tripped at 1209H (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 12:05:32 PM | Luzon Grid-07/24/2024 12:05: Hermosa - BCCPP 230kV Line 3 tripped/reclosed at 1203H (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 11:48:55 AM | Luzon Grid-07/24/2024 11:49: Tayabas PCB 9-04CB04TAY emergency shutdown at 1146H (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 11:17:43 AM | Luzon Grid-07/24/2024 11:17: Tayabas - San Jose 500kV Line 1 restored at 1117H. (Unplanned Outage). [WEBSMS] | CLUZ
7/24/2024 11:10:40 AM | Mindanao Grid-07/24/2024 11:17: WMPC DG10 online at 1055H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2024 10:39:13 AM | Luzon Grid-07/24/2024 10:39: Tayabas - San Jose 500kV Line 1 tripped at 1037H. (Unplanned Outage). [WEBSMS] | CLUZ
7/24/2024 10:07:03 AM | Luzon Grid-07/24/2024 10:07: Tayabas - San Jose 500kV Line 1 restored at 1006H. (Unplanned Outage). [WEBSMS] | CLUZ
7/24/2024 9:48:00 AM | Luzon Grid-07/24/2024 09:48: Tayabas - San Jose 500kV Line 1 tripped at 0946H. (Unplanned Outage). [WEBSMS] | CLUZ
7/24/2024 8:54:02 AM | Luzon Grid-07/24/2024 08:54: Tayabas-San Jose 500kV Line 1 tripped/reclosed at San Jose at 0848H. Looped at Tayabas at 0853H. (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 8:42:46 AM | Luzon Grid-07/24/2024 08:43: Tayabas-San Jose 500kV Line 1 tripped/reclosed both side at 0840H (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 8:12:25 AM | Luzon Grid-07/24/2024 08:12: SCPC 3 tripped with 139MW at 0810H. Lowest system frequency was 59.66Hz (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 7:31:03 AM | Luzon Grid-07/24/2024 07:31: Tayabas-San Jose 500kV Line 1 tripped/reclosed at Tayabas at 0725H. Looped at San Jose at 0726H. (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 7:29:14 AM | Luzon Grid-07/24/2024 07:29: Tayabas-San Jose 500kV Line 1 tripped/reclosed at San Jose at 0723H. Looped at Tayabas at 0725H. (Unplanned Outage) [WEBSMS] | CLUZ
7/24/2024 5:43:43 AM | [NSO Update] Mindanao Grid-07/24/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3077MW, PK=2336MW, RR=73MW, NetOpMargin: AM=667, PM=589, EVE=662 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/24/2024 5:42:16 AM | [NSO Update] Visayas Grid-07/24/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2549MW, PK=2120MW, RR=86MW, NetOpMargin: AM=343, PM=176, EVE=175 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @258MW, CEDC 3 @75MW, PB104-2 @4.5MW, PB104-4 @6.5MW, PDPP1-2 @4MW, PDPP1-5 @4MW [WEBSMS] | CVIS
7/24/2024 5:38:21 AM | [NSO Update] Luzon Grid-07/24/2024 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13804MW, PK=10384MW, RR=427MW, NetOpMargin: AM=2993, PM=3010, EVE=2924 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @49MW, SLPGC 2 @120MW, Limay 8 @60MW, Masinloc 1 @300MW, SCPC 1 @125MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
7/24/2024 4:35:38 AM | [NSO Update] Luzon Grid-07/24/2024 04:35: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "CARINA" (GAEMI) was estimated based on all available data at 280 km Northeast of Itbayat, Batanes (22.8N, 123.5E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving Northwestward at 25 km/h. [WEBSMS] | CLUZ
7/24/2024 4:33:53 AM | [NSO Update] Visayas Grid-07/24/2024 04:34: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "CARINA" (GAEMI) was estimated based on all available data at 280 km Northeast of Itbayat, Batanes (22.8N, 123.5E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving Northwestward at 25 km/h. [WEBSMS] | CVIS
7/24/2024 4:33:36 AM | [NSO Update] Mindanao Grid-07/24/2024 04:40: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "CARINA" (GAEMI) was estimated based on all available data at 280 km Northeast of Itbayat, Batanes (22.8N, 123.5E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving Northwestward at 25 km/h. [WEBSMS] | CMIN
7/24/2024 4:31:58 AM | [NSO Update] Luzon Grid-07/24/2024 04:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0429H with power going to Visayas. [WEBSMS] | CLUZ
7/24/2024 4:31:34 AM | [NSO Update] Visayas Grid-07/24/2024 04:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0429H with power going to Visayas. [WEBSMS] | CVIS
7/24/2024 4:22:52 AM | [NSO Update] Visayas Grid-07/24/2024 04:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0419H from forward power direction. [WEBSMS] | CVIS
7/24/2024 4:20:59 AM | [NSO Update] Luzon Grid-07/24/2024 04:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0419H from forward power direction. [WEBSMS] | CLUZ
7/24/2024 1:39:01 AM | [NSO Update] Luzon Grid-07/24/2024 01:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0137H with power going to Luzon. [WEBSMS] | CLUZ
7/24/2024 1:38:38 AM | [NSO Update] Visayas Grid-07/24/2024 01:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0137H with power going to Luzon. [WEBSMS] | CVIS
7/24/2024 1:26:12 AM | [NSO Update] Visayas Grid-07/24/2024 01:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0123H from reverse power direction. [WEBSMS] | CVIS
7/24/2024 1:25:36 AM | [NSO Update] Luzon Grid-07/24/2024 01:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0123H from reverse power direction. [WEBSMS] | CLUZ
7/24/2024 1:14:41 AM | Mindanao Grid-07/24/2024 01:21: TSI Unit 2 online at 0104H (Unplanned Outage) [WEBSMS] | CMIN
7/23/2024 10:22:16 PM | Luzon Grid-07/23/2024 22:22: Calaca 1 emergency shutdown at 2219H (Unplanned Outage) [WEBSMS] | CLUZ
7/23/2024 8:27:50 PM | Luzon Grid-07/23/2024 20:28: Tayabas-San Jose 500kV Line 1 tripped/reclosed both side at 2022H (Unplanned Outage) [WEBSMS] | CLUZ
7/23/2024 6:57:24 PM | Mindanao Grid-07/23/2024 19:04: WMPC DG05 shutdown at 1716H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/23/2024 6:35:26 PM | Luzon Grid-07/23/2024 18:35: SLTEC 2 with 108MW load tripped at 1830H. Lowest Frequency is 59.65Hz (Unplanned Outage) [WEBSMS] | CLUZ
7/23/2024 5:41:51 PM | [NSO Update] Mindanao Grid-07/23/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2906MW, PK=2199MW, RR=73MW, NetOpMargin: EVE=73 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/23/2024 5:37:38 PM | [NSO Update] Visayas Grid-07/23/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2443MW, PK=2098MW, RR=87MW, NetOpMargin: EVE=258 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @258MW, CEDC 3 @75MW, PB104-2 @4.5MW, PB104-4 @6.5MW, PDPP1-2 @4MW, PDPP1-5 @4MW [WEBSMS] | CVIS
7/23/2024 5:35:47 PM | [NSO Update] Luzon Grid-07/23/2024 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13107MW, PK=9538MW, RR=440MW, NetOpMargin: EVE=3129 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @118MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc 1 @300MW, SCPC 1 @125MW, Masinloc 3 @290MW, Calaca 1 @130MW [WEBSMS] | CLUZ
7/23/2024 4:18:44 PM | [NSO Update] Visayas Grid-07/23/2024 16:18: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2497MW, PK=2174MW, RR=88MW, NetOpMargin: PM=235, EVE=367 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @252MW, CEDC 3 @75MW, PB104-2 @4.5MW, PB104-4 @6.5MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW [WEBSMS] | CVIS
7/23/2024 4:12:47 PM | [NSO Update] Visayas Grid-07/23/2024 16:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1042H with power going to Visayas. [WEBSMS] | CVIS
7/23/2024 3:41:37 PM | Mindanao Grid-07/23/2024 15:48: Aurora SS 100MVA Power Transformer No. 3 energized at 1539H. (Planned Outage) [WEBSMS] | CMIN
7/23/2024 2:05:30 PM | Mindanao Grid-07/23/2024 14:12: WMPC DG05 online at 1317H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/23/2024 1:08:06 PM | [NSO Update] Mindanao Grid-07/23/2024 13:14: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2965MW, PK=2333MW, RR=73MW, NetOpMargin: PM=559, EVE=638 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/23/2024 1:03:39 PM | [NSO Update] Luzon Grid-07/23/2024 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13568MW, PK=10329MW, RR=472MW, NetOpMargin: PM=2766, EVE=1519 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @118MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc 1 @300MW, SCPC 1 @125MW, Masinloc 3 @280MW [WEBSMS] | CLUZ
7/23/2024 10:47:18 AM | [NSO Update] Luzon Grid-07/23/2024 10:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1042H with power going to Visayas [WEBSMS] | CLUZ
7/23/2024 10:37:09 AM | [NSO Update] Visayas Grid-07/23/2024 10:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1032H from forward power direction [WEBSMS] | CVIS
7/23/2024 10:35:34 AM | [NSO Update] Luzon Grid-07/23/2024 10:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1032H from forward power direction [WEBSMS] | CLUZ
7/23/2024 10:35:06 AM | Mindanao Grid-07/23/2024 10:41: DCP (TSI) Unit 2 with 150.31MW load tripped at 0946H. Lowest frequency recorded was 59.11Hz. ALD=22.05MW (Unplanned Outage) [WEBSMS] | CMIN
7/23/2024 10:30:33 AM | Mindanao Grid-07/23/2024 10:37: DCP (TSI) Unit 2 with 150.31MW load tripped at 0946H. Lowest frequency recorded was 59.11Hz. ALD=22.05MW (Unplanned Outage) [WEBSMS] | CMIN
7/23/2024 9:57:32 AM | Mindanao Grid-07/23/2024 10:04: Matanao - Culaman 230kV L1 tripped and auto-reclosed at 0946H. (Unplanned Outage) [WEBSMS] | CMIN
7/23/2024 9:56:22 AM | Mindanao Grid-07/23/2024 10:03: Matanao - Culaman 230kV tripped and auto-reclosed at 0946H. (Unplanned Outage) [WEBSMS] | CMIN
7/23/2024 9:07:59 AM | Mindanao Grid-07/23/2024 09:14: Aurora SS 100MVA Power Transformer No. 3 de-energized at 0902H. (Planned Outage) [WEBSMS] | CMIN
7/23/2024 5:52:02 AM | [NSO Update] Mindanao Grid-07/23/2024 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3110MW, PK=2194MW, RR=73MW, NetOpMargin: AM=843, PM=711, EVE=711 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/23/2024 5:51:14 AM | [NSO Update] Visayas Grid-07/23/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2692MW, PK=2289MW, RR=85MW, NetOpMargin: AM=318, PM=176, EVE=193 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @253MW, CEDC 3 @75MW, PB104-2 @4.5MW, PB104-4 @6.5MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW [WEBSMS] | CVIS
7/23/2024 5:49:49 AM | [NSO Update] Luzon Grid-07/23/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13899MW, PK=10502MW, RR=458MW, NetOpMargin: AM=2939, PM=1678, EVE=1925 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @118MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc 1 @300MW, SCPC 1 @125MW [WEBSMS] | CLUZ
7/23/2024 5:31:05 AM | [NSO Update] Visayas Grid-07/23/2024 05:31: Weather Update: At 3:00 AM today, the center of Typhoon CARINA was estimated based on all available data at 380 km East of Aparri, Cagayan (18.8N, 125.2E) with maximum sustained winds of 130 km/h near the center and gustiness of up to 160 km/h. It is moving North Northwestward at 10 km/h. [WEBSMS] | CVIS
7/23/2024 4:56:21 AM | [NSO Update] Mindanao Grid-07/23/2024 05:03: Weather Update: At 3:00 AM today, the center of Typhoon CARINA was estimated based on all available data at 380 km East of Aparri, Cagayan (18.8N, 125.2E) with maximum sustained winds of 130 km/h near the center and gustiness of up to 160 km/h. It is moving North Northwestward at 10 km/h. [WEBSMS] | CMIN
7/23/2024 4:54:27 AM | [NSO Update] Luzon Grid-07/23/2024 04:54: Weather Update: At 3:00 AM today, the center of Typhoon CARINA was estimated based on all available data at 380 km East of Aparri, Cagayan (18.8N, 125.2E) with maximum sustained winds of 130 km/h near the center and gustiness of up to 160 km/h. It is moving North Northwestward at 10 km/h. [WEBSMS] | CLUZ
7/22/2024 8:43:05 PM | [NSO Update] Visayas Grid-07/22/2024 20:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2011H with power going to Luzon [WEBSMS] | CVIS
7/22/2024 8:42:49 PM | [NSO Update] Luzon Grid-07/22/2024 20:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2011H with power going to Luzon [WEBSMS] | CLUZ
7/22/2024 8:41:55 PM | [NSO Update] Visayas Grid-07/22/2024 20:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2001H from reverse power direction [WEBSMS] | CVIS
7/22/2024 8:41:39 PM | [NSO Update] Luzon Grid-07/22/2024 20:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2001H from reverse power direction [WEBSMS] | CLUZ
7/22/2024 6:04:06 PM | [NSO Update] Mindanao Grid-07/22/2024 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3066MW, PK=2220MW, RR=73MW, NetOpMargin: EVE=772 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/22/2024 6:02:18 PM | [NSO Update] Visayas Grid-07/22/2024 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2561MW, PK=2146MW, RR=85MW, NetOpMargin: EVE=331 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @247MW, CEDC 3 @75MW, PDPP3-E @8MW, PB104-2 @5MW, PB104-3 @5MW, PB104-4 @6.5MW [WEBSMS] | CVIS
7/22/2024 6:00:15 PM | [NSO Update] Luzon Grid-07/22/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13465MW, PK=9900MW, RR=431MW, NetOpMargin: EVE=3134 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @118MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc 1 @300MW, SCPC 1 @125MW, Masinloc 3 @315MW, Calaca 1 @165MW [WEBSMS] | CLUZ
7/22/2024 5:19:25 PM | Mindanao Grid-07/22/2024 17:26: WMPC DG10 shutdown at 1716H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/22/2024 5:08:43 PM | [NSO Update] Mindanao Grid-07/22/2024 17:15: Weather Update: At 3:00 PM today, the center of Typhoon CARINA was estimated based on all available data at 420 km East of Tuguegarao City, Cagayan (17.8N, 125.7E) with maximum sustained winds of 120 km/h near the center and gustiness of up to 150 km/h. It is moving North Northeastward slowly. [WEBSMS] | CMIN
7/22/2024 5:08:30 PM | [NSO Update] Visayas Grid-07/22/2024 17:08: Weather Update: At 3:00 PM today, the center of Typhoon CARINA was estimated based on all available data at 420 km East of Tuguegarao City, Cagayan (17.8N, 125.7E) with maximum sustained winds of 120 km/h near the center and gustiness of up to 150 km/h. It is moving North Northeastward slowly. [WEBSMS] | CVIS
7/22/2024 5:08:10 PM | Mindanao Grid-07/22/2024 17:14: Libertad Power online at 1558H (Planned Outage) [WEBSMS] | CMIN
7/22/2024 5:08:09 PM | [NSO Update] Luzon Grid-07/22/2024 17:08: Weather Update: At 3:00 PM today, the center of Typhoon CARINA was estimated based on all available data at 420 km East of Tuguegarao City, Cagayan (17.8N, 125.7E) with maximum sustained winds of 120 km/h near the center and gustiness of up to 150 km/h. It is moving North Northeastward slowly. [WEBSMS] | CLUZ
7/22/2024 4:21:32 PM | Luzon Grid-07/22/2024 16:21: Hermosa-Duhat 230kV Line tripped/reclosed both side at 1617H (Unplanned Outage) [WEBSMS] | CLUZ
7/22/2024 1:33:47 PM | Luzon Grid-07/22/2024 13:33: San Gabriel shutdown at 1327H (Reserved Shutdown) [WEBSMS] | CLUZ
7/22/2024 1:03:45 PM | [NSO Update] Mindanao Grid-07/22/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3097MW, PK=2308MW, RR=73MW, NetOpMargin: PM=717, EVE=784 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/22/2024 12:59:14 PM | [NSO Update] Visayas Grid-07/22/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2539MW, PK=2268MW, RR=89MW, NetOpMargin: PM=182, EVE=351 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @236MW, CEDC 3 @75MW, PDPP3-E @8MW, PB104-4 @6.5MW, PB104-2 @5MW, PB104-3 @5MW [WEBSMS] | CVIS
7/22/2024 12:54:42 PM | [NSO Update] Luzon Grid-07/22/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14089MW, PK=10861MW, RR=473MW, NetOpMargin: PM=2755, EVE=2132 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: SLTEC 1 @118MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc 1 @310MW, SCPC 1 @125MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
7/22/2024 12:18:36 PM | [NSO Update] Visayas Grid-07/22/2024 12:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1213H with power going to Visayas [WEBSMS] | CVIS
7/22/2024 12:17:44 PM | [NSO Update] Luzon Grid-07/22/2024 12:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1213H with power going to Visayas [WEBSMS] | CLUZ
7/22/2024 12:16:07 PM | [NSO Update] Visayas Grid-07/22/2024 12:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1203H from forward power direction [WEBSMS] | CVIS
7/22/2024 12:15:03 PM | [NSO Update] Luzon Grid-07/22/2024 12:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1203H from forward power direction [WEBSMS] | CLUZ
7/22/2024 11:26:42 AM | Luzon Grid-07/22/2024 11:26: Tuguegarao PCB 8-02CB04TUG and 8-02CB24TUG sub protection commissioned at 1123H. [WEBSMS] | CLUZ
7/22/2024 10:06:24 AM | Luzon Grid-07/22/2024 10:06: Malaya 2 online at 1003H (Unplanned Outage) [WEBSMS] | CLUZ
7/22/2024 9:49:26 AM | Visayas Grid-07/22/2024 09:49: KSPC U2 cut-in at 0947H. (Unplanned Outage) [WEBSMS] | CVIS
7/22/2024 6:09:14 AM | [NSO Update] Mindanao Grid-07/22/2024 06:15: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3169MW, PK=2217MW, RR=73MW, NetOpMargin: AM=879, PM=837, EVE=911 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/22/2024 6:03:21 AM | [NSO Update] Visayas Grid-07/22/2024 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2595MW, PK=2233MW, RR=86MW, NetOpMargin: AM=276, PM=240, EVE=247 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @267MW, CEDC 3 @75MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-4 @6.5MW, PB104-2 @5MW, PB104-3 @5MW [WEBSMS] | CVIS
7/22/2024 5:56:00 AM | [NSO Update] Luzon Grid-07/22/2024 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14318MW, PK=11201MW, RR=451MW, NetOpMargin: AM=2666, PM=1914, EVE=2214 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: SLTEC 1 @118MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc 1 @310MW, SCPC 1 @125MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
7/22/2024 4:19:26 AM | [NSO Update] Luzon Grid-07/22/2024 04:19: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm "CARINA" {GAEMI} was estimated based on all available data at 390 km East Northeast of Casiguran, Aurora or 425 km East of Tuguegarao City, Cagayan (17.1�N, 125.7�E) with maximum sustained winds of 100 km/h near the center and gustiness of up to 125 km/h. It is moving North Northwestward slowly. [WEBSMS] | CLUZ
7/22/2024 4:19:12 AM | [NSO Update] Visayas Grid-07/22/2024 04:19: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm "CARINA" {GAEMI} was estimated based on all available data at 390 km East Northeast of Casiguran, Aurora or 425 km East of Tuguegarao City, Cagayan (17.1�N, 125.7�E) with maximum sustained winds of 100 km/h near the center and gustiness of up to 125 km/h. It is moving North Northwestward slowly. [WEBSMS] | CVIS
7/22/2024 4:18:57 AM | [NSO Update] Mindanao Grid-07/22/2024 04:25: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm "CARINA" {GAEMI} was estimated based on all available data at 390 km East Northeast of Casiguran, Aurora or 425 km East of Tuguegarao City, Cagayan (17.1�N, 125.7�E) with maximum sustained winds of 100 km/h near the center and gustiness of up to 125 km/h. It is moving North Northwestward slowly. [WEBSMS] | CMIN
7/22/2024 12:53:29 AM | Luzon Grid-07/22/2024 00:53: Santiago-Tuguegarao 230kV Line restored at 0047H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 11:52:31 PM | Luzon Grid-07/21/2024 23:52: Binan-Balibago 115kV Line restored at 2352H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 11:50:22 PM | Luzon Grid-07/21/2024 23:50: Binan 300MVA T02 restored at 2348H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 8:58:41 PM | Mindanao Grid-07/21/2024 21:05: Agus4 U3 online at 2032H. (Unplanned Outage) [WEBSMS] | CMIN
7/21/2024 7:18:04 PM | Mindanao Grid-07/21/2024 19:24: Agus 4 Unit 1 online at 1911H (Unplanned Outage) [WEBSMS] | CMIN
7/21/2024 6:08:12 PM | Mindanao Grid-07/21/2024 18:14: Agus4 U3 HEPP tripped with 35MW Load at 1750H. Lowest frequency recorded is 59.46Hz. No ALD. (Unplanned Outage) [WEBSMS] | CMIN
7/21/2024 6:06:22 PM | Mindanao Grid-07/21/2024 18:12: Agus4 U1 HEPP tripped with 35MW load at 0550H. Lowest Frequency was recorded is 59.46Hz. No ALD. (Unplanned Outage) [WEBSMS] | CMIN
7/21/2024 5:59:14 PM | Mindanao Grid-07/21/2024 18:05: Agus4 U3 HEPP tripped with 35MW load at 1750H. (Unplanned Outage) [WEBSMS] | CMIN
7/21/2024 5:58:18 PM | Mindanao Grid-07/21/2024 18:04: Agus4 U1 HEPP tripped with 35MW at 1750H. (Unplanned Outage) [WEBSMS] | CMIN
7/21/2024 5:42:09 PM | [NSO Update] Luzon Grid-07/21/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13192MW, PK=9855MW, RR=311MW, NetOpMargin: EVE=3026 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: SLTEC 1 @118MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc 1 @310MW, SCPC 1 @125MW, SCPC 2 @75MW, SCPC 4 @90MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
7/21/2024 5:38:57 PM | [NSO Update] Visayas Grid-07/21/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2390MW, PK=1996MW, RR=87MW, NetOpMargin: EVE=307 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @240MW, CEDC 3 @75MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-4 @6.5MW, PB104-2 @5MW, PB104-3 @5MW, TGPP @115.5MW [WEBSMS] | CVIS
7/21/2024 5:37:34 PM | [NSO Update] Mindanao Grid-07/21/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3080MW, PK=2074MW, RR=73MW, NetOpMargin: EVE=933 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/21/2024 5:16:55 PM | Luzon Grid-07/21/2024 17:17: Correction: Duhat-Hermosa 230kV Line restored at 1716H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 5:16:11 PM | Luzon Grid-07/21/2024 17:16: San Jose-Camarin 115kV Line restored at 1703H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 5:04:30 PM | Luzon Grid-07/21/2024 17:04: Duhat-Hermosa 230kV Line restored at 1703H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 4:54:47 PM | Mindanao Grid-07/21/2024 17:01: Aurora SS Power Transformer T1 and T3 re-energized in parallel at 1514H. (Unplanned Outage) [WEBSMS] | CMIN
7/21/2024 4:18:04 PM | [NSO Update] Luzon Grid-07/21/2024 16:18: Weather Update: At 3:00 PM today, the center of Tropical Storm "CARINA" {GAEMI} was estimated based on all available data at 375 km East of Casiguran, Aurora (16.8�N, 125.6�E) with maximum sustained winds of 85 km/h near the center and gustiness of up to 115 km/h. It is almost stationary. [WEBSMS] | CLUZ
7/21/2024 4:17:52 PM | [NSO Update] Mindanao Grid-07/21/2024 16:24: Weather Update: At 3:00 PM today, the center of Tropical Storm "CARINA" {GAEMI} was estimated based on all available data at 375 km East of Casiguran, Aurora (16.8�N, 125.6�E) with maximum sustained winds of 85 km/h near the center and gustiness of up to 115 km/h. It is almost stationary. [WEBSMS] | CMIN
7/21/2024 4:17:37 PM | [NSO Update] Visayas Grid-07/21/2024 16:17: Weather Update: At 3:00 PM today, the center of Tropical Storm "CARINA" {GAEMI} was estimated based on all available data at 375 km East of Casiguran, Aurora (16.8�N, 125.6�E) with maximum sustained winds of 85 km/h near the center and gustiness of up to 115 km/h. It is almost stationary. [WEBSMS] | CVIS
7/21/2024 2:30:53 PM | Mindanao Grid-07/21/2024 14:37: Aurora SS 138/69kV 100MVA each T1 and T3 tripped at 1417H. (Unplanned Outage) [WEBSMS] | CMIN
7/21/2024 1:06:16 PM | Luzon Grid-07/21/2024 13:06: Laoag 115kV Bus 2 restored at 1303H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 12:51:31 PM | [NSO Update] Mindanao Grid-07/21/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3115MW, PK=1983MW, RR=73MW, NetOpMargin: PM=1059, EVE=883 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/21/2024 12:50:30 PM | [NSO Update] Visayas Grid-07/21/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2544MW, PK=1821MW, RR=81MW, NetOpMargin: PM=641, EVE=227 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @235MW, CEDC 3 @75MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-4 @6.5MW, PB104-2 @5MW, PB104-3 @5MW [WEBSMS] | CVIS
7/21/2024 12:48:26 PM | [NSO Update] Luzon Grid-07/21/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14063MW, PK=9991MW, RR=334MW, NetOpMargin: PM=3737, EVE=2534 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @118MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc 1 @310MW, SCPC 1 @125MW [WEBSMS] | CLUZ
7/21/2024 12:06:18 PM | Luzon Grid-07/21/2024 12:06: SCPC 2 online at 1204H (Unplanned Outage) [WEBSMS] | CLUZ
7/21/2024 11:32:05 AM | Mindanao Grid-07/21/2024 11:38: Agus4 U2 HEPP with 30MW load tripped at 1126H. (Unplanned Outage) [WEBSMS] | CMIN
7/21/2024 9:09:30 AM | Mindanao Grid-07/21/2024 09:16: AGUS 4 Unit 3 online at 0907H (Planned Outage) [WEBSMS] | CMIN
7/21/2024 8:49:54 AM | Luzon Grid-07/21/2024 08:50: Binan 300MVA T02 de-energized at 0849H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 8:45:52 AM | Luzon Grid-07/21/2024 08:45: Binan-Balibago 115kV Line de-energized at 0845H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 7:38:01 AM | Luzon Grid-07/21/2024 07:38: San Jose-Camarin 115kV Line de-energized at 0735H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 7:21:53 AM | Luzon Grid-07/21/2024 07:21: Tuguegarao 230kV Bus 1 restored at 0721H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 7:06:40 AM | Luzon Grid-07/21/2024 07:06: Laoag 115kV Bus 2 de-energized at 0705H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 5:37:12 AM | [NSO Update] Mindanao Grid-07/21/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3126MW, PK=1793MW, RR=73MW, NetOpMargin: AM=1260, PM=1096, EVE=868 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/21/2024 5:36:09 AM | [NSO Update] Visayas Grid-07/21/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2623MW, PK=1714MW, RR=80MW, NetOpMargin: AM=829, PM=769, EVE=317 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @243MW, CEDC 3 @75MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-4 @6.5MW, PB104-2 @5MW, PB104-3 @5MW [WEBSMS] | CVIS
7/21/2024 5:33:41 AM | [NSO Update] Luzon Grid-07/21/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14041MW, PK=9654MW, RR=326MW, NetOpMargin: AM=4061, PM=3341, EVE=2052 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @118MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc 1 @310MW, Masinloc 3 @315MW, Calaca 1 @140MW [WEBSMS] | CLUZ
7/21/2024 5:21:27 AM | Luzon Grid-07/21/2024 05:21: Duhat-Hermosa 230kV Line de-energized at 0518H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 5:07:38 AM | Luzon Grid-07/21/2024 05:07: Tuguegarao SS 230kV Bus 1 de-energized at 0507H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 5:05:05 AM | Luzon Grid-07/21/2024 05:05: Santiago-Tuguegarao 230kV Line de-energized at 0505H (Planned Outage) [WEBSMS] | CLUZ
7/21/2024 4:09:32 AM | [NSO Update] Mindanao Grid-07/21/2024 04:16: Weather Update: At 3:00 AM today, the center of Tropical Storm "CARINA" (GAEMI) was estimated based on all available data at 490 km East of Casiguran, Aurora (16.6N, 126.7E) with maximum sustained winds of 75 km/h near the center and gustiness of up to 90 km/h. It is moving West Northwestward at 10 km/h. [WEBSMS] | CMIN
7/21/2024 4:09:07 AM | [NSO Update] Visayas Grid-07/21/2024 04:09: Weather Update: At 3:00 AM today, the center of Tropical Storm "CARINA" (GAEMI) was estimated based on all available data at 490 km East of Casiguran, Aurora (16.6N, 126.7E) with maximum sustained winds of 75 km/h near the center and gustiness of up to 90 km/h. It is moving West Northwestward at 10 km/h. [WEBSMS] | CVIS
7/21/2024 4:08:41 AM | [NSO Update] Luzon Grid-07/21/2024 04:08: Weather Update: At 3:00 AM today, the center of Tropical Storm "CARINA" (GAEMI) was estimated based on all available data at 490 km East of Casiguran, Aurora (16.6N, 126.7E) with maximum sustained winds of 75 km/h near the center and gustiness of up to 90 km/h. It is moving West Northwestward at 10 km/h. [WEBSMS] | CLUZ
7/21/2024 3:58:52 AM | Visayas Grid-07/21/2024 03:59: Cebu-Mandaue 138KV Line 1 energized at 0355H (Planned Outage) [WEBSMS] | CVIS
7/21/2024 3:55:57 AM | Luzon Grid-07/21/2024 03:56: SCPC 4 online at 0353H (Unplanned Outage) [WEBSMS] | CLUZ
7/21/2024 3:21:52 AM | Luzon Grid-07/21/2024 03:22: San Gabriel online at 0317H (Unplanned Outage) [WEBSMS] | CLUZ
7/21/2024 2:58:35 AM | Luzon Grid-07/21/2024 02:58: For info: Sta Rita-San Lorenzo 230kV Bus 1 and Bus 2 Tie Breakers were unlooped at 0242H and 0243H, respectively. Batangas 300MVA T04 and T05 are in parallel configuration at 0257H. This is in preparation for the synchronization of San Gabriel. [WEBSMS] | CLUZ
7/20/2024 10:15:22 PM | Visayas Grid-07/20/2024 22:15: Cebu-Mandaue 138KV Line 1 de-energized at 2212H (Planned Outage) [WEBSMS] | CVIS
7/20/2024 7:17:52 PM | Luzon Grid-07/20/2024 19:17: Binan-San Pedro 115kV Line restored at 1917H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 7:15:57 PM | Luzon Grid-07/20/2024 19:16: Binan-Balibago 115kV Line restored at 1915H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 7:04:02 PM | Luzon Grid-07/20/2024 19:04: SCPC Unit 1 online at 1903H (Unplanned Outage) [WEBSMS] | CLUZ
7/20/2024 6:47:55 PM | Luzon Grid-07/20/2024 18:48: SCPC Unit 3 online at 1846H (Unplanned Outage) [WEBSMS] | CLUZ
7/20/2024 5:54:26 PM | Luzon Grid-07/20/2024 17:54: Taytay-Malaya 230kV Line 1 restored at 1753H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 5:32:29 PM | [NSO Update] Luzon Grid-07/20/2024 17:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11981MW, PK=10771MW, RR=361MW, NetOpMargin: EVE=849 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @300MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
7/20/2024 5:29:27 PM | [NSO Update] Mindanao Grid-07/20/2024 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3147MW, PK=2198MW, RR=73MW, NetOpMargin: EVE=876 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/20/2024 5:28:22 PM | [NSO Update] Visayas Grid-07/20/2024 17:28: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2388MW, PK=2008MW, RR=91MW, NetOpMargin: EVE=289 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @235MW, CEDC 3 @75MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-4 @6.5MW, PB104-2 @5MW, PB104-3 @5MW, TGPP @115.5MW [WEBSMS] | CVIS
7/20/2024 5:20:18 PM | Luzon Grid-07/20/2024 17:20: Hermosa-Balsik 230kV Line 2 restored at 1718H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 4:47:25 PM | Visayas Grid-07/20/2024 16:47: Colon SS 69 kV COL-NAY feeder energized at 1647H (Planned Outage) [WEBSMS] | CVIS
7/20/2024 4:41:31 PM | Mindanao Grid-07/20/2024 16:48: Manolo-Maramag 138kV L1 energized/restored at 1636H. (Planned Outage) [WEBSMS] | CMIN
7/20/2024 4:40:21 PM | Visayas Grid-07/20/2024 16:40: Colon SS 100 MVA 138/69/13.8 kV TR2 energized at 1640H (Planned Outage) [WEBSMS] | CVIS
7/20/2024 4:23:29 PM | [NSO Update] Luzon Grid-07/20/2024 16:23: Weather Update: At 3:00 PM today, the center of Tropical Storm CARINA (GAEMI) was estimated based on all available data at 470 km East Northeast of Virac, Catanduanes or 630 km East of Casiguran, Aurora (15.7N, 128.0E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CLUZ
7/20/2024 4:23:07 PM | [NSO Update] Visayas Grid-07/20/2024 16:23: Weather Update: At 3:00 PM today, the center of Tropical Storm CARINA (GAEMI) was estimated based on all available data at 470 km East Northeast of Virac, Catanduanes or 630 km East of Casiguran, Aurora (15.7N, 128.0E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CVIS
7/20/2024 4:22:39 PM | [NSO Update] Mindanao Grid-07/20/2024 16:29: Weather Update: At 3:00 PM today, the center of Tropical Storm CARINA (GAEMI) was estimated based on all available data at 470 km East Northeast of Virac, Catanduanes or 630 km East of Casiguran, Aurora (15.7N, 128.0E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CMIN
7/20/2024 4:20:17 PM | Visayas Grid-07/20/2024 16:20: Colon SS 138 kV Bus 2 energized at 1620H (Planned Outage) [WEBSMS] | CVIS
7/20/2024 4:17:30 PM | Mindanao Grid-07/20/2024 16:24: Baloi-Agus 6 138kV L2 energized/restored at 1616H. (Planned Outage) [WEBSMS] | CMIN
7/20/2024 4:12:41 PM | Luzon Grid-07/20/2024 16:12: Laoag SS 115kV Bus 1 restored at 1611H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 4:11:18 PM | Luzon Grid-07/20/2024 16:11: Dasmarinas-MEC-Rosario 115kV Line restored at 1609H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 3:46:18 PM | Luzon Grid-07/20/2024 15:46: Bay SS 230kV Bus 2 restored at 1545H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 3:32:52 PM | Luzon Grid-07/20/2024 15:32: Calaca Unit 1 online at 1530H (Unplanned Outage) [WEBSMS] | CLUZ
7/20/2024 3:07:02 PM | Luzon Grid-07/20/2024 15:07: MPGC 1 online at 1505H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 2:56:50 PM | Visayas Grid-07/20/2024 14:56: Corella SS 300 MVA 230/138/13.8 kV TR1 energized at 1455H without load, under test and commissioning. [WEBSMS] | CVIS
7/20/2024 2:12:57 PM | Mindanao Grid-07/20/2024 14:19: Baloi-Agus 6 138kV L2 de-energized at 1408H. (Planned Outage) [WEBSMS] | CMIN
7/20/2024 12:40:21 PM | [NSO Update] Mindanao Grid-07/20/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3174MW, PK=2179MW, RR=73MW, NetOpMargin: PM=922, EVE=913 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/20/2024 12:38:58 PM | [NSO Update] Visayas Grid-07/20/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2502MW, PK=2049MW, RR=90MW, NetOpMargin: PM=364, EVE=242 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @235MW, CEDC 3 @75MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-4 @6.5MW, PB104-2 @5MW, PB104-3 @5MW, TGPP @115.5MW [WEBSMS] | CVIS
7/20/2024 12:37:44 PM | [NSO Update] Luzon Grid-07/20/2024 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13009MW, PK=11000MW, RR=441MW, NetOpMargin: PM=1568, EVE=734 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @120MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @280MW [WEBSMS] | CLUZ
7/20/2024 12:11:05 PM | [NSO Update] Mindanao Grid-07/20/2024 12:17: The Weather Disturbance Alert Notice (WDAN) for Tropical Depression BUTCHOY has been lifted today, July 20, 2024, at 1100H, as it is now outside the Philippine Area of Responsibility (PAR). The center of Tropical Depression BUTCHOY was estimated based on all available data at 565 km West of Iba, Zambales (15.1 N, 114.7 E). Please note that the WDAN for Tropical Depression CARINA remains active. [WEBSMS] | CMIN
7/20/2024 12:10:21 PM | [NSO Update] Visayas Grid-07/20/2024 12:10: The Weather Disturbance Alert Notice (WDAN) for Tropical Depression BUTCHOY has been lifted today, July 20, 2024, at 1100H, as it is now outside the Philippine Area of Responsibility (PAR). The center of Tropical Depression BUTCHOY was estimated based on all available data at 565 km West of Iba, Zambales (15.1 N, 114.7 E). Please note that the WDAN for Tropical Depression CARINA remains active. [WEBSMS] | CVIS
7/20/2024 12:09:57 PM | [NSO Update] Luzon Grid-07/20/2024 12:09: The Weather Disturbance Alert Notice (WDAN) for Tropical Depression BUTCHOY has been lifted today, July 20, 2024, at 1100H, as it is now outside the Philippine Area of Responsibility (PAR). The center of Tropical Depression BUTCHOY was estimated based on all available data at 565 km West of Iba, Zambales (15.1 N, 114.7 E). Please note that the WDAN for Tropical Depression CARINA remains active. [WEBSMS] | CLUZ
7/20/2024 11:18:41 AM | Mindanao Grid-07/20/2024 11:25: Butuan-Placer 138kV L2 energized/restored at 1115H. (Planned Outage) [WEBSMS] | CMIN
7/20/2024 10:52:05 AM | Visayas Grid-07/20/2024 10:52: Mandaue GIS 69 kV Feeder 1 and 4 energized at 1051H (Planned Outage) [WEBSMS] | CVIS
7/20/2024 10:43:06 AM | Luzon Grid-07/20/2024 10:43: Nagsaag SS PCB 9Z-02CB08NGS restored at 1042H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 9:56:41 AM | Mindanao Grid-07/20/2024 10:03: San Francisco SS 100MVA 138kV Power Transformer No. 2 energized/restored at 0955H. (Planned Outage) [WEBSMS] | CMIN
7/20/2024 9:18:25 AM | Luzon Grid-07/20/2024 09:18: Binga-La Trinidad 230kV Line 1 auto-tripped/auto-reclosed at 0914H (Unplanned Outage) [WEBSMS] | CLUZ
7/20/2024 8:48:49 AM | Luzon Grid-07/20/2024 08:48: Bay SS 230kV Bus 2 de-energized at 0848H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 8:13:24 AM | Visayas Grid-07/20/2024 08:13: Colon SS 138 kV Bus 2 de-energized at 0812H (Planned Outage) [WEBSMS] | CVIS
7/20/2024 8:08:42 AM | Mindanao Grid-07/20/2024 08:15: Butuan-Placer 138kV L2 de-energized at 0808H. (Planned Outage) [WEBSMS] | CMIN
7/20/2024 7:49:46 AM | Luzon Grid-07/20/2024 07:49: Binan-San Pedro 115kV Line de-energized at 0746H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 7:46:06 AM | Luzon Grid-07/20/2024 07:46: Binan-Balibago 115kV Line de-energized at 0744H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 7:40:51 AM | Visayas Grid-07/20/2024 07:40: Colon SS 100 MVA 138/69/13.8 kV TR2 de-energized at 0737H (Planned Outage) [WEBSMS] | CVIS
7/20/2024 7:29:57 AM | Visayas Grid-07/20/2024 07:30: Colon SS 69 kV COL-NAY feeder de-energized at 0725H (Planned Outage) [WEBSMS] | CVIS
7/20/2024 7:09:56 AM | Luzon Grid-07/20/2024 07:09: Nagsaag SS PCB 9Z-02CB08NGS de-energized at 0708H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 7:07:04 AM | Luzon Grid-07/20/2024 07:07: Laoag SS 115kV Bus 1 de-energized at 0703H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 7:05:36 AM | Visayas Grid-07/20/2024 07:05: Mandaue GIS 69 kV Feeder 1 and 4 de-energized at 0702H (Planned Outage) [WEBSMS] | CVIS
7/20/2024 6:55:37 AM | Mindanao Grid-07/20/2024 07:02: San Francisco SS 100MVA 138kV Power Transformer No. 2 de-energized at 0652H. (Planned Outage) [WEBSMS] | CMIN
7/20/2024 6:42:42 AM | Luzon Grid-07/20/2024 06:42: Dasmarinas-MEC-Rosario 115kV Line de-energized at 0642H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 6:40:38 AM | Mindanao Grid-07/20/2024 06:47: Manolo-Maramag 138kV L1 de-energized at 0640H. (Planned Outage) [WEBSMS] | CMIN
7/20/2024 6:37:25 AM | Luzon Grid-07/20/2024 06:37: Hermosa-Balsik 230kV Line 2 de-energized at 0637H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 6:33:45 AM | Mindanao Grid-07/20/2024 06:40: WMPC DG10 shutdown at 0627H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/20/2024 6:30:42 AM | Luzon Grid-07/20/2024 06:30: Taytay-Malaya 230kV Line 1 de-energized at 0628H (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 6:18:48 AM | [NSO Update] Mindanao Grid-07/20/2024 06:25: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3161MW, PK=2020MW, RR=73MW, NetOpMargin: AM=1068, PM=934, EVE=927 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: Derated Plant: Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/20/2024 6:16:12 AM | [NSO Update] Visayas Grid-07/20/2024 06:16: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2637MW, PK=1931MW, RR=84MW, NetOpMargin: AM=622, PM=513, EVE=373 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @260MW, CEDC 3 @75MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-4 @6.5MW, PB104-2 @5MW, PB104-3 @5MW [WEBSMS] | CVIS
7/20/2024 6:12:51 AM | [NSO Update] Luzon Grid-07/20/2024 06:12: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13231MW, PK=10576MW, RR=430MW, NetOpMargin: AM=2226, PM=1712, EVE=848 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @121MW, SLTEC 2 @121MW, Limay 8 @60MW, Masinloc 1 @300MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
7/20/2024 6:08:12 AM | Mindanao Grid-07/20/2024 06:14: Naga Mindanao SS SVC online at 0605H. (Unplanned Outage) [WEBSMS] | CMIN
7/20/2024 5:53:46 AM | [NSO Update] Luzon Grid-07/20/2024 05:53: Weather Disturbance Alert Notice (WDAN) is issued at 3:00 AM today, the center of Tropical Depression "CARINA" was estimated based on all available data at 645 km East of Virac, Catanduanes (14.6�N, 130.1�E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving Northwestward at 30 km/h. [WEBSMS] | CLUZ
7/20/2024 5:53:13 AM | [NSO Update] Mindanao Grid-07/20/2024 05:59: Weather Disturbance Alert Notice (WDAN) is issued at 3:00 AM today, the center of Tropical Depression "CARINA" was estimated based on all available data at 645 km East of Virac, Catanduanes (14.6�N, 130.1�E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving Northwestward at 30 km/h. [WEBSMS] | CMIN
7/20/2024 5:52:46 AM | [NSO Update] Visayas Grid-07/20/2024 05:52: Weather Disturbance Alert Notice (WDAN) is issued at 3:00 AM today, the center of Tropical Depression "CARINA" was estimated based on all available data at 645 km East of Virac, Catanduanes (14.6�N, 130.1�E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving Northwestward at 30 km/h. [WEBSMS] | CVIS
7/20/2024 5:51:33 AM | [NSO Update] Mindanao Grid-07/20/2024 05:58: Weather Disturbance Alert Notice (WDAN) is issued at 3:00 AM today, the center of Tropical Depression "BUTCHOY" was estimated based on all available data at 615 km West of Tanauan City, Batangas or 525 km West of Subic Bay (14.5�N, 115.4�E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving West Northwestward at 20 km/h. [WEBSMS] | CMIN
7/20/2024 5:51:12 AM | [NSO Update] Visayas Grid-07/20/2024 05:51: Weather Disturbance Alert Notice (WDAN) is issued at 3:00 AM today, the center of Tropical Depression "BUTCHOY" was estimated based on all available data at 615 km West of Tanauan City, Batangas or 525 km West of Subic Bay (14.5�N, 115.4�E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving West Northwestward at 20 km/h. [WEBSMS] | CVIS
7/20/2024 5:50:40 AM | [NSO Update] Luzon Grid-07/20/2024 05:50: Weather Disturbance Alert Notice (WDAN) is issued at 3:00 AM today, the center of Tropical Depression "BUTCHOY" was estimated based on all available data at 615 km West of Tanauan City, Batangas or 525 km West of Subic Bay (14.5�N, 115.4�E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving West Northwestward at 20 km/h. [WEBSMS] | CLUZ
7/20/2024 5:19:18 AM | [NSO Update] Mindanao Grid-07/20/2024 05:25: At 0300H today, Tropical Depression "BUTCHOY" estimated at 615 km West of Tanauan, Batangas (14.5�N, 115.4�E) - max sustained winds 55 km/h, gustiness up to 70 km/h, and moving Northwestward at 20 km/h. Meanwhile, Tropical Depression "CARINA" estimated at 645 km East of Virac, Catanduanes (14.6�N, 130.1�E) - max sustained winds 55 km/h, gustiness up to 70 km/h, and moving Northwestward at 30 km/h [WEBSMS] | CMIN
7/20/2024 5:19:07 AM | [NSO Update] Visayas Grid-07/20/2024 05:19: At 0300H today, Tropical Depression "BUTCHOY" estimated at 615 km West of Tanauan, Batangas (14.5�N, 115.4�E) - max sustained winds 55 km/h, gustiness up to 70 km/h, and moving Northwestward at 20 km/h. Meanwhile, Tropical Depression "CARINA" estimated at 645 km East of Virac, Catanduanes (14.6�N, 130.1�E) - max sustained winds 55 km/h, gustiness up to 70 km/h, and moving Northwestward at 30 km/h [WEBSMS] | CVIS
7/20/2024 5:19:02 AM | [NSO Update] Luzon Grid-07/20/2024 05:19: At 0300H today, Tropical Depression "BUTCHOY" estimated at 615 km West of Tanauan, Batangas (14.5�N, 115.4�E) - max sustained winds 55 km/h, gustiness up to 70 km/h, and moving Northwestward at 20 km/h. Meanwhile, Tropical Depression "CARINA" estimated at 645 km East of Virac, Catanduanes (14.6�N, 130.1�E) - max sustained winds 55 km/h, gustiness up to 70 km/h, and moving Northwestward at 30 km/h [WEBSMS] | CLUZ
7/20/2024 4:09:28 AM | Luzon Grid-07/20/2024 04:09: Batangas 300MVA T04 and T05 were unparalleled at 0403H. Sta Rita-San Lorenzo 230kV Bus 1 and Bus 2 Tie Breakers were looped at 0407H and 0408H respectively. [WEBSMS] | CLUZ
7/20/2024 2:00:34 AM | Mindanao Grid-07/20/2024 02:07: WMPC DG10 online at 0158H. Replacement Unit. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/20/2024 1:47:09 AM | Mindanao Grid-07/20/2024 01:53: WMPC DG4 tripped at 0142H. (Planned Outage) [WEBSMS] | CMIN
7/20/2024 12:27:53 AM | Luzon Grid-07/20/2024 00:27: Malamig 300MVA T04(CO) was de-energized at 0024H. (Planned Outage) [WEBSMS] | CLUZ
7/20/2024 12:13:37 AM | Mindanao Grid-07/20/2024 00:20: Naga Mindanao SS SVC shutdown at 0011H. (Planned Outage) [WEBSMS] | CMIN
7/20/2024 12:03:51 AM | Mindanao Grid-07/20/2024 00:10: WMPC DG4 Online at 0000H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/19/2024 7:49:39 PM | Mindanao Grid-07/19/2024 19:56: WMPC DG04 shutdown at 1946H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/19/2024 6:01:38 PM | [NSO Update] Luzon Grid-07/19/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12408MW, PK=11094MW, RR=416MW, NetOpMargin: EVE=898 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 2 @120MW, Limay 8 @60MW, Masinloc 1 @300MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
7/19/2024 5:44:41 PM | [NSO Update] Mindanao Grid-07/19/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3084MW, PK=2120MW, RR=73MW, NetOpMargin: EVE=891 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/19/2024 5:39:29 PM | [NSO Update] Visayas Grid-07/19/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2409MW, PK=2025MW, RR=86MW, NetOpMargin: EVE=298 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @253MW, CEDC 3 @75MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-4 @6.5MW, PB104-2 @5MW, PB104-3 @5MW [WEBSMS] | CVIS
7/19/2024 4:14:32 PM | Visayas Grid-07/19/2024 16:14: Sangi-Pinamungahan (CPJ) 34.5 KV feeder tripped/restored at 1557H/1610. (Unplanned Outage) [WEBSMS] | CVIS
7/19/2024 4:11:34 PM | [NSO Update] Visayas Grid-07/19/2024 16:11: Testing [WEBSMS] | CVIS
7/19/2024 3:30:01 PM | Luzon Grid-07/19/2024 15:30: Laoag-Pagudpud Wind Farm 115kV Line (CO) was restored at 1528H. (Planned Outage) [WEBSMS] | CLUZ
7/19/2024 12:37:50 PM | [NSO Update] Mindanao Grid-07/19/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3077MW, PK=2278MW, RR=73MW, NetOpMargin: PM=726, EVE=787 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/19/2024 12:34:22 PM | [NSO Update] Visayas Grid-07/19/2024 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2585MW, PK=2157MW, RR=91MW, NetOpMargin: PM=337, EVE=269 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @253MW, CEDC 3 @75MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-4 @6.5MW, PB104-2 @5MW, PB104-3 @5MW [WEBSMS] | CVIS
7/19/2024 12:32:23 PM | [NSO Update] Luzon Grid-07/19/2024 12:32: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13168MW, PK=11653MW, RR=434MW, NetOpMargin: PM=1080, EVE=891 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLPGC 1 @120MW, Limay 8 @60MW, Masinloc 1 @300MW, Masinloc 3 @330MW [WEBSMS] | CLUZ
7/19/2024 12:22:38 PM | Mindanao Grid-07/19/2024 12:29: FDC U3 emergency shutdown at 1218H due to boiler tube leak. (Unplanned Outage) [WEBSMS] | CMIN
7/19/2024 10:33:55 AM | Mindanao Grid-07/19/2024 10:40: WMPC DG4 online at 1030H. RPS -System Voltage Requirement. [WEBSMS] | CMIN
7/19/2024 9:25:40 AM | Mindanao Grid-07/19/2024 09:32: Agus4 U1 online at 0917H. (Planned Outage) [WEBSMS] | CMIN
7/19/2024 9:09:38 AM | Mindanao Grid-07/19/2024 09:16: Pulangi4 U2 online at 0903H (Planned Outage) [WEBSMS] | CMIN
7/19/2024 8:12:25 AM | Luzon Grid-07/19/2024 08:12: Laoag-Pagudpud Wind Farm 115kV Line (CO) de-energized at 0811H (Planned Outage) [WEBSMS] | CLUZ
7/19/2024 7:29:20 AM | Mindanao Grid-07/19/2024 07:35: Steag U1 online at 0725H. (Planned Outage) [WEBSMS] | CMIN
7/19/2024 5:53:25 AM | [NSO Update] Luzon Grid-07/19/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13260MW, PK=11293MW, RR=434MW, NetOpMargin: AM=1533, PM=933, EVE=857 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Calaca 2 @270MW, SLPGC 1 @80MW, SLTEC 2 @120MW, Limay 8 @60MW, Masinloc 1 @300MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
7/19/2024 5:49:37 AM | [NSO Update] Visayas Grid-07/19/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2546MW, PK=2091MW, RR=84MW, NetOpMargin: AM=370, PM=387, EVE=307 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @260MW, CEDC 3 @75MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-4 @6.5MW, PB104-2 @5MW, PB104-3 @5MW [WEBSMS] | CVIS
7/19/2024 5:47:13 AM | [NSO Update] Mindanao Grid-07/19/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3041MW, PK=2222MW, RR=73MW, NetOpMargin: AM=747, PM=738, EVE=810 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/19/2024 4:09:33 AM | [NSO Update] Mindanao Grid-07/19/2024 04:16: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 135 km West Southwest of Calapan City, Oriental Mindoro (13.1�N, 120.0�E). Meanwhile, another LPA was estimated based on all available data at 880 km East of Eastern Visayas (11.1�N, 133.8�E). [WEBSMS] | CMIN
7/19/2024 4:09:32 AM | [NSO Update] Luzon Grid-07/19/2024 04:09: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 135 km West Southwest of Calapan City, Oriental Mindoro (13.1�N, 120.0�E). Meanwhile, another LPA was estimated based on all available data at 880 km East of Eastern Visayas (11.1�N, 133.8�E). [WEBSMS] | CLUZ
7/19/2024 4:09:28 AM | [NSO Update] Visayas Grid-07/19/2024 04:09: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 135 km West Southwest of Calapan City, Oriental Mindoro (13.1�N, 120.0�E). Meanwhile, another LPA was estimated based on all available data at 880 km East of Eastern Visayas (11.1�N, 133.8�E). [WEBSMS] | CVIS
7/19/2024 2:32:18 AM | Mindanao Grid-07/19/2024 02:38: WMPC DG04 shutdown at 0231H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/19/2024 2:17:36 AM | Mindanao Grid-07/19/2024 02:24: NagaMin SVC energized at 0213H. Unplanned Outage/Emergency shutdown. [WEBSMS] | CMIN
7/19/2024 12:51:04 AM | Visayas Grid-07/19/2024 00:51: LGPP U1 cut in at 0047H (Unplanned Outage) [WEBSMS] | CVIS
7/19/2024 12:22:17 AM | Mindanao Grid-07/19/2024 00:28: NagaMin SVC de-energized at 0010H. Unplanned Outage/Emergency shutdown. [WEBSMS] | CMIN
7/19/2024 12:05:18 AM | Mindanao Grid-07/19/2024 00:11: WMPC DG04 Online at 0004H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/18/2024 11:05:01 PM | Mindanao Grid-07/18/2024 23:11: LAKE MAINIT Hydro online at 2300H (Unplanned Outage) [WEBSMS] | CMIN
7/18/2024 9:17:17 PM | Luzon Grid-07/18/2024 21:17: SCPC 1 shutdown at 2117H (Unplanned Outage) [WEBSMS] | CLUZ
7/18/2024 8:17:41 PM | Luzon Grid-07/18/2024 20:17: SCPC 3 shutdown at 2016H (Unplanned Outage) [WEBSMS] | CLUZ
7/18/2024 8:14:22 PM | Mindanao Grid-07/18/2024 20:20: Correction: PPE (10PPEI_U01) online at 1452H (Planned Outage, Non-GOMP) [WEBSMS] | CMIN
7/18/2024 8:12:55 PM | Mindanao Grid-07/18/2024 20:19: PPE (10PPEI_U01) online at 1452H (Unplanned Outage) [WEBSMS] | CMIN
7/18/2024 8:10:34 PM | Luzon Grid-07/18/2024 20:10: Tayabas-San Jose 500kV Line 1 tripped/reclosed both side at 2005H (Unplanned Outage) [WEBSMS] | CLUZ
7/18/2024 7:56:45 PM | Mindanao Grid-07/18/2024 20:03: LAKE MAINIT Hydro with 12.3MW load tripped at 1952H (Unplanned Outage) [WEBSMS] | CMIN
7/18/2024 7:29:25 PM | [NSO Update] Luzon Grid-07/18/2024 19:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1927H with power going to Luzon. [WEBSMS] | CLUZ
7/18/2024 7:28:21 PM | [NSO Update] Visayas Grid-07/18/2024 19:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1927H with power going to Luzon. [WEBSMS] | CVIS
7/18/2024 7:21:54 PM | Mindanao Grid-07/18/2024 19:28: AGUS 1 Unit 2 online at 1919H (Unplanned Outage) [WEBSMS] | CMIN
7/18/2024 7:19:04 PM | Luzon Grid-07/18/2024 19:19: SCPC 2 shutdown at 1918H (Unplanned Outage) [WEBSMS] | CLUZ
7/18/2024 7:15:07 PM | [NSO Update] Visayas Grid-07/18/2024 19:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1914H from reverse power direction. [WEBSMS] | CVIS
7/18/2024 7:15:04 PM | [NSO Update] Luzon Grid-07/18/2024 19:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1914H from reverse power direction. [WEBSMS] | CLUZ
7/18/2024 6:27:03 PM | Luzon Grid-07/18/2024 18:27: SCPC 4 shutdown at 1826H (Unplanned Outage) [WEBSMS] | CLUZ
7/18/2024 6:03:36 PM | Mindanao Grid-07/18/2024 18:10: AGUS 4 Unit 2 online at 1802H (Planned Outage) [WEBSMS] | CMIN
7/18/2024 5:50:56 PM | [NSO Update] Luzon Grid-07/18/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12084MW, PK=10528MW, RR=404MW, NetOpMargin: EVE=1152 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Limay 8 @60MW, Masinloc 1 @310MW, Masinloc 3 @315MW, SCPC 1 @60MW, SCPC 2 @60MW, SCPC 3 @60MW, SCPC 4 @60MW [WEBSMS] | CLUZ
7/18/2024 5:50:33 PM | [NSO Update] Visayas Grid-07/18/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2317MW, PK=1966MW, RR=86MW, NetOpMargin: EVE=265 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @256MW, CEDC 3 @75MW, PDPP1-2 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, TGPP @79.5MW, PB104-2 @5MW, PB104-3 @5MW, PB104-4 @6.5MW, PEDC U3 @125MW [WEBSMS] | CVIS
7/18/2024 5:49:55 PM | [NSO Update] Mindanao Grid-07/18/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2945MW, PK=2146MW, RR=73MW, NetOpMargin: EVE=726 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/18/2024 4:21:52 PM | Mindanao Grid-07/18/2024 16:28: AGUS 6 Unit 2 online at 1616H (Unplanned Outage) [WEBSMS] | CMIN
7/18/2024 4:19:02 PM | Mindanao Grid-07/18/2024 16:25: WMPC DG04 shutdown at 1616H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/18/2024 3:59:51 PM | Luzon Grid-07/18/2024 15:59: Tayabas-Naga 230kV L2 restored at 1556H (Planned Outage) [WEBSMS] | CLUZ
7/18/2024 3:55:13 PM | Mindanao Grid-07/18/2024 16:01: Agus 6 SWY- Agus 6 U2 138kV Line energized at 1548H. Unplanned Outage. [WEBSMS] | CMIN
7/18/2024 2:27:44 PM | Mindanao Grid-07/18/2024 14:34: LAKE MAINIT Hydro online at 1426H (Unplanned Outage) [WEBSMS] | CMIN
7/18/2024 1:41:38 PM | [NSO Update] Luzon Grid-07/18/2024 13:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1339H with power going to Visayas. [WEBSMS] | CLUZ
7/18/2024 1:41:18 PM | [NSO Update] Visayas Grid-07/18/2024 13:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1339H with power going to Visayas. [WEBSMS] | CVIS
7/18/2024 1:29:57 PM | Mindanao Grid-07/18/2024 13:36: WMPC DG04 online at 1327H. RPS-system voltage requirement. [WEBSMS] | CMIN
7/18/2024 1:28:31 PM | [NSO Update] Visayas Grid-07/18/2024 13:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1326H from forward power direction. [WEBSMS] | CVIS
7/18/2024 1:28:10 PM | [NSO Update] Luzon Grid-07/18/2024 13:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1326H from forward power direction. [WEBSMS] | CLUZ
7/18/2024 1:02:57 PM | [NSO Update] Luzon Grid-07/18/2024 13:02: Update on System Advisory: The Luzon Grid Yellow Alert Notice issued today has been lifted effective 1300H. [WEBSMS] | CLUZ
7/18/2024 12:59:34 PM | [NSO Update] Luzon Grid-07/18/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13049MW, PK=11655MW, RR=474MW, NetOpMargin: PM=920, EVE=806 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, SLTEC 1 @121MW, SLTEC 2 @120MW, Limay 8 @60MW, Masinloc 1 @310MW, Masinloc 3 @310MW, SCPC 1 @60MW, SCPC 2 @60MW, SCPC 3 @60MW, SCPC 4 @60MW [WEBSMS] | CLUZ
7/18/2024 12:56:02 PM | [NSO Update] Mindanao Grid-07/18/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2969MW, PK=2226MW, RR=73MW, NetOpMargin: PM=670, EVE=736 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/18/2024 12:54:10 PM | [NSO Update] Visayas Grid-07/18/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2487MW, PK=2132MW, RR=91MW, NetOpMargin: PM=264, EVE=249 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @256MW, CEDC 3 @75MW, PDPP1-2 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, TGPP @79.5MW, PB104-2 @5MW, PB104-3 @5MW, PB104-4 @6.5MW, PEDC U3 @125MW [WEBSMS] | CVIS
7/18/2024 12:48:24 PM | Mindanao Grid-07/18/2024 12:54: LAKE MAINIT shutdown at 1201H to facilitate massive line clearing activity by ANECO (Unplanned Outage) [WEBSMS] | CMIN
7/18/2024 11:19:14 AM | Mindanao Grid-07/18/2024 11:25: AGUS 1 Unit 2 shutdown at 1116H (Unplanned Outage) [WEBSMS] | CMIN
7/18/2024 8:39:19 AM | Visayas Grid-07/18/2024 08:39: LGPP U1 emergency shutdown at 0831H, steam leak (Unplanned Outage) [WEBSMS] | CVIS
7/18/2024 7:37:36 AM | Mindanao Grid-07/18/2024 07:44: LAKE MAINIT Hydro online at 0734H (Unplanned Outage) [WEBSMS] | CMIN
7/18/2024 6:34:15 AM | Luzon Grid-07/18/2024 06:34: Tayabas-Naga 230kV L2 de-energized at 0633H (Planned Outage) [WEBSMS] | CLUZ
7/18/2024 6:25:10 AM | [NSO Update] Luzon Grid-07/18/2024 06:25: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=12985MW, PK=11647MW, RR=434MW, NetOpMargin: AM=904, PM=374, EVE=205 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @500MW, SLTEC 1 @120MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @305MW, SCPC 1 @60MW, SCPC 2 @60MW, SCPC 3 @60MW, SCPC 4 @60MW, Sual 1 @550MW (Total of de-rated capacity: 633MW) [WEBSMS] | CLUZ
7/18/2024 6:22:17 AM | [NSO Update] Luzon Grid-07/18/2024 06:22: System Advisory: 18-Jul-2024, Luzon Grid is on YELLOW Alert for interval hours 1400H-2200H. Total capacity on forced outage is 1260.5MW. Total of de-rated capacity is 633MW. [WEBSMS] | CLUZ
7/18/2024 5:49:03 AM | Mindanao Grid-07/18/2024 05:55: SEC 1 online at 0546H (Unplanned Outage) [WEBSMS] | CMIN
7/18/2024 5:45:19 AM | [NSO Update] Mindanao Grid-07/18/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2871MW, PK=2220MW, RR=73MW, NetOpMargin: AM=578, PM=490, EVE=545 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @28.5MW [WEBSMS] | CMIN
7/18/2024 5:44:25 AM | [NSO Update] Visayas Grid-07/18/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2270MW, PK=2014MW, RR=87MW, NetOpMargin: AM=169, PM=229, EVE=227 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @256MW, CEDC 3 @75MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, TGPP @79.5MW, PB104-2 @5MW, PB104-3 @5MW, PB104-4 @6.5MW, PEDC U3 @75MW, PDPP3-G @12MW [WEBSMS] | CVIS
7/18/2024 5:42:27 AM | [NSO Update] Mindanao Grid-07/18/2024 05:48: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data in the vicinity of Catbalogan City, Samar (11.8 N, 124.7 E). Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
7/18/2024 5:42:14 AM | [NSO Update] Visayas Grid-07/18/2024 05:42: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data in the vicinity of Catbalogan City, Samar (11.8 N, 124.7 E). Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
7/18/2024 5:42:02 AM | [NSO Update] Luzon Grid-07/18/2024 05:42: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data in the vicinity of Catbalogan City, Samar (11.8 N, 124.7 E). Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/18/2024 5:31:30 AM | Luzon Grid-07/18/2024 05:31: Hermosa - Malolos 230kV Line restored at 0530H (Unplanned Outage) [WEBSMS] | CLUZ
7/18/2024 4:48:32 AM | Luzon Grid-07/18/2024 04:48: SLPGC Unit 1 online at 0442H (Unplanned Outage) [WEBSMS] | CLUZ
7/18/2024 4:45:57 AM | Luzon Grid-07/18/2024 04:45: SLPGC Unit 1 online at 0442H (Unplanned Outage) [WEBSMS] | CLUZ
7/18/2024 3:22:03 AM | Luzon Grid-07/18/2024 03:22: Hermosa - Malolos 230kV Line de-energized at 0317H (Unplanned Outage) [WEBSMS] | CLUZ
7/18/2024 12:24:07 AM | Visayas Grid-07/18/2024 00:24: Dumanjug - Corella 230 kV Line 1 energized from Dumanjug SS at 0021H, under test and commissioning [WEBSMS] | CVIS
7/17/2024 10:35:34 PM | Visayas Grid-07/17/2024 22:35: TGPP U2 cut-in at 2230H (Unplanned Outage) [WEBSMS] | CVIS
7/17/2024 10:02:26 PM | Mindanao Grid-07/17/2024 22:08: SEC 1 tripped with 121MW load at 2054H due to Induced Draft Fan Trip. The lowest frequency recorded is 59.316Hz. No ALD (Unplanned Outage) [WEBSMS] | CMIN
7/17/2024 9:55:42 PM | Mindanao Grid-07/17/2024 22:02: GNPK Unit 1 declared full capability at 2150H with 151.9MW (gross). [WEBSMS] | CMIN
7/17/2024 8:58:36 PM | Mindanao Grid-07/17/2024 21:05: GNPK Unit 1 derated to 117MW gross (from 151.9MW) due to Unit 1 Coal feeder E trip [WEBSMS] | CMIN
7/17/2024 8:33:28 PM | Mindanao Grid-07/17/2024 20:39: WMPC DG04 shutdown at 2017H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
7/17/2024 7:22:46 PM | [NSO Update] Visayas Grid-07/17/2024 19:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1917H with power going to Luzon [WEBSMS] | CVIS
7/17/2024 7:21:53 PM | [NSO Update] Luzon Grid-07/17/2024 19:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1917H with power going to Luzon [WEBSMS] | CLUZ
7/17/2024 7:09:07 PM | [NSO Update] Visayas Grid-07/17/2024 19:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1858H from reverse power direction [WEBSMS] | CVIS
7/17/2024 7:06:42 PM | [NSO Update] Luzon Grid-07/17/2024 19:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1858H from reverse power direction [WEBSMS] | CLUZ
7/17/2024 6:31:30 PM | Mindanao Grid-07/17/2024 18:38: GNPK Unit 4 online at 1826H (Unplanned Outage) [WEBSMS] | CMIN
7/17/2024 6:21:55 PM | [NSO Update] Luzon Grid-07/17/2024 18:21: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12157MW, PK=10792MW, RR=961MW, NetOpMargin: EVE=961 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @500MW, SLTEC 1 @120MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @325MW, SCPC 1 @125MW, Sual 1 @550MW [WEBSMS] | CLUZ
7/17/2024 6:01:05 PM | [NSO Update] Mindanao Grid-07/17/2024 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2804MW, PK=2168MW, RR=73MW, NetOpMargin: EVE=563 Highest Unit O/L: GNPK 1, 2, 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @29.5MW [WEBSMS] | CMIN
7/17/2024 5:54:35 PM | [NSO Update] Visayas Grid-07/17/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2391MW, PK=1981MW, RR=84MW, NetOpMargin: EVE=327 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @260MW, CEDC 3 @75MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, TGPP @81MW, PB104-2 @5MW, PB104-3 @5MW, PB104-4 @6.5MW [WEBSMS] | CVIS
7/17/2024 5:53:47 PM | Visayas Grid-07/17/2024 17:53: Magdugo-Dumanjug 230 kV Line 1 energized at 1750H (Unplanned Outage) [WEBSMS] | CVIS
7/17/2024 5:02:47 PM | Mindanao Grid-07/17/2024 17:09: AGUS 6 HEP Unit 2 with 31MW load tripped at 1656H. Frequency dipped at 59.73Hz. Cause: For verification (Unplanned Outage). [WEBSMS] | CMIN
7/17/2024 4:58:41 PM | Mindanao Grid-07/17/2024 17:05: Toril - Matanao 138kV L1 energized at 1657H. (Planned Outage) [WEBSMS] | CMIN
7/17/2024 4:55:31 PM | [NSO Update] Luzon Grid-07/17/2024 16:53: Update on System Advisory: The Luzon Grid Yellow Alert Notice issued today has been lifted effective 1600H. [WEBSMS] | CLUZ
7/17/2024 4:14:20 PM | Mindanao Grid-07/17/2024 16:20: AGUS 2 Unit 2 online at 1545H (Planned Outage) [WEBSMS] | CMIN
7/17/2024 3:52:12 PM | Luzon Grid-07/17/2024 15:52: EDC Burgos 115kV Bus 1 restored at 1548H (Planned Outage) [WEBSMS] | CLUZ
7/17/2024 3:48:37 PM | Luzon Grid-07/17/2024 15:48: Tayabas-Naga 230kV line 1 restored at 1547H (Planned Outage) [WEBSMS] | CLUZ
7/17/2024 2:16:48 PM | Visayas Grid-07/17/2024 14:16: PEDC U3 cut in at 1407H (Unplanned Outage) [WEBSMS] | CVIS
7/17/2024 1:27:02 PM | Mindanao Grid-07/17/2024 13:33: GNPK Unit 4 tripped at 1317H with gross gen of 150.3MW. No ALD. Lowest frequency at 59.218 Hz. (Unplanned Outage) [WEBSMS] | CMIN
7/17/2024 1:13:26 PM | [NSO Update] Luzon Grid-07/17/2024 13:13: System Advisory: 17-Jul-2024, Luzon grid is on YELLOW Alert for interval hours 1600H-2100H. Total capacity on forced outage is 1358.7MW. Total of de-rated capacity is 294MW. [WEBSMS] | CLUZ
7/17/2024 1:11:29 PM | Mindanao Grid-07/17/2024 13:17: Toril - Matanao 138kV L1 de-energized at 1303H.(Planned Outage) [WEBSMS] | CMIN
7/17/2024 1:10:16 PM | [NSO Update] Luzon Grid-07/17/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=13198MW, PK=12028MW, RR=434MW, NetOpMargin: PM=736, EVE=378 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @295MW, SCPC 1 @120MW, Sual 1 @550MW [WEBSMS] | CLUZ
7/17/2024 12:59:30 PM | [NSO Update] Mindanao Grid-07/17/2024 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2969MW, PK=2265MW, RR=73MW, NetOpMargin: PM=632, EVE=703 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @29.5MW [WEBSMS] | CMIN
7/17/2024 12:57:11 PM | [NSO Update] Visayas Grid-07/17/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2377MW, PK=2061MW, RR=87MW, NetOpMargin: PM=229, EVE=231 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @267MW, CEDC 3 @75MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PB104-2 @5MW, PB104-3 @5MW, PB104-4 @6.5MW [WEBSMS] | CVIS
7/17/2024 12:51:27 PM | Mindanao Grid-07/17/2024 12:57: LAKE MAINIT Hydro with 11.33MW tripped at 1240H. Indication: Generator Master tripped (Unplanned Outage) [WEBSMS] | CMIN
7/17/2024 12:11:45 PM | Visayas Grid-07/17/2024 12:11: Magdugo-Dumanjug 230 kV Line 1 de-energized at 1211H (Planned Outage) [WEBSMS] | CVIS
7/17/2024 11:25:33 AM | Luzon Grid-07/17/2024 11:25: San Gabriel tripped at 1117H from 372MW load. The lowest system frequency was 59.105Hz. There was no ALD incurred. (Unplanned Outage) [WEBSMS] | CLUZ
7/17/2024 10:09:33 AM | [NSO Update] Luzon Grid-07/17/2024 10:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1008H with power going to Visayas. [WEBSMS] | CLUZ
7/17/2024 10:09:28 AM | [NSO Update] Visayas Grid-07/17/2024 10:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1008H with power going to Visayas. [WEBSMS] | CVIS
7/17/2024 10:01:48 AM | Mindanao Grid-07/17/2024 10:08: WMPC DG04 online at 0951H. RPS-system voltage requirement. [WEBSMS] | CMIN
7/17/2024 9:59:28 AM | [NSO Update] Visayas Grid-07/17/2024 09:59: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0956H from forward power direction. [WEBSMS] | CVIS
7/17/2024 9:59:25 AM | [NSO Update] Luzon Grid-07/17/2024 09:59: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0956H from forward power direction. [WEBSMS] | CLUZ
7/17/2024 6:17:19 AM | [NSO Update] Visayas Grid-07/17/2024 06:17: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2357MW, PK=2067MW, RR=90MW, NetOpMargin: AM=200, PM=226, EVE=228 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @267MW, CEDC 3 @75MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-2 @5MW, PB104-3 @5MW, PB104-4 @6.5MW [WEBSMS] | CVIS
7/17/2024 6:16:09 AM | Luzon Grid-07/17/2024 06:16: Tayabas-Naga 230kV line 1 was de-energized at 0614H. (Planned Outage) [WEBSMS] | CLUZ
7/17/2024 6:15:18 AM | [NSO Update] Luzon Grid-07/17/2024 06:15: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13728MW, PK=11871MW, RR=434MW, NetOpMargin: AM=1422, PM=792, EVE=687 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @310MW, SCPC 1 @120MW, Sual 1 @550MW [WEBSMS] | CLUZ
7/17/2024 5:44:04 AM | [NSO Update] Mindanao Grid-07/17/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2984MW, PK=2187MW, RR=73MW, NetOpMargin: AM=724, PM=649, EVE=715 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @29.5MW [WEBSMS] | CMIN
7/17/2024 5:22:51 AM | [NSO Update] Mindanao Grid-07/17/2024 05:29: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 200 km East Northeast of Surigao City, Surigao del Norte (10.4 N, 127.2 E). Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
7/17/2024 5:22:35 AM | [NSO Update] Visayas Grid-07/17/2024 05:22: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 200 km East Northeast of Surigao City, Surigao del Norte (10.4 N, 127.2 E). Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
7/17/2024 5:22:16 AM | [NSO Update] Luzon Grid-07/17/2024 05:22: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 200 km East Northeast of Surigao City, Surigao del Norte (10.4 N, 127.2 E). Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/17/2024 3:50:02 AM | Visayas Grid-07/17/2024 03:50: Cebu - Mandaue 138 kV Line 1 energized at 0349H (Unplanned Outage) [WEBSMS] | CVIS
7/17/2024 1:04:09 AM | Visayas Grid-07/17/2024 01:04: PGPP1 U3 cut-in at 0101H (Unplanned Outage) [WEBSMS] | CVIS
7/16/2024 10:24:26 PM | Visayas Grid-07/16/2024 22:24: Cebu - Mandaue 138 kV Line 1 de-energized at 2222H (Unplanned Outage) [WEBSMS] | CVIS
7/16/2024 8:40:49 PM | [NSO Update] Luzon Grid-07/16/2024 20:40: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2036H with power going to Luzon [WEBSMS] | CLUZ
7/16/2024 8:38:03 PM | [NSO Update] Visayas Grid-07/16/2024 20:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2036H with power going to Luzon [WEBSMS] | CVIS
7/16/2024 8:30:37 PM | [NSO Update] Visayas Grid-07/16/2024 20:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2026H from reverse power direction [WEBSMS] | CVIS
7/16/2024 8:29:10 PM | [NSO Update] Luzon Grid-07/16/2024 20:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2026H from reverse power direction [WEBSMS] | CLUZ
7/16/2024 6:07:26 PM | [NSO Update] Mindanao Grid-07/16/2024 18:14: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2953MW, PK=2138MW, RR=73MW, NetOpMargin: EVE=742 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @29.5MW [WEBSMS] | CMIN
7/16/2024 5:59:07 PM | [NSO Update] Visayas Grid-07/16/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2347MW, PK=2033MW, RR=86MW, NetOpMargin: EVE=228 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @260MW, CEDC 3 @75MW, PGPP1 @73MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-2 @5MW, PB104-3 @5MW, PB104-4 @6.5MW [WEBSMS] | CVIS
7/16/2024 5:54:04 PM | [NSO Update] Luzon Grid-07/16/2024 17:54: [CORRECTION] GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12734MW, PK=10973MW, RR=443MW, NetOpMargin: EVE=1318 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @500MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @315MW, Masinloc 3 @300MW, SCPC 1 @120MW [WEBSMS] | CLUZ
7/16/2024 5:47:51 PM | [NSO Update] Luzon Grid-07/16/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12734MW, PK=10973MW, RR=443MW, NetOpMargin: EVE=12734 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @500MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @315MW, Masinloc 3 @300MW, SCPC 1 @120MW [WEBSMS] | CLUZ
7/16/2024 5:15:10 PM | Mindanao Grid-07/16/2024 17:21: WMPC DG04 shutdown at 1712H. RPS-system voltage requirements. [WEBSMS] | CMIN
7/16/2024 4:25:51 PM | Visayas Grid-07/16/2024 16:26: Carcon SS 34.5 kV Bus 1 energized at 1609H. (Planned Outage) [WEBSMS] | CVIS
7/16/2024 3:45:50 PM | Visayas Grid-07/16/2024 15:46: Magdugo-Dumanjug 230kV Line 1 closed loop at Dumanjug side at 1543H (Unplanned Outage) [WEBSMS] | CVIS
7/16/2024 3:36:12 PM | Visayas Grid-07/16/2024 15:36: Magdugo-Dumanjug 230kV Line 1 tripped/reclosed at Magdugo side at 1526H (Unplanned Outage) [WEBSMS] | CVIS
7/16/2024 3:05:34 PM | Mindanao Grid-07/16/2024 15:12: Culaman SS - MCO (SMCPC) 230kV L2 (8LI2CMA-MCO) energized at 1502H. ( From Planned Outage/Non-GOMP) [WEBSMS] | CMIN
7/16/2024 12:49:53 PM | [NSO Update] Mindanao Grid-07/16/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2989MW, PK=2214MW, RR=73MW, NetOpMargin: PM=702, EVE=780 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @29.5MW [WEBSMS] | CMIN
7/16/2024 12:49:24 PM | [NSO Update] Visayas Grid-07/16/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2451MW, PK=2157MW, RR=91MW, NetOpMargin: PM=202, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @260MW, CEDC 3 @75MW, PGPP1 @73MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-2 @5MW, PB104-3 @5MW, PB104-4 @6.5MW [WEBSMS] | CVIS
7/16/2024 12:49:13 PM | [NSO Update] Luzon Grid-07/16/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13952MW, PK=12198MW, RR=474MW, NetOpMargin: PM=1280, EVE=1283 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @500MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @300MW, SCPC 1 @120MW [WEBSMS] | CLUZ
7/16/2024 12:11:00 PM | Visayas Grid-07/16/2024 12:11: Dumanjug-Corella 230 kV Line 1 tripped at 1207H while under the test and commissioning stage. (Unplanned Outage) [WEBSMS] | CVIS
7/16/2024 11:01:15 AM | Mindanao Grid-07/16/2024 11:07: WMPC DG04 online at 1051H. RPS-system voltage requirements. [WEBSMS] | CMIN
7/16/2024 10:27:05 AM | Visayas Grid-07/16/2024 10:27: Carcon SS 34.5 kV Bus 1 de-energized at 1007H. (Planned Outage) [WEBSMS] | CVIS
7/16/2024 9:47:07 AM | Mindanao Grid-07/16/2024 09:53: Tagoloan-STEAG 138kV L2 de-energized at 0943H. Planned Outage. [WEBSMS] | CMIN
7/16/2024 9:21:23 AM | Mindanao Grid-07/16/2024 09:28: Culaman SS - MCO (SMCPC) 230kV L2 (8LI2CMA-MCO) deenergized at 0910H. (Planned Outage/Non-GOMP) [WEBSMS] | CMIN
7/16/2024 9:16:57 AM | [NSO Update] Visayas Grid-07/16/2024 09:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0911H with power going to Visayas. [WEBSMS] | CVIS
7/16/2024 9:16:51 AM | [NSO Update] Luzon Grid-07/16/2024 09:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0911H with power going to Visayas. [WEBSMS] | CLUZ
7/16/2024 9:02:35 AM | [NSO Update] Visayas Grid-07/16/2024 09:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0901H from forward power direction. [WEBSMS] | CVIS
7/16/2024 9:02:30 AM | [NSO Update] Luzon Grid-07/16/2024 09:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0901H from forward power direction. [WEBSMS] | CLUZ
7/16/2024 6:22:17 AM | Luzon Grid-07/16/2024 06:22: San Jose 750MVA T04 was restored at 0619H. (Planned Outage) [WEBSMS] | CLUZ
7/16/2024 5:54:45 AM | [NSO Update] Mindanao Grid-07/16/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2989MW, PK=2176MW, RR=73MW, NetOpMargin: AM=740, PM=671, EVE=743 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @37.5MW, MA2 @29.5MW [WEBSMS] | CMIN
7/16/2024 5:53:02 AM | [NSO Update] Visayas Grid-07/16/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2379MW, PK=2092MW, RR=91MW, NetOpMargin: AM=196, PM=342, EVE=244 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @267MW, CEDC 3 @75MW, PGPP1 @75MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-2 @5.5MW, PB104-3 @5MW [WEBSMS] | CVIS
7/16/2024 5:51:10 AM | [NSO Update] Luzon Grid-07/16/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14009MW, PK=11360MW, RR=463MW, NetOpMargin: AM=2186, PM=1467, EVE=1257 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @500MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @295MW, Masinloc 3 @290MW, SCPC 1 @120MW [WEBSMS] | CLUZ
7/16/2024 4:53:32 AM | [NSO Update] Mindanao Grid-07/16/2024 05:00: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 310 km East Northeast of Davao City (8.3 N, 128.2 E). Southwest Monsoon affecting the western sections of Southern Luzon and Mindanao. [WEBSMS] | CMIN
7/16/2024 4:53:14 AM | [NSO Update] Visayas Grid-07/16/2024 04:53: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 310 km East Northeast of Davao City (8.3 N, 128.2 E). Southwest Monsoon affecting the western sections of Southern Luzon and Mindanao. [WEBSMS] | CVIS
7/16/2024 4:52:46 AM | [NSO Update] Luzon Grid-07/16/2024 04:52: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 310 km East Northeast of Davao City (8.3 N, 128.2 E). Southwest Monsoon affecting the western sections of Southern Luzon and Mindanao. [WEBSMS] | CLUZ
7/16/2024 4:08:51 AM | Visayas Grid-07/16/2024 04:09: Dumanjug-Corella 230 kV Line 1 energized at 0407H, from Dumanjug side (Planned Outage) [WEBSMS] | CVIS
7/15/2024 11:45:15 PM | Mindanao Grid-07/15/2024 23:51: ASIGA Hydro online at 2316H (Unplanned Outage) [WEBSMS] | CMIN
7/15/2024 10:55:58 PM | Mindanao Grid-07/15/2024 23:02: ASIGA Hydro with 4.05MW load emergency shutdown at 2221H due to overheating of shaft seal (Unplanned Outage) [WEBSMS] | CMIN
7/15/2024 10:54:18 PM | Mindanao Grid-07/15/2024 23:00: ASIGA Hydro online at 2216H (Unplanned Outage) [WEBSMS] | CMIN
7/15/2024 10:40:23 PM | Luzon Grid-07/15/2024 22:40: San Jose 750MVA T04 de-energized at 2237H (Planned Outage) [WEBSMS] | CLUZ
7/15/2024 10:02:01 PM | [NSO Update] Luzon Grid-07/15/2024 22:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2148H with power going to Luzon [WEBSMS] | CLUZ
7/15/2024 10:01:43 PM | [NSO Update] Visayas Grid-07/15/2024 22:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2148H with power going to Luzon [WEBSMS] | CVIS
7/15/2024 10:00:02 PM | [NSO Update] Visayas Grid-07/15/2024 22:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2126H from reverse power direction [WEBSMS] | CVIS
7/15/2024 9:59:49 PM | [NSO Update] Luzon Grid-07/15/2024 21:59: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2126H from reverse power direction [WEBSMS] | CLUZ
7/15/2024 6:21:28 PM | [NSO Update] Mindanao Grid-07/15/2024 18:28: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2959MW, PK=2134MW, RR=73MW, NetOpMargin: EVE=753 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
7/15/2024 6:11:15 PM | Mindanao Grid-07/15/2024 18:17: AGUS 7 Unit 1 online at 1810H (Planned Outage) [WEBSMS] | CMIN
7/15/2024 6:09:15 PM | [NSO Update] Visayas Grid-07/15/2024 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2350MW, PK=2033MW, RR=90MW, NetOpMargin: EVE=227 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @257MW, CEDC 3 @75MW, PGPP1 @75MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-2 @5MW, PB104-3 @5MW [WEBSMS] | CVIS
7/15/2024 6:08:02 PM | [NSO Update] Luzon Grid-07/15/2024 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12793MW, PK=10843MW, RR=456MW, NetOpMargin: EVE=1494 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @500MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
7/15/2024 6:03:39 PM | Visayas Grid-07/15/2024 18:03: PGPP1 U3 emergency shutdown at 1754H (Unplanned Outage) [WEBSMS] | CVIS
7/15/2024 4:36:01 PM | Luzon Grid-07/15/2024 16:36: Naga-Tiwi C 230kV Line 2 restored at 1634H (Planned Outage) [WEBSMS] | CLUZ
7/15/2024 3:21:23 PM | Visayas Grid-07/15/2024 15:21: Colon - KSPC 138 kV L2 energized at 1455H (Planned Outage) [WEBSMS] | CVIS
7/15/2024 2:55:51 PM | Visayas Grid-07/15/2024 14:56: CEDC U1 cut-in at 1452H (Unplanned Outage) [WEBSMS] | CVIS
7/15/2024 12:55:51 PM | [NSO Update] Luzon Grid-07/15/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13899MW, PK=11879MW, RR=497MW, NetOpMargin: PM=1523, EVE=917 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @500MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @305MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
7/15/2024 12:54:46 PM | [NSO Update] Mindanao Grid-07/15/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2983MW, PK=2264MW, RR=73MW, NetOpMargin: PM=646, EVE=733 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
7/15/2024 8:44:08 AM | Mindanao Grid-07/15/2024 08:50: WMPC DG10 declared forced outage at 0816H. Cause: Generator rubber coupling for replacement (Unplanned Outage) [WEBSMS] | CMIN
7/15/2024 8:33:37 AM | [NSO Update] Visayas Grid-07/15/2024 08:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2577MW, PK=2109MW, RR=91MW, NetOpMargin: AM=377, PM=296, EVE=317 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @233MW, PGPP1 @100MW, GTEC @7MW, PB101-2 @5.5MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-2 @5.5MW, PB104-3 @5MW, PB104-4 @7MW [WEBSMS] | CVIS
7/15/2024 8:27:56 AM | Visayas Grid-07/15/2024 08:28: CEDC U3 online at 0827H. (Unplanned Outage) [WEBSMS] | CVIS
7/15/2024 8:25:56 AM | [NSO Update] Visayas Grid-07/15/2024 08:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0822H with power going to Visayas [WEBSMS] | CVIS
7/15/2024 8:25:23 AM | [NSO Update] Luzon Grid-07/15/2024 08:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0822H with power going to Visayas [WEBSMS] | CLUZ
7/15/2024 8:19:07 AM | [NSO Update] Mindanao Grid-07/15/2024 08:25: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2861MW, PK=2146MW, RR=73MW, NetOpMargin: AM=642, PM=622, EVE=684 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
7/15/2024 8:15:42 AM | [NSO Update] Visayas Grid-07/15/2024 08:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0812H from forward power direction [WEBSMS] | CVIS
7/15/2024 8:15:24 AM | [NSO Update] Luzon Grid-07/15/2024 08:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0812H from forward power direction [WEBSMS] | CLUZ
7/15/2024 8:14:11 AM | [NSO Update] Luzon Grid-07/15/2024 08:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0812H from forward power direction [WEBSMS] | CLUZ
7/15/2024 6:13:12 AM | Luzon Grid-07/15/2024 06:13: Naga-Tiwi C 230kV Line 2 de-energized at 0607H (Planned Outage) [WEBSMS] | CLUZ
7/15/2024 5:47:52 AM | [NSO Update] Luzon Grid-07/15/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14024MW, PK=11450MW, RR=468MW, NetOpMargin: AM=2106, PM=1461, EVE=1366 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @500MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @315MW, Masinloc 3 @310MW [WEBSMS] | CLUZ
7/15/2024 5:10:25 AM | Luzon Grid-07/15/2024 05:10: Muntinlupa-Sun Valley 115kV line was energized at 0509H (Planned Outage) [WEBSMS] | CLUZ
7/15/2024 4:44:30 AM | Luzon Grid-07/15/2024 04:44: Muntinlupa 115kV Bus 1 was energized at 0442H (Planned Outage) [WEBSMS] | CLUZ
7/15/2024 4:03:20 AM | [NSO Update] Luzon Grid-07/15/2024 04:03: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/15/2024 3:47:55 AM | Luzon Grid-07/15/2024 03:48: Sta Rita Module 30 online at 0345H (Planned Outage) [WEBSMS] | CLUZ
7/15/2024 2:53:17 AM | Luzon Grid-07/15/2024 02:53: Dona Imelda-Sta Mesa 115kV line 2 was energized at 0250H (Planned Outage) [WEBSMS] | CLUZ
7/15/2024 12:55:59 AM | [NSO Update] Luzon Grid-07/15/2024 00:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0053H with power going to Luzon. [WEBSMS] | CLUZ
7/15/2024 12:47:56 AM | [NSO Update] Luzon Grid-07/15/2024 00:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0043H from reverse power direction. [WEBSMS] | CLUZ
7/15/2024 12:20:22 AM | Luzon Grid-07/15/2024 00:20: Dona Imelda-Sta Mesa 115kV line 2 was de-energized at 0018H. (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 11:59:22 PM | Luzon Grid-07/14/2024 23:59: Sta Rita Module 40 online at 2356H. (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 11:29:36 PM | Visayas Grid-07/14/2024 23:29: Cebu-Mandaue 138 kV Line 1 energized at 2329H (Unplanned Outage) [WEBSMS] | CVIS
7/14/2024 11:22:09 PM | Luzon Grid-07/14/2024 23:22: GNPD Unit 2 tripped at 2318H from 137MW load. The lowest system frequency was 59.592Hz. (Unplanned Outage) [WEBSMS] | CLUZ
7/14/2024 11:14:05 PM | Luzon Grid-07/14/2024 23:14: Batangas 300MVA T04 and T05 were paralleled on the 69kV side at 2311H. [WEBSMS] | CLUZ
7/14/2024 11:08:26 PM | Luzon Grid-07/14/2024 23:08: Sta Rita-San Lorenzo 230kV Busses were unlooped at 2306H. [WEBSMS] | CLUZ
7/14/2024 11:02:30 PM | [NSO Update] Visayas Grid-07/14/2024 23:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2204H with power going to Visayas. [WEBSMS] | CVIS
7/14/2024 11:00:34 PM | Luzon Grid-07/14/2024 23:00: Muntinlupa 115kV Bus 1 was de-energized at 2259H. (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 10:46:33 PM | Luzon Grid-07/14/2024 22:46: Muntinlupa-Sun Valley 115kV line was de-energized at 2245H. (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 10:30:06 PM | [NSO Update] Luzon Grid-07/14/2024 22:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2204H with power going to Visayas. [WEBSMS] | CLUZ
7/14/2024 10:28:00 PM | [NSO Update] Visayas Grid-07/14/2024 22:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2154H from forward power direction. [WEBSMS] | CVIS
7/14/2024 10:27:53 PM | [NSO Update] Luzon Grid-07/14/2024 22:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2154H from forward power direction. [WEBSMS] | CLUZ
7/14/2024 9:57:36 PM | Visayas Grid-07/14/2024 21:57: PGPP2 Sogongon Units 1 & 2 tripped at 2146H (Unplanned Outage) [WEBSMS] | CVIS
7/14/2024 9:52:03 PM | Visayas Grid-07/14/2024 21:52: PGPP1 Units 1, 2 & 3 Tripped at 2145H (Unplanned Outage) [WEBSMS] | CVIS
7/14/2024 9:50:40 PM | Visayas Grid-07/14/2024 21:50: CEDC Units 1, 2 & 3 tripped at 2145H (Unplanned Outage) [WEBSMS] | CVIS
7/14/2024 9:46:20 PM | Visayas Grid-07/14/2024 21:46: Cebu - Mandaue 138 kV Line 1 and Cebu SS 300 MVA 230/138/13.8 kV TR2 tripped at 2139H (Unplanned Outage) [WEBSMS] | CVIS
7/14/2024 7:29:43 PM | [NSO Update] Luzon Grid-07/14/2024 19:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1926H with power going to Luzon. [WEBSMS] | CLUZ
7/14/2024 7:27:56 PM | [NSO Update] Visayas Grid-07/14/2024 19:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1926H with power going to Luzon. [WEBSMS] | CVIS
7/14/2024 7:18:28 PM | [NSO Update] Visayas Grid-07/14/2024 19:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1916H from reverse power direction. [WEBSMS] | CVIS
7/14/2024 7:18:18 PM | Mindanao Grid-07/14/2024 19:24: Agus 6 SS - Agus 7 HEPP Unit 1 138kV Line energized at 1846H. From Planned Outage (U1 PMS). [WEBSMS] | CMIN
7/14/2024 7:18:03 PM | [NSO Update] Luzon Grid-07/14/2024 19:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1916H from reverse power direction. [WEBSMS] | CLUZ
7/14/2024 6:53:50 PM | Visayas Grid-07/14/2024 18:53: PGPP1 U2 cut-in at 1850H (Unplanned Outage) [WEBSMS] | CVIS
7/14/2024 6:30:14 PM | [NSO Update] Visayas Grid-07/14/2024 18:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1827H with power going to Visayas. [WEBSMS] | CVIS
7/14/2024 6:29:50 PM | [NSO Update] Luzon Grid-07/14/2024 18:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1827H with power going to Visayas. [WEBSMS] | CLUZ
7/14/2024 6:18:38 PM | [NSO Update] Visayas Grid-07/14/2024 18:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1817H from forward power direction. [WEBSMS] | CVIS
7/14/2024 6:18:04 PM | [NSO Update] Luzon Grid-07/14/2024 18:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1817H from forward power direction. [WEBSMS] | CLUZ
7/14/2024 6:05:46 PM | Luzon Grid-07/14/2024 18:05: Calaca-Amadeo 230kV Line 1 was restored at 1804H. (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 5:48:02 PM | [NSO Update] Mindanao Grid-07/14/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2814MW, PK=1982MW, RR=73MW, NetOpMargin: EVE=759 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
7/14/2024 5:47:08 PM | [NSO Update] Visayas Grid-07/14/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2161MW, PK=1873MW, RR=86MW, NetOpMargin: EVE=203 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @268MW, CEDC 3 @75MW, PGPP1 @75MW, GTEC @7MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @12MW, PB104-2 @5.5MW, PB104-3 @5MW, PB104-4 @7MW [WEBSMS] | CVIS
7/14/2024 5:45:24 PM | Mindanao Grid-07/14/2024 17:52: Maramag - Kibawe 138kV L2 (7LI2MRM-KIB) energized/restored at 1738H. Note: Affected by the shutdown of 7BS02MRM (PO/Non-GOMP), since 7-08CB24MRM is open due to PMS of PULANGI IV HEP U2. [WEBSMS] | CMIN
7/14/2024 5:43:39 PM | Luzon Grid-07/14/2024 17:43: Lal-lo-Cagayan North Solar 69kV lines 1 and 2 were energized at 1726H and 1731H respectively. (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 5:43:07 PM | [NSO Update] Luzon Grid-07/14/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12465MW, PK=10166MW, RR=311MW, NetOpMargin: EVE=1988 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @315MW, Ilijan A @500MW [WEBSMS] | CLUZ
7/14/2024 5:34:18 PM | Mindanao Grid-07/14/2024 17:40: Tagoloan SS 100MVA Power Transformer No.1 (7XF01TAG) energized/restored at 1729H. From Planned Outage/Non-GOMP). [WEBSMS] | CMIN
7/14/2024 5:26:24 PM | Luzon Grid-07/14/2024 17:26: Lal-lo-Magapit BESS 69kV line was restored at 1724H. (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 4:40:23 PM | Luzon Grid-07/14/2024 16:40: Pagbilao CFTPP 230kV Bus 1 was energized at 1639H. (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 4:31:10 PM | Mindanao Grid-07/14/2024 16:37: Maramag SS 138kV Bus 2 (7BS02MRM) energized/restored at 1628H. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
7/14/2024 4:01:49 PM | Luzon Grid-07/14/2024 16:01: San Gabriel online at 1559H. (Reserve Shutdown) [WEBSMS] | CLUZ
7/14/2024 3:54:56 PM | Luzon Grid-07/14/2024 15:55: Naga-Tiwi C 230kV Line 3 was restored at 1554H. (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 3:48:31 PM | Luzon Grid-07/14/2024 15:48: San Jose-Camarin 115kV Line was restored at 1548H. (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 2:24:36 PM | Luzon Grid-07/14/2024 14:24: Correction: San Esteban 230kV Bus 2 was energized at 1417H. (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 2:19:16 PM | Luzon Grid-07/14/2024 14:19: San Jose 230kV Bus 2 was energized at 1417H. (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 1:32:37 PM | Visayas Grid-07/14/2024 13:32: Colon SS TR1 50MVA 138/69/13.8KV energized at 1325H. Colon-CVC 69KV feeder energized at 1332H. (Planned Outage) [WEBSMS] | CVIS
7/14/2024 1:04:18 PM | [NSO Update] Visayas Grid-07/14/2024 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2382MW, PK=1795MW, RR=83MW, NetOpMargin: PM=503, EVE=291 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @262MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-3 @4MW, TPC-Thermal 1A @77MW, PB104-3 @5MW, PDPP3-G @12MW, PB104-2 @5.5MW, PB104-3 @5MW, PB104-4 @7MW, PGPP1 @73.5MW [WEBSMS] | CVIS
7/14/2024 12:51:43 PM | [NSO Update] Mindanao Grid-07/14/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2840MW, PK=1836MW, RR=73MW, NetOpMargin: PM=931, EVE=677 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
7/14/2024 12:51:27 PM | Mindanao Grid-07/14/2024 12:58: Bunawan - Maco 138kV Line (7LI1BUN-MAC) energized/restored at 1248H. From Planned Outage/Non-GOMP). [WEBSMS] | CMIN
7/14/2024 12:50:31 PM | [NSO Update] Luzon Grid-07/14/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13898MW, PK=10114MW, RR=334MW, NetOpMargin: PM=3450, EVE=1668 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @310MW, Masinloc 3 @320MW, Ilijan A @500MW, MPGC 2 @75MW [WEBSMS] | CLUZ
7/14/2024 8:04:21 AM | Mindanao Grid-07/14/2024 08:10: Maramag SS 138kV Bus 2 (7BS02MRM) de-energized at 0755H. (Planned Outage/Non-GOMP) [WEBSMS] | CMIN
7/14/2024 7:52:54 AM | Mindanao Grid-07/14/2024 07:59: Maramag - Kibawe 138kV L2 (7LI2MRM-KIB) de-energized at 0741H. (Notes: 1.0) Affected by the shutdown of 7BS02MRM (PO/Non-GOMP), since 7-08CB24MRM is open due to PMS of PULANGI IV HEP Unit 2). 2.0 No power customers and no connected/associated TL/STL were affected). [WEBSMS] | CMIN
7/14/2024 7:50:25 AM | Luzon Grid-07/14/2024 07:50: San Jose-Camarin 115kV Line de-energized at 0749H (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 7:31:33 AM | Luzon Grid-07/14/2024 07:31: San Gabriel shutdown at 0727H (Reserve Shutdown) [WEBSMS] | CLUZ
7/14/2024 7:28:46 AM | Mindanao Grid-07/14/2024 07:35: Tagoloan SS 100MVA Power Transformer No.1 (7XF01TAG) de-energized at 0754H. (Planned Outage/Non-GOMP). Note: P & E approved request shutdown. [WEBSMS] | CMIN
7/14/2024 7:07:23 AM | Luzon Grid-07/14/2024 07:07: San Esteban 230kV Bus 2 de-energized at 0706H (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 7:00:00 AM | Mindanao Grid-07/14/2024 07:06: Bunawan - Maco 138kV Line (7LI1BUN-MAC) de-energized at 0654H. (Planned Outage/Non-GOMP). Note: P & E approved request shutdown. [WEBSMS] | CMIN
7/14/2024 6:54:52 AM | Luzon Grid-07/14/2024 06:54: Naga-Tiwi C 230kV Line 3 de-energized at 0652H (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 6:46:20 AM | Luzon Grid-07/14/2024 06:46: Calaca-Amadeo 230kV Line 1 de-energized at 0644H (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 6:18:14 AM | Visayas Grid-07/14/2024 06:18: Colon SS TR1 50MVA 138/69/13.8KV de-energized at 0614H. Colon-CVC 69KV feeder de-energized at 0610H. (Planned Outage) [WEBSMS] | CVIS
7/14/2024 5:50:47 AM | Luzon Grid-07/14/2024 05:50: Lal-lo-Magapit BESS 69kV Line de-energized at 0549H (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 5:44:08 AM | Luzon Grid-07/14/2024 05:44: Lal-lo - Cagayan North Solar 69kV Line 1 and Line 2 de-energized at 0538H and 0539H, respectively. (Planned Outage) [WEBSMS] | CLUZ
7/14/2024 5:43:51 AM | [NSO Update] Luzon Grid-07/14/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14105MW, PK=9812MW, RR=326MW, NetOpMargin: AM=3967, PM=2956, EVE=1645 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @315MW, Masinloc 3 @290MW, Ilijan A @500MW, MPGC 2 @75MW [WEBSMS] | CLUZ
7/14/2024 5:40:48 AM | [NSO Update] Mindanao Grid-07/14/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2820MW, PK=1881MW, RR=73MW, NetOpMargin: AM=867, PM=818, EVE=620 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
7/14/2024 5:39:07 AM | [NSO Update] Visayas Grid-07/14/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2484MW, PK=1747MW, RR=80MW, NetOpMargin: AM=657, PM=362, EVE=238 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @265MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-3 @4MW, TPC-Thermal 1A @77MW, PB104-3 @5MW, PDPP3-G @12MW, PDPP1-2 @4MW, PB101-2 @5.5MW [WEBSMS] | CVIS
7/14/2024 4:25:45 AM | [NSO Update] Luzon Grid-07/14/2024 04:25: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/14/2024 4:25:38 AM | [NSO Update] Mindanao Grid-07/14/2024 04:32: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
7/14/2024 4:25:16 AM | [NSO Update] Visayas Grid-07/14/2024 04:25: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
7/14/2024 1:10:02 AM | Mindanao Grid-07/14/2024 01:16: LAKE MAINIT online at 0033H (Unplanned Outage) [WEBSMS] | CMIN
7/14/2024 1:09:28 AM | Mindanao Grid-07/14/2024 01:16: LAKE MAINIT Hydro with 7.6MW load tripped at 0023H. Indication: Shutdown from external (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 11:58:07 PM | Mindanao Grid-07/14/2024 00:04: Manolo Fortich - Maramag 138kV L2 energized at 2356H. (Planned Outage) [WEBSMS] | CMIN
7/13/2024 10:04:45 PM | Mindanao Grid-07/13/2024 22:11: SBPI MACO BESS online at 2203H (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 9:49:44 PM | [NSO Update] Visayas Grid-07/13/2024 21:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2147H with power going to Luzon. [WEBSMS] | CVIS
7/13/2024 9:49:25 PM | [NSO Update] Luzon Grid-07/13/2024 21:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2147H with power going to Luzon. [WEBSMS] | CLUZ
7/13/2024 9:37:43 PM | [NSO Update] Luzon Grid-07/13/2024 21:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2136H from reverse power direction. [WEBSMS] | CLUZ
7/13/2024 9:37:07 PM | [NSO Update] Visayas Grid-07/13/2024 21:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2136H from reverse power direction. [WEBSMS] | CVIS
7/13/2024 8:08:29 PM | Mindanao Grid-07/13/2024 20:15: TM2 Unit 1 declared available at 1917H (Unplanned Outage). [WEBSMS] | CMIN
7/13/2024 8:07:21 PM | Mindanao Grid-07/13/2024 20:13: TM2 Unit 1 failed to synchronized at 1831H on MRU-System Voltage dispatch instruction (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 7:59:11 PM | Mindanao Grid-07/13/2024 20:05: LAKE MAINIT Hydro online at 1911H (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 7:58:17 PM | Mindanao Grid-07/13/2024 20:04: SEDI (EEI) online at 1801H (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 7:56:44 PM | Mindanao Grid-07/13/2024 20:03: SEDI (EEI) Unit 3 with 4.6MW load tripped at 1752H. Indication: Overfrequency (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 7:48:25 PM | Mindanao Grid-07/13/2024 19:55: LAKE MAINIT Hydro with 7.6MW tripped at 1751H. Indication: Undervoltage (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 7:20:50 PM | Mindanao Grid-07/13/2024 19:27: Jasaan - Butuan 138kV L energized at 1918H. (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 7:18:53 PM | Visayas Grid-07/13/2024 19:18: PGPP1 U3 on line at 1912H (Unplanned Outage) [WEBSMS] | CVIS
7/13/2024 7:14:38 PM | Visayas Grid-07/13/2024 19:14: Dumanjug SS 230 kV bus 1 energized at 1913H (Planned Outage) [WEBSMS] | CVIS
7/13/2024 7:01:18 PM | Luzon Grid-07/13/2024 19:01: Calaca - Amadeo 230kV Line 2 restored at 1900H (Planned Outage) [WEBSMS] | CLUZ
7/13/2024 6:54:09 PM | Mindanao Grid-07/13/2024 19:00: Jasaan - Nasipit 138kV line energized at 1851H . (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 6:36:51 PM | Mindanao Grid-07/13/2024 18:43: MACO BESS with -12MW load tripped at 1752H (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 6:14:47 PM | Luzon Grid-07/13/2024 18:14: San Esteban SS 230kV Bus 1 restored at 1813H (Planned Outage) [WEBSMS] | CLUZ
7/13/2024 6:12:06 PM | Mindanao Grid-07/13/2024 18:18: Jasaan - Nasipit 138kV L and Jasaan - Butuan 138kV L simultaneously at 1751H causing SIPS activation tripping multiple feeders. Details to follow. (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 5:51:50 PM | [NSO Update] Luzon Grid-07/13/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12392MW, PK=10795MW, RR=311MW, NetOpMargin: EVE=1286 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @315MW, Masinloc 3 @300MW, Ilijan A @500MW, Sual 1 @500MW, Sual 2 @500MW [WEBSMS] | CLUZ
7/13/2024 5:38:51 PM | [NSO Update] Mindanao Grid-07/13/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2823MW, PK=2101MW, RR=73MW, NetOpMargin: EVE=650 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
7/13/2024 5:38:06 PM | [NSO Update] Visayas Grid-07/13/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2317MW, PK=1995MW, RR=91MW, NetOpMargin: EVE=231 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @267MW, PGPP1 @75MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-3 @4MW, PB104-2 @5.5MW, PDPP3-E @8MW, PDPP3-G @12MW, PDPP1-2 @4MW, PB101-2 @5.5MW, PB104-3 @5MW [WEBSMS] | CVIS
7/13/2024 5:24:53 PM | Luzon Grid-07/13/2024 17:24: Ilijan SS 500kV Bus 2 restored at 1724H (Planned Outage) [WEBSMS] | CLUZ
7/13/2024 4:52:00 PM | [NSO Update] Visayas Grid-07/13/2024 16:52: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1634H with power going to Visayas. [WEBSMS] | CVIS
7/13/2024 4:51:44 PM | [NSO Update] Luzon Grid-07/13/2024 16:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1634H with power going to Visayas. [WEBSMS] | CLUZ
7/13/2024 4:06:27 PM | Visayas Grid-07/13/2024 16:06: PGPP1 U3 tripped at 1602H (Unplanned Outage) [WEBSMS] | CVIS
7/13/2024 4:04:40 PM | [NSO Update] Luzon Grid-07/13/2024 16:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1601H from reverse power direction. [WEBSMS] | CLUZ
7/13/2024 4:03:56 PM | [NSO Update] Visayas Grid-07/13/2024 16:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1601H from reverse power direction. [WEBSMS] | CVIS
7/13/2024 4:01:53 PM | Visayas Grid-07/13/2024 16:01: Carcon-2nd Lift 34.5 kV line energized at 1559H (Unplanned Outage) [WEBSMS] | CVIS
7/13/2024 3:35:02 PM | Mindanao Grid-07/13/2024 15:41: LIANGAN Hydro tripped at 1530H. Indication: Reverse Power. Note: Unit under test and commissioning (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 2:46:43 PM | [NSO Update] Luzon Grid-07/13/2024 14:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1442H with power going to Visayas. [WEBSMS] | CLUZ
7/13/2024 2:46:19 PM | [NSO Update] Visayas Grid-07/13/2024 14:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1442H with power going to Visayas. [WEBSMS] | CVIS
7/13/2024 2:21:59 PM | [NSO Update] Luzon Grid-07/13/2024 14:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1420H from forward power direction. [WEBSMS] | CLUZ
7/13/2024 2:21:31 PM | [NSO Update] Visayas Grid-07/13/2024 14:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1420H from forward power direction. [WEBSMS] | CVIS
7/13/2024 1:44:18 PM | Visayas Grid-07/13/2024 13:44: CEDC Unit #1 cut-out/ cut-in, 0753H/1339H (Unplanned Outage) [WEBSMS] | CVIS
7/13/2024 12:51:37 PM | [NSO Update] Mindanao Grid-07/13/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2854MW, PK=2038MW, RR=73MW, NetOpMargin: PM=744, EVE=709 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
7/13/2024 12:48:20 PM | [NSO Update] Visayas Grid-07/13/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2298MW, PK=2022MW, RR=91MW, NetOpMargin: PM=185, EVE=208 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @260MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-3 @4MW, PB104-2 @5.5MW, PDPP3-E @8MW, PDPP3-G @12MW, PDPP1-2 @4MW, PB101-2 @5.5MW, PB104-3 @5MW [WEBSMS] | CVIS
7/13/2024 12:45:44 PM | [NSO Update] Luzon Grid-07/13/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13821MW, PK=11109MW, RR=334MW, NetOpMargin: PM=2378, EVE=1168 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @300MW, Masinloc 3 @290MW, Ilijan A @400MW [WEBSMS] | CLUZ
7/13/2024 12:26:45 PM | Mindanao Grid-07/13/2024 12:33: TSI (DCP) Unit 1 declared full capability of 150MW gross at 1150H. [WEBSMS] | CMIN
7/13/2024 12:10:11 PM | Mindanao Grid-07/13/2024 12:16: LIANGAN Hydro online at 0937H. Test and Commissioning. [WEBSMS] | CMIN
7/13/2024 12:09:12 PM | Luzon Grid-07/13/2024 12:09: San Gabriel online at 1200H (Reserve Shutdown) [WEBSMS] | CLUZ
7/13/2024 11:13:05 AM | Mindanao Grid-07/13/2024 11:19: LAKE MAINIT Hydro online at 1111H (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 10:52:03 AM | Mindanao Grid-07/13/2024 10:58: LAKE MAINIT Hydro with 7.6MW load isolated at 0938H due to outage of customer-owned Butuan-Santiago 69 kV feeder (Unplanned Outage) [WEBSMS] | CMIN
7/13/2024 10:46:37 AM | Luzon Grid-07/13/2024 10:46: Calaca 1 shutdown at 1043H (Unplanned Outage) [WEBSMS] | CLUZ
7/13/2024 10:46:05 AM | Mindanao Grid-07/13/2024 10:52: TSI (DCP) Unit 1 derated to 100MW gross (from 150MW gross) at 0934H due to governor problem. [WEBSMS] | CMIN
7/13/2024 8:12:58 AM | Luzon Grid-07/13/2024 08:13: Pagbilao PP SS 230kV Bus 1 de-energized at 0812H (Planned Outage) [WEBSMS] | CLUZ
7/13/2024 7:17:44 AM | Luzon Grid-07/13/2024 07:17: Quezon-Mexico 230kV Line restored at 0716H (Planned Outage) [WEBSMS] | CLUZ
7/13/2024 7:02:16 AM | Luzon Grid-07/13/2024 07:02: San Esteban SS 230kV Bus 1 de-energized at 0701H (Planned Outage) [WEBSMS] | CLUZ
7/13/2024 7:00:17 AM | Mindanao Grid-07/13/2024 07:06: Manolo Fortich - Maramag 138kV L2 de-energized at 0654H. (Planned Outage) [WEBSMS] | CMIN
7/13/2024 6:50:18 AM | Luzon Grid-07/13/2024 06:50: Calaca-Amadeo 230kV Line 2 de-energized at 0649H (Planned Outage) [WEBSMS] | CLUZ
7/13/2024 6:30:14 AM | Luzon Grid-07/13/2024 06:30: Ilijan SS 500kV Bus 2 de-energized at 0628H (Planned Outage) [WEBSMS] | CLUZ
7/13/2024 5:49:26 AM | Luzon Grid-07/13/2024 05:49: San Gabriel shutdown at 0545H. (Reserve Shutdown) [WEBSMS] | CLUZ
7/13/2024 5:46:51 AM | [NSO Update] Mindanao Grid-07/13/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2866MW, PK=1891MW, RR=73MW, NetOpMargin: AM=902, PM=633, EVE=564 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
7/13/2024 5:46:32 AM | [NSO Update] Visayas Grid-07/13/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2304MW, PK=1964MW, RR=91MW, NetOpMargin: AM=249, PM=284, EVE=252 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @267MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-3 @4MW, PB104-2 @5.5MW, PDPP3-E @8MW, PDPP3-G @12MW, PDPP1-2 @3.5MW, PDPP1-5 @4MW, PB101-2 @5.5MW, PB104-3 @5MW [WEBSMS] | CVIS
7/13/2024 5:46:29 AM | [NSO Update] Luzon Grid-07/13/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14228MW, PK=10958MW, RR=334MW, NetOpMargin: AM=2936, PM=2858, EVE=1545 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @300MW, Masinloc 3 @290MW, Ilijan A @400MW [WEBSMS] | CLUZ
7/13/2024 5:10:25 AM | Luzon Grid-07/13/2024 05:10: Quezon-Mexico 230kV line was de-energized at 0507H. (Planned Outage) [WEBSMS] | CLUZ
7/13/2024 4:31:32 AM | Luzon Grid-07/13/2024 04:31: Batangas 230kV Bus 1 was energized at 0427H (Planned Outage) [WEBSMS] | CLUZ
7/13/2024 4:14:52 AM | [NSO Update] Mindanao Grid-07/13/2024 04:21: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
7/13/2024 4:14:30 AM | [NSO Update] Visayas Grid-07/13/2024 04:14: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
7/13/2024 4:14:27 AM | [NSO Update] Luzon Grid-07/13/2024 04:14: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/13/2024 1:24:03 AM | Luzon Grid-07/13/2024 01:24: Sta Rita 230kV Bus 1 and San Lorenzo 230kV Bus 1 were looped at 0123H. [WEBSMS] | CLUZ
7/13/2024 1:12:09 AM | Luzon Grid-07/13/2024 01:12: Batangas 230kV Bus 1 was de-energized at 0111H. (Planned Outage) [WEBSMS] | CLUZ
7/13/2024 1:03:39 AM | Luzon Grid-07/13/2024 01:03: Sta Rita 230kV Bus 2 and San Lorenzo 230kV Bus 2 were looped at 0101H. [WEBSMS] | CLUZ
7/13/2024 12:19:39 AM | Luzon Grid-07/13/2024 00:19: Batangas 300MVA T04 and T05 were unparalleled at the 69kV side at 0013H. (Preparation for the looping Sta Rita-San Lorenzo 230kV Busses. [WEBSMS] | CLUZ
7/12/2024 11:40:50 PM | Luzon Grid-07/12/2024 23:40: Sta Rita Module 40 shutdown at 2340H. (Planned Outage) [WEBSMS] | CLUZ
7/12/2024 11:26:37 PM | Luzon Grid-07/12/2024 23:26: Sta Rita Module 30 shutdown at 2324H. (Planned Outage) [WEBSMS] | CLUZ
7/12/2024 10:22:17 PM | [NSO Update] Visayas Grid-07/12/2024 22:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2221H with power going to Luzon. [WEBSMS] | CVIS
7/12/2024 10:22:15 PM | [NSO Update] Luzon Grid-07/12/2024 22:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2221H with power going to Luzon. [WEBSMS] | CLUZ
7/12/2024 10:14:05 PM | [NSO Update] Luzon Grid-07/12/2024 22:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2211H from reverse power direction. [WEBSMS] | CLUZ
7/12/2024 10:13:00 PM | [NSO Update] Visayas Grid-07/12/2024 22:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2211H from reverse power direction. [WEBSMS] | CVIS
7/12/2024 5:44:57 PM | [NSO Update] Mindanao Grid-07/12/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2824MW, PK=2107MW, RR=73MW, NetOpMargin: EVE=645 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
7/12/2024 5:44:16 PM | [NSO Update] Visayas Grid-07/12/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2435MW, PK=2054MW, RR=91MW, NetOpMargin: EVE=290 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @260MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-3 @4MW, PB104-2 @5.5MW, PDPP3-E @8MW, PDPP3-G @12MW, PDPP1-2 @3.5MW, PDPP1-5 @4MW, PB101-2 @5.5MW, PB104-3 @5MW, PB104-4 @7MW [WEBSMS] | CVIS
7/12/2024 5:41:20 PM | [NSO Update] Luzon Grid-07/12/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13617MW, PK=11439MW, RR=445MW, NetOpMargin: EVE=1733 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @300MW, Masinloc 3 @290MW, Ilijan A @400MW [WEBSMS] | CLUZ
7/12/2024 5:22:10 PM | Luzon Grid-07/12/2024 17:22: Laoag-EDC Burgos Wind Farm 115kV line was restored at 1720H. (Planned Outage) [WEBSMS] | CLUZ
7/12/2024 4:33:22 PM | Mindanao Grid-07/12/2024 16:39: Pulangi 4 Unit 3 online at 1607H. (Unplanned Outage) [WEBSMS] | CMIN
7/12/2024 2:06:10 PM | Mindanao Grid-07/12/2024 14:12: WMPC DG02 shutdown at 1351H. End of Dispatchable Reserve utilization. Advised to stop at 1334H. [WEBSMS] | CMIN
7/12/2024 2:05:13 PM | Mindanao Grid-07/12/2024 14:11: WMPC DG03 shutdown at 1345H. End of Dispatchable Reserve utilization. Advised to stop at 1336H. [WEBSMS] | CMIN
7/12/2024 1:27:35 PM | Mindanao Grid-07/12/2024 13:34: WMPC DG03 online at 1315H. Utilized as 10MW Dispatchable Reserve. Call Time: 1253H. [WEBSMS] | CMIN
7/12/2024 1:26:40 PM | Mindanao Grid-07/12/2024 13:33: WMPC DG02 online at 1315H. Utilized as 10MW Dispatchable Reserve. Call Time: 1253H. [WEBSMS] | CMIN
7/12/2024 12:58:32 PM | [NSO Update] Mindanao Grid-07/12/2024 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2773MW, PK=2299MW, RR=73MW, NetOpMargin: PM=401, EVE=530 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
7/12/2024 12:53:28 PM | [NSO Update] Visayas Grid-07/12/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2546MW, PK=2191MW, RR=91MW, NetOpMargin: PM=263, EVE=217 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @260MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-3 @4MW, PB104-2 @5.5MW, PDPP3-E @8MW, PDPP3-G @12MW, PDPP1-2 @4MW, PDPP1-5 @4MW [WEBSMS] | CVIS
7/12/2024 12:51:51 PM | [NSO Update] Luzon Grid-07/12/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14649MW, PK=12517MW, RR=334MW, NetOpMargin: PM=1797, EVE=1431 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @290MW, Masinloc 3 @330MW, Ilijan A @400MW, Calaca 1 @190MW [WEBSMS] | CLUZ
7/12/2024 12:50:22 PM | Mindanao Grid-07/12/2024 12:56: Pulangi IV HEP Unit 3 tripped at 1241H. (Unplanned Outage). [WEBSMS] | CMIN
7/12/2024 12:27:40 PM | Luzon Grid-07/12/2024 12:27: San Jose-Tayabas 500kV L1 restored at 1226H (Unplanned Outage) [WEBSMS] | CLUZ
7/12/2024 11:48:47 AM | Luzon Grid-07/12/2024 11:48: SLPGC 1 shutdown at 1146H (Unplanned Outage) [WEBSMS] | CLUZ
7/12/2024 11:46:58 AM | Luzon Grid-07/12/2024 11:46: San Jose-Tayabas tripped at 1144H (Unplanned Outage) [WEBSMS] | CLUZ
7/12/2024 11:01:33 AM | Luzon Grid-07/12/2024 11:01: San Gabriel online at 1056H (Reserved Shutdown) [WEBSMS] | CLUZ
7/12/2024 8:26:07 AM | Visayas Grid-07/12/2024 08:26: Dumanjug SS 230kV Bus 1 de-energized at 0817H (Planned Outage) [WEBSMS] | CVIS
7/12/2024 7:24:20 AM | [NSO Update] Visayas Grid-07/12/2024 07:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0702H with power going to Visayas [WEBSMS] | CVIS
7/12/2024 7:24:09 AM | [NSO Update] Luzon Grid-07/12/2024 07:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0702H with power going to Visayas [WEBSMS] | CLUZ
7/12/2024 7:21:39 AM | [NSO Update] Visayas Grid-07/12/2024 07:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0647H from forward power direction [WEBSMS] | CVIS
7/12/2024 7:21:26 AM | [NSO Update] Luzon Grid-07/12/2024 07:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0647H from forward power direction [WEBSMS] | CLUZ
7/12/2024 5:49:09 AM | [NSO Update] Mindanao Grid-07/12/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2869MW, PK=2252MW, RR=73MW, NetOpMargin: AM=544, PM=382, EVE=454 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
7/12/2024 5:47:26 AM | [NSO Update] Visayas Grid-07/12/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2740MW, PK=2166MW, RR=91MW, NetOpMargin: AM=483, PM=334, EVE=297 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @264MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-3 @4MW, PB104-2 @5.5MW, PDPP3-E @8MW, PDPP3-G @12MW, PDPP1-2 @4MW, PDPP1-5 @4MW [WEBSMS] | CVIS
7/12/2024 5:43:56 AM | [NSO Update] Luzon Grid-07/12/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14948MW, PK=11548MW, RR=334MW, NetOpMargin: AM=3066, PM=2354, EVE=1995 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @290MW, Masinloc 3 @330MW, Ilijan A @400MW, Calaca 1 @190MW [WEBSMS] | CLUZ
7/12/2024 5:16:46 AM | Luzon Grid-07/12/2024 05:16: Laoag-EDC Burgos Wind Farm 115kV Line (CO) de-energized at 0516H (Planned Outage) [WEBSMS] | CLUZ
7/12/2024 4:22:33 AM | [NSO Update] Visayas Grid-07/12/2024 04:22: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
7/12/2024 4:22:06 AM | [NSO Update] Luzon Grid-07/12/2024 04:22: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/12/2024 4:22:03 AM | [NSO Update] Mindanao Grid-07/12/2024 04:28: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
7/12/2024 3:31:43 AM | Luzon Grid-07/12/2024 03:31: San Jose - North Caloocan 115kV Line energized at 0329H (Planned Outage) [WEBSMS] | CLUZ
7/12/2024 2:31:28 AM | Luzon Grid-07/12/2024 02:31: San Gabriel shutdown at 0227H (Reserve shutdown) [WEBSMS] | CLUZ
7/12/2024 1:49:54 AM | Luzon Grid-07/12/2024 01:49: Sta. Rita 20 online at 0147H (Unplanned Outage) [WEBSMS] | CLUZ
7/11/2024 11:16:52 PM | Visayas Grid-07/11/2024 23:16: Dumanjug SS 150 MVA 230/138/13.8 kV TR1 energized at 2311H (Planned Outage) [WEBSMS] | CVIS
7/11/2024 11:14:30 PM | Visayas Grid-07/11/2024 23:14: Dumanjug SS 230 kV Bus 2 energized at 2300H (Planned Outage) [WEBSMS] | CVIS
7/11/2024 11:11:22 PM | Mindanao Grid-07/11/2024 23:17: SIGUIL Hydro online at 2309H. Root-cause: mechnical overspeeding (Unplanned Outage) [WEBSMS] | CMIN
7/11/2024 10:42:33 PM | [NSO Update] Luzon Grid-07/11/2024 22:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2241H with power going to Luzon. [WEBSMS] | CLUZ
7/11/2024 10:42:29 PM | [NSO Update] Visayas Grid-07/11/2024 22:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2241H with power going to Luzon. [WEBSMS] | CVIS
7/11/2024 10:30:42 PM | [NSO Update] Visayas Grid-07/11/2024 22:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2229H from reverse power direction. [WEBSMS] | CVIS
7/11/2024 10:30:36 PM | [NSO Update] Luzon Grid-07/11/2024 22:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2229H from reverse power direction. [WEBSMS] | CLUZ
7/11/2024 10:08:13 PM | Luzon Grid-07/11/2024 22:08: San Jose - North Caloocan 115kV Line de-energized at 2207H (Planned Outage) [WEBSMS] | CLUZ
7/11/2024 9:27:23 PM | Mindanao Grid-07/11/2024 21:33: WMPC DG10 declared available at 2125H. From forced outage. [WEBSMS] | CMIN
7/11/2024 9:19:24 PM | Mindanao Grid-07/11/2024 21:25: WMPC DG10 with 5.08MW load tripped at 2110H. Cause: HT low pressure stop. (Unplanned Outage) [WEBSMS] | CMIN
7/11/2024 9:12:56 PM | Mindanao Grid-07/11/2024 21:19: SIGUIL Hydro with 11.8MW load tripped at 2108H. Cause for verification. (Unplanned Outage) [WEBSMS] | CMIN
7/11/2024 8:44:13 PM | Luzon Grid-07/11/2024 20:44: Sta. Rita 20 emergency shutdown at 2043H (Unplanned Outage) [WEBSMS] | CLUZ
7/11/2024 8:01:58 PM | Mindanao Grid-07/11/2024 20:08: GNPK unit 2 declared full capability at 2000H with 151MW (gross). [WEBSMS] | CMIN
7/11/2024 7:17:53 PM | Mindanao Grid-07/11/2024 19:24: WMPC DG10 end of RPS-System Voltage Requirement at 1915H, converted to energy. [WEBSMS] | CMIN
7/11/2024 6:52:05 PM | Mindanao Grid-07/11/2024 18:58: GNPK Unit 2 derated to 120MW gross (from 151MW) due to tripped Mill C. [WEBSMS] | CMIN
7/11/2024 5:52:19 PM | [NSO Update] Luzon Grid-07/11/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13576MW, PK=11265MW, RR=454MW, NetOpMargin: EVE=1857 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, MSLC1 @290MW, MSLC3 @325MW, SLTEC 1 @119MW, SLTEC 2 @119MW, ILIJAN A @400MW, Limay 8 @60MW [WEBSMS] | CLUZ
7/11/2024 5:52:03 PM | [NSO Update] Mindanao Grid-07/11/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2813MW, PK=2224MW, RR=73MW, NetOpMargin: EVE=516 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/11/2024 5:51:59 PM | [NSO Update] Visayas Grid-07/11/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2508MW, PK=2131MW, RR=87MW, NetOpMargin: EVE=290 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @263MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-3 @4MW, PB104-2 @5.5MW, PB104-3 @5MW, PDPP3-G @12MW, PDPP1-2 @4MW, PDPP1-5 @4MW [WEBSMS] | CVIS
7/11/2024 5:08:37 PM | Luzon Grid-07/11/2024 17:08: Laoag-EDC Burgos Wind Farm 115kV Line (CO) restored at 1708H (Planned Outage) [WEBSMS] | CLUZ
7/11/2024 4:01:58 PM | Mindanao Grid-07/11/2024 16:08: LIANGAN Unit 2 shutdown at 1558H. End of commercial testing. [WEBSMS] | CMIN
7/11/2024 2:17:34 PM | Mindanao Grid-07/11/2024 14:24: WMPC DG04 declared available at 1155H (Unplanned Outage) [WEBSMS] | CMIN
7/11/2024 12:56:02 PM | [NSO Update] Mindanao Grid-07/11/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2842MW, PK=2413MW, RR=73MW, NetOpMargin: PM=356, EVE=456 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/11/2024 12:54:56 PM | [NSO Update] Visayas Grid-07/11/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2619MW, PK=2273MW, RR=91MW, NetOpMargin: PM=255, EVE=261 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @258MW, CEDC 3 @75MW, GTEC @7MW, PB104-4 @7MW, PB104-2 @5.5MW, PB104-3 @5MW, PDPP3-G @12MW, PDPP1-2 @4MW, PDPP1-5 @4MW [WEBSMS] | CVIS
7/11/2024 12:50:02 PM | [NSO Update] Luzon Grid-07/11/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14634MW, PK=12125MW, RR=334MW, NetOpMargin: PM=2175, EVE=1764 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, MSLC1 @325MW, MSLC3 @320MW, SLTEC 1 @119MW, SLTEC 2 @119MW, ILIJAN A @400MW, Limay 8 @60MW [WEBSMS] | CLUZ
7/11/2024 11:43:16 AM | Luzon Grid-07/11/2024 11:43: San Jose-Tayabas 500kV L1 tripped/reclosed at 1138H (Unplanned Outage) [WEBSMS] | CLUZ
7/11/2024 11:28:47 AM | Mindanao Grid-07/11/2024 11:35: MANOLO FORTICH 2 online at 1121H (Unplanned Outage, outside management control) [WEBSMS] | CMIN
7/11/2024 11:16:26 AM | Mindanao Grid-07/11/2024 11:22: Manolo Fortich - Manolo HEDCOR 2 HEPP (7LI2MNO-MN2) 138kV L2 restored at 1106H. From Unplanned Outage. [WEBSMS] | CMIN
7/11/2024 10:22:40 AM | Mindanao Grid-07/11/2024 10:29: Tagoloan-Manolo 138kV L2 (7LI2TAG-MNO) energized/restored at 1015H. From Planned Outage/Non-GOMP [WEBSMS] | CMIN
7/11/2024 10:03:04 AM | Mindanao Grid-07/11/2024 10:09: Liangan Unit 2 online at 1000H. Commercial Testing. [WEBSMS] | CMIN
7/11/2024 9:54:06 AM | Mindanao Grid-07/11/2024 10:00: WMPC DG04 with 3.85MW load tripped at 0931H. Indication: Turbo charge alarm B-bank compressor-side. (Unplanned Outage) [WEBSMS] | CMIN
7/11/2024 9:52:33 AM | Mindanao Grid-07/11/2024 09:59: WMPC DG10 online at 0950H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/11/2024 9:41:35 AM | Mindanao Grid-07/11/2024 09:48: WMPC DG04 online at 0927H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/11/2024 9:06:51 AM | Mindanao Grid-07/11/2024 09:13: Manolo Fortich - Manolo HEDCOR 2 (7LI2MNO-MN2) 138kV L2 shutdown at 0900H. (Unplanned Outage) [WEBSMS] | CMIN
7/11/2024 8:49:39 AM | Mindanao Grid-07/11/2024 08:56: MANOLO FORTICH 2 with 23.7MW load emergency shutdown at 0840H due to shutdown of Tagoloan-Manolo Fortich 2 138 kV Line to facilitate line right-of-way clearing (Unplanned Outage). [WEBSMS] | CMIN
7/11/2024 8:16:58 AM | Mindanao Grid-07/11/2024 08:23: SMC Unit 1 with 30MW remaining load (from 130MW) emergency shutdown at 0807H due to boiler tube leak. Lowest frequency=59.584Hz (Unplanned Outage) [WEBSMS] | CMIN
7/11/2024 8:13:07 AM | Mindanao Grid-07/11/2024 08:19: Tagoloan-Manolo 138kV L2 (7LI2TAG-MNO) deenergized at 0808H. (Planned Outage/Non-GOMP) [WEBSMS] | CMIN
7/11/2024 6:30:19 AM | [NSO Update] Visayas Grid-07/11/2024 06:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0628H with power going to Visayas. [WEBSMS] | CVIS
7/11/2024 6:29:57 AM | [NSO Update] Luzon Grid-07/11/2024 06:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0628H with power going to Visayas. [WEBSMS] | CLUZ
7/11/2024 6:23:10 AM | [NSO Update] Luzon Grid-07/11/2024 06:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0617H from forward power direction. [WEBSMS] | CLUZ
7/11/2024 6:22:43 AM | [NSO Update] Visayas Grid-07/11/2024 06:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0617H from forward power direction. [WEBSMS] | CVIS
7/11/2024 5:57:53 AM | [NSO Update] Mindanao Grid-07/11/2024 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2997MW, PK=2212MW, RR=73MW, NetOpMargin: AM=711, PM=570, EVE=646 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @30.5MW [WEBSMS] | CMIN
7/11/2024 5:55:56 AM | [NSO Update] Visayas Grid-07/11/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2432MW, PK=2165MW, RR=91MW, NetOpMargin: AM=176, PM=232, EVE=260 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @258MW, CEDC 3 @75MW, GTEC @7MW, PB104-4 @7MW, PB104-2 @6MW, PDPP3-E @8MW, PDPP3-G @12MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP3-H @8MW [WEBSMS] | CVIS
7/11/2024 5:53:01 AM | [NSO Update] Luzon Grid-07/11/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14571MW, PK=11737MW, RR=334MW, NetOpMargin: AM=2500, PM=1715, EVE=1339 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @325MW, Masinloc 3 @320MW, Ilijan A @400MW, Calaca 1 @120MW, San Lorenzo 60 @80MW [WEBSMS] | CLUZ
7/11/2024 5:16:13 AM | Luzon Grid-07/11/2024 05:16: Laoag-EDC Burgos Wind Farm 115kV Line (CO) de-energized at 0515H (Planned Outage) [WEBSMS] | CLUZ
7/11/2024 4:35:58 AM | Luzon Grid-07/11/2024 04:36: Limay-PAVI Green ORS 69kV Line restored at 0434H (Planned Outage) [WEBSMS] | CLUZ
7/11/2024 4:22:22 AM | Luzon Grid-07/11/2024 04:22: Limay - Limay BESS 69kV Line energized at 0422H (Planned Outage) [WEBSMS] | CLUZ
7/11/2024 4:14:39 AM | [NSO Update] Mindanao Grid-07/11/2024 04:21: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
7/11/2024 4:14:24 AM | [NSO Update] Visayas Grid-07/11/2024 04:14: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
7/11/2024 4:14:13 AM | [NSO Update] Luzon Grid-07/11/2024 04:14: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/11/2024 3:06:26 AM | Luzon Grid-07/11/2024 03:06: Limay - Limay UPSI BESS 69kV Line de-energized at 0302H (Planned Outage) [WEBSMS] | CLUZ
7/11/2024 1:10:45 AM | Luzon Grid-07/11/2024 01:10: Calaca 1 online at 0105H (Unplanned Outage) [WEBSMS] | CLUZ
7/11/2024 12:14:06 AM | Luzon Grid-07/11/2024 00:14: Limay-PAVI Green ORS 69kV Line de-energized at 0006H (Planned Outage) [WEBSMS] | CLUZ
7/10/2024 10:50:52 PM | [NSO Update] Visayas Grid-07/10/2024 22:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2249H with power going to Luzon. [WEBSMS] | CVIS
7/10/2024 10:50:36 PM | [NSO Update] Luzon Grid-07/10/2024 22:50: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2249H with power going to Luzon. [WEBSMS] | CLUZ
7/10/2024 10:39:26 PM | [NSO Update] Visayas Grid-07/10/2024 22:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2238H from reverse power direction. [WEBSMS] | CVIS
7/10/2024 10:39:05 PM | [NSO Update] Luzon Grid-07/10/2024 22:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2238H from reverse power direction. [WEBSMS] | CLUZ
7/10/2024 10:36:57 PM | Luzon Grid-07/10/2024 22:37: San Lorenzo 60 online at 2234H (Unplanned Outage) [WEBSMS] | CLUZ
7/10/2024 9:00:32 PM | Luzon Grid-07/10/2024 21:00: San Lorenzo 60 tripped at 2053H @14MW from 80MW (Unplanned Outage) [WEBSMS] | CLUZ
7/10/2024 8:05:49 PM | Luzon Grid-07/10/2024 20:06: San Lorenzo 60 online at 2004H (Planned Outage) [WEBSMS] | CLUZ
7/10/2024 7:31:38 PM | Mindanao Grid-07/10/2024 19:38: WMPC DG04 Shutdown at 1916H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/10/2024 6:35:28 PM | Luzon Grid-07/10/2024 18:35: Gumaca-Labo 230kV Line 1 restored at 1833H (Unplanned Outage) [WEBSMS] | CLUZ
7/10/2024 6:33:36 PM | Luzon Grid-07/10/2024 18:33: Correction: Gumaca-Labo 230kV Line 1 & 2 simultaneously tripped at 1811H. Gumaca-Labo 230kV Line 2 successfully reclosed both side (Unplanned Outage) [WEBSMS] | CLUZ
7/10/2024 6:30:55 PM | Luzon Grid-07/10/2024 18:31: Gumaca-Labo 230kV Line 1 & 2 simultaneously tripped at 1811H. Gumaca-Labo 230kV Line 2 successfully reclosed both side. (Planned Outage) [WEBSMS] | CLUZ
7/10/2024 5:47:41 PM | [NSO Update] Mindanao Grid-07/10/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2913MW, PK=2296MW, RR=73MW, NetOpMargin: EVE=544 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @30.5MW [WEBSMS] | CMIN
7/10/2024 5:46:16 PM | [NSO Update] Visayas Grid-07/10/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2505MW, PK=2143MW, RR=91MW, NetOpMargin: EVE=270 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @258MW, CEDC 3 @75MW, GTEC @7MW, PB104-4 @7MW, PB104-2 @5.5MW, PDPP3-E @8MW, PDPP3-G @12MW, PDPP1-2 @4MW, PDPP1-3 @4MW, PDPP1-5 @4MW [WEBSMS] | CVIS
7/10/2024 5:41:10 PM | [NSO Update] Luzon Grid-07/10/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13316MW, PK=11247MW, RR=454MW, NetOpMargin: EVE=1615 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @325MW, Masinloc 3 @325MW, Ilijan A @400MW [WEBSMS] | CLUZ
7/10/2024 5:20:21 PM | Luzon Grid-07/10/2024 17:20: Laoag-EDC Burgos Wind Farm 115kV Line (CO) restored at 1716H (Planned Outage) [WEBSMS] | CLUZ
7/10/2024 4:45:59 PM | Mindanao Grid-07/10/2024 16:52: WMPC DG07 Shutdown at 1641H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/10/2024 1:37:17 PM | Mindanao Grid-07/10/2024 13:44: WMPC DG07 Online at 1326H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/10/2024 1:22:06 PM | Mindanao Grid-07/10/2024 13:28: Talomo 2 Unit 1 shutdown at 1302H. (Planned Outage). [WEBSMS] | CMIN
7/10/2024 1:19:07 PM | Mindanao Grid-07/10/2024 13:25: Agus 2 - Kibawe 138KV Line 2 Energized at 1314H. Note: Energized up to Tower 33 only for anti pilferage purposes. (Unplanned Outage) [WEBSMS] | CMIN
7/10/2024 12:58:37 PM | [NSO Update] Luzon Grid-07/10/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14288MW, PK=11954MW, RR=334MW, NetOpMargin: PM=2000, EVE=917 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @90MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @325MW, Masinloc 3 @325MW, Ilijan A @400MW [WEBSMS] | CLUZ
7/10/2024 12:35:51 PM | [NSO Update] Mindanao Grid-07/10/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2953MW, PK=2379MW, RR=73MW, NetOpMargin: PM=502, EVE=570 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/10/2024 12:34:28 PM | [NSO Update] Visayas Grid-07/10/2024 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2691MW, PK=2235MW, RR=91MW, NetOpMargin: PM=365, EVE=302 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @258MW, CEDC 3 @75MW, GTEC @7MW, PDPP3-E @8MW, PDPP3-G @12MW [WEBSMS] | CVIS
7/10/2024 12:26:35 PM | Mindanao Grid-07/10/2024 12:33: Talomo 2 Unit 2 online at 1112H (Planned Outage). [WEBSMS] | CMIN
7/10/2024 12:24:31 PM | Mindanao Grid-07/10/2024 12:31: Agus 7 HEP U2 online at 1000H (Planned Outage). [WEBSMS] | CMIN
7/10/2024 10:01:04 AM | Mindanao Grid-07/10/2024 10:07: Talomo 2 Unit 2 shutdown at 0957H (Planned Outage). [WEBSMS] | CMIN
7/10/2024 10:00:23 AM | Mindanao Grid-07/10/2024 10:07: Talomo 2 Unit 3 online at 0956H (Planned Outage). [WEBSMS] | CMIN
7/10/2024 9:50:52 AM | Mindanao Grid-07/10/2024 09:57: WMPC DG04 Online at 0948H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/10/2024 9:09:06 AM | Luzon Grid-07/10/2024 09:09: Nagsaag PCB 9-02CB04NGS tripped at 0904H and was closed at 0907H.(Unplanned Outage-No affected line) [WEBSMS] | CLUZ
7/10/2024 8:44:12 AM | Mindanao Grid-07/10/2024 08:50: Talomo 2 Unit 3 shutdown at 0831H (Planned Outage). [WEBSMS] | CMIN
7/10/2024 8:37:29 AM | Visayas Grid-07/10/2024 08:37: Dumanjug SS 230 kV Bus 2 de-energized at 0835H (Planned Outage) [WEBSMS] | CVIS
7/10/2024 8:27:05 AM | Visayas Grid-07/10/2024 08:27: Dumanjug SS 150 MVA 230/138/13.8 kV TR1 de-energized at 0825H (Planned Outage) [WEBSMS] | CVIS
7/10/2024 8:20:40 AM | Mindanao Grid-07/10/2024 08:27: Agus 7 HEP U2 shutdown at 0802H (Planned Outage). [WEBSMS] | CMIN
7/10/2024 6:46:51 AM | [NSO Update] Visayas Grid-07/10/2024 06:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0644H with power going to Visayas. [WEBSMS] | CVIS
7/10/2024 6:46:14 AM | [NSO Update] Luzon Grid-07/10/2024 06:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0644H with power going to Visayas. [WEBSMS] | CLUZ
7/10/2024 6:41:16 AM | [NSO Update] Luzon Grid-07/10/2024 06:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0631H from forward power direction. [WEBSMS] | CLUZ
7/10/2024 6:36:35 AM | [NSO Update] Visayas Grid-07/10/2024 06:36: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0631H from forward power direction. [WEBSMS] | CVIS
7/10/2024 5:48:10 AM | [NSO Update] Mindanao Grid-07/10/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2942MW, PK=2225MW, RR=73MW, NetOpMargin: AM=644, PM=566, EVE=617 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/10/2024 5:33:36 AM | [NSO Update] Visayas Grid-07/10/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2663MW, PK=2129MW, RR=91MW, NetOpMargin: AM=442, PM=378, EVE=333 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @258MW, CEDC 3 @75MW, GTEC @7MW, PB104-4 @7MW, PB104-2 @5.5MW, PDPP3-E @8MW, PDPP3-G @12MW, PDPP1-2 @4MW, PDPP1-3 @4MW [WEBSMS] | CVIS
7/10/2024 5:29:20 AM | [NSO Update] Luzon Grid-07/10/2024 05:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14405MW, PK=11677MW, RR=334MW, NetOpMargin: AM=2394, PM=1160, EVE=1210 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @90MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @325MW, Masinloc 3 @330MW [WEBSMS] | CLUZ
7/10/2024 5:29:08 AM | [NSO Update] Luzon Grid-07/10/2024 05:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14405MW, PK=11677MW, RR=334MW, NetOpMargin: AM=2394, PM=1160, EVE=1210 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @90MW, SLTEC 2 @119MW, Limay 8 @60MW, Masinloc 1 @325MW, Masinloc 3 @330MW [WEBSMS] | CLUZ
7/10/2024 5:05:52 AM | [NSO Update] Mindanao Grid-07/10/2024 05:12: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
7/10/2024 5:05:40 AM | [NSO Update] Visayas Grid-07/10/2024 05:05: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
7/10/2024 5:05:29 AM | [NSO Update] Luzon Grid-07/10/2024 05:05: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/10/2024 5:03:36 AM | Luzon Grid-07/10/2024 05:03: Laoag-EDC Burgos Wind Farm 115kV Line (CO) de-energized at 0503H (Planned Outage) [WEBSMS] | CLUZ
7/10/2024 4:55:49 AM | Luzon Grid-07/10/2024 04:56: Ilijan A GT 1-2 online at 0453H. (Unplanned Outage) [WEBSMS] | CLUZ
7/10/2024 3:43:26 AM | Visayas Grid-07/10/2024 03:43: Carcon-Sangi 34.5kV Line 3 close loop at Sangi side at 0340H (Unplanned Outage) [WEBSMS] | CVIS
7/10/2024 3:37:56 AM | Visayas Grid-07/10/2024 03:38: Carcon-Sangi 34.5kV Line 3 tripped at Sangi side at 0319H (Unplanned Outage) [WEBSMS] | CVIS
7/10/2024 2:43:10 AM | Luzon Grid-07/10/2024 02:43: Ilijan ST 1 online at 0235H (Unplanned Outage) [WEBSMS] | CLUZ
7/10/2024 2:35:52 AM | Visayas Grid-07/10/2024 02:36: Carcon-2nd Lift 34.5kV line tripped at 0228H (Unplanned Outage) [WEBSMS] | CVIS
7/10/2024 1:38:13 AM | Luzon Grid-07/10/2024 01:38: Ilijan A GT1-1 online at 0137H (Unplanned Outage) [WEBSMS] | CLUZ
7/10/2024 1:32:40 AM | Mindanao Grid-07/10/2024 01:39: LAMSAN (LSK) shutdown at 0001H. PMS-GOMP (Planned Outage). [WEBSMS] | CMIN
7/9/2024 11:48:29 PM | Visayas Grid-07/09/2024 23:48: PEDC U3 tripped at 2337H (Unplanned Outage) [WEBSMS] | CVIS
7/9/2024 10:05:39 PM | Mindanao Grid-07/09/2024 22:12: SEC 1 online at 2202H. (Unplanned Outage) [WEBSMS] | CMIN
7/9/2024 9:09:57 PM | [NSO Update] Visayas Grid-07/09/2024 21:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2109H with power going to Luzon [WEBSMS] | CVIS
7/9/2024 9:09:37 PM | [NSO Update] Luzon Grid-07/09/2024 21:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2109H with power going to Luzon [WEBSMS] | CLUZ
7/9/2024 9:01:38 PM | [NSO Update] Visayas Grid-07/09/2024 21:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2059H from reverse power direction [WEBSMS] | CVIS
7/9/2024 9:01:22 PM | [NSO Update] Luzon Grid-07/09/2024 21:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2059H from reverse power direction [WEBSMS] | CLUZ
7/9/2024 7:54:33 PM | Luzon Grid-07/09/2024 19:54: Ilijan A ST1 and GT 1-2 manually tripped at 1951H and 1952H, respectively. Lowest system frequency was 59.533Hz. (Unplanned Outage) [WEBSMS] | CLUZ
7/9/2024 7:41:23 PM | Luzon Grid-07/09/2024 19:41: Ilijan A GT 1-1 with 185MW manually tripped at 1937H. Lowest system frequency was 59.554Hz. (Unplanned Outage) [WEBSMS] | CLUZ
7/9/2024 6:03:34 PM | Mindanao Grid-07/09/2024 18:10: Baloi-Agus 2 138kV Line 1 energized/restored at 1800H. From Planned Outage/ Non-GOMP. [WEBSMS] | CMIN
7/9/2024 5:59:12 PM | Luzon Grid-07/09/2024 17:59: Laoag-EDC Burgos Wind Farm 115kV Line (CO) restored at 1758H (Planned Outage) [WEBSMS] | CLUZ
7/9/2024 5:41:14 PM | [NSO Update] Mindanao Grid-07/09/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2805MW, PK=2123MW, RR=73MW, NetOpMargin: EVE=608 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @30.5MW [WEBSMS] | CMIN
7/9/2024 5:39:39 PM | [NSO Update] Visayas Grid-07/09/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2526MW, PK=2183MW, RR=90MW, NetOpMargin: EVE=254 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @240MW, CEDC 3 @75MW, GTEC @7MW, PEDC 3 @120MW, PB104-4 @7MW, PB104-2 @6MW, PDPP3-E @8MW, PDPP3-G @12MW, PDPP1-U2 @4.5MW, PDPP1-U3 @4MW, PDPP1-U5 @4MW [WEBSMS] | CVIS
7/9/2024 5:36:49 PM | [NSO Update] Luzon Grid-07/09/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13014MW, PK=11361MW, RR=404MW, NetOpMargin: EVE=1249 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Ilijan B @400MW, Masinloc 1 @325MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
7/9/2024 5:17:20 PM | Mindanao Grid-07/09/2024 17:24: WMPC DG10 Shutdown at 1716H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/9/2024 5:10:43 PM | Mindanao Grid-07/09/2024 17:17: CORRECTION: At 1458H, General Santos (GSA)-Tinoto 69kV L1 (owned & maintained by SOCOTECO 2) tripped with line-to-ground indication and estimated load of 93.29MW, affecting SEC (SMF) U1 with a gross gen of 120.0MW. System frequency recorded was 59.78HZ without ALD. No activation of SIPS. SIPS was deactivated after the sustained fault of GSA-Tinoto 69kV L2 last July 7, 2024. [WEBSMS] | CMIN
7/9/2024 4:37:11 PM | Mindanao Grid-07/09/2024 16:43: Baloi-Agus 2 138kV Line 1 de-energized at 1559H. (Planned Outage) Non-GOMP. [WEBSMS] | CMIN
7/9/2024 4:35:17 PM | Luzon Grid-07/09/2024 16:35: Gumaca-Labo 230kV line 2 restored at 1635H. (Planned Outage) [WEBSMS] | CLUZ
7/9/2024 3:40:32 PM | Mindanao Grid-07/09/2024 15:47: Agus 2 - Baloi 138kV L2 energized at 1525H. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
7/9/2024 3:33:18 PM | Mindanao Grid-07/09/2024 15:40: SEC (SMF) U1 with a gross gen of 120.0MW was isolated at 1501H with SOCOTECO 2 Main SIPS activation . System frequency recorded was 59.78Hz without ALD. Unplanned Outage. Note: SEC U1 was directly affected by the forced outage of General Santos (GSA)-Tinoto 69kV L1 (Phase A to ground fault-owned & maintained by SOCOTECO 2), while GSA-Tinoto 69kV L2 was on sustained fault since July 7, 2024 at 1412H. [WEBSMS] | CMIN
7/9/2024 2:34:19 PM | Mindanao Grid-07/09/2024 14:41: WMPC DG07 Shutdown at 1411H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/9/2024 2:32:44 PM | Mindanao Grid-07/09/2024 14:39: WMPC DG07 Online at 1331H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/9/2024 2:29:15 PM | Mindanao Grid-07/09/2024 14:36: WMPC DG10 Online at 1319H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/9/2024 2:26:22 PM | Mindanao Grid-07/09/2024 14:33: WMPC DG04 on emergency shutdown at 1330H due to Exhaust leak cylinder B9 Manifold, the unit is running as RPS - System Voltage Requirement and will be replaced by WMPC DG10. [WEBSMS] | CMIN
7/9/2024 12:56:57 PM | [NSO Update] Visayas Grid-07/09/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2575MW, PK=2283MW, RR=91MW, NetOpMargin: PM=201, EVE=251 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @240MW, CEDC 3 @75MW, GTEC @7MW, PEDC 3 @120MW, PB104-2 @5.5MW, PDPP3-E @8MW, PDPP3-G @12MW, PDPP1-U2 @4.5MW, PDPP1-U5 @4MW [WEBSMS] | CVIS
7/9/2024 12:47:14 PM | [NSO Update] Luzon Grid-07/09/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14067MW, PK=12310MW, RR=469MW, NetOpMargin: PM=1288, EVE=1165 Highest Unit O/L: GNPD 1@668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Ilijan B @400MW, Masinloc 1 @320MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
7/9/2024 12:41:12 PM | [NSO Update] Mindanao Grid-07/09/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2951MW, PK=2325MW, RR=73MW, NetOpMargin: PM=553, EVE=645 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @30.5MW [WEBSMS] | CMIN
7/9/2024 11:00:16 AM | Visayas Grid-07/09/2024 11:00: Naga SS 138 kV Bus 2 and 50 MVA 138/69/13.8 kV TR1 energized at 1057H (Planned Outage) [WEBSMS] | CVIS
7/9/2024 10:59:03 AM | Mindanao Grid-07/09/2024 11:05: WMPC DG04 Online at 1048H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/9/2024 9:54:04 AM | Mindanao Grid-07/09/2024 10:00: Agus 2 - Baloi 138kV L2 de-energized at 0944H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
7/9/2024 8:34:24 AM | Visayas Grid-07/09/2024 08:34: Naga SS 138 kV Bus 2 and 50 MVA 138/69/13.8 kV TR1 de-energized at 0830H (Planned Outage) [WEBSMS] | CVIS
7/9/2024 7:31:21 AM | [NSO Update] Visayas Grid-07/09/2024 07:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0728H with power going to Visayas. [WEBSMS] | CVIS
7/9/2024 7:31:17 AM | [NSO Update] Luzon Grid-07/09/2024 07:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0728H with power going to Visayas. [WEBSMS] | CLUZ
7/9/2024 7:21:03 AM | [NSO Update] Visayas Grid-07/09/2024 07:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0718H from forward power direction. [WEBSMS] | CVIS
7/9/2024 7:21:00 AM | [NSO Update] Luzon Grid-07/09/2024 07:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0718H from forward power direction. [WEBSMS] | CLUZ
7/9/2024 6:09:32 AM | Luzon Grid-07/09/2024 06:09: Gumaca-Labo 230kV line 2 was de-energized at 0607H. (Planned Outage) [WEBSMS] | CLUZ
7/9/2024 6:04:24 AM | [NSO Update] Visayas Grid-07/09/2024 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2474MW, PK=2168MW, RR=91MW, NetOpMargin: AM=215, PM=374, EVE=295 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @267MW, CEDC 3 @75MW, GTEC @7MW, PEDC 3 @120MW, PB101-2 @5.5MW, PB104-2 @5.5MW, PDPP3-E @8MW, PDPP3-G @12MW, PDPP1-U2 @4.5MW, PDPP1-U3 @4MW, PDPP1-U5 @4MW [WEBSMS] | CVIS
7/9/2024 5:54:14 AM | [NSO Update] Luzon Grid-07/09/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14366MW, PK=11868MW, RR=474MW, NetOpMargin: AM=2024, PM=1419, EVE=1816 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Ilijan B @400MW, Masinloc 1 @320MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
7/9/2024 5:48:49 AM | [NSO Update] Mindanao Grid-07/09/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2959MW, PK=2250MW, RR=73MW, NetOpMargin: AM=636, PM=635, EVE=752 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @30.5MW [WEBSMS] | CMIN
7/9/2024 4:07:44 AM | [NSO Update] Luzon Grid-07/09/2024 04:07: Weather Advisory: Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CLUZ
7/9/2024 4:07:31 AM | [NSO Update] Mindanao Grid-07/09/2024 04:14: Weather Advisory: Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CMIN
7/9/2024 4:07:15 AM | [NSO Update] Visayas Grid-07/09/2024 04:07: Weather Advisory: Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CVIS
7/9/2024 12:15:24 AM | Luzon Grid-07/09/2024 00:15: San Lorenzo 50 online at 0012H (Planned Outage) [WEBSMS] | CLUZ
7/8/2024 11:16:54 PM | Luzon Grid-07/08/2024 23:17: For info: Sta Rita-San Lorenzo 230kV Bus 1 and Bus 2 Tie Breakers were unlooped at 2309H and 2312H, respectively. Batangas 300MVA T04 and T05 are in parallel configuration at 2315H. This is in preparation for the synchronization of San Lorenzo Module 50. [WEBSMS] | CLUZ
7/8/2024 9:32:11 PM | Luzon Grid-07/08/2024 21:32: Bay-Batangas 230kV Line 1 restored at 2131H (Planned Outage) [WEBSMS] | CLUZ
7/8/2024 7:24:29 PM | Mindanao Grid-07/08/2024 19:31: WMPC DG04 Shutdown at 1908H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/8/2024 7:18:46 PM | [NSO Update] Visayas Grid-07/08/2024 19:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1917H with power going to Luzon [WEBSMS] | CVIS
7/8/2024 7:18:17 PM | [NSO Update] Luzon Grid-07/08/2024 19:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1917H with power going to Luzon [WEBSMS] | CLUZ
7/8/2024 7:13:06 PM | [NSO Update] Visayas Grid-07/08/2024 19:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1907H from reverse power direction [WEBSMS] | CVIS
7/8/2024 7:12:34 PM | [NSO Update] Luzon Grid-07/08/2024 19:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1907H from reverse power direction [WEBSMS] | CLUZ
7/8/2024 7:10:16 PM | Mindanao Grid-07/08/2024 19:17: WMPC DG04 Shutdown at 1908H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/8/2024 6:09:46 PM | [NSO Update] Luzon Grid-07/08/2024 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12539MW, PK=11426MW, RR=361MW, NetOpMargin: EVE=752 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @119MW, Limay 8 @60MW, Ilijan B @400MW, Masinloc 1 @320MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
7/8/2024 6:07:49 PM | [NSO Update] Mindanao Grid-07/08/2024 18:14: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2898MW, PK=2183MW, RR=73MW, NetOpMargin: EVE=643 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @30.5MW [WEBSMS] | CMIN
7/8/2024 6:03:59 PM | Mindanao Grid-07/08/2024 18:10: Siguil Hydro shutdown at 1800H. Test & commissioning. [WEBSMS] | CMIN
7/8/2024 6:00:46 PM | Luzon Grid-07/08/2024 18:00: Bay - Batangas 230kV Line 1 de-energized at 1757H (Planned Outage) [WEBSMS] | CLUZ
7/8/2024 5:41:31 PM | [NSO Update] Visayas Grid-07/08/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2461MW, PK=2123MW, RR=91MW, NetOpMargin: EVE=247 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @265MW, CEDC 3 @75MW, PEDC 3 @120MW, PB101-2 @5.5MW, PB104-2 @5.5MW, PDPP3-E @8MW, PDPP3-G @12MW [WEBSMS] | CVIS
7/8/2024 5:22:59 PM | Visayas Grid-07/08/2024 17:23: Naga SS 138KV Bus 2 de-energized at 0906H/energized at 1707H.Planned Outage) [WEBSMS] | CVIS
7/8/2024 5:12:32 PM | Mindanao Grid-07/08/2024 17:19: Mt Apo U3 with 2.8MW load emergency shutdown at 1628H due to leakages at static mixer. (Unplanned Outage) [WEBSMS] | CMIN
7/8/2024 4:39:51 PM | Mindanao Grid-07/08/2024 16:46: WMPC DG07 Shutdown at 1636H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/8/2024 4:16:53 PM | Luzon Grid-07/08/2024 16:17: Bay-Batangas 230kV Line 2 restored at 1616H (Planned Outage) [WEBSMS] | CLUZ
7/8/2024 4:09:11 PM | Luzon Grid-07/08/2024 16:09: Gumaca-Labo 230kV Line 1 restored at 1609H (Planned Outage) [WEBSMS] | CLUZ
7/8/2024 3:57:04 PM | Mindanao Grid-07/08/2024 16:03: Agus 2 - Kibawe 138KV Line 2 auto-tripped at 1354H. Note: Energized up to Tower 33 only for anti pilferage purposes. Advised for line patrol. (Unplanned Outage) [WEBSMS] | CMIN
7/8/2024 2:18:55 PM | Mindanao Grid-07/08/2024 14:25: Liangan Hydro Plant shutdown at 1416H. Test & commissioning. [WEBSMS] | CMIN
7/8/2024 1:32:49 PM | Mindanao Grid-07/08/2024 13:39: Liangan Hydro Plant online at 1331H. Test & commissioning. [WEBSMS] | CMIN
7/8/2024 1:32:38 PM | Mindanao Grid-07/08/2024 13:39: WMPC DG07 online at 1328H. RPS system voltage requirement. [WEBSMS] | CMIN
7/8/2024 1:18:03 PM | Mindanao Grid-07/08/2024 13:24: Liangan Hydro Plant tripped at 1313H. Indication: High vibration. Test & commissioning. [WEBSMS] | CMIN
7/8/2024 1:12:31 PM | Mindanao Grid-07/08/2024 13:19: Liangan Hydro Plant online at 1309H. Test & commissioning. [WEBSMS] | CMIN
7/8/2024 12:56:10 PM | [NSO Update] Mindanao Grid-07/08/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2926MW, PK=2255MW, RR=73MW, NetOpMargin: PM=598, EVE=693 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @30.5MW [WEBSMS] | CMIN
7/8/2024 12:54:38 PM | [NSO Update] Luzon Grid-07/08/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13660MW, PK=12240MW, RR=498MW, NetOpMargin: PM=922, EVE=676 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @119MW, SLTEC 2 @118MW, Limay 8 @60MW, Ilijan A @400MW, Masinloc 1 @320MW [WEBSMS] | CLUZ
7/8/2024 12:51:41 PM | [NSO Update] Visayas Grid-07/08/2024 12:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1237H with power going to Visayas. [WEBSMS] | CVIS
7/8/2024 12:50:37 PM | [NSO Update] Visayas Grid-07/08/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2637MW, PK=2377MW, RR=91MW, NetOpMargin: PM=170, EVE=211 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @250MW, CEDC 3 @75MW, PEDC 3 @120MW [WEBSMS] | CVIS
7/8/2024 12:48:31 PM | [NSO Update] Luzon Grid-07/08/2024 12:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1237H with power going to Visayas. [WEBSMS] | CLUZ
7/8/2024 12:05:56 PM | [NSO Update] Luzon Grid-07/08/2024 12:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1204H from reverse power direction. [WEBSMS] | CLUZ
7/8/2024 12:05:50 PM | [NSO Update] Visayas Grid-07/08/2024 12:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1204H from reverse power direction. [WEBSMS] | CVIS
7/8/2024 10:58:32 AM | Visayas Grid-07/08/2024 10:58: Colon-KSPC L2 de-energized at 1053H (Planned Outage) [WEBSMS] | CVIS
7/8/2024 10:11:01 AM | Mindanao Grid-07/08/2024 10:17: WMPC DG04 Online at 1005H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/8/2024 8:35:52 AM | Mindanao Grid-07/08/2024 08:42: Manolo Fortich U3 online at 0800H from forced outage. (Unplanned Outage) [WEBSMS] | CMIN
7/8/2024 8:12:23 AM | Mindanao Grid-07/08/2024 08:19: Toril SS 138kV Bus #2 restored/energized at 0809H. Unplanned Outage. [WEBSMS] | CMIN
7/8/2024 7:53:08 AM | Luzon Grid-07/08/2024 07:53: Bay-Batangas 230kV Line 2 de-energized at 0752H (Planned Outage) [WEBSMS] | CLUZ
7/8/2024 7:39:47 AM | [NSO Update] Visayas Grid-07/08/2024 07:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0737H with power going to Visayas. [WEBSMS] | CVIS
7/8/2024 7:39:45 AM | [NSO Update] Luzon Grid-07/08/2024 07:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0737H with power going to Visayas. [WEBSMS] | CLUZ
7/8/2024 7:30:09 AM | [NSO Update] Luzon Grid-07/08/2024 07:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0727H from forward power direction. [WEBSMS] | CLUZ
7/8/2024 7:29:36 AM | [NSO Update] Visayas Grid-07/08/2024 07:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0727H from forward power direction. [WEBSMS] | CVIS
7/8/2024 7:28:54 AM | Mindanao Grid-07/08/2024 07:35: Toril SS 138kV Bus #2 tripped at 0717H. Unplanned Outage. [WEBSMS] | CMIN
7/8/2024 6:55:47 AM | Mindanao Grid-07/08/2024 07:02: Manolo Fortich 1 U3 with 12MW load tripped at 0649H. Indication: Nozzle failure position needle four (4). (Unplanned Outage) [WEBSMS] | CMIN
7/8/2024 6:16:37 AM | Luzon Grid-07/08/2024 06:16: Gumaca-Labo 230kV Line 1 de-energized at 0616H (Planned Outage) [WEBSMS] | CLUZ
7/8/2024 5:57:15 AM | [NSO Update] Mindanao Grid-07/08/2024 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2809MW, PK=2313MW, RR=73MW, NetOpMargin: AM=424, PM=307, EVE=403 Highest Unit O/L: GNPK 1, 2, & 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @30.5MW [WEBSMS] | CMIN
7/8/2024 5:56:26 AM | Luzon Grid-07/08/2024 05:56: Muntinlupa 230kV Bus 2 restored at 0529H (Planned Outage) [WEBSMS] | CLUZ
7/8/2024 5:55:29 AM | [NSO Update] Visayas Grid-07/08/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2603MW, PK=2260MW, RR=91MW, NetOpMargin: AM=252, PM=308, EVE=268 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @240MW, CEDC 3 @75MW, TGPP @113.5MW, PEDC 3 @120MW, PB101-2 @5.5MW, PB104-2 @5.5MW, PDPP3-E @8MW, PDPP3-G @12MW [WEBSMS] | CVIS
7/8/2024 5:54:03 AM | [NSO Update] Luzon Grid-07/08/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14027MW, PK=11315MW, RR=466MW, NetOpMargin: AM=2246, PM=1278, EVE=1716 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @118MW, SLTEC 2 @118MW, Limay 8 @60MW, Ilijan A @400MW, SCPC 1 @145MW, Masinloc 1 @320MW [WEBSMS] | CLUZ
7/8/2024 5:52:57 AM | Luzon Grid-07/08/2024 05:52: Muntinlupa-Binan 230kV Line 3 restored at 0551H (Planned Outage) [WEBSMS] | CLUZ
7/8/2024 5:20:30 AM | Luzon Grid-07/08/2024 05:20: Laoag-EDC Burgos Wind Farm 115kV Line (CO) de-energized at 0519H (Planned Outage) [WEBSMS] | CLUZ
7/8/2024 4:06:02 AM | [NSO Update] Mindanao Grid-07/08/2024 04:12: Weather Update: Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CMIN
7/8/2024 4:05:42 AM | [NSO Update] Visayas Grid-07/08/2024 04:05: Weather Update: Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CVIS
7/8/2024 4:05:27 AM | [NSO Update] Luzon Grid-07/08/2024 04:05: Weather Update: Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CLUZ
7/8/2024 4:01:41 AM | Mindanao Grid-07/08/2024 04:08: GNPK Unit 4 online at 0357H. From PMS (Non-GOMP). [WEBSMS] | CMIN
7/8/2024 2:52:07 AM | Luzon Grid-07/08/2024 02:52: San Jose-San Rafael 230kV Line restored at 0251H (Planned Outage) [WEBSMS] | CLUZ
7/8/2024 2:11:18 AM | Mindanao Grid-07/08/2024 02:18: LAMSAN BIOMASS online at 0009H (Unplanned Outage) [WEBSMS] | CMIN
7/8/2024 2:10:13 AM | Luzon Grid-07/08/2024 02:10: MERALCO New Mauban SS 50MVA T01 restored at 0210H (Planned Outage) [WEBSMS] | CLUZ
7/8/2024 2:10:11 AM | Mindanao Grid-07/08/2024 02:16: LAMSAN BIOMASS with 13.5MW load tripped at 2354H. Cause: Affected from 5LI1SKU-SMY line fault. Indication: 50N Non-Directional Earth Fault (Unplanned Outage). [WEBSMS] | CMIN
7/8/2024 1:41:49 AM | Luzon Grid-07/08/2024 01:41: Gamu-Tuguegarao 230kV Line looped at 0140H at Gamu side. Ongoing commissioning (Planned Outage) [WEBSMS] | CLUZ
7/8/2024 1:27:32 AM | Luzon Grid-07/08/2024 01:27: For info: Gamu-Tuguegarao 230kV Line energized at 0124H at Tuguegarao side. Ongoing commissioning for the transfer of the said line from Bay 81 to Bay 84 of Tuguegarao SS. [WEBSMS] | CLUZ
7/8/2024 12:58:40 AM | Mindanao Grid-07/08/2024 01:05: STEAG Unit 2 shutdown at 0000H (Planned Outage) [WEBSMS] | CMIN
7/8/2024 12:04:03 AM | Luzon Grid-07/08/2024 00:04: Sta Rita 10 online at 0002H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 11:53:31 PM | Luzon Grid-07/07/2024 23:53: Muntinlupa 230kV Bus 2 de-energized at 2352H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 11:50:03 PM | Luzon Grid-07/07/2024 23:50: San Lorenzo 50 shutdown at 2348H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 11:42:06 PM | Luzon Grid-07/07/2024 23:42: Calaca 1 emergency shutdown at 2305H (Unplanned Outage) [WEBSMS] | CLUZ
7/7/2024 11:29:09 PM | Luzon Grid-07/07/2024 23:29: San Jose-San Rafael 230kV Line de-energized at 2328H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 11:24:02 PM | Luzon Grid-07/07/2024 23:24: Muntinlupa-Binan 230kV Line 3 de-energized at 2320H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 10:24:02 PM | Luzon Grid-07/07/2024 22:24: Correction: Sta Rita 20 online at 2209H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 10:20:02 PM | [NSO Update] Visayas Grid-07/07/2024 22:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2155H with power going to Luzon [WEBSMS] | CVIS
7/7/2024 10:19:38 PM | [NSO Update] Luzon Grid-07/07/2024 22:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2155H with power going to Luzon [WEBSMS] | CLUZ
7/7/2024 10:15:32 PM | Luzon Grid-07/07/2024 22:15: Sta Rita 10 online at 2209H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 9:47:22 PM | [NSO Update] Visayas Grid-07/07/2024 21:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2144H from reverse power direction [WEBSMS] | CVIS
7/7/2024 9:46:55 PM | [NSO Update] Luzon Grid-07/07/2024 21:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2144H from reverse power direction [WEBSMS] | CLUZ
7/7/2024 9:34:45 PM | Mindanao Grid-07/07/2024 21:41: Aurora-NagaMin 138kV L2 (7LI2AUR-NAA) auto-tripped and auto-reclosed at 2104H. Unplanned Outage [WEBSMS] | CMIN
7/7/2024 8:36:13 PM | Mindanao Grid-07/07/2024 20:42: SIGUIL Hydro online at 1844H (Unplanned Outage) [WEBSMS] | CMIN
7/7/2024 8:32:40 PM | Mindanao Grid-07/07/2024 20:39: SIGUIL Hydro with 11.2MW tripped at 1807H. Indication: F511 BT Alarm (Unplanned Outage) [WEBSMS] | CMIN
7/7/2024 7:44:05 PM | Mindanao Grid-07/07/2024 19:50: SEC 1 online at 1942H (Unplanned Outage) [WEBSMS] | CMIN
7/7/2024 7:39:57 PM | Visayas Grid-07/07/2024 19:40: Daanbantayan - Lanao 69 kV Line energized at 1939H (Planned Outage) [WEBSMS] | CVIS
7/7/2024 7:24:15 PM | Visayas Grid-07/07/2024 19:24: Daanbantayan SS 100 MVA 230/69/13.8 kV TR energized thru bay 84 at 1909H (Planned Outage) [WEBSMS] | CVIS
7/7/2024 6:58:43 PM | Luzon Grid-07/07/2024 18:58: Subic 230kV Bus 1 restored at 1857H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 6:35:44 PM | Mindanao Grid-07/07/2024 18:42: Davao SS 150MVA Power Transformer No.3 is energized/restored back to the Mindanao Grid at 1817H. From Planned Outage/GOMP (APMS). [WEBSMS] | CMIN
7/7/2024 6:31:31 PM | Mindanao Grid-07/07/2024 18:38: General Santos SS 100MVA Power Tmer No.5 (Operating in parallel with 100MVA Power Tmer No.4) is successfully restored at 1755H, with proper clearance from MTD-B group. From Unplanned Outage. [WEBSMS] | CMIN
7/7/2024 6:16:10 PM | Luzon Grid-07/07/2024 18:16: Bay-Ormat 69kV Line restored at 1814H (Unplanned Outage) [WEBSMS] | CLUZ
7/7/2024 6:11:01 PM | [NSO Update] Visayas Grid-07/07/2024 18:11: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1809H with power going to Visayas [WEBSMS] | CVIS
7/7/2024 6:10:44 PM | [NSO Update] Luzon Grid-07/07/2024 18:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1809H with power going to Visayas [WEBSMS] | CLUZ
7/7/2024 6:03:50 PM | [NSO Update] Visayas Grid-07/07/2024 18:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1759H from forward power direction [WEBSMS] | CVIS
7/7/2024 6:03:31 PM | [NSO Update] Luzon Grid-07/07/2024 18:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1759H from forward power direction [WEBSMS] | CLUZ
7/7/2024 5:58:45 PM | [NSO Update] Mindanao Grid-07/07/2024 18:05: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2818MW, PK=2087MW, RR=73MW, NetOpMargin: EVE=658 Highest Unit O/L: GNPK 1, 2, & 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/7/2024 5:57:36 PM | [NSO Update] Visayas Grid-07/07/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2393MW, PK=2062MW, RR=88MW, NetOpMargin: EVE=243 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC 3 @75MW, TGPP @113.5MW, PEDC 3 @120MW, PB101-2 @5.5MW, PB104-2 @5.5MW, PDPP3-H @8MW, PDPP3-E @8MW, PDPP3-G @12MW [WEBSMS] | CVIS
7/7/2024 5:55:10 PM | [NSO Update] Luzon Grid-07/07/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12364MW, PK=10213MW, RR=271MW, NetOpMargin: EVE=1879 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, SLTEC 1 @118MW, SLTEC 2 @118MW, Limay 8 @60MW, Ilijan A @400MW [WEBSMS] | CLUZ
7/7/2024 5:44:23 PM | Luzon Grid-07/07/2024 17:44: Las Pinas 300MVA T01 restored at 1742H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 4:56:24 PM | Mindanao Grid-07/07/2024 17:03: Baloi SS 138kV 100MVA Power Transformer No.3 (7XF03BLO) energized back to the Mindanao Grid at 1644H. From Planned Outage/GOMP [WEBSMS] | CMIN
7/7/2024 4:49:48 PM | Mindanao Grid-07/07/2024 16:56: General Santos SS 100MVA Power Tmer No.5 (Operating in parallel with 100MVA Power Tmer No.4) auto-tripped at 1554H, in an attempt to reclose GenSan-Tinoto 69kV L2 (Note: Reclosing attempt of Gensan-Tinoto 69kV L2 was failed). (Unplanned Outage) [WEBSMS] | CMIN
7/7/2024 4:07:54 PM | Luzon Grid-07/07/2024 16:07: Calaca-Binan 230kV Line restored at 1607H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 4:03:16 PM | Mindanao Grid-07/07/2024 16:09: SIGUIL Hydro online at 1539H (Unplanned Outage) [WEBSMS] | CMIN
7/7/2024 4:02:47 PM | Luzon Grid-07/07/2024 16:02: San Gabriel online at 1559H (Reserve Shutdown) [WEBSMS] | CLUZ
7/7/2024 4:02:24 PM | Mindanao Grid-07/07/2024 16:09: SIGUIL Hydro with 11.2MW isolated at 1412H due to isolation of Kamanga SS brought by tripping of 5LI2GSA-TIN and opening of PCBs of 5LI1GSA-TIN at Kamanga SS-side only. (Unplanned Outage, outside management control) [WEBSMS] | CMIN
7/7/2024 3:45:49 PM | Mindanao Grid-07/07/2024 15:52: SEC1 with 120.9MW (gross) load isolated at 1412H due to line fault (CN) at 5LI2GSA-TIN (LD=43.8MW) and opening of PCBs of 5LI1GSA-KAM at Kamanga SS-side only. SOC II SIPS activated with LD=20.5MW. Lowest frequency recorded at 59.67Hz. (Unplanned Outage) [WEBSMS] | CMIN
7/7/2024 3:26:09 PM | Luzon Grid-07/07/2024 15:26: Hermosa-San Jose 230kV Line restored at 1525H (Unplanned Outage) [WEBSMS] | CLUZ
7/7/2024 3:18:31 PM | Luzon Grid-07/07/2024 15:18: Hermosa-San Jose 230kV Line tripped at 1513H (Unplanned Outage) [WEBSMS] | CLUZ
7/7/2024 3:04:31 PM | Luzon Grid-07/07/2024 15:04: Daraga-Tiwi C 230kV Line restored at 1502H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 1:45:24 PM | Mindanao Grid-07/07/2024 13:52: Butuan-Placer 138kV L1 (7LI1BUT-PLA) auto-tripped and auto-reclosed at 1325H. Unplanned Outage. [WEBSMS] | CMIN
7/7/2024 12:49:31 PM | [NSO Update] Luzon Grid-07/07/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13998MW, PK=10196MW, RR=334MW, NetOpMargin: PM=3468, EVE=2272 Highest Unit O/L: GNPD 1@668MW Derated Plant: GNPD 2 @640MW, Masinloc 1 @330MW, SLTEC 1 @118MW, SLTEC 2 @118MW, Limay 8 @60MW, Ilijan A @340MW [WEBSMS] | CLUZ
7/7/2024 12:42:25 PM | [NSO Update] Mindanao Grid-07/07/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2968MW, PK=1940MW, RR=73MW, NetOpMargin: PM=956, EVE=815 Highest Unit O/L: GNPK 1,2&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/7/2024 12:38:34 PM | [NSO Update] Visayas Grid-07/07/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2441MW, PK=1836MW, RR=84MW, NetOpMargin: PM=522, EVE=234 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @298MW, CEDC 3 @75MW, TGPP @113.5MW, PEDC 3 @120MW, PB101-2 @5.5MW, PB104-2 @5.5MW, PDPP3-H @8MW, PDPP3-E @8MW, PDPP3-G @12MW [WEBSMS] | CVIS
7/7/2024 12:06:29 PM | Luzon Grid-07/07/2024 12:06: MERALCO New Mauban SS 50MVA T01 de-energized at 1204H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 11:18:28 AM | Luzon Grid-07/07/2024 11:18: San Jose 750MVA T05 restored at 1117H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 10:47:28 AM | Luzon Grid-07/07/2024 10:47: San Jose 230kV Bus 2 restored at 1044H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 8:36:00 AM | Luzon Grid-07/07/2024 08:36: Las Pinas 300MVA T01 de-energized at 0833H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 8:02:39 AM | Mindanao Grid-07/07/2024 08:09: Baloi SS 138kV 100MVA Power Transformer No.3 (7XF03BLO) deenergized at 0731H. (Planned Outage/GOMP) [WEBSMS] | CMIN
7/7/2024 7:39:07 AM | Luzon Grid-07/07/2024 07:39: Subic 230kV Bus 1 de-energized at 0736H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 7:32:19 AM | Visayas Grid-07/07/2024 07:32: DaanBantayan SS 100 MVA TR1 de-energized at 0730H (Planned Outage) [WEBSMS] | CVIS
7/7/2024 7:08:31 AM | Luzon Grid-07/07/2024 07:08: Daraga-Tiwi c 230kV Line de-energized at 0706H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 7:01:00 AM | Mindanao Grid-07/07/2024 07:07: Davao SS 138KV 150MVA Power Transformer # 3 on shutdown at 0644H for APMS. (Planned Outage) GOMP. [WEBSMS] | CMIN
7/7/2024 6:22:42 AM | Luzon Grid-07/07/2024 06:22: Gamu-Tuguegarao 230kV Line de-energized at 0621H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 6:20:02 AM | Luzon Grid-07/07/2024 06:20: Calaca-Binan 230kV Line de-energized at 0613H (Planned Outage) [WEBSMS] | CLUZ
7/7/2024 5:45:10 AM | [NSO Update] Luzon Grid-07/07/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14013MW, PK=9356MW, RR=326MW, NetOpMargin: AM=4331, PM=3697, EVE=2001 Highest Unit O/L: GNPD 1@668MW Derated Plant: GNPD 2 @640MW, Masinloc 1 @330MW, SLTEC 1 @118MW, SLTEC 2 @118MW, Limay 8 @60MW, Ilijan A @340MW [WEBSMS] | CLUZ
7/7/2024 5:41:55 AM | [NSO Update] Mindanao Grid-07/07/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2978MW, PK=1888MW, RR=73MW, NetOpMargin: AM=1018, PM=972, EVE=797 Highest Unit O/L: GNPK 1,2&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/7/2024 5:39:56 AM | [NSO Update] Visayas Grid-07/07/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2310MW, PK=1832MW, RR=81MW, NetOpMargin: AM=396, PM=544, EVE=200 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @298MW, CEDC 3 @75MW, TGPP @113.5MW, PEDC 3 @120MW [WEBSMS] | CVIS
7/7/2024 5:17:55 AM | Visayas Grid-07/07/2024 05:18: Daanbantayan SS 100 MVA 230/69/13.8 kV TR de-energized at 0515H (Planned Outage) [WEBSMS] | CVIS
7/7/2024 5:06:36 AM | Luzon Grid-07/07/2024 05:06: SCPC 1 online at 0501H (Unplanned Outage) [WEBSMS] | CLUZ
7/7/2024 5:04:38 AM | Visayas Grid-07/07/2024 05:04: Daanbantayan - Lanao 69 kV Line de-energized at 0501H (Planned Outage) [WEBSMS] | CVIS
7/7/2024 4:19:46 AM | [NSO Update] Mindanao Grid-07/07/2024 04:26: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. Easterlies affecting the eastern section of Northern and Central Luzon. [WEBSMS] | CMIN
7/7/2024 4:19:32 AM | [NSO Update] Visayas Grid-07/07/2024 04:19: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. Easterlies affecting the eastern section of Northern and Central Luzon. [WEBSMS] | CVIS
7/7/2024 4:19:10 AM | [NSO Update] Luzon Grid-07/07/2024 04:19: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. Easterlies affecting the eastern section of Northern and Central Luzon. [WEBSMS] | CLUZ
7/7/2024 4:00:26 AM | Mindanao Grid-07/07/2024 04:07: SMC U2 shutdown at 0353H. PMS non-GOMP. (Unplanned Outage) [WEBSMS] | CMIN
7/7/2024 12:17:24 AM | Luzon Grid-07/07/2024 00:17: San Jose 750MVA T05 was de-energized at 0016H. (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 11:09:26 PM | Luzon Grid-07/06/2024 23:09: San Jose-North Caloocan 115kV line was restored at 2308H. (Unplanned Outage) [WEBSMS] | CLUZ
7/6/2024 9:25:25 PM | Luzon Grid-07/06/2024 21:25: San Jose-North Caloocan 115kV line(CO) auto-tripped at 2121H. (Unplanned Outage) [WEBSMS] | CLUZ
7/6/2024 9:13:07 PM | Luzon Grid-07/06/2024 21:13: San Jose 230kV Bus 2 was de-energized at 2112H. (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 8:17:03 PM | [NSO Update] Visayas Grid-07/06/2024 20:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2013H with power going to Luzon. [WEBSMS] | CVIS
7/6/2024 8:16:36 PM | [NSO Update] Luzon Grid-07/06/2024 20:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2013H with power going to Luzon. [WEBSMS] | CLUZ
7/6/2024 8:04:24 PM | [NSO Update] Luzon Grid-07/06/2024 20:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2003H from reverse power direction. [WEBSMS] | CLUZ
7/6/2024 8:04:06 PM | [NSO Update] Visayas Grid-07/06/2024 20:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2003H from reverse power direction. [WEBSMS] | CVIS
7/6/2024 7:32:24 PM | Mindanao Grid-07/06/2024 19:38: WMPC DG10 Shutdown at 1916H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/6/2024 5:58:21 PM | Luzon Grid-07/06/2024 17:58: Hermosa-Calaguiman 69kV line was restored at 1757H. (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 5:53:05 PM | [NSO Update] Luzon Grid-07/06/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12423MW, PK=10491MW, RR=401MW, NetOpMargin: EVE=1531 Highest Unit O/L: GNPD 1@668MW Derated Plant: GNPD 2 @640MW, Masinloc 1 @330MW, SLTEC 1 @118MW, SLTEC 2 @118MW, Limay 8 @60MW, Ilijan A @400MW [WEBSMS] | CLUZ
7/6/2024 5:45:19 PM | [NSO Update] Mindanao Grid-07/06/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2994MW, PK=2252MW, RR=73MW, NetOpMargin: EVE=669 Highest Unit O/L: GNPK 1,2&3 Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/6/2024 5:43:14 PM | [NSO Update] Visayas Grid-07/06/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2441MW, PK=2136MW, RR=86MW, NetOpMargin: EVE=219 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC 3 @75MW, TGPP @113.5MW, PEDC 3 @120MW [WEBSMS] | CVIS
7/6/2024 5:38:30 PM | Luzon Grid-07/06/2024 17:38: Mexico-Concepcion 230kV line 2 was restored at 1737H. (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 5:28:44 PM | Luzon Grid-07/06/2024 17:28: Calaca-Malamig 230kV line was restored at 1727H. (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 4:55:51 PM | Visayas Grid-07/06/2024 16:55: Calong-calong - Century Peak 69 kV Line energized at 1653H. (Planned Outage) [WEBSMS] | CVIS
7/6/2024 4:49:33 PM | Luzon Grid-07/06/2024 16:49: Concepcion 230kV Bus 1 was energized at 1649H. (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 4:06:05 PM | Luzon Grid-07/06/2024 16:06: San Esteban-Bacnotan 230kV line was restored at 1605H. (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 3:52:02 PM | Luzon Grid-07/06/2024 15:52: Bauang-La Trinidad 230kV line 1 was restored at 1550H. (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 1:48:03 PM | Luzon Grid-07/06/2024 13:48: Correction: Tayabas-Pagbiao 500kV L1 & L2 tripped at 1236H, L2 reclosed successfully both side, L1 reclosed at Pagbilao side.(Unplanned Outage) [WEBSMS] | CLUZ
7/6/2024 1:40:06 PM | Mindanao Grid-07/06/2024 13:45: WMPC DG10 Online at 1338H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/6/2024 1:23:28 PM | Luzon Grid-07/06/2024 13:23: Tayabas-Pagbilao 500kV L1 restored at 1322H (Unplanned Outage) [WEBSMS] | CLUZ
7/6/2024 1:09:12 PM | Luzon Grid-07/06/2024 13:09: Tayabas-Pagbiao 500kV L1 & L2 tripped at 1236H, L2 reclosed successfully both side, L1 reclosed at Pagbilao side. tripped at 1309H (Unplanned Outage) [WEBSMS] | CLUZ
7/6/2024 12:59:34 PM | Luzon Grid-07/06/2024 12:59: Tayabas-Pagbiao 500kV L1 & L2 tripped at 1236H, L2 reclosed successfully both side, L1 reclosed at Pagbilao side. (Unplanned Outage) [WEBSMS] | CLUZ
7/6/2024 12:53:07 PM | [NSO Update] Luzon Grid-07/06/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13782MW, PK=10896MW, RR=465MW, NetOpMargin: PM=2421, EVE=1317 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, Masinloc 1 @325MW, SLTEC 1 @118MW, SLTEC 2 @118MW, Limay 8 @60MW, Ilijan A @400MW, GMEC 2 @240MW [WEBSMS] | CLUZ
7/6/2024 12:49:05 PM | [NSO Update] Mindanao Grid-07/06/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3040MW, PK=2162MW, RR=73MW, NetOpMargin: PM=805, EVE=777 Highest Unit O/L: GNPK 1,2,&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/6/2024 12:42:19 PM | [NSO Update] Visayas Grid-07/06/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2396MW, PK=2065MW, RR=86MW, NetOpMargin: PM=245, EVE=231 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @302MW, CEDC 3 @75MW, TGPP @113.5MW, PEDC 3 @120MW, PB101-2 @5.5MW, PB104-2 @5.5MW [WEBSMS] | CVIS
7/6/2024 10:37:50 AM | Mindanao Grid-07/06/2024 10:43: Kibawe - Tacurong 138kV line energized at 1034H. (Planned Outage) [WEBSMS] | CMIN
7/6/2024 8:37:25 AM | Luzon Grid-07/06/2024 08:37: Tuguegarao SS 230kV Bus 1 restored at 0836H (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 8:30:56 AM | Luzon Grid-07/06/2024 08:31: La Trinidad-Bauang 230kV Line 1 de-energized at 0828H (Unplanned Outage) [WEBSMS] | CLUZ
7/6/2024 8:14:22 AM | Luzon Grid-07/06/2024 08:14: Bacnotan-San Esteban 230kV Line de-energized at 0813H (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 8:09:16 AM | Mindanao Grid-07/06/2024 08:14: Kibawe - Tacurong 18kV line de-energized at 0807H. (Planned Outage) [WEBSMS] | CMIN
7/6/2024 7:31:07 AM | [NSO Update] Visayas Grid-07/06/2024 07:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0724H with power going to Visayas [WEBSMS] | CVIS
7/6/2024 7:30:19 AM | [NSO Update] Luzon Grid-07/06/2024 07:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0724H with power going to Visayas [WEBSMS] | CLUZ
7/6/2024 7:18:38 AM | Visayas Grid-07/06/2024 07:18: Calong-calong - Century Peak 69 kV Line de-energized at 0715H. (Planned Outage) [WEBSMS] | CVIS
7/6/2024 7:18:19 AM | [NSO Update] Visayas Grid-07/06/2024 07:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0714H from forward power direction [WEBSMS] | CVIS
7/6/2024 7:17:44 AM | [NSO Update] Luzon Grid-07/06/2024 07:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0714H from forward power direction [WEBSMS] | CLUZ
7/6/2024 7:15:08 AM | Luzon Grid-07/06/2024 07:15: Mexico-Concepcion 230kV Line 2 and Concepcion SS 230kV Bus 1 de-energized at 0711H and 0713H, respectively (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 6:10:37 AM | Luzon Grid-07/06/2024 06:10: Sta. Rosa-Calaca 230kV Line de-energized at 0610H (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 5:52:13 AM | [NSO Update] Luzon Grid-07/06/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14106MW, PK=10608MW, RR=450MW, NetOpMargin: AM=3048, PM=1906, EVE=791 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @400MW, GNPD 2 @640MW, Masinloc 1 @325MW, SLTEC 1 @118MW, SLTEC 2 @118MW, Limay 8 @60MW, GMEC 2 @240MW [WEBSMS] | CLUZ
7/6/2024 5:52:09 AM | [NSO Update] Mindanao Grid-07/06/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3047MW, PK=2098MW, RR=73MW, NetOpMargin: AM=876, PM=825, EVE=860 Highest Unit O/L: GNPK 1,2,&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/6/2024 5:52:07 AM | [NSO Update] Visayas Grid-07/06/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2436MW, PK=1981MW, RR=82MW, NetOpMargin: AM=373, PM=332, EVE=231 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC 3 @75MW, TGPP @113.5MW, PEDC 3 @120MW [WEBSMS] | CVIS
7/6/2024 5:23:44 AM | Mindanao Grid-07/06/2024 05:29: Jasaan - Nasipit 138kV Line energize/loop at 0520H. (Planned Outage) [WEBSMS] | CMIN
7/6/2024 4:28:35 AM | Luzon Grid-07/06/2024 04:28: Hermosa-Calaguiman 69kV Line de-energized at 0426H (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 4:06:49 AM | Luzon Grid-07/06/2024 04:06: Malaya SS 230kV Bus 2 and Lumban-Malaya 230kV Line 2 restored at 0402H and 0405H, respectively. (Planned Outage) [WEBSMS] | CLUZ
7/6/2024 4:04:06 AM | [NSO Update] Luzon Grid-07/06/2024 04:04: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/6/2024 4:03:47 AM | [NSO Update] Visayas Grid-07/06/2024 04:03: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
7/6/2024 4:03:45 AM | [NSO Update] Mindanao Grid-07/06/2024 04:09: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
7/6/2024 2:04:41 AM | Mindanao Grid-07/06/2024 02:10: Jasaan - Nasipit 138kV Line de-energized/shutdown at 0202H. (Planned Outage) [WEBSMS] | CMIN
7/6/2024 12:47:41 AM | Luzon Grid-07/06/2024 00:47: For info: Batangas 300MVA T04 and T05 were unparalleled at 0031H. Sta Rita-San Lorenzo 230kV Bus 1 and Bus 2 Tie Breakers were closed at 0045H. [WEBSMS] | CLUZ
7/6/2024 12:35:38 AM | Luzon Grid-07/06/2024 00:35: Correction: Tuguegarao SS 230kV Bus 1 de-energized at 2205H (Planned Outage) [WEBSMS] | CLUZ
7/5/2024 11:57:40 PM | Luzon Grid-07/05/2024 23:57: Sta. Rita Module 20 shutdown at 2356H (Planned Outage) [WEBSMS] | CLUZ
7/5/2024 11:25:47 PM | Luzon Grid-07/05/2024 23:25: Sta. Rita Module 10 shutdown at 2325H (Planned Outage) [WEBSMS] | CLUZ
7/5/2024 10:15:44 PM | Luzon Grid-07/05/2024 22:15: Lumban-Malaya 230kV Line 2 and Malaya SS 230kV Bus 2 de-energized at 2213H and 2214H, respectively. (Planned Outage) [WEBSMS] | CLUZ
7/5/2024 10:06:19 PM | Luzon Grid-07/05/2024 22:06: Tuguegarao SS 230kV Bus 1 restored at 2205H (Planned Outage) [WEBSMS] | CLUZ
7/5/2024 8:12:12 PM | [NSO Update] Visayas Grid-07/05/2024 20:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2008H with power going to Luzon. [WEBSMS] | CVIS
7/5/2024 8:11:49 PM | [NSO Update] Luzon Grid-07/05/2024 20:11: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2008H with power going to Luzon. [WEBSMS] | CLUZ
7/5/2024 8:02:10 PM | [NSO Update] Visayas Grid-07/05/2024 20:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1957H from reverse power direction. [WEBSMS] | CVIS
7/5/2024 8:01:50 PM | [NSO Update] Luzon Grid-07/05/2024 20:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1957H from reverse power direction. [WEBSMS] | CLUZ
7/5/2024 7:17:59 PM | Mindanao Grid-07/05/2024 19:23: WMPC DG10 shutdown at 1916H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/5/2024 5:56:08 PM | Luzon Grid-07/05/2024 17:56: Bauang 230kV Bus 2 restored at 1755H (Planned Outage) [WEBSMS] | CLUZ
7/5/2024 5:47:12 PM | [NSO Update] Luzon Grid-07/05/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12818MW, PK=10535MW, RR=401MW, NetOpMargin: EVE=1882 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, Masinloc 1 @310MW, SLTEC 1 @118MW, SLTEC 2 @118MW, Limay 8 @60MW, Ilijan A @400MW, Masinloc 3 @330MW [WEBSMS] | CLUZ
7/5/2024 5:32:16 PM | [NSO Update] Mindanao Grid-07/05/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2943MW, PK=2215MW, RR=73MW, NetOpMargin: EVE=655 Highest Unit O/L: GNPK 1,2,&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/5/2024 5:31:16 PM | [NSO Update] Visayas Grid-07/05/2024 17:31: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2448MW, PK=2128MW, RR=91MW, NetOpMargin: EVE=229 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC 3 @75MW, TGPP @113.5MW, PEDC 3 @120MW [WEBSMS] | CVIS
7/5/2024 5:21:46 PM | Mindanao Grid-07/05/2024 17:27: Agus6 SS 138/69kV 100MVA Tie Power Transformer3 energize/loop at 1717H. (Unplanned Outage) [WEBSMS] | CMIN
7/5/2024 1:40:05 PM | Mindanao Grid-07/05/2024 13:45: Liangan HEPP U2 online at 1305H. Under Test and Commissioning. (Planned Outage) [WEBSMS] | CMIN
7/5/2024 1:18:40 PM | Mindanao Grid-07/05/2024 13:24: WMPC DG10 online at 1316H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/5/2024 1:01:48 PM | Luzon Grid-07/05/2024 13:01: San Gabriel online at 1259H (Reserve Shutdown [WEBSMS] | CLUZ
7/5/2024 12:59:08 PM | [NSO Update] Mindanao Grid-07/05/2024 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2985MW, PK=2349MW, RR=73MW, NetOpMargin: PM=563, EVE=654 Highest Unit O/L: GNPK 1, 2, & 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/5/2024 12:57:55 PM | [NSO Update] Visayas Grid-07/05/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2649MW, PK=2269MW, RR=91MW, NetOpMargin: PM=289, EVE=227 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC 3 @75MW, TGPP @113.5MW, PEDC 3 @120MW, PB101-2 @5.2MW, PB104 U2 @5.5MW [WEBSMS] | CVIS
7/5/2024 12:52:27 PM | [NSO Update] Luzon Grid-07/05/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14015MW, PK=11732MW, RR=508MW, NetOpMargin: PM=1775, EVE=1593 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, Masinloc 1 @310MW, SLTEC 1 @118MW, SLTEC 2 @118MW, Limay 8 @30MW, Calaca 1 @210MW, Ilijan A @400MW [WEBSMS] | CLUZ
7/5/2024 12:23:22 PM | [NSO Update] Visayas Grid-07/05/2024 12:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1206H with power going to Visayas [WEBSMS] | CVIS
7/5/2024 12:23:00 PM | [NSO Update] Luzon Grid-07/05/2024 12:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1206H with power going to Visayas [WEBSMS] | CLUZ
7/5/2024 12:22:12 PM | [NSO Update] Visayas Grid-07/05/2024 12:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1156H from forward power direction [WEBSMS] | CVIS
7/5/2024 12:21:55 PM | [NSO Update] Luzon Grid-07/05/2024 12:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1156H from forward power direction [WEBSMS] | CLUZ
7/5/2024 10:21:18 AM | Mindanao Grid-07/05/2024 10:26: Agus6 SS 138/69kV 100MVA Tie Power Transformer3(7XF03AG6) de-energized/shutdown at 1018H. (Planned Outage) [WEBSMS] | CMIN
7/5/2024 9:29:45 AM | Luzon Grid-07/05/2024 09:29: GMEC 2 online at 0922H (Unplanned Outage) [WEBSMS] | CLUZ
7/5/2024 9:16:57 AM | Mindanao Grid-07/05/2024 09:22: Agus6 SS - Agus6 HEPP 138kV Line(7LI1AG6-AP6) de-energize/shutdown at 0912H. (Planned Outage) [WEBSMS] | CMIN
7/5/2024 8:16:32 AM | Mindanao Grid-07/05/2024 08:22: Tagoloan - Steag 138kV Line1 de-energized/shutdown at 0814H. (Planned Outage) [WEBSMS] | CMIN
7/5/2024 7:13:07 AM | Luzon Grid-07/05/2024 07:13: Correction: Bauang 230kV Bus 2 de-energized at 0710H (Planned Outage) [WEBSMS] | CLUZ
7/5/2024 7:11:50 AM | Luzon Grid-07/05/2024 07:11: Bauang 230kV Bus 1 de-energized at 0710H (Planned Outage) [WEBSMS] | CLUZ
7/5/2024 6:47:14 AM | Luzon Grid-07/05/2024 06:47: San Gabriel shutdown at 0638H (Reserve Shutdown) [WEBSMS] | CLUZ
7/5/2024 5:49:42 AM | [NSO Update] Luzon Grid-07/05/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14108MW, PK=11392MW, RR=466MW, NetOpMargin: AM=2250, PM=1000, EVE=843 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @400MW, GNPD 2 @640MW, Masinloc 1 @310MW, Masinloc 3 @325MW, Limay 8 @30MW, SLTEC 1 @118MW, SLTEC 2 @118MW [WEBSMS] | CLUZ
7/5/2024 5:37:50 AM | [NSO Update] Visayas Grid-07/05/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2475MW, PK=2148MW, RR=91MW, NetOpMargin: AM=236, PM=178, EVE=174 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @320MW, CEDC 3 @75MW, TGPP @113.5MW, PEDC 3 @120MW [WEBSMS] | CVIS
7/5/2024 5:37:25 AM | [NSO Update] Mindanao Grid-07/05/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2990MW, PK=2251MW, RR=73MW, NetOpMargin: AM=666, PM=428, EVE=543 Highest Unit O/L: GNPK 1,2 & 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/5/2024 4:28:06 AM | [NSO Update] Luzon Grid-07/05/2024 04:28: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/5/2024 4:27:45 AM | [NSO Update] Visayas Grid-07/05/2024 04:27: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
7/5/2024 4:27:41 AM | [NSO Update] Mindanao Grid-07/05/2024 04:33: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
7/4/2024 11:37:58 PM | Luzon Grid-07/04/2024 23:37: Ilijan A GT 1-2 online at 2335H (Unplanned Outage) [WEBSMS] | CLUZ
7/4/2024 10:24:37 PM | Luzon Grid-07/04/2024 22:24: Ilijan A ST-1 online at 2224H (Unplanned Outage) [WEBSMS] | CLUZ
7/4/2024 9:17:18 PM | Luzon Grid-07/04/2024 21:17: Ilijan A GT 1-1 online at 2116H (Unplanned Outage) [WEBSMS] | CLUZ
7/4/2024 8:23:15 PM | Mindanao Grid-07/04/2024 20:28: WMPC DG10 Shutdown at 2016H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/4/2024 5:50:47 PM | Visayas Grid-07/04/2024 17:50: Dumanjug SS 150MVA TR1 energized at 1750H (Planned Outage) [WEBSMS] | CVIS
7/4/2024 5:42:52 PM | Visayas Grid-07/04/2024 17:42: Dumanjug SS 230 kV bus 2 energized at 1741H (Planned Outage) [WEBSMS] | CVIS
7/4/2024 5:38:28 PM | Luzon Grid-07/04/2024 17:38: Tuguegarao 230kV Bus 2 restored at 1737H (Planned Outage) [WEBSMS] | CLUZ
7/4/2024 5:38:20 PM | [NSO Update] Mindanao Grid-07/04/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2945MW, PK=2230MW, RR=73MW, NetOpMargin: EVE=642 Highest Unit O/L: GNPK 1,2&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/4/2024 5:35:37 PM | [NSO Update] Visayas Grid-07/04/2024 17:35: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2457MW, PK=2129MW, RR=85MW, NetOpMargin: EVE=243 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @320MW, CEDC 3 @75MW, TGPP @113.5MW, PEDC 3 @120MW [WEBSMS] | CVIS
7/4/2024 5:32:22 PM | [NSO Update] Luzon Grid-07/04/2024 17:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12609MW, PK=11382MW, RR=274MW, NetOpMargin: EVE=954 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, Masinloc 1 @265MW, SLTEC 1 @118MW, SLTEC 2 @117MW, Limay 8 @30MW, Masinloc 3 @320MW, Sual 2 @600MW [WEBSMS] | CLUZ
7/4/2024 3:24:03 PM | Luzon Grid-07/04/2024 15:24: Ilijan A GT 1-2 with 12MW tripped at 1515H (Unplanned Outage) [WEBSMS] | CLUZ
7/4/2024 3:13:50 PM | Mindanao Grid-07/04/2024 15:19: Villanueva SS 10MVA Transformer no. 1 energized at 1512H. (Planned Outage) [WEBSMS] | CMIN
7/4/2024 2:54:19 PM | Visayas Grid-07/04/2024 14:54: Dumanjug SS 230 kV bus 2 de-energized at 1453H (Planned Outage) [WEBSMS] | CVIS
7/4/2024 2:45:55 PM | Visayas Grid-07/04/2024 14:45: Dumanjug SS 150MVA TR1 de-energized at 1445H (Planned Outage) [WEBSMS] | CVIS
7/4/2024 2:16:56 PM | Luzon Grid-07/04/2024 14:16: Ilijan A GT 1-2 online at 1413H (Unplanned Outage) [WEBSMS] | CLUZ
7/4/2024 2:02:51 PM | Mindanao Grid-07/04/2024 14:08: WMPC DG02 Shutdown at 1401H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/4/2024 1:41:13 PM | Mindanao Grid-07/04/2024 13:46: WMPC DG06 online at 1338H. MO dispatched. [WEBSMS] | CMIN
7/4/2024 1:09:10 PM | [NSO Update] Mindanao Grid-07/04/2024 13:14: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2975MW, PK=2384MW, RR=73MW, NetOpMargin: PM=518, EVE=605 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/4/2024 1:04:57 PM | [NSO Update] Visayas Grid-07/04/2024 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2547MW, PK=2182MW, RR=60MW, NetOpMargin: PM=305, EVE=266 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @318MW, CEDC 3 @75MW, TGPP @112.6MW, PEDC 3 @120MW, PB101-2 @5.2MW, PB101-1 @5.5MW, PB104 U2 @5.5MW, PB104 U3 @5MW [WEBSMS] | CVIS
7/4/2024 12:54:58 PM | [NSO Update] Luzon Grid-07/04/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13869MW, PK=12581MW, RR=334MW, NetOpMargin: PM=954, EVE=865 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, Masinloc 1 @265MW, SLTEC 1 @118MW, SLTEC 2 @117MW, Limay 8 @30MW, Masinloc 3 @330MW, Sual 2 @600MW [WEBSMS] | CLUZ
7/4/2024 12:39:41 PM | Mindanao Grid-07/04/2024 12:45: Liangan Hydro Plant tripped at 1231H. Indication: High vibration. (Unplanned Outage) [WEBSMS] | CMIN
7/4/2024 12:31:45 PM | Mindanao Grid-07/04/2024 12:37: Liangan Hydro Plant online at 1230H. Test & Commissioning. [WEBSMS] | CMIN
7/4/2024 12:18:33 PM | [NSO Update] Visayas Grid-07/04/2024 12:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1202H with power going to Luzon [WEBSMS] | CVIS
7/4/2024 12:18:21 PM | [NSO Update] Luzon Grid-07/04/2024 12:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1202H with power going to Luzon [WEBSMS] | CLUZ
7/4/2024 12:16:09 PM | [NSO Update] Visayas Grid-07/04/2024 12:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1152H from reverse power direction [WEBSMS] | CVIS
7/4/2024 12:15:51 PM | [NSO Update] Luzon Grid-07/04/2024 12:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1152H from reverse power direction [WEBSMS] | CLUZ
7/4/2024 11:35:01 AM | Mindanao Grid-07/04/2024 11:40: WMPC DG04 failed to start at 1127H. MO dispatched (Unplanned Outage) [WEBSMS] | CMIN
7/4/2024 11:03:35 AM | Mindanao Grid-07/04/2024 11:09: WMPC DG02 Online at 1057H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/4/2024 10:54:54 AM | Luzon Grid-07/04/2024 10:54: Ilijan GT2-1 online at 1053H (Unplanned Outage) [WEBSMS] | CLUZ
7/4/2024 10:47:55 AM | [NSO Update] Visayas Grid-07/04/2024 10:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1044H with power going to Visayas [WEBSMS] | CVIS
7/4/2024 10:46:47 AM | [NSO Update] Luzon Grid-07/04/2024 10:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1044H with power going to Visayas [WEBSMS] | CLUZ
7/4/2024 10:44:30 AM | [NSO Update] Visayas Grid-07/04/2024 10:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1034H from forward power direction [WEBSMS] | CVIS
7/4/2024 10:44:17 AM | [NSO Update] Luzon Grid-07/04/2024 10:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1034H from forward power direction [WEBSMS] | CLUZ
7/4/2024 9:22:03 AM | Mindanao Grid-07/04/2024 09:27: WMPC DG10 Online at 0919H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/4/2024 8:55:07 AM | Luzon Grid-07/04/2024 08:55: Ilijan Block A and Ilijan GT2-1 tripped at 0848H. Lowest system frequency is 59.428Hz. [WEBSMS] | CLUZ
7/4/2024 8:51:31 AM | Mindanao Grid-07/04/2024 08:57: Villanueva SS 10MVA Transformer no. 1 de-energized at 0850H. (Planned Outage) [WEBSMS] | CMIN
7/4/2024 6:11:55 AM | Luzon Grid-07/04/2024 06:11: Tuguegarao 230kV Bus 2 de-energized at 0611H (Planned Outage) [WEBSMS] | CLUZ
7/4/2024 5:55:55 AM | [NSO Update] Mindanao Grid-07/04/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2983MW, PK=2373MW, RR=73MW, NetOpMargin: AM=538, PM=496, EVE=616 Highest Unit O/L: GNPK 1,2,3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/4/2024 5:53:40 AM | [NSO Update] Visayas Grid-07/04/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2620MW, PK=2303MW, RR=60MW, NetOpMargin: AM=257, PM=231, EVE=258 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @318MW, CEDC 3 @75MW, TGPP @112.6MW, PEDC 3 @120MW, PB101-2 @5.2MW, PB101-1 @5.5MW, PB104 U2 @5.5MW, PB104 U3 @5MW [WEBSMS] | CVIS
7/4/2024 5:50:01 AM | [NSO Update] Luzon Grid-07/04/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14222MW, PK=12464MW, RR=334MW, NetOpMargin: AM=1425, PM=1286, EVE=1771 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan Block A @550MW, GNPD 2 @640MW, Masinloc 1 @265MW, SLTEC 1 @117MW, SLTEC 2 @117MW, Limay 8 @30MW, Masinloc 3 @325MW, Sual 2 @600MW, Calaca 1 @190MW [WEBSMS] | CLUZ
7/4/2024 4:20:04 AM | [NSO Update] Mindanao Grid-07/04/2024 04:25: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Palawan. Easterlies affecting the eastern sections of the country. [WEBSMS] | CMIN
7/4/2024 4:19:07 AM | [NSO Update] Visayas Grid-07/04/2024 04:19: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Palawan. Easterlies affecting the eastern sections of the country. [WEBSMS] | CVIS
7/4/2024 4:15:59 AM | [NSO Update] Luzon Grid-07/04/2024 04:15: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Palawan. Easterlies affecting the eastern sections of the country. [WEBSMS] | CLUZ
7/4/2024 12:06:00 AM | Mindanao Grid-07/04/2024 00:11: GNPK Unit 4 shutdown at 2356H. PMS (Non-GOMP) [WEBSMS] | CMIN
7/3/2024 8:55:38 PM | [NSO Update] Luzon Grid-07/03/2024 20:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2045H with power going to Luzon. [WEBSMS] | CLUZ
7/3/2024 8:55:08 PM | [NSO Update] Visayas Grid-07/03/2024 20:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2045H with power going to Luzon. [WEBSMS] | CVIS
7/3/2024 8:24:36 PM | [NSO Update] Luzon Grid-07/03/2024 20:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2022H from reverse power direction. [WEBSMS] | CLUZ
7/3/2024 8:23:23 PM | [NSO Update] Visayas Grid-07/03/2024 20:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2022H from reverse power direction. [WEBSMS] | CVIS
7/3/2024 8:20:07 PM | Mindanao Grid-07/03/2024 20:26: WMPC DG10 Shutdown at 2016H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/3/2024 7:10:04 PM | Visayas Grid-07/03/2024 19:10: Dumanjug SS 150 MVA Tr2 energized at 1909H (Planned Outage) [WEBSMS] | CVIS
7/3/2024 6:07:24 PM | [NSO Update] Luzon Grid-07/03/2024 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12796MW, PK=11554MW, RR=274MW, NetOpMargin: EVE=968 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @265MW, Limay 8 @30MW, Masinloc 3 @320MW, Sual 2 @570MW, Calaca 1 @190MW [WEBSMS] | CLUZ
7/3/2024 6:02:35 PM | [NSO Update] Mindanao Grid-07/03/2024 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3066MW, PK=2313MW, RR=73MW, NetOpMargin: EVE=680 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/3/2024 6:02:32 PM | [NSO Update] Visayas Grid-07/03/2024 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2566MW, PK=2280MW, RR=60MW, NetOpMargin: EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @320MW, CEDC 3 @75MW, PEDC 3 @120MW [WEBSMS] | CVIS
7/3/2024 5:19:00 PM | Mindanao Grid-07/03/2024 17:24: WMPC DG1 shutdown at 1716H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/3/2024 5:13:23 PM | Luzon Grid-07/03/2024 17:13: MPGC Unit 4 online at 1708H. (On-going test and commissioning.) [WEBSMS] | CLUZ
7/3/2024 5:07:05 PM | Mindanao Grid-07/03/2024 17:12: Balo-i - Agus6 69kV Tie Line energized at 1706H. (Planned Outage) [WEBSMS] | CMIN
7/3/2024 5:06:46 PM | Luzon Grid-07/03/2024 17:07: MPGC Unit 4 successfully completed the 100%(150MW) Load Rejection Test(LRT) at 1702H. (On-going test and commissioning.) [WEBSMS] | CLUZ
7/3/2024 2:31:29 PM | Luzon Grid-07/03/2024 14:31: Mexico-Concepcion 230kV line 2 auto-tripped/auto-reclosed at 1428H. (Unplanned Outage) [WEBSMS] | CLUZ
7/3/2024 1:42:13 PM | [NSO Update] Visayas Grid-07/03/2024 13:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1339H with power going to Visayas. [WEBSMS] | CVIS
7/3/2024 1:42:09 PM | [NSO Update] Luzon Grid-07/03/2024 13:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1339H with power going to Visayas. [WEBSMS] | CLUZ
7/3/2024 1:33:48 PM | [NSO Update] Luzon Grid-07/03/2024 13:33: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1329H from forward power direction. [WEBSMS] | CLUZ
7/3/2024 1:31:42 PM | [NSO Update] Visayas Grid-07/03/2024 13:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1329H from forward power direction. [WEBSMS] | CVIS
7/3/2024 1:06:51 PM | Mindanao Grid-07/03/2024 13:12: WMPC DG1 Online at 1304H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/3/2024 12:53:56 PM | [NSO Update] Visayas Grid-07/03/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2586MW, PK=2445MW, RR=60MW, NetOpMargin: PM=223, EVE=220 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @320MW, CEDC 3 @75MW, PEDC 3 @120MW [WEBSMS] | CVIS
7/3/2024 12:51:52 PM | [NSO Update] Mindanao Grid-07/03/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3112MW, PK=2423MW, RR=73MW, NetOpMargin: PM=616, EVE=738 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/3/2024 12:49:33 PM | [NSO Update] Luzon Grid-07/03/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14018MW, PK=12476MW, RR=334MW, NetOpMargin: PM=1208, EVE=1262 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @265MW, Limay 8 @30MW, Masinloc 3 @300MW, Sual 2 @550MW, Calaca 1 @210MW [WEBSMS] | CLUZ
7/3/2024 11:43:14 AM | Mindanao Grid-07/03/2024 11:49: WMPC DG10 Online at 1141H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/3/2024 9:05:08 AM | Mindanao Grid-07/03/2024 09:11: Agus6 HEPP U5 shutdown at 0901H. (Planned Outage) [WEBSMS] | CMIN
7/3/2024 8:40:50 AM | Mindanao Grid-07/03/2024 08:46: Balo-i - Agus6 69kV Tie Line de-energized/shutdown at 0839H. (Planned Outage) [WEBSMS] | CMIN
7/3/2024 7:43:10 AM | [NSO Update] Visayas Grid-07/03/2024 07:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0739H with power going to Luzon. [WEBSMS] | CVIS
7/3/2024 7:42:37 AM | [NSO Update] Luzon Grid-07/03/2024 07:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0739H with power going to Luzon. [WEBSMS] | CLUZ
7/3/2024 6:14:26 AM | [NSO Update] Luzon Grid-07/03/2024 06:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0608H from forward power direction. [WEBSMS] | CLUZ
7/3/2024 6:12:36 AM | [NSO Update] Visayas Grid-07/03/2024 06:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0608H from forward power direction. [WEBSMS] | CVIS
7/3/2024 5:54:04 AM | [NSO Update] Luzon Grid-07/03/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14278MW, PK=11759MW, RR=334MW, NetOpMargin: AM=2185, PM=1042, EVE=1352 Highest Unit O/L: GNPD 1@668MW Derated Plant: Ilijan Block A @550MW, GNPD 2 @640MW, Masinloc 1 @265MW, SLTEC 1 @117MW, SLTEC 2 @117MW, Limay 8 @30MW, Masinloc 3 @330MW, Sual 2 @550MW [WEBSMS] | CLUZ
7/3/2024 5:40:35 AM | [NSO Update] Mindanao Grid-07/03/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3147MW, PK=2306MW, RR=73MW, NetOpMargin: AM=768, PM=589, EVE=725 Highest Unit O/L: GNPK 1, 2, 3 & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/3/2024 5:36:54 AM | [NSO Update] Visayas Grid-07/03/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2569MW, PK=2184MW, RR=60MW, NetOpMargin: AM=326, PM=208, EVE=240 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @320MW, CEDC 3 @75MW, TGPP @117.5MW, PEDC 3 @70MW, PB101-2 @5.2MW, PDPP3-E @8MW, PB104 U2 @5.5MW, PB104 U3 @5MW [WEBSMS] | CVIS
7/3/2024 4:11:57 AM | [NSO Update] Mindanao Grid-07/03/2024 04:17: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Palawan and Western Mindanao. Easterlies affecting the eastern sections of the country. [WEBSMS] | CMIN
7/3/2024 4:10:48 AM | [NSO Update] Visayas Grid-07/03/2024 04:11: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Palawan and Western Mindanao. Easterlies affecting the eastern sections of the country. [WEBSMS] | CVIS
7/3/2024 4:10:22 AM | [NSO Update] Luzon Grid-07/03/2024 04:10: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Palawan and Western Mindanao. Easterlies affecting the eastern sections of the country. [WEBSMS] | CLUZ
7/3/2024 4:03:51 AM | Luzon Grid-07/03/2024 04:04: SCPC Unit 1 shutdown at 0403H (Unplanned Outage) [WEBSMS] | CLUZ
7/3/2024 12:27:42 AM | Luzon Grid-07/03/2024 00:27: Ilijan GT1-2 online at 0027H (Unplanned Outage) [WEBSMS] | CLUZ
7/2/2024 11:57:55 PM | Luzon Grid-07/02/2024 23:58: San Lorenzo 60 shutdown at 2357H (Planned Outage) [WEBSMS] | CLUZ
7/2/2024 11:10:18 PM | Luzon Grid-07/02/2024 23:10: Ilijan A ST1 online at 2309H (Unplanned Outage) [WEBSMS] | CLUZ
7/2/2024 9:31:14 PM | Mindanao Grid-07/02/2024 21:37: WMPC DG10 Shutdown at 2130H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/2/2024 9:23:01 PM | [NSO Update] Visayas Grid-07/02/2024 21:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2113H with power going to Luzon. [WEBSMS] | CVIS
7/2/2024 9:20:56 PM | Luzon Grid-07/02/2024 21:21: Ilijan A GT1-1 online at 2119H (Unplanned Outage) [WEBSMS] | CLUZ
7/2/2024 9:16:13 PM | [NSO Update] Luzon Grid-07/02/2024 21:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2113H with power going to Luzon. [WEBSMS] | CLUZ
7/2/2024 8:03:14 PM | [NSO Update] Visayas Grid-07/02/2024 20:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2002H from reverse power direction. [WEBSMS] | CVIS
7/2/2024 8:03:09 PM | [NSO Update] Luzon Grid-07/02/2024 20:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2002H from reverse power direction. [WEBSMS] | CLUZ
7/2/2024 5:52:32 PM | [NSO Update] Luzon Grid-07/02/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12477MW, PK=10976MW, RR=311MW, NetOpMargin: EVE=1191 Highest Unit O/L: GNPD 1@668MW Derated Plant: GNPD 2 @640MW, Masinloc 1 @265MW, SLTEC 1 @117MW, SLTEC 2 @117MW, Limay 8 @30MW, SCPC 1 @90MW [WEBSMS] | CLUZ
7/2/2024 5:49:44 PM | [NSO Update] Mindanao Grid-07/02/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3178MW, PK=2298MW, RR=73MW, NetOpMargin: EVE=807 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/2/2024 5:48:27 PM | [NSO Update] Visayas Grid-07/02/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2517MW, PK=2180MW, RR=60MW, NetOpMargin: EVE=277 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @320MW, CEDC 3 @75MW, TGPP @116.5MW, PEDC 3 @120MW, PB101-2 @5.2MW, PDPP3-E @8MW, PB104 U4 @7MW, PDPP3-H @8MW, PB104 U2 @4.5MW, PB104 U3 @5MW [WEBSMS] | CVIS
7/2/2024 5:41:55 PM | Luzon Grid-07/02/2024 17:42: Balsik - San Marcelino 230kV Line 2 and Line 1 restored at 1736H/1737H respectively (Unplanned Outage). [WEBSMS] | CLUZ
7/2/2024 5:32:35 PM | Luzon Grid-07/02/2024 17:32: Ilijan Block A with 339MW load tripped at 1724H. Lowest Frequency is 59.31Hz (Unplanned Outage) [WEBSMS] | CLUZ
7/2/2024 5:16:09 PM | Mindanao Grid-07/02/2024 17:22: WMPC DG01 Shutdown at 1716H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/2/2024 4:22:51 PM | Mindanao Grid-07/02/2024 16:28: Agus 6 U3 online at 1616H. (Planned Outage) [WEBSMS] | CMIN
7/2/2024 3:52:02 PM | Luzon Grid-07/02/2024 15:52: Balsik-San Marcelino 230kV Line 1 tripped but reclosed at Balsik side at 1541H. Balsik-San Marcelino 230kV Line 2 was unloop due to opening of San Marcelino PCB CB04(8LI2BIK-SMK)SMK resulting to isolation of San Marcelino Solar Plant (Unplanned Outage) [WEBSMS] | CLUZ
7/2/2024 3:17:30 PM | Mindanao Grid-07/02/2024 15:23: WMPC DG06 Shutdown at 1516H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/2/2024 2:56:06 PM | Visayas Grid-07/02/2024 14:56: Toledo SS 30MVA TR1 energized at 1452H (Planned Outage) [WEBSMS] | CVIS
7/2/2024 2:05:49 PM | Visayas Grid-07/02/2024 14:06: Pal 1 U3 cut in at 1049H (Unplanned Outage) [WEBSMS] | CVIS
7/2/2024 2:04:23 PM | Visayas Grid-07/02/2024 14:04: Pal 1 U3 tripped at 1033H (Unplanned Outage) [WEBSMS] | CVIS
7/2/2024 1:49:16 PM | Mindanao Grid-07/02/2024 13:55: WMPC DG06 Online at 1346H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/2/2024 1:47:53 PM | [NSO Update] Visayas Grid-07/02/2024 13:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2563MW, PK=2307MW, RR=60MW, NetOpMargin: PM=196, EVE=250 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @302MW, CEDC 3 @75MW, TGPP @116.5MW, PB101-2 @5.2MW, PDPP3-E @8MW, PB104 U4 @7MW, PDPP3-H @8MW, PB104 U2 @4.5MW, PB104 U3 @5MW [WEBSMS] | CVIS
7/2/2024 12:42:55 PM | [NSO Update] Luzon Grid-07/02/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14471MW, PK=12808MW, RR=334MW, NetOpMargin: PM=1328, EVE=1241 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @265MW, SLTEC 1 @117MW, SLTEC 2 @117MW, Limay 8 @30MW, SCPC 1 @90MW [WEBSMS] | CLUZ
7/2/2024 12:41:07 PM | [NSO Update] Mindanao Grid-07/02/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3171MW, PK=2453MW, RR=73MW, NetOpMargin: PM=645, EVE=775 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
7/2/2024 11:11:28 AM | Mindanao Grid-07/02/2024 11:17: WMPC DG01 Online at 1108H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/2/2024 9:33:05 AM | Visayas Grid-07/02/2024 09:33: Toledo SS 30MVA TR 1 de-energized at 0928H (Planned Outage) [WEBSMS] | CVIS
7/2/2024 9:25:48 AM | Mindanao Grid-07/02/2024 09:31: WMPC DG10 Online at 0923H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/2/2024 9:25:42 AM | [NSO Update] Luzon Grid-07/02/2024 09:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0924H with power going to Visayas. [WEBSMS] | CLUZ
7/2/2024 9:25:28 AM | [NSO Update] Visayas Grid-07/02/2024 09:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0924H with power going to Visayas. [WEBSMS] | CVIS
7/2/2024 9:16:06 AM | [NSO Update] Visayas Grid-07/02/2024 09:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0914H from forward power direction. [WEBSMS] | CVIS
7/2/2024 9:15:50 AM | [NSO Update] Luzon Grid-07/02/2024 09:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0914H from forward power direction. [WEBSMS] | CLUZ
7/2/2024 9:09:37 AM | Visayas Grid-07/02/2024 09:09: PEDC U3 cut-in at 0904H (Unplanned Outage) [WEBSMS] | CVIS
7/2/2024 9:07:12 AM | Visayas Grid-07/02/2024 09:07: Dumanjug SS Transformer 2 de-energized at 0851H (Planned Outage) [WEBSMS] | CVIS
7/2/2024 5:48:52 AM | [NSO Update] Mindanao Grid-07/02/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3175MW, PK=2305MW, RR=73MW, NetOpMargin: AM=798, PM=780, EVE=979 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @27.5MW [WEBSMS] | CMIN
7/2/2024 5:47:51 AM | [NSO Update] Visayas Grid-07/02/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2536MW, PK=2221MW, RR=60MW, NetOpMargin: AM=255, PM=218, EVE=239 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @320MW, CEDC 3 @75MW, TGPP @116.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP3-G @10MW, PB104 U4 @7MW, PDPP3-H @8MW, PB104 U2 @4.5MW, PB104 U3 @5MW [WEBSMS] | CVIS
7/2/2024 5:45:09 AM | [NSO Update] Luzon Grid-07/02/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14649MW, PK=12130MW, RR=334MW, NetOpMargin: AM=2184, PM=1357, EVE=1108 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, SLTEC 1 @117MW, SLTEC 2 @117MW, Limay 8 @30MW, SCPC 1 @90MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
7/2/2024 4:07:13 AM | [NSO Update] Mindanao Grid-07/02/2024 04:13: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Palawan and Southern Mindanao. Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CMIN
7/2/2024 4:06:51 AM | [NSO Update] Visayas Grid-07/02/2024 04:07: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Palawan and Southern Mindanao. Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CVIS
7/2/2024 4:06:32 AM | [NSO Update] Luzon Grid-07/02/2024 04:06: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Palawan and Southern Mindanao. Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CLUZ
7/2/2024 4:04:05 AM | Mindanao Grid-07/02/2024 04:09: Agus6 SS 138/69kV 100MVA Tie Power Transformer 3 (7XF03AG6) energized/looped at 0401H. (Unplanned Outage) [WEBSMS] | CMIN
7/2/2024 1:27:22 AM | Mindanao Grid-07/02/2024 01:33: Agus6 SS138/69kV 100MVA Tie Power Transformer 3 tripped at 0051H. (Unplanned Outage) [WEBSMS] | CMIN
7/2/2024 12:20:58 AM | Mindanao Grid-07/02/2024 00:26: STEAG U1 shutdown at 0000H. (Planned Outage) [WEBSMS] | CMIN
7/1/2024 10:00:00 PM | [NSO Update] Visayas Grid-07/01/2024 22:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2151H with power going to Luzon [WEBSMS] | CVIS
7/1/2024 9:59:30 PM | [NSO Update] Luzon Grid-07/01/2024 21:59: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2151H with power going to Luzon [WEBSMS] | CLUZ
7/1/2024 9:44:48 PM | [NSO Update] Luzon Grid-07/01/2024 21:45: undefined at 2141H Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2141H from reverse power direction [WEBSMS] | CLUZ
7/1/2024 9:44:12 PM | [NSO Update] Visayas Grid-07/01/2024 21:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2141H from reverse power direction [WEBSMS] | CVIS
7/1/2024 6:01:45 PM | [NSO Update] Luzon Grid-07/01/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13187MW, PK=11548MW, RR=404MW, NetOpMargin: EVE=1234 Highest Unit O/L: GNPD 1@668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, SLTEC 1 @116MW, SLTEC 2 @117MW, Limay 8 @30MW, SCPC 1 @75MW, Masinloc 3 @325MW [WEBSMS] | CLUZ
7/1/2024 5:54:48 PM | [NSO Update] Visayas Grid-07/01/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2537MW, PK=2205MW, RR=90MW, NetOpMargin: EVE=242 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @317MW, CEDC 3 @75MW, TGPP @116.5MW, PEDC U3 @120MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP3-G @10MW, PB104 U4 @7MW, PDPP3-H @8MW, PB104 U2 @4.5MW, PB104 U2 @5MW [WEBSMS] | CVIS
7/1/2024 5:50:46 PM | [NSO Update] Mindanao Grid-07/01/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3268MW, PK=2216MW, RR=73MW, NetOpMargin: EVE=980 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32.5MW [WEBSMS] | CMIN
7/1/2024 5:34:22 PM | Mindanao Grid-07/01/2024 17:40: WMPC DG10 Shutdown at 1731H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/1/2024 5:13:19 PM | Luzon Grid-07/01/2024 17:13: MPGC 4 online at 1712H (On-going testing and commissioning). [WEBSMS] | CLUZ
7/1/2024 5:07:16 PM | Luzon Grid-07/01/2024 17:07: MPGC Unit 4 from 113MW (75%) conducted load rejection test (LRT) at 1706H. (On-going test and commissioning.) [WEBSMS] | CLUZ
7/1/2024 4:01:49 PM | Luzon Grid-07/01/2024 16:02: San Gabriel online at 1600H (from Reserve shutdown) [WEBSMS] | CLUZ
7/1/2024 3:59:05 PM | Luzon Grid-07/01/2024 15:59: Kalayaan 3 with 180MW tripped at 1556H. Lowest system frequency was 59.478Hz. (Unplanned Outage) [WEBSMS] | CLUZ
7/1/2024 12:57:21 PM | [NSO Update] Mindanao Grid-07/01/2024 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3300MW, PK=2353MW, RR=73MW, NetOpMargin: PM=875, EVE=1027 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32.5MW [WEBSMS] | CMIN
7/1/2024 12:55:15 PM | [NSO Update] Visayas Grid-07/01/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2685MW, PK=2368MW, RR=91MW, NetOpMargin: PM=226, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @310MW, CEDC 3 @75MW, TGPP @116.5MW, PEDC U3 @120MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP3-G @10MW, PDPP 3-E @8MW, PDPP3-H @8MW, PB104 U2 @4.5MW, PB104 U4 @7MW [WEBSMS] | CVIS
7/1/2024 12:52:40 PM | [NSO Update] Luzon Grid-07/01/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14522MW, PK=12296MW, RR=424MW, NetOpMargin: PM=1802, EVE=1552 Highest Unit O/L: GNPD 1@668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, SLTEC 1 @116MW, SLTEC 2 @117MW, Limay 8 @30MW, SCPC 1 @75MW, Masinloc 3 @325MW, Calaca 1 @200MW [WEBSMS] | CLUZ
7/1/2024 11:07:19 AM | Mindanao Grid-07/01/2024 11:13: Agus6 U3 shutdown at 1103H. (Planned Outage) [WEBSMS] | CMIN
7/1/2024 10:59:44 AM | Mindanao Grid-07/01/2024 11:05: Agus6 U2 online at 1052H. (Unplanned Outage) [WEBSMS] | CMIN
7/1/2024 10:41:50 AM | Mindanao Grid-07/01/2024 10:47: WMPC DG10 Online at 1025H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/1/2024 9:38:02 AM | [NSO Update] Luzon Grid-07/01/2024 09:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0921H power to Visayas. [WEBSMS] | CLUZ
7/1/2024 9:37:38 AM | [NSO Update] Visayas Grid-07/01/2024 09:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0921H power to Visayas. [WEBSMS] | CVIS
7/1/2024 9:15:13 AM | [NSO Update] Luzon Grid-07/01/2024 09:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0911H from forward power direction. [WEBSMS] | CLUZ
7/1/2024 9:14:39 AM | [NSO Update] Visayas Grid-07/01/2024 09:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0911H from forward power direction. [WEBSMS] | CVIS
7/1/2024 9:07:59 AM | Mindanao Grid-07/01/2024 09:13: Agus 6 U2 tripped with 30.9MW load at 0851H.The lowest frequency recorded is 59.51Hz. (Unplanned Outage) [WEBSMS] | CMIN
7/1/2024 8:31:36 AM | Mindanao Grid-07/01/2024 08:37: Agus6 SS - Agus7 138kV L1 (7LI1AG6-AG7) de-energized/shutdown at 0824H. (Planned Outage) [WEBSMS] | CMIN
7/1/2024 8:16:46 AM | Mindanao Grid-07/01/2024 08:22: Agus2 U2 shutdown at 0811H. (Planned Outage) [WEBSMS] | CMIN
7/1/2024 7:04:38 AM | Mindanao Grid-07/01/2024 07:10: Agus7 U1 shutdown at 0701H. (Planned Outage) [WEBSMS] | CMIN
7/1/2024 6:15:15 AM | Luzon Grid-07/01/2024 06:15: EDC Burgos 115kV Bus 1 and 75MVA T01 were de-energized at 0609H. (Planned Outage) [WEBSMS] | CLUZ
7/1/2024 6:13:29 AM | Luzon Grid-07/01/2024 06:13: QPPL online at 0608H. (From Maintenance Outage) [WEBSMS] | CLUZ
7/1/2024 6:03:45 AM | [NSO Update] Mindanao Grid-07/01/2024 06:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3314MW, PK=2243MW, RR=73MW, NetOpMargin: AM=998, PM=889, EVE=1050 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32.5MW [WEBSMS] | CMIN
7/1/2024 5:53:29 AM | [NSO Update] Visayas Grid-07/01/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2570MW, PK=2223MW, RR=91MW, NetOpMargin: AM=256, PM=231, EVE=275 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @314MW, CEDC 3 @75MW, TGPP @116MW, PEDC U3 @120MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP3-G @10MW, PDPP 3-E @8MW, PDPP3-H @8MW, GTEC @7MW, PB104 U2 @4.5MW, PB104 U3 @6MW, PB104 U4 @7MW [WEBSMS] | CVIS
7/1/2024 5:41:43 AM | [NSO Update] Luzon Grid-07/01/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14199MW, PK=11773MW, RR=424MW, NetOpMargin: AM=2003, PM=929, EVE=1091 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, SLTEC 1 @116MW, SLTEC 2 @117MW, Limay 8 @30MW, SCPC 1 @90MW [WEBSMS] | CLUZ
7/1/2024 5:11:06 AM | [NSO Update] Mindanao Grid-07/01/2024 05:16: Weather Update: Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CMIN
7/1/2024 5:10:52 AM | [NSO Update] Visayas Grid-07/01/2024 05:11: Weather Update: Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CVIS
7/1/2024 5:10:39 AM | [NSO Update] Luzon Grid-07/01/2024 05:10: Weather Update: Easterlies affecting the eastern sections of Luzon and Visayas. [WEBSMS] | CLUZ
7/1/2024 12:57:28 AM | Luzon Grid-07/01/2024 00:57: San Jose SS PCB 9Z-03CB04SJO energized at 0055H (Planned Outage) [WEBSMS] | CLUZ
7/1/2024 12:50:12 AM | Luzon Grid-07/01/2024 00:50: Pagbilao 1 shutdown at 0049H (Planned Outage) [WEBSMS] | CLUZ
7/1/2024 12:08:20 AM | Luzon Grid-07/01/2024 00:08: MPGC 1shutdown at 0006H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 11:20:54 PM | Luzon Grid-06/30/2024 23:21: San Jose SS PCB 9Z-03CB04SJO de-energized at 2320H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 5:48:08 PM | [NSO Update] Luzon Grid-06/30/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13531MW, PK=10480MW, RR=339MW, NetOpMargin: EVE=2712 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, Masinloc 3 @320MW, SLTEC 1 @116MW, SLTEC 2 @117MW, Limay 8 @60MW, SCPC 1 @90MW, SCPC 3 @140MW, SCPC 4 @140MW [WEBSMS] | CLUZ
6/30/2024 5:41:07 PM | Luzon Grid-06/30/2024 17:41: Muntinlupa (Sucat) 115kV Bus 1 energized at 1739H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 5:40:45 PM | [NSO Update] Visayas Grid-06/30/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2471MW, PK=2046MW, RR=86MW, NetOpMargin: EVE=339 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @315MW, PDPP3-H @8MW, CEDC 3 @75MW, TGPP @116.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-G @10MW, PEDC U3 @70MW, PDPP 3-E @8MW [WEBSMS] | CVIS
6/30/2024 5:40:35 PM | [NSO Update] Mindanao Grid-06/30/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3278MW, PK=2077MW, RR=73MW, NetOpMargin: EVE=1128 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/30/2024 5:12:38 PM | Luzon Grid-06/30/2024 17:12: Tayabas-Naga 230kV Line 2 restored at 1712H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 5:12:21 PM | Luzon Grid-06/30/2024 17:12: MPGC 4 online at 1711H (on commissioning) [WEBSMS] | CLUZ
6/30/2024 5:04:39 PM | Luzon Grid-06/30/2024 17:04: MPGC 4 load reject with 77MW at 1703H (on commissioning) [WEBSMS] | CLUZ
6/30/2024 4:48:10 PM | Luzon Grid-06/30/2024 16:48: San Jose 750MVA T05 restored at 1647H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 4:46:22 PM | Luzon Grid-06/30/2024 16:46: Santiago-Magat HEPP 230kV Line 1 restored at 1645H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 4:40:36 PM | Mindanao Grid-06/30/2024 16:46: Pulangi4 U3 online at 1622H from emergency shutdown. [WEBSMS] | CMIN
6/30/2024 3:30:20 PM | Luzon Grid-06/30/2024 15:30: Laoag SS 230kV Bus 2 restored at 1528H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 3:19:42 PM | Luzon Grid-06/30/2024 15:19: Muntinlupa SS 115kV Bus 1 de-energized at 1517H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 3:01:31 PM | Luzon Grid-06/30/2024 15:01: Muntinlupa SS 115kV Bus 2 restored at 1501H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 2:47:18 PM | Visayas Grid-06/30/2024 14:47: Carcon - Sangi 34.5 kV Line 2 energized at 1446H (Planned Outage) [WEBSMS] | CVIS
6/30/2024 2:41:41 PM | Luzon Grid-06/30/2024 14:41: La Trinidad-Bauang 230kV Line 1 restored at 1441H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 1:19:20 PM | Luzon Grid-06/30/2024 13:19: San Jose-Balsik 500kV Line restored at 1319H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 12:58:03 PM | [NSO Update] Mindanao Grid-06/30/2024 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2646MW, PK=1922MW, RR=85MW, NetOpMargin: PM=639, EVE=310 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/30/2024 12:55:02 PM | [NSO Update] Visayas Grid-06/30/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2646MW, PK=1922MW, RR=85MW, NetOpMargin: PM=639, EVE=310 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @300MW, PDPP3-H @8MW, CEDC 3 @75MW, TGPP @114.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PB104-2 @5.5MW, PB104-3 @6MW, PB104-4 @7MW, PDPP1-2 @4.5MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-G @10MW, PEDC U3 @70MW, PDPP 3-E @8MW [WEBSMS] | CVIS
6/30/2024 12:50:03 PM | [NSO Update] Luzon Grid-06/30/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14836MW, PK=10623MW, RR=356MW, NetOpMargin: PM=3857, EVE=2701 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, Masinloc 3 @310MW, SLTEC 1 @116MW, SLTEC 2 @117MW, Limay 8 @60MW, SCPC 1 @90MW, SCPC 3 @130MW, SCPC 4 @130MW [WEBSMS] | CLUZ
6/30/2024 9:47:11 AM | Mindanao Grid-06/30/2024 09:52: Pulangi4 U3 on emergency shutdown at 0918H due to electronic governor failure. [WEBSMS] | CMIN
6/30/2024 8:52:55 AM | Visayas Grid-06/30/2024 08:53: KSPC U2 emergency shutdown at 0850H (Unplanned Outage) [WEBSMS] | CVIS
6/30/2024 8:44:43 AM | Visayas Grid-06/30/2024 08:44: Carcon - Sangi 34.5 kV Line 2 de-energized at 0844H (Planned Outage) [WEBSMS] | CVIS
6/30/2024 8:12:11 AM | Luzon Grid-06/30/2024 08:12: Santiago-Magat HEPP 230kV Line 1 de-energized at 0811H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 8:05:15 AM | [NSO Update] Visayas Grid-06/30/2024 08:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0752H with power going to Luzon [WEBSMS] | CVIS
6/30/2024 8:04:24 AM | Luzon Grid-06/30/2024 08:04: La Trinidad-Bauang 230kV Line 1 de-energized at 0803H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 8:04:09 AM | [NSO Update] Luzon Grid-06/30/2024 08:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0752H with power going to Luzon [WEBSMS] | CLUZ
6/30/2024 7:49:58 AM | [NSO Update] Visayas Grid-06/30/2024 07:50: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0742H from reverse power direction [WEBSMS] | CVIS
6/30/2024 7:49:14 AM | [NSO Update] Luzon Grid-06/30/2024 07:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0742H from reverse power direction [WEBSMS] | CLUZ
6/30/2024 7:10:19 AM | Luzon Grid-06/30/2024 07:10: Muntinlupa SS 115kV Bus 2 de-energized at 0710H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 6:34:49 AM | Luzon Grid-06/30/2024 06:34: Tayabas-Naga 230kV Line 2 de-energized at 0634H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 5:56:04 AM | [NSO Update] Visayas Grid-06/30/2024 05:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0554H with power going to Visayas. [WEBSMS] | CVIS
6/30/2024 5:55:24 AM | [NSO Update] Luzon Grid-06/30/2024 05:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0554H with power going to Visayas. [WEBSMS] | CLUZ
6/30/2024 5:47:04 AM | Mindanao Grid-06/30/2024 05:52: WMPC DG04 Shutdown at 0546H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/30/2024 5:44:27 AM | [NSO Update] Luzon Grid-06/30/2024 05:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0542H from forward power direction. [WEBSMS] | CLUZ
6/30/2024 5:44:09 AM | [NSO Update] Visayas Grid-06/30/2024 05:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0542H from forward power direction. [WEBSMS] | CVIS
6/30/2024 5:41:12 AM | [NSO Update] Luzon Grid-06/30/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15003MW, PK=10174MW, RR=356MW, NetOpMargin: AM=4473, PM=3705, EVE=2668 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, Masinloc 3 @310MW, SLTEC 1 @116MW, SLTEC 2 @117MW, Limay 8 @60MW, SCPC 1 @90MW, SCPC 3 @130MW, SCPC 4 @130MW [WEBSMS] | CLUZ
6/30/2024 5:37:42 AM | Luzon Grid-06/30/2024 05:37: Limay-Orion Solar 69kV Line restored at 0537H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 5:31:58 AM | Luzon Grid-06/30/2024 05:32: Laoag SS 230kV Bus 2 de-energized at 0531H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 5:24:25 AM | [NSO Update] Mindanao Grid-06/30/2024 05:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3292MW, PK=1956MW, RR=73MW, NetOpMargin: AM=1264, PM=1118, EVE=1046 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/30/2024 5:23:18 AM | [NSO Update] Visayas Grid-06/30/2024 05:23: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2719MW, PK=1769MW, RR=83MW, NetOpMargin: AM=867, PM=752, EVE=428 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @317MW, KSPC 2 @50MW, CEDC 3 @75MW, TGPP @114.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PB104-2 @5.5MW, PB104-3 @6MW, PB104-4 @7MW, PDPP1-2 @4.5MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/30/2024 5:20:13 AM | Mindanao Grid-06/30/2024 05:25: Aurora - Nagamin 138kV Line 1 energized at 0514H. (Planned Outage) [WEBSMS] | CMIN
6/30/2024 5:02:51 AM | [NSO Update] Luzon Grid-06/30/2024 05:02: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
6/30/2024 5:02:19 AM | Luzon Grid-06/30/2024 05:02: San Jose-Balsik 500kV Line de-energized at 0502H (Planned Outage) [WEBSMS] | CLUZ
6/30/2024 5:01:52 AM | [NSO Update] Mindanao Grid-06/30/2024 05:07: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
6/30/2024 5:01:41 AM | [NSO Update] Visayas Grid-06/30/2024 05:01: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
6/30/2024 3:56:52 AM | Luzon Grid-06/30/2024 03:57: San Gabriel shutdown at 0347H (Reserve Shutdown) [WEBSMS] | CLUZ
6/30/2024 12:25:56 AM | Mindanao Grid-06/30/2024 00:31: Aurora - Nagamin 138kV Line 1 de-energized at 0023H. (Planned Outage) [WEBSMS] | CMIN
6/30/2024 12:04:30 AM | Mindanao Grid-06/30/2024 00:10: WMPC DG04 Online at 0003H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/29/2024 9:16:19 PM | Luzon Grid-06/29/2024 21:16: San Gabriel online at 2114H (Reserve Shutdown) [WEBSMS] | CLUZ
6/29/2024 8:46:34 PM | Mindanao Grid-06/29/2024 20:52: WMPC DG04 Shutdown at 2046H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/29/2024 8:30:46 PM | Luzon Grid-06/29/2024 20:30: Subic 230kV Bus 2 restored at 2030H (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 7:19:43 PM | Luzon Grid-06/29/2024 19:19: Limay-Orion Solar 69kV Line de-energized at 1915H (Planned Outage). [WEBSMS] | CLUZ
6/29/2024 6:14:49 PM | [NSO Update] Luzon Grid-06/29/2024 18:14: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13426MW, PK=10998MW, RR=339MW, NetOpMargin: EVE=2090 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, SCPC 1 @110MW, SLTEC 1 @116MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc 3 @280MW, SCPC 3 @125MW, SCPC 4 @120MW [WEBSMS] | CLUZ
6/29/2024 6:04:07 PM | [NSO Update] Mindanao Grid-06/29/2024 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3273MW, PK=2163MW, RR=73MW, NetOpMargin: EVE=1036 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/29/2024 6:03:18 PM | [NSO Update] Visayas Grid-06/29/2024 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2656MW, PK=2101MW, RR=87MW, NetOpMargin: EVE=467 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @317MW, PEDC 3 @120MW, PDPP3-E @8MW, CEDC 3 @75MW, TGPP @114.5MW, PDPP3-G @10MW, PB104-2 @5.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, PDPP1-3 @4.5MW, PDPP1-5 @4MW, PB104-3 @6MW, PB104-4 @7MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/29/2024 5:47:18 PM | Luzon Grid-06/29/2024 17:47: GMEC Unit 2 shutdown at 1747H (Unplanned Outage) [WEBSMS] | CLUZ
6/29/2024 5:34:25 PM | Luzon Grid-06/29/2024 17:34: Tayabas-Naga 230kV Line 1 restored at 1734H (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 5:24:07 PM | Luzon Grid-06/29/2024 17:24: San Jose-Angat 115kV Line 1 restored at 1722H (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 4:33:29 PM | Visayas Grid-06/29/2024 16:33: Dumanjug - Samboan 138 kV Line 2 energized at 1632H (Planned Outage) [WEBSMS] | CVIS
6/29/2024 4:14:08 PM | Visayas Grid-06/29/2024 16:14: Samboan - Ginatilan 69 kV Line energized at 1554H (Planned Outage) [WEBSMS] | CVIS
6/29/2024 4:11:38 PM | Visayas Grid-06/29/2024 16:11: Samboan 30 MVA 138/69/13.8 kV TR1 energized at 1551H (Planned Outage) [WEBSMS] | CVIS
6/29/2024 4:10:06 PM | Visayas Grid-06/29/2024 16:10: Samboan SS 50 MVA 138/69/13.8 kV TR2 energized at 1550H (Planned Outage) [WEBSMS] | CVIS
6/29/2024 3:42:01 PM | Luzon Grid-06/29/2024 15:42: Laoag 230kV Bus 1 restored at 1541H (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 3:21:13 PM | Mindanao Grid-06/29/2024 15:26: Liangan Hydro Plant online at 1519H. Test & Commissioning. [WEBSMS] | CMIN
6/29/2024 3:07:26 PM | Mindanao Grid-06/29/2024 15:13: Liangan Hydro Plant online at 1500H but tripped at 1503H with 1MW load. Test & Commissioning. (Planned Outage) [WEBSMS] | CMIN
6/29/2024 2:23:40 PM | Visayas Grid-06/29/2024 14:23: Compostela - Consolacion 69 kV Line energized at 1421H (Planned Outage) [WEBSMS] | CVIS
6/29/2024 2:23:32 PM | Mindanao Grid-06/29/2024 14:29: WMPC DG10 running as RPS shutdown at 1416H due to exhaust gas leak. Replaced by WMPC DG04. (Unplanned Outage) [WEBSMS] | CMIN
6/29/2024 2:05:28 PM | Mindanao Grid-06/29/2024 14:11: WMPC DG04 online at 1357H as replacement RPS for WMPC DG10. RPS-system voltage requirement. [WEBSMS] | CMIN
6/29/2024 12:44:49 PM | Luzon Grid-06/29/2024 12:44: Ambuklao - Bayombong 230kV Line 1 restored at 1244H (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 12:40:04 PM | [NSO Update] Mindanao Grid-06/29/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3292MW, PK=2168MW, RR=73MW, NetOpMargin: PM=1051, EVE=1039 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/29/2024 12:39:57 PM | [NSO Update] Visayas Grid-06/29/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2663MW, PK=2087MW, RR=89MW, NetOpMargin: PM=487, EVE=378 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @313MW, PEDC 3 @120MW, PDPP3-E @8MW, CEDC 3 @75MW, TGPP @113.5MW, PDPP3-G @10MW, PB104-2 @5.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, PDPP1-3 @4.5MW, PDPP1-5 @4MW, PDPP3-H @8MW, Nasulo @40MW [WEBSMS] | CVIS
6/29/2024 12:39:23 PM | [NSO Update] Luzon Grid-06/29/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15212MW, PK=11681MW, RR=356MW, NetOpMargin: PM=3175, EVE=2065 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, SCPC 1 @90MW, SLTEC 1 @116MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc 3 @285MW [WEBSMS] | CLUZ
6/29/2024 11:42:01 AM | Luzon Grid-06/29/2024 11:42: MPGC 4 online at 1141H (On-going testing and commissioning) [WEBSMS] | CLUZ
6/29/2024 11:34:30 AM | Luzon Grid-06/29/2024 11:34: MPGC 4 tripped at 1109H (On-going testing and commissioning) [WEBSMS] | CLUZ
6/29/2024 11:08:42 AM | Mindanao Grid-06/29/2024 11:14: WMPC DG10 Online at 1103H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/29/2024 10:39:17 AM | Luzon Grid-06/29/2024 10:39: Balsik SS PCB 9Z-01CB04BIK energized at 1039H (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 10:28:03 AM | [NSO Update] Visayas Grid-06/29/2024 10:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1025H with power going to Luzon. [WEBSMS] | CVIS
6/29/2024 10:27:43 AM | [NSO Update] Luzon Grid-06/29/2024 10:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1025H with power going to Luzon. [WEBSMS] | CLUZ
6/29/2024 10:15:13 AM | [NSO Update] Visayas Grid-06/29/2024 10:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1014H from reverse power direction. [WEBSMS] | CVIS
6/29/2024 10:14:59 AM | [NSO Update] Luzon Grid-06/29/2024 10:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1014H from reverse power direction. [WEBSMS] | CLUZ
6/29/2024 9:41:55 AM | Luzon Grid-06/29/2024 09:42: Nagsaag - San Roque 230kV Line 2 energized at 0936H (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 9:17:18 AM | [NSO Update] Visayas Grid-06/29/2024 09:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0916H with power going to Visayas. [WEBSMS] | CVIS
6/29/2024 9:17:01 AM | [NSO Update] Luzon Grid-06/29/2024 09:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0916H with power going to Visayas. [WEBSMS] | CLUZ
6/29/2024 9:00:26 AM | [NSO Update] Visayas Grid-06/29/2024 09:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0859H from forward power direction. [WEBSMS] | CVIS
6/29/2024 9:00:10 AM | [NSO Update] Luzon Grid-06/29/2024 09:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0859H from forward power direction. [WEBSMS] | CLUZ
6/29/2024 8:13:52 AM | Luzon Grid-06/29/2024 08:13: Balsik SS PCB 9Z-01CB04BIK de-energized at 0813H (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 7:17:19 AM | Visayas Grid-06/29/2024 07:17: Samboan SS 50 MVA 138/69/13.8 kV TR2 de-energized at 0712H (Planned Outage) [WEBSMS] | CVIS
6/29/2024 7:16:01 AM | Visayas Grid-06/29/2024 07:16: Samboan 30 MVA 138/69/13.8 kV TR1 de-energized at 0711H (Planned Outage) [WEBSMS] | CVIS
6/29/2024 7:13:57 AM | Visayas Grid-06/29/2024 07:14: Samboan - Ginatilan 69 kV Line de-energized at 0709H (Planned Outage) [WEBSMS] | CVIS
6/29/2024 7:02:44 AM | Luzon Grid-06/29/2024 07:02: Subic SS 230kV Bus 2 de-energized at 0702H (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 6:40:14 AM | Luzon Grid-06/29/2024 06:40: San Gabriel offline at 0638H (Reserve shutdown) [WEBSMS] | CLUZ
6/29/2024 6:37:26 AM | Visayas Grid-06/29/2024 06:37: Dumanjug - Samboan 138 kV Line 2 de-energized at 0636H (Planned Outage) [WEBSMS] | CVIS
6/29/2024 6:35:17 AM | Luzon Grid-06/29/2024 06:35: Tayabas-Naga 230kV Line 1 de-energized at 0635H (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 6:32:20 AM | Mindanao Grid-06/29/2024 06:38: New Bataan Hydro shutdown at 0602H. Affected by the shutdown of Nabunturan -Monkayo 69kV line. (Planned outage) [WEBSMS] | CMIN
6/29/2024 6:28:37 AM | Luzon Grid-06/29/2024 06:28: Balsik PCB 9-01CB08BIK energized at 0623H (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 6:17:36 AM | Luzon Grid-06/29/2024 06:17: San Jose-Angat 115kV Line 1 de-energized at 0617H (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 6:16:45 AM | Visayas Grid-06/29/2024 06:16: Compostela - Consolacion 69 kV Line de-energized at 0614H (Planned Outage) [WEBSMS] | CVIS
6/29/2024 6:04:15 AM | Luzon Grid-06/29/2024 06:04: Nagsaag-San Roque 230kV line 2 was de-energized at 0603H. (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 6:00:33 AM | [NSO Update] Mindanao Grid-06/29/2024 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3302MW, PK=2198MW, RR=73MW, NetOpMargin: AM=1031, PM=966, EVE=921 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/29/2024 5:59:31 AM | [NSO Update] Visayas Grid-06/29/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2637MW, PK=2062MW, RR=86MW, NetOpMargin: AM=489, PM=327, EVE=273 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @317MW, PEDC 3 @120MW, CEDC 3 @75MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/29/2024 5:55:06 AM | [NSO Update] Luzon Grid-06/29/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15320MW, PK=11357MW, RR=356MW, NetOpMargin: AM=3607, PM=3038, EVE=2012 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, MSLC1 @315MW, MSLC3 @295MW, ILIJAN A @550MW [WEBSMS] | CLUZ
6/29/2024 5:33:46 AM | Luzon Grid-06/29/2024 05:33: Laoag 230kV Bus 1 was de-energized at 0531H. (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 5:12:35 AM | Luzon Grid-06/29/2024 05:12: Balsik PCB 9-01CB08BIK de-energized at 0500H (Planned Outage) [WEBSMS] | CLUZ
6/29/2024 4:57:33 AM | [NSO Update] Mindanao Grid-06/29/2024 05:03: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 0454H. Market operations will resume starting interval 0500H. [WEBSMS] | CMIN
6/29/2024 4:56:49 AM | [NSO Update] Visayas Grid-06/29/2024 04:56: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 0454H. Market operations will resume starting interval 0500H. [WEBSMS] | CVIS
6/29/2024 4:55:51 AM | [NSO Update] Luzon Grid-06/29/2024 04:55: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 0454H. Market operations will resume starting interval 0500H. [WEBSMS] | CLUZ
6/29/2024 4:34:58 AM | [NSO Update] Mindanao Grid-06/29/2024 04:40: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 0430H due to failure to generate RTD. [WEBSMS] | CMIN
6/29/2024 4:34:37 AM | [NSO Update] Visayas Grid-06/29/2024 04:34: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 0430H due to failure to generate RTD. [WEBSMS] | CVIS
6/29/2024 4:34:07 AM | [NSO Update] Luzon Grid-06/29/2024 04:34: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 0430H due to failure to generate RTD. [WEBSMS] | CLUZ
6/29/2024 4:16:02 AM | [NSO Update] Luzon Grid-06/29/2024 04:16: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
6/29/2024 4:15:43 AM | [NSO Update] Visayas Grid-06/29/2024 04:15: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
6/29/2024 4:15:29 AM | [NSO Update] Mindanao Grid-06/29/2024 04:21: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
6/29/2024 4:06:38 AM | Luzon Grid-06/29/2024 04:06: Ambuklao - Bayombong 230kV Line 1 de-energized at 0405H (Planned Outage) [WEBSMS] | CLUZ
6/28/2024 10:33:36 PM | Mindanao Grid-06/28/2024 22:39: WMPC DG10 Shutdown at 2232H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/28/2024 7:49:31 PM | Mindanao Grid-06/28/2024 19:55: WMPC DG1 Shutdown at 1947H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/28/2024 7:32:16 PM | [NSO Update] Visayas Grid-06/28/2024 19:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1912H with power going to Luzon [WEBSMS] | CVIS
6/28/2024 7:31:59 PM | [NSO Update] Luzon Grid-06/28/2024 19:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1912H with power going to Luzon [WEBSMS] | CLUZ
6/28/2024 7:31:15 PM | [NSO Update] Visayas Grid-06/28/2024 19:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1902H from reverse power direction [WEBSMS] | CVIS
6/28/2024 7:30:59 PM | [NSO Update] Luzon Grid-06/28/2024 19:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1902H from reverse power direction [WEBSMS] | CLUZ
6/28/2024 6:53:47 PM | [NSO Update] Visayas Grid-06/28/2024 18:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1808H with power going to Visayas [WEBSMS] | CVIS
6/28/2024 6:53:29 PM | [NSO Update] Luzon Grid-06/28/2024 18:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1808H with power going to Visayas [WEBSMS] | CLUZ
6/28/2024 6:52:55 PM | [NSO Update] Visayas Grid-06/28/2024 18:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1740H from forward power direction [WEBSMS] | CVIS
6/28/2024 6:52:34 PM | [NSO Update] Luzon Grid-06/28/2024 18:52: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1740H from forward power direction [WEBSMS] | CLUZ
6/28/2024 6:44:11 PM | Luzon Grid-06/28/2024 18:44: MPGC Unit 4 online at 1842H. (On-going test and commissioning.) [WEBSMS] | CLUZ
6/28/2024 6:32:17 PM | Luzon Grid-06/28/2024 18:32: MPGC Unit 4 from 38MW(25%) conducted load rejection test(LRT) at 1829H. (On-going test and commissioning.) [WEBSMS] | CLUZ
6/28/2024 6:28:55 PM | [NSO Update] Mindanao Grid-06/28/2024 18:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3263MW, PK=2325MW, RR=73MW, NetOpMargin: EVE=866 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/28/2024 6:27:47 PM | [NSO Update] Visayas Grid-06/28/2024 18:27: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2607MW, PK=2257MW, RR=85MW, NetOpMargin: EVE=264 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @295MW, PEDC 3 @120MW, PDPP3-E @8MW, CEDC 3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB104-2 @5.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, PDPP1-3 @4.5MW, PDPP1-5 @4MW, PB104-3 @6MW, PB104-4 @7MW [WEBSMS] | CVIS
6/28/2024 6:10:31 PM | [NSO Update] Luzon Grid-06/28/2024 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13399MW, PK=11410MW, RR=338MW, NetOpMargin: EVE=1651 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, SCPC 1 @90MW, SLTEC 1 @115MW, SLTEC 2 @116MW, Limay 8 @60MW, Masinloc 3 @290MW [WEBSMS] | CLUZ
6/28/2024 5:29:38 PM | Luzon Grid-06/28/2024 17:29: MPGC Unit 4 online at 1728H. (On-going test and commissioning.) [WEBSMS] | CLUZ
6/28/2024 4:33:12 PM | Luzon Grid-06/28/2024 16:33: La Trinidad 230kV Bus 1 was energized at 1631H. (Planned Outage) [WEBSMS] | CLUZ
6/28/2024 4:20:18 PM | Mindanao Grid-06/28/2024 16:26: LPP U2 emergency stop/shutdown at 1407H. Under Test and Commissioning. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 4:19:01 PM | Luzon Grid-06/28/2024 16:19: MPGC Unit 4 from 38MW(25%) conducted load rejection test(LRT) at 1615H. (On-going test and commissioning.) [WEBSMS] | CLUZ
6/28/2024 4:03:00 PM | Mindanao Grid-06/28/2024 16:08: Agus 6 U1 online at 1552H. From forced outage. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 3:57:29 PM | Mindanao Grid-06/28/2024 16:03: LPP U2 online at 1400H. (Planned Outage) [WEBSMS] | CMIN
6/28/2024 3:49:55 PM | Mindanao Grid-06/28/2024 15:55: WMPC DG8 Shutdown at 1546H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/28/2024 3:46:22 PM | Luzon Grid-06/28/2024 15:46: San Gabriel online at 1541H. (From Reserve Shutdown) [WEBSMS] | CLUZ
6/28/2024 3:02:39 PM | Luzon Grid-06/28/2024 15:02: MPGC Unit 4 online at 1458H. (On-going test and commissioning.) [WEBSMS] | CLUZ
6/28/2024 1:49:05 PM | Mindanao Grid-06/28/2024 13:54: WMPC DG8 online at 1346H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/28/2024 1:31:05 PM | Luzon Grid-06/28/2024 13:30: MPGC 4 tripped at 1323H with a load of 38MW (on commissioning) [WEBSMS] | CLUZ
6/28/2024 12:50:26 PM | [NSO Update] Mindanao Grid-06/28/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3295MW, PK=2474MW, RR=73MW, NetOpMargin: PM=748, EVE=874 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/28/2024 12:48:55 PM | [NSO Update] Visayas Grid-06/28/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2751MW, PK=2439MW, RR=89MW, NetOpMargin: PM=223, EVE=240 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @295MW, PEDC 3 @120MW, PDPP3-E @8MW, CEDC 3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB104-2 @5.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, PDPP3-H @8MW, PDPP1-5 @4MW, PB104-3 @6MW, PB104-4 @7MW [WEBSMS] | CVIS
6/28/2024 12:46:32 PM | [NSO Update] Luzon Grid-06/28/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14449MW, PK=12705MW, RR=356MW, NetOpMargin: PM=1388, EVE=1464 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @310MW, SCPC 1 @90MW, SLTEC 1 @115MW, SLTEC 2 @115MW, Limay 8 @60MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
6/28/2024 12:38:24 PM | Mindanao Grid-06/28/2024 12:44: LSK U1 re-energized at 1212H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 12:37:29 PM | Mindanao Grid-06/28/2024 12:43: LSK U1 tripped with 15MW load at 1148H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 12:06:32 PM | Mindanao Grid-06/28/2024 12:12: Kibawe - Sultan Kudarat 138kV Line Loop at 1157H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 11:57:46 AM | Mindanao Grid-06/28/2024 12:03: LPP U1 online at 1137H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 11:55:48 AM | Mindanao Grid-06/28/2024 12:01: Kibawe - Sultan Kudarat 138kV tripped and autoreclosed at Kibawe side at 1151H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 11:25:58 AM | Mindanao Grid-06/28/2024 11:31: LPP U1 tripped with 1MW load at 1055H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 11:24:10 AM | Mindanao Grid-06/28/2024 11:29: LPP U1 tripped with 1MW load at 1117H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 11:18:07 AM | Mindanao Grid-06/28/2024 11:23: LPP U1 online at 1115H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 11:02:25 AM | Mindanao Grid-06/28/2024 11:08: LPP U1 tripped with 1.4MW load at 1055H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 11:01:34 AM | Mindanao Grid-06/28/2024 11:07: LPP U1 online at 1052H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 11:00:30 AM | Mindanao Grid-06/28/2024 11:06: LPP U1 tripped with 0.6MW load at 1036H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 10:57:21 AM | Mindanao Grid-06/28/2024 11:03: LPP U1 online at 1035H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 10:53:15 AM | Mindanao Grid-06/28/2024 10:58: WMPC DG1 Online at 1049H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/28/2024 10:21:59 AM | Mindanao Grid-06/28/2024 10:27: Liangan HEPP (LPP) tripped with 1MW load at 1016H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 10:19:35 AM | Mindanao Grid-06/28/2024 10:25: Liangan HEPP (LPP) online at 1013H. (Planned Outage) [WEBSMS] | CMIN
6/28/2024 10:14:51 AM | Mindanao Grid-06/28/2024 10:20: Liangan HEPP U1 tripped with 0.4MW at 0956H. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 10:11:39 AM | Mindanao Grid-06/28/2024 10:17: Liangan HEPP U1 online at 0956H. First synchronization. (Planned Outage) [WEBSMS] | CMIN
6/28/2024 9:57:15 AM | Luzon Grid-06/28/2024 09:57: MPGC 4 online at 0956H (on commissioning) [WEBSMS] | CLUZ
6/28/2024 9:21:36 AM | Mindanao Grid-06/28/2024 09:27: WMPC DG10 Online at 0918H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/28/2024 9:02:20 AM | Mindanao Grid-06/28/2024 09:08: Agus 6 U1 with 10MW load emergency shutdown at 0855H due to Governor failure. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 6:08:30 AM | Luzon Grid-06/28/2024 06:08: La-Trinidad 230kV Bus 1 de-energized at 0607H (Planned Outage) [WEBSMS] | CLUZ
6/28/2024 5:58:28 AM | [NSO Update] Mindanao Grid-06/28/2024 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3304MW, PK=2372MW, RR=73MW, NetOpMargin: AM=858, PM=840, EVE=976 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/28/2024 5:54:51 AM | [NSO Update] Luzon Grid-06/28/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14723MW, PK=11886MW, RR=356MW, NetOpMargin: AM=2481, PM=1690, EVE=1392 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @310MW, SCPC 1 @105MW, SLTEC 1 @115MW, SLTEC 2 @115MW, Limay 8 @60MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
6/28/2024 5:41:33 AM | Mindanao Grid-06/28/2024 05:47: Agus 6 U1 online at 0540H. From forced outage. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 5:33:37 AM | [NSO Update] Visayas Grid-06/28/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2586MW, PK=2258MW, RR=88MW, NetOpMargin: AM=241, PM=240, EVE=418 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @295MW, PEDC 3 @120MW, PDPP3-E @8MW, CEDC 3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB104-2 @5.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, TGPP @111.5MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/28/2024 5:04:17 AM | Mindanao Grid-06/28/2024 05:09: SEC U1 online at 0459H from forced outage. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 4:55:13 AM | Mindanao Grid-06/28/2024 05:00: Agus 6 U1 with 20MW load emergency shutdown at 0446H due to Governor failure. (Unplanned Outage) [WEBSMS] | CMIN
6/28/2024 4:14:23 AM | [NSO Update] Mindanao Grid-06/28/2024 04:20: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
6/28/2024 4:13:47 AM | [NSO Update] Luzon Grid-06/28/2024 04:13: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
6/28/2024 4:12:39 AM | [NSO Update] Visayas Grid-06/28/2024 04:12: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
6/27/2024 11:43:32 PM | Luzon Grid-06/27/2024 23:43: Masinloc 2 shutdown at 2340H (Unplanned Outage) [WEBSMS] | CLUZ
6/27/2024 8:37:43 PM | Mindanao Grid-06/27/2024 20:43: WMPC DG04 with 10MW load running as RPS tripped at 2029H. Cause: Exhaust Gas leak at B bank bellow. (Unplanned Outage) [WEBSMS] | CMIN
6/27/2024 8:12:58 PM | Luzon Grid-06/27/2024 20:12: Correction: QPPL shutdown at 2000H (Unplanned Outage) [WEBSMS] | CLUZ
6/27/2024 8:04:34 PM | Luzon Grid-06/27/2024 20:04: QPPL shutdown at 2000H (Planned Outage) [WEBSMS] | CLUZ
6/27/2024 7:06:39 PM | [NSO Update] Visayas Grid-06/27/2024 19:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1901H with power going to Luzon [WEBSMS] | CVIS
6/27/2024 7:06:19 PM | [NSO Update] Luzon Grid-06/27/2024 19:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1901H with power going to Luzon [WEBSMS] | CLUZ
6/27/2024 7:05:34 PM | [NSO Update] Visayas Grid-06/27/2024 19:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1849H from reverse power direction [WEBSMS] | CVIS
6/27/2024 7:05:18 PM | [NSO Update] Luzon Grid-06/27/2024 19:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1849H from reverse power direction [WEBSMS] | CLUZ
6/27/2024 5:57:45 PM | [NSO Update] Mindanao Grid-06/27/2024 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3169MW, PK=2248MW, RR=73MW, NetOpMargin: EVE=848 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/27/2024 5:56:43 PM | [NSO Update] Visayas Grid-06/27/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2567MW, PK=2186MW, RR=84MW, NetOpMargin: EVE=297 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @310MW, PEDC 3 @70MW, PDPP3-E @8MW, CEDC 3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB104-2 @5.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, TGPP @111.5MW, PDPP3-H @8MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PB104-3 @6MW, PB104-4 @7MW, THVI 2 @140MW [WEBSMS] | CVIS
6/27/2024 5:54:26 PM | [NSO Update] Luzon Grid-06/27/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14392MW, PK=11406MW, RR=336MW, NetOpMargin: EVE=2650 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, Masinloc 2 @150MW, SLTEC 1 @115MW, SLTEC 2 @115MW, Limay 8 @60MW, Masinloc 3 @280MW, Bacman 2 @55MW, SCPC 1 @95MW [WEBSMS] | CLUZ
6/27/2024 4:17:47 PM | Mindanao Grid-06/27/2024 16:23: WMPC DG10 shutdown at 1616H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/27/2024 2:24:11 PM | Mindanao Grid-06/27/2024 14:29: WMPC DG10 Online at 1421H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/27/2024 1:01:14 PM | [NSO Update] Mindanao Grid-06/27/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3210MW, PK=2363MW, RR=73MW, NetOpMargin: PM=775, EVE=877 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/27/2024 1:00:00 PM | [NSO Update] Visayas Grid-06/27/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2626MW, PK=2243MW, RR=91MW, NetOpMargin: PM=291, EVE=304 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @290MW, PEDC 3 @120MW, PDPP3-E @8MW, CEDC 3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB104-2 @5.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, TGPP @106.5MW, PDPP3-H @8MW, PDPP1-3 @4MW, PDPP1-5 @4MW, PB104-3 @6MW, PB104-4 @7MW [WEBSMS] | CVIS
6/27/2024 12:58:02 PM | [NSO Update] Luzon Grid-06/27/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15442MW, PK=12409MW, RR=356MW, NetOpMargin: PM=2677, EVE=2351 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan B @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, Masinloc 2 @150MW, SLTEC 1 @115MW, SLTEC 2 @115MW, Limay 8 @60MW, Masinloc 3 @250MW, Bacman 2 @55MW, SCPC 1 @90MW [WEBSMS] | CLUZ
6/27/2024 9:40:38 AM | Mindanao Grid-06/27/2024 09:46: WMPC DG04 Online at 0937H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/27/2024 8:05:20 AM | [NSO Update] Visayas Grid-06/27/2024 08:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0748H with power going to Visayas [WEBSMS] | CVIS
6/27/2024 8:05:06 AM | [NSO Update] Luzon Grid-06/27/2024 08:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0748H with power going to Visayas [WEBSMS] | CLUZ
6/27/2024 7:41:39 AM | [NSO Update] Visayas Grid-06/27/2024 07:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0738H from forward power direction [WEBSMS] | CVIS
6/27/2024 7:41:23 AM | [NSO Update] Luzon Grid-06/27/2024 07:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0738H from forward power direction [WEBSMS] | CLUZ
6/27/2024 5:48:30 AM | [NSO Update] Mindanao Grid-06/27/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3201MW, PK=2142MW, RR=73MW, NetOpMargin: AM=986, PM=941, EVE=903 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/27/2024 5:45:30 AM | [NSO Update] Visayas Grid-06/27/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2557MW, PK=2157MW, RR=90MW, NetOpMargin: AM=310, PM=290, EVE=390 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @290MW, PEDC 3 @120MW, PDPP3-E @8MW, CEDC 3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB104-2 @5.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, TGPP @106.5MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/27/2024 5:41:36 AM | [NSO Update] Luzon Grid-06/27/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15776MW, PK=11972MW, RR=356MW, NetOpMargin: AM=3448, PM=2554, EVE=2476 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan B @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, Masinloc 2 @200MW, SLTEC 1 @115MW, SLTEC 2 @115MW, Limay 8 @60MW, Masinloc 3 @250MW, Bacman 2 @55MW, SCPC 1 @120MW [WEBSMS] | CLUZ
6/27/2024 4:09:12 AM | [NSO Update] Mindanao Grid-06/27/2024 04:14: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 45 km East Northeast of Dipolog City, Zamboanga del Norte (8.8�N, 123.7�E). It is embedded along the Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
6/27/2024 4:08:50 AM | [NSO Update] Visayas Grid-06/27/2024 04:08: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 45 km East Northeast of Dipolog City, Zamboanga del Norte (8.8�N, 123.7�E). It is embedded along the Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
6/27/2024 4:08:23 AM | [NSO Update] Luzon Grid-06/27/2024 04:08: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 45 km East Northeast of Dipolog City, Zamboanga del Norte (8.8�N, 123.7�E). It is embedded along the Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
6/27/2024 3:24:48 AM | Luzon Grid-06/27/2024 03:24: Bay - Calamba 230kV Line 2 energized at 0323H (Planned Outage) [WEBSMS] | CLUZ
6/26/2024 11:15:29 PM | Luzon Grid-06/26/2024 23:15: Bay-Calamba 230kV Line 2 de-energized at 2315H (Planned Outage) [WEBSMS] | CLUZ
6/26/2024 7:31:11 PM | [NSO Update] Luzon Grid-06/26/2024 19:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1847H with power going to Luzon [WEBSMS] | CLUZ
6/26/2024 7:17:46 PM | Mindanao Grid-06/26/2024 19:23: WMPC DG10 Shutdown at 1916H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/26/2024 6:50:29 PM | [NSO Update] Visayas Grid-06/26/2024 18:50: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1847H with power going to Luzon [WEBSMS] | CVIS
6/26/2024 6:39:43 PM | [NSO Update] Visayas Grid-06/26/2024 18:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1837H from reverse power direction [WEBSMS] | CVIS
6/26/2024 6:39:20 PM | [NSO Update] Luzon Grid-06/26/2024 18:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1837H from reverse power direction [WEBSMS] | CLUZ
6/26/2024 6:00:46 PM | [NSO Update] Mindanao Grid-06/26/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3164MW, PK=2099MW, RR=73MW, NetOpMargin: EVE=992 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/26/2024 5:58:29 PM | [NSO Update] Visayas Grid-06/26/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2536MW, PK=2077MW, RR=83MW, NetOpMargin: EVE=376 Highest Unit O/L: THVI 1@169MW Derated Plant: Leyte A @295MW, PEDC 3 @120MW, PDPP3-E @8MW, CEDC 3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB104-2 @5.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, TGPP @90MW, THVI 2 @130MW [WEBSMS] | CVIS
6/26/2024 5:55:13 PM | [NSO Update] Luzon Grid-06/26/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14266MW, PK=10952MW, RR=338MW, NetOpMargin: EVE=2976 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan B @550MW, GNPD 2 @640MW, Masinloc 1 @315MW, Masinloc 2 @200MW, SLTEC 1 @115MW, SLTEC 2 @115MW, Limay 8 @60MW, Masinloc 3 @240MW, Bacman 2 @55MW [WEBSMS] | CLUZ
6/26/2024 5:36:58 PM | Mindanao Grid-06/26/2024 17:42: Opol SS 138kV Bus 2 energized at 1735H. (Planned Outage) [WEBSMS] | CMIN
6/26/2024 5:19:17 PM | Visayas Grid-06/26/2024 17:19: LGPP U1 cut-in at 1708H (Unplanned Outage) [WEBSMS] | CVIS
6/26/2024 3:50:38 PM | Visayas Grid-06/26/2024 15:50: Maha B tripped at 1544H (Unplanned Outage) [WEBSMS] | CVIS
6/26/2024 3:47:30 PM | Visayas Grid-06/26/2024 15:47: Correction: Pal 1 U2 cut-in at 1532H (Unplanned Outage) [WEBSMS] | CVIS
6/26/2024 3:34:48 PM | Visayas Grid-06/26/2024 15:34: Pal 1 U2 cut-in at 1417H (Unplanned Outage) [WEBSMS] | CVIS
6/26/2024 3:16:34 PM | Mindanao Grid-06/26/2024 15:22: WMPC DG03 shutdown at 1510H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/26/2024 2:27:32 PM | Visayas Grid-06/26/2024 14:27: Pal 1 U2 tripped at 1417H (Unplanned Outage) [WEBSMS] | CVIS
6/26/2024 2:21:45 PM | Mindanao Grid-06/26/2024 14:27: Agus 5 HEPP U1 online at 1415H. (Planned Outage) [WEBSMS] | CMIN
6/26/2024 1:43:36 PM | Mindanao Grid-06/26/2024 13:49: WMPC DG3 Online at 1338H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/26/2024 1:12:15 PM | Mindanao Grid-06/26/2024 13:17: Agus 5 SY - Agus 5 HEP 138kV L1 energized at 1308H. (Planned Outage) [WEBSMS] | CMIN
6/26/2024 12:54:46 PM | [NSO Update] Mindanao Grid-06/26/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3184MW, PK=2248MW, RR=73MW, NetOpMargin: PM=863, EVE=984 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/26/2024 12:53:47 PM | [NSO Update] Visayas Grid-06/26/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2649MW, PK=2290MW, RR=91MW, NetOpMargin: PM=268, EVE=286 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @327MW, PEDC 3 @120MW, TGPP @79.5MW, CEDC 3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB104-2 @5.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, PDPP3-E @8MW [WEBSMS] | CVIS
6/26/2024 12:52:10 PM | [NSO Update] Luzon Grid-06/26/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15539MW, PK=11977MW, RR=356MW, NetOpMargin: PM=3206, EVE=2543 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan B @550MW, GNPD 2 @640MW, Masinloc 1 @310MW, Masinloc 2 @200MW, SLTEC 1 @115MW, SLTEC 2 @115MW, Limay 8 @60MW, Masinloc 3 @240MW, Bacman 2 @55MW, QPPL @430MW [WEBSMS] | CLUZ
6/26/2024 12:49:58 PM | [NSO Update] Visayas Grid-06/26/2024 12:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1215H with power going to Visayas [WEBSMS] | CVIS
6/26/2024 12:49:39 PM | [NSO Update] Luzon Grid-06/26/2024 12:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1215H with power going to Visayas [WEBSMS] | CLUZ
6/26/2024 12:48:50 PM | [NSO Update] Visayas Grid-06/26/2024 12:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1205H from forward power direction [WEBSMS] | CVIS
6/26/2024 12:48:37 PM | [NSO Update] Luzon Grid-06/26/2024 12:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1205H from forward power direction [WEBSMS] | CLUZ
6/26/2024 10:36:17 AM | Mindanao Grid-06/26/2024 10:41: WMPC DG10 Online at 1031H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/26/2024 9:58:25 AM | [NSO Update] Visayas Grid-06/26/2024 09:58: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0954H with power going to Luzon [WEBSMS] | CVIS
6/26/2024 9:58:18 AM | [NSO Update] Luzon Grid-06/26/2024 09:58: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0954H with power going to Luzon [WEBSMS] | CLUZ
6/26/2024 9:57:13 AM | [NSO Update] Visayas Grid-06/26/2024 09:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0944H from reverse power direction [WEBSMS] | CVIS
6/26/2024 9:56:53 AM | [NSO Update] Luzon Grid-06/26/2024 09:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0944H from reverse power direction [WEBSMS] | CLUZ
6/26/2024 9:22:31 AM | Mindanao Grid-06/26/2024 09:28: Opol SS 138kV Bus 2 de-energized/shutdown at 0918H. (Planned Outage) [WEBSMS] | CMIN
6/26/2024 8:26:21 AM | [NSO Update] Visayas Grid-06/26/2024 08:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0750H with power going to Visayas [WEBSMS] | CVIS
6/26/2024 8:26:07 AM | [NSO Update] Luzon Grid-06/26/2024 08:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0750H with power going to Visayas [WEBSMS] | CLUZ
6/26/2024 8:25:25 AM | [NSO Update] Visayas Grid-06/26/2024 08:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0740H from forward power direction [WEBSMS] | CVIS
6/26/2024 8:25:10 AM | [NSO Update] Luzon Grid-06/26/2024 08:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0740H from forward power direction [WEBSMS] | CLUZ
6/26/2024 8:01:25 AM | Visayas Grid-06/26/2024 08:01: LGPP U1 emergency shutdown at 0800H due to steam leak at the 1st stage motive steam supply isolation valve. (Unplanned Outage) [WEBSMS] | CVIS
6/26/2024 6:11:11 AM | Mindanao Grid-06/26/2024 06:16: Agus 5 SY - Agus 5 HEP 138kV L1 de-energized at 0609H. (Planned Outage) [WEBSMS] | CMIN
6/26/2024 6:04:11 AM | Mindanao Grid-06/26/2024 06:09: Agus 5 U1 shutdown at 0602H. Affected by P&E activity (Planned Outage) [WEBSMS] | CMIN
6/26/2024 5:49:34 AM | [NSO Update] Luzon Grid-06/26/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15741MW, PK=12313MW, RR=356MW, NetOpMargin: AM=3072, PM=2698, EVE=2474 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Ilijan B @550MW, GNPD 2 @640MW, Masinloc 1 @310MW, Masinloc 2 @200MW, SLTEC 1 @115MW, SLTEC 2 @115MW, Limay 8 @60MW, Masinloc 3 @210MW, Bacman 2 @55MW [WEBSMS] | CLUZ
6/26/2024 5:37:14 AM | [NSO Update] Visayas Grid-06/26/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2681MW, PK=2250MW, RR=89MW, NetOpMargin: AM=343, PM=284, EVE=346 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @322MW, PEDC 3 @120MW, TGPP @116.5MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-5 @4MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-2 @5.5MW, PDPP1-3 @4MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, PB104-4 @7MW, PDPP3-E @8MW [WEBSMS] | CVIS
6/26/2024 5:33:54 AM | [NSO Update] Mindanao Grid-06/26/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3182MW, PK=2381MW, RR=73MW, NetOpMargin: AM=728, PM=639, EVE=773 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/26/2024 5:31:58 AM | [NSO Update] Luzon Grid-06/26/2024 05:31: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
6/26/2024 5:31:45 AM | [NSO Update] Mindanao Grid-06/26/2024 05:37: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
6/26/2024 5:31:33 AM | [NSO Update] Visayas Grid-06/26/2024 05:31: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
6/26/2024 4:45:12 AM | Luzon Grid-06/26/2024 04:45: Bay-Calamba 230kV line 1 energized at 0441H (Planned Outage) [WEBSMS] | CLUZ
6/26/2024 3:43:19 AM | Luzon Grid-06/26/2024 03:43: Nagsaag PCB 9-01CB24NGS restored at 0342H (Unplanned Outage) [WEBSMS] | CLUZ
6/25/2024 11:30:19 PM | Luzon Grid-06/25/2024 23:30: Bay-Calamba 230kV line 1 was de-energized at 2329H. (Planned Outage) [WEBSMS] | CLUZ
6/25/2024 9:25:35 PM | Mindanao Grid-06/25/2024 21:31: WMPC DG10 shutdown at 2116H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/25/2024 9:24:50 PM | Mindanao Grid-06/25/2024 21:30: WMPC DG10 shutdown at 2116H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/25/2024 8:14:35 PM | Mindanao Grid-06/25/2024 20:20: STEAG Unit No.1 online at 2012H. (Unplanned Outage) [WEBSMS] | CMIN
6/25/2024 6:22:07 PM | Mindanao Grid-06/25/2024 18:28: Manolo Fortich 1 HEP Unit 4 online at 1818H. (Unplanned Outage) [WEBSMS] | CMIN
6/25/2024 5:57:54 PM | [NSO Update] Luzon Grid-06/25/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14417MW, PK=11659MW, RR=338MW, NetOpMargin: EVE=2420 Highest Unit O/L: GNPD 1@668MW Derated Plant: Ilijan B @550MW, GNPD 2 @640MW, Masinloc 1 @310MW, Masinloc 2 @200MW, SLTEC 1 @116MW, SLTEC 2 @116MW, Limay 8 @60MW, Masinloc 3 @300MW, Bacman 2 @50MW, SCPC 3 @140MW [WEBSMS] | CLUZ
6/25/2024 5:40:53 PM | [NSO Update] Mindanao Grid-06/25/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3050MW, PK=2365MW, RR=73MW, NetOpMargin: EVE=612 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @26.5MW [WEBSMS] | CMIN
6/25/2024 5:33:41 PM | [NSO Update] Visayas Grid-06/25/2024 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2545MW, PK=2215MW, RR=88MW, NetOpMargin: EVE=242 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @318MW, PEDC 3 @120MW, TGPP @117MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-5 @4MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-2 @5.5MW, PDPP1-3 @4MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, PB104-1 @7MW, PDPP3-E @8MW [WEBSMS] | CVIS
6/25/2024 5:14:08 PM | Mindanao Grid-06/25/2024 17:20: WMPC DG03 shutdown at 1713H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/25/2024 3:41:48 PM | Mindanao Grid-06/25/2024 15:47: Agus 5 Unit 2 online at 1503H (Planned Outage) [WEBSMS] | CMIN
6/25/2024 3:33:47 PM | Mindanao Grid-06/25/2024 15:39: Manolo Fortich 1 HEP Unit 4 shutdown at 1511H for turbine inspection. (Unplanned outage) [WEBSMS] | CMIN
6/25/2024 2:51:50 PM | Mindanao Grid-06/25/2024 14:57: Agus 5 SY - Agus 5 HEP 138kV L2 energized at 1447H. (Planned Outage) [WEBSMS] | CMIN
6/25/2024 2:49:59 PM | [NSO Update] Visayas Grid-06/25/2024 14:50: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1447H with power going to Luzon. [WEBSMS] | CVIS
6/25/2024 2:49:41 PM | [NSO Update] Luzon Grid-06/25/2024 14:50: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1447H with power going to Luzon. [WEBSMS] | CLUZ
6/25/2024 2:42:33 PM | [NSO Update] Luzon Grid-06/25/2024 14:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1436H from reverse power direction. [WEBSMS] | CLUZ
6/25/2024 2:41:30 PM | [NSO Update] Visayas Grid-06/25/2024 14:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1436H from reverse power direction. [WEBSMS] | CVIS
6/25/2024 2:06:29 PM | Mindanao Grid-06/25/2024 14:12: Opol SS 138kV Bus 1 energized at 1405H (Planned Outage). [WEBSMS] | CMIN
6/25/2024 1:13:49 PM | [NSO Update] Luzon Grid-06/25/2024 13:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1226H with power going to Visayas. [WEBSMS] | CLUZ
6/25/2024 1:12:35 PM | [NSO Update] Visayas Grid-06/25/2024 13:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1226H with power going to Visayas. [WEBSMS] | CVIS
6/25/2024 12:51:58 PM | [NSO Update] Mindanao Grid-06/25/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3074MW, PK=2422MW, RR=73MW, NetOpMargin: PM=579, EVE=733 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @26.5MW [WEBSMS] | CMIN
6/25/2024 12:50:06 PM | [NSO Update] Visayas Grid-06/25/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2619MW, PK=2260MW, RR=91MW, NetOpMargin: PM=268, EVE=299 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @316MW, PEDC 3 @120MW, TGPP @117MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-5 @4MW, PDPP3-H @8MW, PB104-2 @5.5MW, PDPP1-3 @4MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, PB104-1 @7MW, PDPP3-E @8MW [WEBSMS] | CVIS
6/25/2024 12:47:47 PM | [NSO Update] Luzon Grid-06/25/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15789MW, PK=12595MW, RR=356MW, NetOpMargin: PM=2838, EVE=2846 Highest Unit O/L: GNPD 1@668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @310MW, Masinloc 2 @200MW, SLTEC 1 @116MW, SLTEC 2 @116MW, Limay 8 @60MW, Masinloc 3 @330MW, Bacman 2 @35MW, Calaca 2 @270MW [WEBSMS] | CLUZ
6/25/2024 12:17:47 PM | [NSO Update] Visayas Grid-06/25/2024 12:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1216H from forward power direction. [WEBSMS] | CVIS
6/25/2024 12:17:44 PM | [NSO Update] Luzon Grid-06/25/2024 12:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1216H from forward power direction. [WEBSMS] | CLUZ
6/25/2024 10:09:41 AM | Mindanao Grid-06/25/2024 10:15: Baloi - Agus 6 SY 69kV Tie-line energized at 1007H. (Unplanned Outage) [WEBSMS] | CMIN
6/25/2024 10:04:35 AM | Mindanao Grid-06/25/2024 10:10: WMPC DG03 online at 1001H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/25/2024 9:05:14 AM | Mindanao Grid-06/25/2024 09:11: WMPC DG10 online at 0855H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/25/2024 9:05:11 AM | Mindanao Grid-06/25/2024 09:11: Baloi - Agus 6 SY 69kV Tie-line tripped at 0842H. (Unplanned Outage) [WEBSMS] | CMIN
6/25/2024 8:06:10 AM | Mindanao Grid-06/25/2024 08:12: Opol SS 138kV Bus 1 de-energized at 0803H. (Planned Outage) [WEBSMS] | CMIN
6/25/2024 6:18:09 AM | Mindanao Grid-06/25/2024 06:24: Agus 5 SY - Agus 5 HEP 138kV L2 de-energized at 0613H. (Planned Outage) [WEBSMS] | CMIN
6/25/2024 6:11:40 AM | Mindanao Grid-06/25/2024 06:17: Agus 5 U2 shutdown at 0602H. Affected by P&E activity (Planned Outage) [WEBSMS] | CMIN
6/25/2024 6:04:54 AM | Mindanao Grid-06/25/2024 06:11: Update: SEC 1 tripped at 0329H with a 67.14 MW load due to an Induced Draft Fan problem (IDF). [WEBSMS] | CMIN
6/25/2024 5:56:31 AM | Luzon Grid-06/25/2024 05:57: Taytay (Dolores) 115kV Bus 1 (Customer Owned) restored at 0354H (Planned Outage) [WEBSMS] | CLUZ
6/25/2024 5:52:17 AM | [NSO Update] Mindanao Grid-06/25/2024 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3097MW, PK=2347MW, RR=73MW, NetOpMargin: AM=677, PM=669, EVE=765 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @26.5MW [WEBSMS] | CMIN
6/25/2024 5:50:14 AM | [NSO Update] Visayas Grid-06/25/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2574MW, PK=2277MW, RR=91MW, NetOpMargin: AM=206, PM=215, EVE=233 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @320MW, PEDC 3 @75MW, TGPP @116.5MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-5 @4MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-2 @5.5MW, PDPP1-3 @4MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, PB104-4 @7MW, PDPP3-E @8MW [WEBSMS] | CVIS
6/25/2024 5:48:52 AM | [NSO Update] Luzon Grid-06/25/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15762MW, PK=11744MW, RR=356MW, NetOpMargin: AM=3661, PM=2492, EVE=2279 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @310MW, Masinloc 2 @200MW, SLTEC 1 @116MW, SLTEC 2 @116MW, Limay 8 @60MW, Masinloc 3 @330MW [WEBSMS] | CLUZ
6/25/2024 4:07:07 AM | [NSO Update] Luzon Grid-06/25/2024 04:07: Weather Advisory: Easterlies affecting the eastern sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
6/25/2024 4:06:47 AM | [NSO Update] Mindanao Grid-06/25/2024 04:12: Weather Advisory: Easterlies affecting the eastern sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
6/25/2024 4:06:30 AM | [NSO Update] Visayas Grid-06/25/2024 04:07: Weather Advisory: Easterlies affecting the eastern sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
6/25/2024 3:33:52 AM | Mindanao Grid-06/25/2024 03:39: SEC 1 tripped at 0329H with 67 MW load. Details to follow. [WEBSMS] | CMIN
6/25/2024 3:11:19 AM | Mindanao Grid-06/25/2024 03:17: STEAG U2 synchronized at 0301H from unplanned oiutage. [WEBSMS] | CMIN
6/25/2024 2:55:07 AM | Luzon Grid-06/25/2024 02:55: Correction: Malaya - Ingrid 230kV Line 2 (CO) energized at 0254H (Unplanned Outage) [WEBSMS] | CLUZ
6/25/2024 2:47:34 AM | Luzon Grid-06/25/2024 02:48: Malaya - Ingrid 230kV Line 2 (CO) energized at 0244H (Unplanned Outage) [WEBSMS] | CLUZ
6/25/2024 2:41:56 AM | Luzon Grid-06/25/2024 02:42: Malaya 230kV Bus 1 energized at 0241H (Unplanned Outage) [WEBSMS] | CLUZ
6/25/2024 12:36:31 AM | Luzon Grid-06/25/2024 00:37: Taytay (Dolores) 115kV Bus 1 de-energized at 0033H (Planned Outage) [WEBSMS] | CLUZ
6/25/2024 12:13:46 AM | Luzon Grid-06/25/2024 00:14: Malaya - Ingrid 230kV Line 2 (CO) de-energized at 2354H (Unplanned Outage) [WEBSMS] | CLUZ
6/25/2024 12:02:05 AM | Luzon Grid-06/25/2024 00:02: Malaya 230kV Bus 1 was de-energized at 2354H (Unplanned Outage) [WEBSMS] | CLUZ
6/24/2024 7:20:54 PM | Mindanao Grid-06/24/2024 19:27: WMPC DG10 shutdown at 1913H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/24/2024 5:57:46 PM | Mindanao Grid-06/24/2024 18:03: WMPC DG003 shutdown at 1711H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/24/2024 5:45:57 PM | Mindanao Grid-06/24/2024 17:52: WMPC DG03 CUT-OUT at 1711H.End of RPS operation [WEBSMS] | CMIN
6/24/2024 5:40:13 PM | [NSO Update] Mindanao Grid-06/24/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3086MW, PK=2200MW, RR=73MW, NetOpMargin: EVE=814 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/24/2024 5:39:06 PM | [NSO Update] Visayas Grid-06/24/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2548MW, PK=2040MW, RR=91MW, NetOpMargin: EVE=417 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @315MW, PEDC 3 @70MW, TGPP @116.5MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-5 @4MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-2 @5.5MW, PDPP1-3 @4MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-2 @4.5MW, PB104-4 @7MW [WEBSMS] | CVIS
6/24/2024 5:37:58 PM | [NSO Update] Luzon Grid-06/24/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14183MW, PK=11224MW, RR=429MW, NetOpMargin: EVE=2531 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @310MW, Masinloc 2 @200MW, SLTEC 1 @116MW, SLTEC 2 @116MW, Limay 8 @60MW [WEBSMS] | CLUZ
6/24/2024 1:42:19 PM | Mindanao Grid-06/24/2024 13:48: WMPC DG003 online at 1336H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/24/2024 1:37:34 PM | Mindanao Grid-06/24/2024 13:43: WMPC DG04 online at 1336H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/24/2024 12:53:31 PM | [NSO Update] Visayas Grid-06/24/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2618MW, PK=2257MW, RR=85MW, NetOpMargin: PM=276, EVE=286 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @322MW, PEDC 3 @70MW, TGPP @115.5MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-5 @4MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-2 @5.5MW, PDPP1-3 @4MW, PB101-1 @5.5MW, PB101-2 @5.2MW [WEBSMS] | CVIS
6/24/2024 12:51:14 PM | [NSO Update] Luzon Grid-06/24/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15578MW, PK=12603MW, RR=496MW, NetOpMargin: PM=2479, EVE=2421 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @310MW, Masinloc 2 @200MW, SLTEC 1 @116MW, SLTEC 2 @116MW, Limay 8 @60MW, Calaca U1 @200MW [WEBSMS] | CLUZ
6/24/2024 12:33:46 PM | [NSO Update] Mindanao Grid-06/24/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3068MW, PK=2381MW, RR=73MW, NetOpMargin: PM=614, EVE=753 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @31.5MW [WEBSMS] | CMIN
6/24/2024 11:27:40 AM | Mindanao Grid-06/24/2024 11:33: Agus 2 unit 3 online at 1121H from FO. Unplanned Outage. [WEBSMS] | CMIN
6/24/2024 11:26:11 AM | Mindanao Grid-06/24/2024 11:32: Agus 2 unit 2 online at 1115H from FO. Unplanned Outage. [WEBSMS] | CMIN
6/24/2024 11:03:58 AM | Mindanao Grid-06/24/2024 11:10: Agus2 Kibawe 138 kV L2 energized back at 1102H from Unplanned Outage. [WEBSMS] | CMIN
6/24/2024 10:33:33 AM | Mindanao Grid-06/24/2024 10:39: Agus2 Kibawe 138 kV L2 tripped at 1008H due to line to ground fault and Agus2 HEP U2 and U3 tripped simultaneously with load drop of 25 MW and 29 MW respectively. Lowest frequency recorded was 59.51 Hz. [WEBSMS] | CMIN
6/24/2024 10:16:05 AM | Mindanao Grid-06/24/2024 10:22: WMPC DG010 online at 1013H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/24/2024 7:15:54 AM | Luzon Grid-06/24/2024 07:16: The commissioning and energization of Bolo-Labrador 230kV line 2 was completed at 0713H. (Swinging of the line from Bay 82 to Bay 83 of Labrador Substation) [WEBSMS] | CLUZ
6/24/2024 6:09:32 AM | [NSO Update] Luzon Grid-06/24/2024 06:10: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15740MW, PK=11656MW, RR=477MW, NetOpMargin: AM=3607, PM=2720, EVE=2689 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @310MW, Masinloc 2 @200MW, SLTEC 1 @117MW, SLTEC 2 @118MW, Limay 8 @60MW, Masinloc U3 @310MW [WEBSMS] | CLUZ
6/24/2024 5:57:42 AM | [NSO Update] Mindanao Grid-06/24/2024 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3172MW, PK=2234MW, RR=73MW, NetOpMargin: AM=866, PM=581, EVE=583 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @31.5MW [WEBSMS] | CMIN
6/24/2024 5:56:42 AM | [NSO Update] Visayas Grid-06/24/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2656MW, PK=2148MW, RR=83MW, NetOpMargin: AM=426, PM=301, EVE=260 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @322MW, PEDC 3 @70MW, TGPP @115.5MW, CEDC 3 @75MW, GTEC @7MW, PDPP1-5 @4MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-2 @5.5MW, PDPP1-3 @4MW, PB101-1 @5.5MW, PB101-2 @5.2MW [WEBSMS] | CVIS
6/24/2024 5:16:09 AM | Luzon Grid-06/24/2024 05:16: Dona Imelda (Araneta) - Sta. Mesa 115kV Line 2 restored at 0516H (Planned Outage) [WEBSMS] | CLUZ
6/24/2024 4:47:09 AM | Luzon Grid-06/24/2024 04:47: Bolo-Labrador 230kV L2 looped at Bolo SS side 0446H on-going commissioning (Planned Outage) [WEBSMS] | CLUZ
6/24/2024 4:42:43 AM | [NSO Update] Mindanao Grid-06/24/2024 04:48: Weather Update: Southwest Monsoon affecting the western section of Southern Luzon. [WEBSMS] | CMIN
6/24/2024 4:42:28 AM | [NSO Update] Visayas Grid-06/24/2024 04:42: Weather Update: Southwest Monsoon affecting the western section of Southern Luzon. [WEBSMS] | CVIS
6/24/2024 4:42:09 AM | [NSO Update] Luzon Grid-06/24/2024 04:42: Weather Update: Southwest Monsoon affecting the western section of Southern Luzon. [WEBSMS] | CLUZ
6/24/2024 4:31:16 AM | Mindanao Grid-06/24/2024 04:37: Manolo Fortich 1 Unit 3 and 4 with 15.12MW and 14.77MW, respectively tripped at 0408H . Details to follow (Unplanned Outage). [WEBSMS] | CMIN
6/24/2024 3:03:15 AM | Luzon Grid-06/24/2024 03:03: Bolo-Labrador 230kV L2 energized at Labrador side 0302H on-going commissioning (Planned Outage) [WEBSMS] | CLUZ
6/24/2024 12:15:16 AM | Luzon Grid-06/24/2024 00:15: Dona Imelda (Araneta) - Sta. Mesa 115kV Line 2 de-energized at 0009H (Planned Outage) [WEBSMS] | CLUZ
6/23/2024 11:43:54 PM | Mindanao Grid-06/23/2024 23:50: Sibulan A HEP (U1 & U2) and Sibulan B HEP (U1 & U2) tripped at 10:43PM. Affected due to forced outage of DLPCs Puan Switching Station. (OMC Outage). (Unplanned Outage) [WEBSMS] | CMIN
6/23/2024 11:36:43 PM | Mindanao Grid-06/23/2024 23:42: Sibulan A HEP (U1 & U2) and Sibulan B HEP (U1 & U2) tripped. Affected due to forced outage of DLPCs Puan Switching Station. (OMC Outage). Unplanned outage. [WEBSMS] | CMIN
6/23/2024 7:33:09 PM | Luzon Grid-06/23/2024 19:33: Labrador 230kV Bus 2 restored at 1932H (Planned Outage) [WEBSMS] | CLUZ
6/23/2024 6:31:26 PM | Mindanao Grid-06/23/2024 18:37: Agus6HEP U1 cut-in at 1820H. Unplanned outage. [WEBSMS] | CMIN
6/23/2024 6:27:31 PM | Luzon Grid-06/23/2024 18:28: Bolo-Nagsaag 500kV L1 and Nagsaag-San Jose 500kV L1 restored at 1824H and 1827H, respectively (Unplanned Outage). [WEBSMS] | CLUZ
6/23/2024 6:23:38 PM | Luzon Grid-06/23/2024 18:24: Bolo-Nagsaag 500kV L1 and Nagsaag-San Jose 500kV L1 de-energized at 1822H (Unplanned Outage) [WEBSMS] | CLUZ
6/23/2024 6:02:01 PM | Luzon Grid-06/23/2024 18:02: Balsik_Tayabas 500kV Line commissioned at 1800H. [WEBSMS] | CLUZ
6/23/2024 5:49:38 PM | [NSO Update] Mindanao Grid-06/23/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3024MW, PK=2127MW, RR=73MW, NetOpMargin: EVE=825 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/23/2024 5:48:31 PM | [NSO Update] Visayas Grid-06/23/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2521MW, PK=1989MW, RR=91MW, NetOpMargin: EVE=441 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @320MW, PEDC 3 @70MW, TGPP @113.5MW, PDPP1-5 @4MW, GTEC @7MW, PB104-4 @7MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-2 @5.5MW, PB104-3 @5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-3 @4MW, CEDC 3 @75MW [WEBSMS] | CVIS
6/23/2024 5:43:46 PM | Luzon Grid-06/23/2024 17:44: San Jose-Nagsaag 500kV L2 tripped/reclosed at 1742H (Unplanned Outage) [WEBSMS] | CLUZ
6/23/2024 5:39:47 PM | [NSO Update] Luzon Grid-06/23/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14585MW, PK=10847MW, RR=339MW, NetOpMargin: EVE=3399 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @117MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc U3 @275MW [WEBSMS] | CLUZ
6/23/2024 5:22:36 PM | Luzon Grid-06/23/2024 17:23: Balsik_Tayabas 500kV Line restored at 1721H (on-commissioning) [WEBSMS] | CLUZ
6/23/2024 5:09:32 PM | Luzon Grid-06/23/2024 17:10: Lumban-Bay 230kV Line 1 restored at 1709H (Planned Outage) [WEBSMS] | CLUZ
6/23/2024 5:03:54 PM | Mindanao Grid-06/23/2024 17:09: Opol SS 75MVA Transformer No. 2 energized at 1659H. (Planned Outage) [WEBSMS] | CMIN
6/23/2024 5:03:05 PM | Luzon Grid-06/23/2024 17:03: San Esteban-Laoag 230kV Line 2 restored at 1703H (Planned Outage) [WEBSMS] | CLUZ
6/23/2024 4:51:12 PM | Luzon Grid-06/23/2024 16:51: San Jose-Nagsaag 500kV L1 tripped/reclosed at 1644H (Unplanned Outage) [WEBSMS] | CLUZ
6/23/2024 4:48:54 PM | Visayas Grid-06/23/2024 16:49: Quiot-Cebu 138KV line energized at 1649H(Planned Outage) [WEBSMS] | CVIS
6/23/2024 4:38:16 PM | Mindanao Grid-06/23/2024 16:44: Bunawan - Maco 138kV line energized at 1631H. (Planned Outage) [WEBSMS] | CMIN
6/23/2024 4:31:00 PM | Luzon Grid-06/23/2024 16:31: Correction: Balsik_Tayabas 500kV Line energized (Tayabas side) at 1615H (Planned Outage) [WEBSMS] | CLUZ
6/23/2024 4:26:13 PM | Luzon Grid-06/23/2024 16:26: Correction: San Jose-Tayabas 500kV Line energized (Tayabas side) at 1615H (on-commissioning) [WEBSMS] | CLUZ
6/23/2024 4:16:59 PM | Luzon Grid-06/23/2024 16:17: San Jose-Balsik 500kV energized (Tayabas) at 1615H (on-commissioning) [WEBSMS] | CLUZ
6/23/2024 4:10:39 PM | Luzon Grid-06/23/2024 16:11: Dasmarinas-Ilijan 500kV Line tripped/reclosed at 1553H (Unplanned Outage) [WEBSMS] | CLUZ
6/23/2024 3:24:41 PM | Mindanao Grid-06/23/2024 15:30: AGUS6 Unit 1 shutdown at 1504H. Reason: Governor Servo Oil Leak. Unplanned Outage. [WEBSMS] | CMIN
6/23/2024 12:46:42 PM | [NSO Update] Visayas Grid-06/23/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2652MW, PK=1827MW, RR=84MW, NetOpMargin: PM=742, EVE=544 Highest Unit O/L: THVI 1 and 2 @169MW Derated Plant: Leyte A @315MW, PEDC U3 @70MW, TGPP @112MW, PDPP1-5 @4MW, GTEC @7MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-2 @5.5MW, PB104-3 @5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-3 @4MW [WEBSMS] | CVIS
6/23/2024 12:44:55 PM | [NSO Update] Mindanao Grid-06/23/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3062MW, PK=1953MW, RR=73MW, NetOpMargin: PM=1036, EVE=894 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/23/2024 12:40:40 PM | [NSO Update] Luzon Grid-06/23/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15743MW, PK=10458MW, RR=356MW, NetOpMargin: PM=4928, EVE=3750 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @117MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc U3 @240MW [WEBSMS] | CLUZ
6/23/2024 12:14:43 PM | Mindanao Grid-06/23/2024 12:20: LAKE MAINIT (AGC) online at 1140H (Unplanned Outage). [WEBSMS] | CMIN
6/23/2024 10:12:28 AM | Mindanao Grid-06/23/2024 10:18: LAKE MAINIT (AGC) Hydro shutdown at 0951H due to critical lake level (Unplanned Outage) [WEBSMS] | CMIN
6/23/2024 9:59:25 AM | Mindanao Grid-06/23/2024 10:05: WMPC DG10 Shutdown at 0955H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/23/2024 9:48:47 AM | Mindanao Grid-06/23/2024 09:54: NagaMin 36MVA Transformer No. 3 (SVC) energized at 0935H (Planned Outage) [WEBSMS] | CMIN
6/23/2024 9:46:55 AM | Visayas Grid-06/23/2024 09:47: Quiot-Cebu 138KV line de-energized at 0945H(Planned Outage) [WEBSMS] | CVIS
6/23/2024 9:37:05 AM | Mindanao Grid-06/23/2024 09:43: NagaMin SS 138kV Bus No. 2 energized at 0933H. (Planned Outage) [WEBSMS] | CMIN
6/23/2024 8:17:54 AM | Mindanao Grid-06/23/2024 08:23: Opol SS 75MVA Transformer No. 2 de-energized at 0816H. (Planned Outage) [WEBSMS] | CMIN
6/23/2024 7:47:05 AM | Mindanao Grid-06/23/2024 07:53: Bunawan - Maco 138kV line de-energized at 0746H. (Planned Outage) [WEBSMS] | CMIN
6/23/2024 6:55:37 AM | Luzon Grid-06/23/2024 06:56: Lumban-Bay 230kV Line 1 de-energized at 0655H (Planned Outage) [WEBSMS] | CLUZ
6/23/2024 6:35:19 AM | Luzon Grid-06/23/2024 06:35: San Esteban-Laoag 230kV Line 2 de-energized at 0635H. (Planned Outage) [WEBSMS] | CLUZ
6/23/2024 5:51:52 AM | [NSO Update] Mindanao Grid-06/23/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3032MW, PK=1808MW, RR=73MW, NetOpMargin: AM=1151, PM=1075, EVE=914 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/23/2024 5:50:19 AM | [NSO Update] Visayas Grid-06/23/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2207MW, PK=1709MW, RR=83MW, NetOpMargin: AM=415, PM=377, EVE=301 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @322MW, PEDC U3 @70MW, TGPP @113.5MW, PDPP1-5 @4MW, GTEC @7MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, CEDC U3 @25MW, PB104-3 @5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-3 @4MW, PB104-2 @5.5MW [WEBSMS] | CVIS
6/23/2024 5:46:46 AM | [NSO Update] Luzon Grid-06/23/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15342MW, PK=10164MW, RR=356MW, NetOpMargin: AM=4822, PM=4323, EVE=3286 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @117MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc U3 @295MW, SCPC U1 @110MW, SCPC U4 @140MW [WEBSMS] | CLUZ
6/23/2024 5:39:34 AM | Visayas Grid-06/23/2024 05:40: TVI U2 recut-in at 0537H. (Unplanned Outage) [WEBSMS] | CVIS
6/23/2024 4:56:04 AM | Luzon Grid-06/23/2024 04:56: San Gabriel shutdown at 0447H (Reserve Shutdown) [WEBSMS] | CLUZ
6/23/2024 4:54:42 AM | Luzon Grid-06/23/2024 04:55: Binan-Muntinlupa 230kV Line 4 restored at 0454H (Planned Outage) [WEBSMS] | CLUZ
6/23/2024 4:50:11 AM | Luzon Grid-06/23/2024 04:50: Binan 300MVA T02 restored at 0450H (Planned Outage) [WEBSMS] | CLUZ
6/23/2024 4:36:06 AM | Visayas Grid-06/23/2024 04:36: Lapulapu-Mactan Newtown 69 kV Line restored at 0434H. (Unplanned Outage) [WEBSMS] | CVIS
6/23/2024 4:29:33 AM | Visayas Grid-06/23/2024 04:29: TVI U2 tripped with 67.2 MW load at 0427H. (Unplanned Outage) [WEBSMS] | CVIS
6/23/2024 4:06:35 AM | [NSO Update] Mindanao Grid-06/23/2024 04:12: Weather Advisory: Southwest Monsoon affecting the western section of Southern Luzon. [WEBSMS] | CMIN
6/23/2024 4:06:17 AM | [NSO Update] Visayas Grid-06/23/2024 04:06: Weather Advisory: Southwest Monsoon affecting the western section of Southern Luzon. [WEBSMS] | CVIS
6/23/2024 4:05:55 AM | [NSO Update] Luzon Grid-06/23/2024 04:06: Weather Advisory: Southwest Monsoon affecting the western section of Southern Luzon. [WEBSMS] | CLUZ
6/23/2024 3:27:28 AM | Visayas Grid-06/23/2024 03:27: Lapulapu-Mactan Newtown 69 kV Line tripped at 0323H. (Unplanned Outage) [WEBSMS] | CVIS
6/23/2024 1:23:48 AM | Visayas Grid-06/23/2024 01:24: CEDC U3 cut-in at 0123H. (Unplanned Outage) [WEBSMS] | CVIS
6/23/2024 12:15:05 AM | Mindanao Grid-06/23/2024 00:21: NagaMin SS 138kV Bus No. 2 (7BS02NAA) de-energized at 0010H. (Planned Outage) [WEBSMS] | CMIN
6/23/2024 12:09:36 AM | Mindanao Grid-06/23/2024 00:15: Nagamin SS SVC de-energized at 0008H. Planned Outage/Non-GOMP. (Affected by Planned Outage of 7BS02NAA). [WEBSMS] | CMIN
6/23/2024 12:05:09 AM | Mindanao Grid-06/23/2024 00:11: WMPC DG10 Online as RPS at 0001H - System Voltage Requirement. [WEBSMS] | CMIN
6/23/2024 12:04:18 AM | Mindanao Grid-06/23/2024 00:10: WMPC DG10 online at 0001H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/23/2024 12:02:31 AM | Luzon Grid-06/23/2024 00:02: San Gabriel online at 0000H (Reserved Shutdown). [WEBSMS] | CLUZ
6/22/2024 11:17:18 PM | Visayas Grid-06/22/2024 23:17: TVI U2 cut-in at 2316H. (Unplanned Outage) [WEBSMS] | CVIS
6/22/2024 9:50:38 PM | [NSO Update] Visayas Grid-06/22/2024 21:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2136H with power going to Luzon [WEBSMS] | CVIS
6/22/2024 9:50:16 PM | [NSO Update] Luzon Grid-06/22/2024 21:50: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2136H with power going to Luzon [WEBSMS] | CLUZ
6/22/2024 9:49:32 PM | [NSO Update] Visayas Grid-06/22/2024 21:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2118H from reverse power direction [WEBSMS] | CVIS
6/22/2024 9:49:15 PM | [NSO Update] Luzon Grid-06/22/2024 21:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2118H from reverse power direction [WEBSMS] | CLUZ
6/22/2024 6:19:57 PM | Mindanao Grid-06/22/2024 18:26: Maramag-Kibawe 138kV L2 energized at 1817H from Planned Outage. [WEBSMS] | CMIN
6/22/2024 6:10:34 PM | Mindanao Grid-06/22/2024 18:16: Maramag SS 138kV Bus #2 energized at 1810H from Planned Outage. [WEBSMS] | CMIN
6/22/2024 5:46:27 PM | [NSO Update] Mindanao Grid-06/22/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3036MW, PK=2101MW, RR=73MW, NetOpMargin: EVE=862 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/22/2024 5:44:09 PM | [NSO Update] Visayas Grid-06/22/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2419MW, PK=2099MW, RR=91MW, NetOpMargin: EVE=229 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @315MW, PEDC U3 @70MW, TGPP @111.5MW, PDPP1-5 @4MW, GTEC @7MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-4 @7MW, PB104-3 @5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1-3 @4MW, PB104-2 @5MW [WEBSMS] | CVIS
6/22/2024 5:42:15 PM | [NSO Update] Luzon Grid-06/22/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14292MW, PK=11126MW, RR=429MW, NetOpMargin: EVE=2737 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @117MW, SLTEC 2 @117MW, Limay 8 @60MW, Masinloc U3 @280MW, SCPC U1 @110MW [WEBSMS] | CLUZ
6/22/2024 5:28:55 PM | Luzon Grid-06/22/2024 17:29: Binan-Muntinlupa 230kV Line 4 de-energized at 0516H (Planned Outage) [WEBSMS] | CLUZ
6/22/2024 5:27:30 PM | Luzon Grid-06/22/2024 17:27: Binan 300MVA T02 de-energized at 1713H (Planned Outage) [WEBSMS] | CLUZ
6/22/2024 5:15:21 PM | Luzon Grid-06/22/2024 17:15: Binan-Balibago 115kV Line unlooped via Binan side at 1712H (Planned Outage) [WEBSMS] | CLUZ
6/22/2024 5:12:05 PM | Visayas Grid-06/22/2024 17:12: Colon-Quiot 138kV Line energized at 1712H (Planned Outage) [WEBSMS] | CVIS
6/22/2024 4:27:47 PM | Luzon Grid-06/22/2024 16:28: San Esteban-Laoag 230kV Line 1 restored at 1625H (Planned Outage) [WEBSMS] | CLUZ
6/22/2024 4:18:42 PM | Mindanao Grid-06/22/2024 16:24: Zamboanga - Pitogo 138 kV L1 energized at 1618H from Planned Outage/Non-GOMP. [WEBSMS] | CMIN
6/22/2024 3:14:54 PM | Mindanao Grid-06/22/2024 15:20: Maramag SS 138kV Bus #2 deenergized at 1503H (Planned Outage) [WEBSMS] | CMIN
6/22/2024 3:08:03 PM | Luzon Grid-06/22/2024 15:08: Pagbilao 1 online at 1503H (Unplanned Outage) [WEBSMS] | CLUZ
6/22/2024 2:59:57 PM | Mindanao Grid-06/22/2024 15:05: Maramag-Kibawe 138kV L2 deenergized at 1451H (Planned Outage) [WEBSMS] | CMIN
6/22/2024 2:54:16 PM | Luzon Grid-06/22/2024 14:54: San Jose-Angat 115kV Line 4 restored at 1451H (Unplanned Outage) [WEBSMS] | CLUZ
6/22/2024 2:45:29 PM | [NSO Update] Visayas Grid-06/22/2024 14:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1418H with power going to Visayas [WEBSMS] | CVIS
6/22/2024 2:45:13 PM | [NSO Update] Luzon Grid-06/22/2024 14:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1418H with power going to Visayas [WEBSMS] | CLUZ
6/22/2024 2:04:13 PM | [NSO Update] Visayas Grid-06/22/2024 14:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1354H from forward power direction [WEBSMS] | CVIS
6/22/2024 2:01:35 PM | [NSO Update] Luzon Grid-06/22/2024 14:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1354H from forward power direction [WEBSMS] | CLUZ
6/22/2024 1:11:44 PM | [NSO Update] Luzon Grid-06/22/2024 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14918MW, PK=11591MW, RR=446MW, NetOpMargin: PM=2881, EVE=1964 Highest Unit O/L: GNPD 1@668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @117MW, SLTEC 2 @117MW, Limay 8 @60MW, GMEC U2 @200MW, Masinloc U3 @250MW, SCPC U1 @120MW [WEBSMS] | CLUZ
6/22/2024 12:47:29 PM | [NSO Update] Mindanao Grid-06/22/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3075MW, PK=2154MW, RR=73MW, NetOpMargin: PM=849, EVE=857 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/22/2024 12:40:49 PM | [NSO Update] Visayas Grid-06/22/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2569MW, PK=2169MW, RR=88MW, NetOpMargin: PM=312, EVE=259 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @308MW, PEDC U3 @70MW, TGPP @111.5MW, PDPP1 U5 @4MW, GTEC @7MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @5.5MW, PB104-3 @5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1 U3 @4MW, PB104-2 @5MW [WEBSMS] | CVIS
6/22/2024 11:47:27 AM | Mindanao Grid-06/22/2024 11:53: Maramag-Kibawe 138 kV L1 energized at 1143H (Planned Outage) [WEBSMS] | CMIN
6/22/2024 10:30:19 AM | Luzon Grid-06/22/2024 10:30: San Gabriel shutdown at 1028H (Reserve Shutdown) [WEBSMS] | CLUZ
6/22/2024 10:03:44 AM | Luzon Grid-06/22/2024 10:04: San Jose-Angat 115kV Line 4 tripped at 0958H (Unplanned Outage) [WEBSMS] | CLUZ
6/22/2024 9:57:50 AM | Mindanao Grid-06/22/2024 10:03: Baloi -Agus6 69 kV Line ( 5LI1BLO-AG6) energized back/restored at 0954H from Unplanned Outage. [WEBSMS] | CMIN
6/22/2024 9:55:59 AM | Mindanao Grid-06/22/2024 10:02: Baloi -Agus6 69 kV Line ( 5LI1BLO-AG6) auto-tripped at 0935H. (Unplanned Outage) [WEBSMS] | CMIN
6/22/2024 9:04:27 AM | Mindanao Grid-06/22/2024 09:10: Zamboanga-Pitogo 138kV L1 deenergized at 0900H (Planned Outage) [WEBSMS] | CMIN
6/22/2024 8:55:46 AM | Mindanao Grid-06/22/2024 09:01: Maramag-Kibawe 138kV L1 deenergized at 0850H (Planned Outage) [WEBSMS] | CMIN
6/22/2024 8:52:27 AM | Luzon Grid-06/22/2024 08:52: San Jose-Tayabas 500kV Line 2 de-energized at 0849H (Planned Outage/For Decommissioning) [WEBSMS] | CLUZ
6/22/2024 8:01:16 AM | Visayas Grid-06/22/2024 08:01: Compostela SS PCB 8-02CB24COM emergency opened at 0756H (Unplanned Outage) [WEBSMS] | CVIS
6/22/2024 7:51:28 AM | Luzon Grid-06/22/2024 07:51: Correction: Dasmarinas 600MVA T05 restored at 0746H (Unplanned Outage) [WEBSMS] | CLUZ
6/22/2024 7:46:46 AM | Luzon Grid-06/22/2024 07:47: Dasmarinas 600MVA restored at 0746H (Unplanned Outage) [WEBSMS] | CLUZ
6/22/2024 7:44:46 AM | Mindanao Grid-06/22/2024 07:50: NagaMin 36MVA Transformer No. 3 (SVC) energized at 0743HH. (Planned Outage) [WEBSMS] | CMIN
6/22/2024 7:40:33 AM | Mindanao Grid-06/22/2024 07:46: NagaMin SS 138kV Bus No. 2 energized at 0739H. (Planned Outage) [WEBSMS] | CMIN
6/22/2024 7:11:07 AM | Luzon Grid-06/22/2024 07:11: Dasmarinas 230kV Bus 2 restored at 0710H (Planned Outage) [WEBSMS] | CLUZ
6/22/2024 6:36:55 AM | Luzon Grid-06/22/2024 06:37: San Esteban-Laoag 230kV Line 1 de-energized at 0636H (Planned Outage) [WEBSMS] | CLUZ
6/22/2024 6:27:39 AM | Visayas Grid-06/22/2024 06:28: TVI U2 tripped at 0622H (Unplanned Outage) [WEBSMS] | CVIS
6/22/2024 6:15:37 AM | Visayas Grid-06/22/2024 06:16: Colon-Quiot 138kV Line de-energized at 0613H (Planned Outage) [WEBSMS] | CVIS
6/22/2024 6:12:48 AM | Luzon Grid-06/22/2024 06:13: Bolo-Labrador 230kV Line 2 de-energized at 0611H (Planned Outage) [WEBSMS] | CLUZ
6/22/2024 5:54:43 AM | [NSO Update] Luzon Grid-06/22/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15073MW, PK=11205MW, RR=446MW, NetOpMargin: AM=3422, PM=2499, EVE=1593 Highest Unit O/L: GNPD 1@668MW Derated Plant: Ilijan A @530MW, Ilijan B @390MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @117MW, SLTEC 2 @116MW, Limay 8 @60MW, [WEBSMS] | CLUZ
6/22/2024 5:52:04 AM | [NSO Update] Mindanao Grid-06/22/2024 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3089MW, PK=2107MW, RR=73MW, NetOpMargin: AM=909, PM=716, EVE=786 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/22/2024 5:49:34 AM | [NSO Update] Visayas Grid-06/22/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2442MW, PK=1965MW, RR=85MW, NetOpMargin: AM=392, PM=293, EVE=193 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @315MW, PEDC U3 @120MW, TGPP @109MW, PDPP1 U5 @4MW, GTEC @7MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @5.5MW, PB104-3 @5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PDPP1 U3 @4MW, PB104-2 @5MW [WEBSMS] | CVIS
6/22/2024 4:02:33 AM | [NSO Update] Luzon Grid-06/22/2024 04:02: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CLUZ
6/22/2024 4:02:31 AM | [NSO Update] Mindanao Grid-06/22/2024 04:08: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CMIN
6/22/2024 4:02:31 AM | [NSO Update] Visayas Grid-06/22/2024 04:02: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CVIS
6/22/2024 3:53:33 AM | Luzon Grid-06/22/2024 03:53: Calauan SS 150MVA T02 (Customer Owned) restored at 0323H (Planned Outage) [WEBSMS] | CLUZ
6/22/2024 3:06:59 AM | Luzon Grid-06/22/2024 03:07: Dasmarinas 230kV Bus 2 de-energized at 0305H (Unplanned Outage) [WEBSMS] | CLUZ
6/22/2024 2:43:20 AM | Luzon Grid-06/22/2024 02:43: Dasmarinas 600MVA TO3 restored at 0241H (Unplanned Outage) [WEBSMS] | CLUZ
6/22/2024 2:39:52 AM | Luzon Grid-06/22/2024 02:40: Calauan SS 150MVA T02 (Customer Owned) de-energized at 0228H (Planned Outage) [WEBSMS] | CLUZ
6/22/2024 2:10:38 AM | Luzon Grid-06/22/2024 02:11: San Juan-Calauan 230kV Line 2 restored at 0206H (Planned Outage) [WEBSMS] | CLUZ
6/22/2024 12:27:29 AM | Mindanao Grid-06/22/2024 00:33: NagaMin SS 138kV Bus No. 2 de-energized at 0017H. (Planned Outage) [WEBSMS] | CMIN
6/22/2024 12:20:28 AM | Luzon Grid-06/22/2024 00:20: San Juan-Calauan 230kV Line 2 de-energized at 0020H (Planned Outage) [WEBSMS] | CLUZ
6/22/2024 12:18:34 AM | Mindanao Grid-06/22/2024 00:24: NagaMin 36MVA Transformer No. 3 (SVC) de-energized at 0013H. (Planned Outage) [WEBSMS] | CMIN
6/22/2024 12:09:23 AM | Luzon Grid-06/22/2024 00:09: Dasmarinas 600MVA TO3 de-energized at 0009H (Unplanned Outage) [WEBSMS] | CLUZ
6/21/2024 9:38:26 PM | Mindanao Grid-06/21/2024 21:44: WMPC DG10 Shutdown at 2136H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/21/2024 9:00:47 PM | Luzon Grid-06/21/2024 21:01: San Gabriel online at 2059H (Reserve Shutdown) [WEBSMS] | CLUZ
6/21/2024 8:06:44 PM | Luzon Grid-06/21/2024 20:07: EERI Unit 1 shutdown at 2001H (On Testing and Commissioning). [WEBSMS] | CLUZ
6/21/2024 6:05:43 PM | [NSO Update] Mindanao Grid-06/21/2024 18:11: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3031MW, PK=2279MW, RR=73MW, NetOpMargin: EVE=679 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/21/2024 6:04:50 PM | [NSO Update] Visayas Grid-06/21/2024 18:05: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2420MW, PK=2095MW, RR=91MW, NetOpMargin: EVE=234 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, PEDC U3 @120MW, TGPP @109MW, PDPP1 U5 @4MW, GTEC @7MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @5.5MW, PB104-3 @5MW, PB101-1 @5.5MW, PB101-2 @5.2MW [WEBSMS] | CVIS
6/21/2024 6:00:19 PM | [NSO Update] Luzon Grid-06/21/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13656MW, PK=11163MW, RR=429MW, NetOpMargin: EVE=2063 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @117MW, SLTEC 2 @116MW, Limay 8 @60MW [WEBSMS] | CLUZ
6/21/2024 5:20:20 PM | Luzon Grid-06/21/2024 17:20: Bay-Makban Plant A 230kV Line 2 restored at 1719H (Planned Outage) [WEBSMS] | CLUZ
6/21/2024 5:05:02 PM | Luzon Grid-06/21/2024 17:05: Laoag 300MVA TO2 restored at 1705H (Planned Outage) [WEBSMS] | CLUZ
6/21/2024 4:26:13 PM | Mindanao Grid-06/21/2024 16:32: WMPC DG01 Shutdown at 1616H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/21/2024 3:21:30 PM | Luzon Grid-06/21/2024 15:21: Dasmarinas 600MVA TO5 de-energized (high side) at 1519H (Unplanned Outage) [WEBSMS] | CLUZ
6/21/2024 3:06:04 PM | Mindanao Grid-06/21/2024 15:12: STEAG Unit No. 2 on emergency shutdown at 1500H due to Boiler Tube Leak. (Unplanned Outage) [WEBSMS] | CMIN
6/21/2024 1:16:25 PM | Luzon Grid-06/21/2024 13:16: EERI Unit 1 online at 1248H. (On Testing and Commissioning) [WEBSMS] | CLUZ
6/21/2024 12:58:09 PM | Mindanao Grid-06/21/2024 13:04: WMPC DG01 online at 1256H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/21/2024 12:47:32 PM | [NSO Update] Mindanao Grid-06/21/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3117MW, PK=2438MW, RR=73MW, NetOpMargin: PM=606, EVE=776 Highest Unit O/L: GNPK 1, 2 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW, GNPK U4 @81MW [WEBSMS] | CMIN
6/21/2024 12:46:25 PM | [NSO Update] Visayas Grid-06/21/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2574MW, PK=2185MW, RR=91MW, NetOpMargin: PM=298, EVE=324 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @310MW, PEDC U3 @120MW, TGPP @109MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, GTEC @7MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-2 @5.5MW, PB104-3 @5MW, PB104-4 @7MW, PB101-1 @5.5MW, PB101-2 @5.2MW, GTEC @7MW [WEBSMS] | CVIS
6/21/2024 12:44:41 PM | [NSO Update] Luzon Grid-06/21/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14880MW, PK=12569MW, RR=446MW, NetOpMargin: PM=1866, EVE=1743 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Ilijan A @550MW, Sual 2 @560MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @117MW, SLTEC 2 @116MW, Limay 8 @60MW [WEBSMS] | CLUZ
6/21/2024 10:57:04 AM | Luzon Grid-06/21/2024 10:57: Dasmarinas 600MVA TO5 de-energized at 1056H (Unplanned Outage) [WEBSMS] | CLUZ
6/21/2024 10:36:02 AM | Luzon Grid-06/21/2024 10:36: For Info: System Frequency reach 60.51Hz at 1031H due to tripping of Las Pinas-Pagcor-MetPark 115kV Line. [WEBSMS] | CLUZ
6/21/2024 10:09:08 AM | Mindanao Grid-06/21/2024 10:15: WMPC DG10 online at 0941H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/21/2024 9:33:24 AM | Luzon Grid-06/21/2024 09:33: San Gabriel shutdown at 0932H (Reserve Shutdown) [WEBSMS] | CLUZ
6/21/2024 8:52:15 AM | Luzon Grid-06/21/2024 08:52: For info: Commissioning of Dasmarinas 600MVA T05 completed at 0851H [WEBSMS] | CLUZ
6/21/2024 8:32:47 AM | Luzon Grid-06/21/2024 08:33: Cayanga-Laoag Solar 230kV Line 1 & 2 (CO) de-energized at 0828H and 0829H, respectively (Unplanned Outage) [WEBSMS] | CLUZ
6/21/2024 8:27:36 AM | Mindanao Grid-06/21/2024 08:33: Manolo Fortich 2 HEP Unit 4 shutdown at 0802H. PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
6/21/2024 8:10:40 AM | Luzon Grid-06/21/2024 08:11: Dasmarinas 600MVA T05 loop at 0808H (On-going commissioning) [WEBSMS] | CLUZ
6/21/2024 7:17:28 AM | Luzon Grid-06/21/2024 07:17: Bay-Makban Plant A 230kV Line 2 de-energized at 0711H (Planned Outage) [WEBSMS] | CLUZ
6/21/2024 6:34:07 AM | Luzon Grid-06/21/2024 06:34: Laoag 300MVA TO2 de-energized at 0633H (Planned Outage) [WEBSMS] | CLUZ
6/21/2024 6:21:03 AM | Luzon Grid-06/21/2024 06:21: Labrador 230kV Bus 1 de-energized at 0620H (Planned Outage) [WEBSMS] | CLUZ
6/21/2024 5:50:13 AM | [NSO Update] Mindanao Grid-06/21/2024 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3179MW, PK=2161MW, RR=73MW, NetOpMargin: AM=945, PM=749, EVE=888 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/21/2024 5:49:01 AM | [NSO Update] Visayas Grid-06/21/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2563MW, PK=2117MW, RR=91MW, NetOpMargin: AM=356, PM=219, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @315MW, PEDC U3 @120MW, TGPP @106.5MW, GTEC @7MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/21/2024 5:44:03 AM | [NSO Update] Luzon Grid-06/21/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14975MW, PK=12168MW, RR=446MW, NetOpMargin: AM=2361, PM=1698, EVE=1843 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, Sual 2 @560MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, Limay 8 @60MW [WEBSMS] | CLUZ
6/21/2024 5:04:23 AM | Luzon Grid-06/21/2024 05:04: Binan-Balibago 115kV Line restored at 0504H (Planned Outage) [WEBSMS] | CLUZ
6/21/2024 4:04:01 AM | [NSO Update] Luzon Grid-06/21/2024 04:04: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
6/21/2024 4:03:37 AM | [NSO Update] Mindanao Grid-06/21/2024 04:09: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
6/21/2024 4:03:04 AM | [NSO Update] Visayas Grid-06/21/2024 04:03: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
6/21/2024 1:43:43 AM | Mindanao Grid-06/21/2024 01:49: STEAG Unit No. 1 on emergency shutdown at 0122H, due to Boiler Tube Leak. (Unplanned Outage) [WEBSMS] | CMIN
6/20/2024 11:38:36 PM | Luzon Grid-06/20/2024 23:38: Binan-Balibago 115kV Line de-energized at 2338H (Planned Outage) [WEBSMS] | CLUZ
6/20/2024 10:31:10 PM | Luzon Grid-06/20/2024 22:31: Dasmarinas 600MVA T05 re-energized via high-side at 2228H (Ongoing Commissioning) [WEBSMS] | CLUZ
6/20/2024 9:02:16 PM | Mindanao Grid-06/20/2024 21:08: STEAG Unit No.2 online at 2057H. (Unplanned Outage) [WEBSMS] | CMIN
6/20/2024 8:00:10 PM | Luzon Grid-06/20/2024 20:00: San Gabriel online at 1959H (Reserve Shutdown) [WEBSMS] | CLUZ
6/20/2024 7:47:15 PM | Luzon Grid-06/20/2024 19:47: San Lorenzo Module 50 online at 1934H (Unplanned Outage) [WEBSMS] | CLUZ
6/20/2024 6:41:13 PM | Luzon Grid-06/20/2024 18:41: Lal-lo-Cagayan North Solar 69kV Lines 1 and 2 restored at 1833H and 1839H, respectively. (Planned Outage) [WEBSMS] | CLUZ
6/20/2024 6:15:21 PM | Luzon Grid-06/20/2024 18:15: Dasmarinas 600MVA T05 de-energized at 1814H (Ongoing Commissioning) [WEBSMS] | CLUZ
6/20/2024 5:54:04 PM | [NSO Update] Luzon Grid-06/20/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14074MW, PK=11324MW, RR=426MW, NetOpMargin: EVE=2324 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, Sual 2 @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, Masinloc 3 @325MW, Limay 8 @60MW [WEBSMS] | CLUZ
6/20/2024 5:51:17 PM | Luzon Grid-06/20/2024 17:51: Laoag SS 300MVA T01 restored at 1750H (Planned Outage) [WEBSMS] | CLUZ
6/20/2024 5:36:37 PM | [NSO Update] Visayas Grid-06/20/2024 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2462MW, PK=2068MW, RR=91MW, NetOpMargin: EVE=303 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @311MW, PEDC U3 @120MW, TGPP @106.5MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/20/2024 5:31:36 PM | [NSO Update] Mindanao Grid-06/20/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3113MW, PK=2133MW, RR=73MW, NetOpMargin: EVE=907 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/20/2024 4:43:10 PM | Luzon Grid-06/20/2024 16:43: EERI Unit 1 shutdown at 1637H (Ongoing Testing and Commissioning) [WEBSMS] | CLUZ
6/20/2024 4:22:24 PM | Mindanao Grid-06/20/2024 16:28: WMPC DG10 end of RPS at 1600H. Shutdown at 1617H from MO Dispatch. [WEBSMS] | CMIN
6/20/2024 4:01:39 PM | Luzon Grid-06/20/2024 16:01: Bay-Makban Plant B 230kV Line 2 restored at 1557H (Planned Outage) [WEBSMS] | CLUZ
6/20/2024 3:43:39 PM | Luzon Grid-06/20/2024 15:43: Dasmarinas 600MVA T05 energized via high-side at 1540H (Ongoing Commissioning) [WEBSMS] | CLUZ
6/20/2024 3:28:27 PM | Visayas Grid-06/20/2024 15:28: Colon SS 138 kV Bus 1 energized at 1528H (Planned Outage) [WEBSMS] | CVIS
6/20/2024 2:45:59 PM | Luzon Grid-06/20/2024 14:46: EERI Unit 1 shutdown at 1437H (Ongoing Testing and Commissioning) [WEBSMS] | CLUZ
6/20/2024 2:44:37 PM | Luzon Grid-06/20/2024 14:44: EERI Unit 1 shutdown at 1437H (Ongoing Testing and Commissioning) [WEBSMS] | CLUZ
6/20/2024 2:40:08 PM | [NSO Update] Visayas Grid-06/20/2024 14:40: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1437H with power going to Luzon. [WEBSMS] | CVIS
6/20/2024 2:39:42 PM | [NSO Update] Luzon Grid-06/20/2024 14:40: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1437H with power going to Luzon. [WEBSMS] | CLUZ
6/20/2024 1:23:37 PM | [NSO Update] Visayas Grid-06/20/2024 13:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1323H from forward power direction. [WEBSMS] | CVIS
6/20/2024 1:23:21 PM | [NSO Update] Luzon Grid-06/20/2024 13:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1323H from forward power direction. [WEBSMS] | CLUZ
6/20/2024 1:13:31 PM | Visayas Grid-06/20/2024 13:13: CEDC U1 tripped at 1310H (Unplanned Outage) [WEBSMS] | CVIS
6/20/2024 1:12:49 PM | Luzon Grid-06/20/2024 13:13: Pagbilao 1 shutdown at 1311H (Unplanned Outage) [WEBSMS] | CLUZ
6/20/2024 12:49:57 PM | [NSO Update] Mindanao Grid-06/20/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3143MW, PK=2205MW, RR=73MW, NetOpMargin: PM=865, EVE=959 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/20/2024 12:48:28 PM | [NSO Update] Visayas Grid-06/20/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2751MW, PK=2286MW, RR=91MW, NetOpMargin: PM=373, EVE=362 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @311MW, PEDC U3 @120MW, GTEC @7MW, PDPP1 U1 @4MW, PDPP1 U3 @4MW, PB101-2 @5.2MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @6MW, PB104-4 @7MW, PB101-1 @5.5MW [WEBSMS] | CVIS
6/20/2024 12:47:00 PM | [NSO Update] Luzon Grid-06/20/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15350MW, PK=12727MW, RR=446MW, NetOpMargin: PM=2177, EVE=1836 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @114MW, SLTEC 2 @114MW, Limay 8 @60MW, Pagbilao 1 @120MW, Sual 2 @550MW [WEBSMS] | CLUZ
6/20/2024 12:20:06 PM | Luzon Grid-06/20/2024 12:20: Hermosa-Malolos 230kV Line restored at 1220H (Unplanned Outage) [WEBSMS] | CLUZ
6/20/2024 12:12:35 PM | Luzon Grid-06/20/2024 12:12: Hermosa-Malolos 230kV tripped at 1210H (Unplanned Outage) [WEBSMS] | CLUZ
6/20/2024 11:58:28 AM | Mindanao Grid-06/20/2024 12:04: Tagoloan - Villanueva 138kV L2 energized/restored at 1156H. (Unplanned outage) [WEBSMS] | CMIN
6/20/2024 10:24:26 AM | Mindanao Grid-06/20/2024 10:30: Agus 2 Unit 3 online at 1022H. (Unplanned Outage) [WEBSMS] | CMIN
6/20/2024 10:06:03 AM | Mindanao Grid-06/20/2024 10:12: WMPC DG10 online at 1003H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/20/2024 9:32:28 AM | Mindanao Grid-06/20/2024 09:38: Agus 2 Unit 3 with 30MW Gross Generation tripped at 0923H. (Unplanned Outage) [WEBSMS] | CMIN
6/20/2024 9:23:28 AM | Visayas Grid-06/20/2024 09:23: Colon SS 138 kV Bus 1 de-energized at 0923H (Planned Outage) [WEBSMS] | CVIS
6/20/2024 8:44:43 AM | Mindanao Grid-06/20/2024 08:50: Tagoloan - Villanueva 138kV L2 de-energized at 0836H. (Unplanned outage) [WEBSMS] | CMIN
6/20/2024 7:45:57 AM | Luzon Grid-06/20/2024 07:46: Bay-Makban Plant B 230kV Line 2 de-energized at 0745H (Planned Outage) [WEBSMS] | CLUZ
6/20/2024 7:24:38 AM | Visayas Grid-06/20/2024 07:24: Compostela - Carmen 69 kV Line energized at 0722H (Unplanned Outage) [WEBSMS] | CVIS
6/20/2024 6:38:55 AM | Visayas Grid-06/20/2024 06:39: Compostela - Carmen 69 kV Line tripped at 0635H (Unplanned Outage) [WEBSMS] | CVIS
6/20/2024 6:35:51 AM | Luzon Grid-06/20/2024 06:36: Laoag SS 300MVA T01 de-energized at 0633H (Planned Outage) [WEBSMS] | CLUZ
6/20/2024 5:56:01 AM | [NSO Update] Mindanao Grid-06/20/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3130MW, PK=2206MW, RR=73MW, NetOpMargin: AM=852, PM=754, EVE=804 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5M [WEBSMS] | CMIN
6/20/2024 5:48:32 AM | [NSO Update] Visayas Grid-06/20/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2615MW, PK=2088MW, RR=91MW, NetOpMargin: AM=436, PM=399, EVE=405 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @318MW, PEDC U3 @70MW, GTEC @7MW, PDPP1 U1 @4MW, PDPP1 U3 @4MW, PB101-2 @5.2MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @6MW, PB104-2 @5.5MW, PB104-3 @5MW, PB104-4 @7MW, PB101-1 @5.5MW [WEBSMS] | CVIS
6/20/2024 5:44:28 AM | [NSO Update] Luzon Grid-06/20/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15904MW, PK=12423MW, RR=446MW, NetOpMargin: AM=3035, PM=1955, EVE=2377 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @114MW, SLTEC 2 @114MW, Limay 8 @60MW [WEBSMS] | CLUZ
6/20/2024 5:44:12 AM | Luzon Grid-06/20/2024 05:44: Lal-lo-Cagayan North Solar 69kV lines 1 and 2 were de-energized at 0540H and 0541H respectively. (Planned Outage) [WEBSMS] | CLUZ
6/20/2024 4:22:51 AM | [NSO Update] Luzon Grid-06/20/2024 04:23: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
6/20/2024 4:22:25 AM | [NSO Update] Mindanao Grid-06/20/2024 04:28: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
6/20/2024 4:21:25 AM | [NSO Update] Visayas Grid-06/20/2024 04:21: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
6/19/2024 7:49:09 PM | Mindanao Grid-06/19/2024 19:55: WMPC DG04 Shutdown at 1947H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/19/2024 7:04:45 PM | Luzon Grid-06/19/2024 19:05: Laoag-Pasuquin 115kV line was restored at 1903H. (Unplanned Outage-Customer Request) [WEBSMS] | CLUZ
6/19/2024 6:43:15 PM | Luzon Grid-06/19/2024 18:43: Laoag-Pasuquin 115kV line was de-energized at 1842H (Unplanned Outage-Customer Request) [WEBSMS] | CLUZ
6/19/2024 6:14:55 PM | Mindanao Grid-06/19/2024 18:20: Pulangi 4 Unit 3 online at 1807H. (Unplanned Outage) [WEBSMS] | CMIN
6/19/2024 6:11:37 PM | Luzon Grid-06/19/2024 18:11: Laoag-Pasuquin 115kV line was restored at 1810H (Planned Outage) [WEBSMS] | CLUZ
6/19/2024 5:59:00 PM | [NSO Update] Luzon Grid-06/19/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13889MW, PK=11376MW, RR=426MW, NetOpMargin: EVE=2086 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @115MW, SLTEC 2 @117MW, Limay 8 @60MW [WEBSMS] | CLUZ
6/19/2024 5:51:33 PM | [NSO Update] Mindanao Grid-06/19/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3032MW, PK=2183MW, RR=73MW, NetOpMargin: EVE=776 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/19/2024 5:42:56 PM | [NSO Update] Visayas Grid-06/19/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2519MW, PK=2088MW, RR=91MW, NetOpMargin: EVE=340 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @317MW, PEDC U3 @120MW, GTEC @7MW, PDPP1 U1 @4MW, PDPP1 U3 @4MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @6MW, PB104-2 @5.5MW, PB104-3 @5MW, PB104-4 @6.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW [WEBSMS] | CVIS
6/19/2024 5:42:34 PM | Luzon Grid-06/19/2024 17:42: Pagbilao Unit 1 online at 1740H. (Unplanned Outage) [WEBSMS] | CLUZ
6/19/2024 4:23:18 PM | Visayas Grid-06/19/2024 16:23: Mandaue GIS 100 MVA 138/69/13.8 kV TR1 energized at 1621H (Planned Outage) [WEBSMS] | CVIS
6/19/2024 4:17:54 PM | Mindanao Grid-06/19/2024 16:23: WMPC DG10 Shutdown at 1616H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/19/2024 2:35:45 PM | Mindanao Grid-06/19/2024 14:41: Agus2 Kibawe 138kV L2 restored/ energized at 1432H from unplanned outage. [WEBSMS] | CMIN
6/19/2024 2:27:26 PM | Mindanao Grid-06/19/2024 14:33: Kidapawan SS New Power Transformer #2 (7XF02KID), 100 MVA successfully energized at 1422H. [WEBSMS] | CMIN
6/19/2024 1:56:44 PM | Visayas Grid-06/19/2024 13:57: Mandaue GIS 100 MVA 138/69/13.8 kV TR1 de-energized at 1356H (Planned Outage) [WEBSMS] | CVIS
6/19/2024 1:18:09 PM | Mindanao Grid-06/19/2024 13:24: WMPC DG10 online at 1316H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/19/2024 12:47:31 PM | [NSO Update] Mindanao Grid-06/19/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3065MW, PK=2306MW, RR=73MW, NetOpMargin: PM=686, EVE=795 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/19/2024 12:46:23 PM | [NSO Update] Visayas Grid-06/19/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2603MW, PK=2188MW, RR=91MW, NetOpMargin: PM=324, EVE=215 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @316MW, PEDC U3 @70MW, GTEC @7MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/19/2024 12:44:20 PM | [NSO Update] Luzon Grid-06/19/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15035MW, PK=12703MW, RR=446MW, NetOpMargin: PM=1885, EVE=1774 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, Masinloc 3 @315MW, Limay 8 @60MW [WEBSMS] | CLUZ
6/19/2024 10:39:07 AM | [NSO Update] Luzon Grid-06/19/2024 10:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1037H with power going to Luzon. [WEBSMS] | CLUZ
6/19/2024 10:38:48 AM | [NSO Update] Visayas Grid-06/19/2024 10:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1037H with power going to Luzon. [WEBSMS] | CVIS
6/19/2024 9:48:24 AM | Mindanao Grid-06/19/2024 09:54: WMPC DG04 online at 0940H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/19/2024 9:31:52 AM | [NSO Update] Luzon Grid-06/19/2024 09:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0928H from forward power direction. [WEBSMS] | CLUZ
6/19/2024 9:31:49 AM | [NSO Update] Visayas Grid-06/19/2024 09:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0928H from forward power direction. [WEBSMS] | CVIS
6/19/2024 9:09:17 AM | Luzon Grid-06/19/2024 09:09: San Lorenzo 60 online at 0905H (Unplanned Outage) [WEBSMS] | CLUZ
6/19/2024 8:37:46 AM | Mindanao Grid-06/19/2024 08:43: Agus2 Kibawe 138kV L2 auto-tripped at 0743H due line to line fault (BC). advised for line Patrol. Note: The said line energized up tower #33 for anti-pilferage [WEBSMS] | CMIN
6/19/2024 8:27:42 AM | Mindanao Grid-06/19/2024 08:33: Manolo 2 Unit 2 shutdown at 0803H for PMS (GOMP). [WEBSMS] | CMIN
6/19/2024 8:21:59 AM | Mindanao Grid-06/19/2024 08:27: Tagoloan -Villanueva 138 kV L2 auto-tripped at Tagoloan SS side only at 0743H. Note : Tagoloan Bus breaker 7-02CB08TAG was open June 18, 2024, 0254H for replacement/decommissioning under MSRP. Line Restored at 0751H. [WEBSMS] | CMIN
6/19/2024 8:21:10 AM | Mindanao Grid-06/19/2024 08:27: Pulangi 4 Unit 3 with 75MW load tripped at 0809H. Indication: Turbine guide bearing oil level high. No ALD activation, lowest frequency recorded at 59.56Hz. (Unplanned Outage) [WEBSMS] | CMIN
6/19/2024 6:12:05 AM | Luzon Grid-06/19/2024 06:12: Laoag-Pasuquin 115kV Line de-energized at 0607H (Planned Outage) [WEBSMS] | CLUZ
6/19/2024 5:52:34 AM | [NSO Update] Luzon Grid-06/19/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14838MW, PK=11759MW, RR=446MW, NetOpMargin: AM=2633, PM=1291, EVE=731 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @305MW, Masinloc 2 @200MW, SLTEC 1 @115MW, SLTEC 2 @115MW, Limay 8 @60MW [WEBSMS] | CLUZ
6/19/2024 5:51:02 AM | [NSO Update] Visayas Grid-06/19/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2550MW, PK=2210MW, RR=91MW, NetOpMargin: AM=249, PM=207, EVE=244 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @316MW, PEDC U3 @70MW, GTEC @7MW, PDPP1 U1 @4MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @6MW, PB104-2 @5.5MW, PB104-4 @6.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW [WEBSMS] | CVIS
6/19/2024 5:33:06 AM | [NSO Update] Mindanao Grid-06/19/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3152MW, PK=2305MW, RR=73MW, NetOpMargin: AM=775, PM=619, EVE=763 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @29.5MW [WEBSMS] | CMIN
6/19/2024 5:11:46 AM | Luzon Grid-06/19/2024 05:12: San Gabriel shutdown at 0508H (Reserve Shutdown) [WEBSMS] | CLUZ
6/19/2024 4:55:48 AM | [NSO Update] Mindanao Grid-06/19/2024 05:01: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
6/19/2024 4:55:34 AM | [NSO Update] Visayas Grid-06/19/2024 04:55: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
6/19/2024 4:55:20 AM | [NSO Update] Luzon Grid-06/19/2024 04:55: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
6/19/2024 2:47:48 AM | Luzon Grid-06/19/2024 02:48: San Lorenzo Module 60 shutdown at 0243H (Unplanned Outage) [WEBSMS] | CLUZ
6/19/2024 1:00:42 AM | Visayas Grid-06/19/2024 01:00: CEDC U3 cut-out at 0058H (Unplanned Outage) [WEBSMS] | CVIS
6/19/2024 12:09:32 AM | Luzon Grid-06/19/2024 00:09: San Lorenzo Module 50 tripped at 0006H from 161MW load. The lowest frequency was 59.641Hz. (Unplanned Outage) [WEBSMS] | CLUZ
6/18/2024 9:31:45 PM | Luzon Grid-06/18/2024 21:31: Santiago-Gamu 230kV line auto-tripped/auto-reclosed at 2122H. (Unplanned Outage) [WEBSMS] | CLUZ
6/18/2024 9:25:25 PM | Mindanao Grid-06/18/2024 21:31: WMPC DG04 Shutdown at 2117H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/18/2024 7:06:23 PM | [NSO Update] Visayas Grid-06/18/2024 19:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1902H with power going to Luzon [WEBSMS] | CVIS
6/18/2024 7:06:05 PM | [NSO Update] Luzon Grid-06/18/2024 19:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1902H with power going to Luzon [WEBSMS] | CLUZ
6/18/2024 6:55:10 PM | [NSO Update] Visayas Grid-06/18/2024 18:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1852H from reverse power direction [WEBSMS] | CVIS
6/18/2024 6:54:56 PM | [NSO Update] Luzon Grid-06/18/2024 18:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1852H from reverse power direction [WEBSMS] | CLUZ
6/18/2024 5:57:11 PM | [NSO Update] Mindanao Grid-06/18/2024 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3099MW, PK=2379MW, RR=73MW, NetOpMargin: EVE=648 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/18/2024 5:55:41 PM | [NSO Update] Visayas Grid-06/18/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2588MW, PK=2249MW, RR=89MW, NetOpMargin: EVE=250 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @307MW, PEDC U3 @120MW, CEDC U3 @75MW, GTEC @7MW, PDPP1 U1 @4MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-2 @5.5MW, PB104-3 @5MW, PB104-4 @6.5MW, PB101-1 @5.5MW, PB101-2 @5.2MW, PB104-1 @6MW [WEBSMS] | CVIS
6/18/2024 5:51:17 PM | [NSO Update] Luzon Grid-06/18/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13869MW, PK=11660MW, RR=429MW, NetOpMargin: EVE=1779 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @115MW, SLTEC 2 @115MW, Limay 8 @60MW [WEBSMS] | CLUZ
6/18/2024 5:21:25 PM | Mindanao Grid-06/18/2024 17:27: WMPC DG10 Shutdown at 1716H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/18/2024 4:22:03 PM | Visayas Grid-06/18/2024 16:22: Naga 138 kV bus 2 energized at 1616H (Planned Outage) [WEBSMS] | CVIS
6/18/2024 2:20:33 PM | [NSO Update] Visayas Grid-06/18/2024 14:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1418H with power going to Visayas [WEBSMS] | CVIS
6/18/2024 2:20:08 PM | [NSO Update] Luzon Grid-06/18/2024 14:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1418H with power going to Visayas [WEBSMS] | CLUZ
6/18/2024 2:19:25 PM | [NSO Update] Visayas Grid-06/18/2024 14:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1408H from forward power direction [WEBSMS] | CVIS
6/18/2024 2:19:04 PM | [NSO Update] Luzon Grid-06/18/2024 14:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1408H from forward power direction [WEBSMS] | CLUZ
6/18/2024 1:12:38 PM | Visayas Grid-06/18/2024 13:12: Naga 138 kV bus 2 de-energized at 1311H (Planned Outage) [WEBSMS] | CVIS
6/18/2024 12:47:19 PM | [NSO Update] Visayas Grid-06/18/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2686MW, PK=2365MW, RR=91MW, NetOpMargin: PM=230, EVE=261 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @318MW, PEDC U3 @70MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-E @8MW, PDPP3-G @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/18/2024 12:42:39 PM | [NSO Update] Mindanao Grid-06/18/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3141MW, PK=2490MW, RR=73MW, NetOpMargin: PM=577, EVE=683 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/18/2024 12:40:03 PM | [NSO Update] Luzon Grid-06/18/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15267MW, PK=13105MW, RR=446MW, NetOpMargin: PM=1716, EVE=1914 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @115MW, SLTEC 2 @115MW, Limay 8 @60MW, Calaca 2 @270MW [WEBSMS] | CLUZ
6/18/2024 12:01:02 PM | Luzon Grid-06/18/2024 12:01: San Gabriel online at 1157H (Reserve Shutdown) [WEBSMS] | CLUZ
6/18/2024 11:33:10 AM | Mindanao Grid-06/18/2024 11:39: WMPC DG10 online at 1130H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/18/2024 10:51:09 AM | Visayas Grid-06/18/2024 10:51: Carcon-Sangi 34.5 kV L1 energized at 0843H (Planned Outage) [WEBSMS] | CVIS
6/18/2024 9:50:33 AM | Mindanao Grid-06/18/2024 09:56: WMPC DG04 online at 0948H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/18/2024 8:40:52 AM | Visayas Grid-06/18/2024 08:41: Carcon-Sangi 34.5 kV L1 de-energized at 0840H (Planned Outage) [WEBSMS] | CVIS
6/18/2024 6:16:35 AM | Luzon Grid-06/18/2024 06:16: Quezon-Dona Imelda 230kV Line restored at 0616H (Planned Outage) [WEBSMS] | CLUZ
6/18/2024 6:13:21 AM | Luzon Grid-06/18/2024 06:13: Correction: Concepcion-Clark 230kV Line 2 tripped/reclosed both side at 0604H (Unplanned Outage) [WEBSMS] | CLUZ
6/18/2024 6:11:52 AM | Luzon Grid-06/18/2024 06:12: Concepcion-Clark 230kV Line 2 de-energized at 0604H (Planned Outage) [WEBSMS] | CLUZ
6/18/2024 5:43:55 AM | [NSO Update] Mindanao Grid-06/18/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3121MW, PK=2339MW, RR=73MW, NetOpMargin: AM=709, PM=514, EVE=669 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/18/2024 5:41:40 AM | [NSO Update] Mindanao Grid-06/18/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3121MW, PK=2339MW, RR=0MW, NetOpMargin: AM=709, PM=514, EVE=669 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/18/2024 5:39:46 AM | [NSO Update] Visayas Grid-06/18/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2654MW, PK=2162MW, RR=401MW, NetOpMargin: AM=401, PM=175, EVE=180 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @318MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB101-2 @5.2MW, PB104-3 @5MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PB104-2 @5.5MW, PEDC U3 @70MW, PDPP3-E @8MW, PDPP3-H @8MW, PDPP1 U1 @4MW, PB101-1 @5.5MW [WEBSMS] | CVIS
6/18/2024 5:36:53 AM | [NSO Update] Luzon Grid-06/18/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15775MW, PK=11994MW, RR=446MW, NetOpMargin: AM=3335, PM=2135, EVE=1906 Highest Unit O/L: GNPD 1@668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @115MW, SLTEC 2 @115MW, Limay 8 @60MW, [WEBSMS] | CLUZ
6/18/2024 5:11:31 AM | Luzon Grid-06/18/2024 05:11: Las Pinas SS 300MVA T03 restored at 0511H. (Planned Outage) [WEBSMS] | CLUZ
6/18/2024 4:25:09 AM | Mindanao Grid-06/18/2024 04:31: Baloi SS 100 MVA Transformer No. 3 energized at 0424H. (Unplanned Outage) [WEBSMS] | CMIN
6/18/2024 4:09:20 AM | [NSO Update] Mindanao Grid-06/18/2024 04:15: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CMIN
6/18/2024 4:08:52 AM | [NSO Update] Visayas Grid-06/18/2024 04:09: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CVIS
6/18/2024 4:08:03 AM | [NSO Update] Luzon Grid-06/18/2024 04:08: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CLUZ
6/17/2024 11:09:44 PM | Luzon Grid-06/17/2024 23:09: Quezon-Dona Imelda 230kV Line de-energized at 2309H (Planned Outage) [WEBSMS] | CLUZ
6/17/2024 10:41:26 PM | Luzon Grid-06/17/2024 22:41: Las Pinas SS 300MVA T03 de-energized at 2241H. (Planned Outage) [WEBSMS] | CLUZ
6/17/2024 9:53:44 PM | Luzon Grid-06/17/2024 21:53: Labrador-Botolan 230kV Line restored at 2153H. (Planned Outage [WEBSMS] | CLUZ
6/17/2024 9:51:04 PM | Mindanao Grid-06/17/2024 21:56: UPSI Jasaan BESS with 6MW load (discharging) tripped at 2118H. Indication: Unbalance voltage: Restored at 2031H. (Unplanned Outage) [WEBSMS] | CMIN
6/17/2024 9:51:03 PM | Visayas Grid-06/17/2024 21:51: Daanbantayan 230 kV bus 1 energized at 2148H (Planned Outage) [WEBSMS] | CVIS
6/17/2024 9:21:32 PM | Mindanao Grid-06/17/2024 21:27: Agus 2 U3 online at 2118H from Forced outage. (Unplanned Outage) [WEBSMS] | CMIN
6/17/2024 9:15:24 PM | Mindanao Grid-06/17/2024 21:21: Agus 2 U2 online at 2112H from Forced outage. (Unplanned Outage) [WEBSMS] | CMIN
6/17/2024 9:02:23 PM | Mindanao Grid-06/17/2024 21:08: Update: AG2 U2 & U3 with 30 & 35MW load respectively tripped at 2017H. AG2 U2 ind: 86T Transformer Protection, AG2 U3 ind: Power Supply Failure. Lowest frequency recorded at 59.648Hz, no ALD activation. (Unplanned Outage) [WEBSMS] | CMIN
6/17/2024 8:41:19 PM | Mindanao Grid-06/17/2024 20:47: Update: Agus 2 Unit 2 & Unit 3 with 30 & 35MW load respectively tripped at 2017H. For investigation. Lowest frequency recorded at 59.648Hz, no ALD activation. (Unplanned Outage) [WEBSMS] | CMIN
6/17/2024 8:29:17 PM | Mindanao Grid-06/17/2024 20:35: Agus 2 Unit 2 & Unit 3 with 30 & 35MW load respectively tripped at 2017H. For investigation. (Unplanned Outage) [WEBSMS] | CMIN
6/17/2024 8:23:36 PM | Mindanao Grid-06/17/2024 20:29: Baloi SS 100 MVA Transformer No. 3 auto-tripped at 2017H. (Unplanned Outage) [WEBSMS] | CMIN
6/17/2024 8:15:45 PM | Visayas Grid-06/17/2024 20:15: Pal 1 U2 cut-in at 2011H (Unplanned outage) [WEBSMS] | CVIS
6/17/2024 7:40:47 PM | Visayas Grid-06/17/2024 19:40: Pal 1 U3 cut-in at 1938H (Unplanned outage) [WEBSMS] | CVIS
6/17/2024 7:31:19 PM | [NSO Update] Visayas Grid-06/17/2024 19:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1921H with power going to Luzon [WEBSMS] | CVIS
6/17/2024 7:30:03 PM | [NSO Update] Luzon Grid-06/17/2024 19:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1921H with power going to Luzon [WEBSMS] | CLUZ
6/17/2024 7:13:42 PM | [NSO Update] Luzon Grid-06/17/2024 19:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1910H from reverse power direction [WEBSMS] | CLUZ
6/17/2024 7:13:08 PM | [NSO Update] Visayas Grid-06/17/2024 19:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1910H from reverse power direction [WEBSMS] | CVIS
6/17/2024 7:11:29 PM | Visayas Grid-06/17/2024 19:11: Pal 1 U1 cut-in at 1907H (Unplanned outage) [WEBSMS] | CVIS
6/17/2024 5:57:40 PM | [NSO Update] Mindanao Grid-06/17/2024 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3109MW, PK=2230MW, RR=73MW, NetOpMargin: EVE=806 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/17/2024 5:54:42 PM | [NSO Update] Visayas Grid-06/17/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2402MW, PK=2047MW, RR=89MW, NetOpMargin: EVE=266 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB101-2 @5.2MW, PB104-3 @5MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PB104-2 @5.5MW, PEDC U3 @70MW, PDPP3-E @8MW, PDPP3-H @8MW, PDPP1 U1 @4MW, PB101-1 @5.5MW [WEBSMS] | CVIS
6/17/2024 5:49:01 PM | [NSO Update] Luzon Grid-06/17/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13826MW, PK=10552MW, RR=412MW, NetOpMargin: EVE=2863 Highest Unit O/L: GNPD 1@668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @115MW, SLTEC 2 @115MW, Limay 8 @60MW, [WEBSMS] | CLUZ
6/17/2024 3:52:25 PM | Mindanao Grid-06/17/2024 15:58: Bunawan - Nabunturan 138kV line energized at 1550H. (Planned Outage) [WEBSMS] | CMIN
6/17/2024 3:09:09 PM | Visayas Grid-06/17/2024 15:09: Naga 138 kV bus 1 energized at 1505H (Planned Outage) [WEBSMS] | CVIS
6/17/2024 2:19:05 PM | Mindanao Grid-06/17/2024 14:24: Agus 2 Unit 1 online at 1413H from PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
6/17/2024 12:39:35 PM | [NSO Update] Mindanao Grid-06/17/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3135MW, PK=2129MW, RR=73MW, NetOpMargin: PM=934, EVE=881 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/17/2024 12:39:05 PM | [NSO Update] Visayas Grid-06/17/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2516MW, PK=1985MW, RR=89MW, NetOpMargin: PM=442, EVE=282 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @316MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB101-2 @5.2MW, PB104-3 @5MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PB104-2 @5.5MW, PEDC U3 @70MW, PDPP3-E @8MW, PDPP3-H @8MW, PDPP1 U1 @4MW, PB101-1 @5.5MW [WEBSMS] | CVIS
6/17/2024 12:38:10 PM | [NSO Update] Luzon Grid-06/17/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15326MW, PK=11376MW, RR=441MW, NetOpMargin: PM=3509, EVE=2524 Highest Unit O/L: GNPD 1@668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @115MW, SLTEC 2 @119MW, Limay 8 @60MW, QPPL @430MW [WEBSMS] | CLUZ
6/17/2024 10:12:19 AM | Visayas Grid-06/17/2024 10:12: Sangi 34.5 kV bus 2 energized at 1011H (Planned Outage) [WEBSMS] | CVIS
6/17/2024 9:47:46 AM | Visayas Grid-06/17/2024 09:47: Naga 138 kV bus 1 de-energized at 0944H (Planned Outage) [WEBSMS] | CVIS
6/17/2024 9:26:13 AM | Visayas Grid-06/17/2024 09:26: DaanBantayan 230 kV bus 1 de-energized at 0925H (Planned Outage) [WEBSMS] | CVIS
6/17/2024 9:18:48 AM | Luzon Grid-06/17/2024 09:18: Dasmarinas-Las Pinas 230kV Line 1 restored at 0916H (Planned Outage) [WEBSMS] | CLUZ
6/17/2024 9:05:29 AM | Mindanao Grid-06/17/2024 09:11: STEAG Unit 2 emergency shutdown at 0900H due to tube leak and boiler fouling (Unplanned Outage) [WEBSMS] | CMIN
6/17/2024 8:59:47 AM | Luzon Grid-06/17/2024 08:59: EERI Unit 1 online at 0853H. (On Testing and Commissioning) [WEBSMS] | CLUZ
6/17/2024 8:56:12 AM | Visayas Grid-06/17/2024 08:56: PGPP1 U2 & U3 tripped at 0853H (Unplanned Outage) [WEBSMS] | CVIS
6/17/2024 8:43:34 AM | [NSO Update] Luzon Grid-06/17/2024 08:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0840H with power going to Visayas. [WEBSMS] | CLUZ
6/17/2024 8:43:15 AM | [NSO Update] Visayas Grid-06/17/2024 08:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0840H with power going to Visayas. [WEBSMS] | CVIS
6/17/2024 8:34:35 AM | [NSO Update] Luzon Grid-06/17/2024 08:34: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0830H from forward power direction. [WEBSMS] | CLUZ
6/17/2024 8:33:39 AM | [NSO Update] Visayas Grid-06/17/2024 08:33: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0830H from forward power direction. [WEBSMS] | CVIS
6/17/2024 8:23:09 AM | Visayas Grid-06/17/2024 08:23: Sangi 34.5 kV bus 2 de-energized at 0820H (Planned Outage) [WEBSMS] | CVIS
6/17/2024 7:10:46 AM | Mindanao Grid-06/17/2024 07:16: Bunawan - Nabunturan 138kV line de-energized at 0709H. (Planned Outage) [WEBSMS] | CMIN
6/17/2024 6:33:03 AM | Mindanao Grid-06/17/2024 06:38: STEAG Unit 1 online at 0623H from Forced outage. (Unplanned Outage) [WEBSMS] | CMIN
6/17/2024 6:22:29 AM | Luzon Grid-06/17/2024 06:22: Labrador-Botolan 230kV Line de-energized at 0613H (Planned Outage) [WEBSMS] | CLUZ
6/17/2024 5:59:30 AM | [NSO Update] Mindanao Grid-06/17/2024 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3256MW, PK=1857MW, RR=73MW, NetOpMargin: AM=1327, PM=763, EVE=734 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/17/2024 5:59:18 AM | Luzon Grid-06/17/2024 05:59: Pagbilao 1 shutdown at 0552H (Unplanned Outage) [WEBSMS] | CLUZ
6/17/2024 5:56:54 AM | [NSO Update] Visayas Grid-06/17/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2546MW, PK=1905MW, RR=86MW, NetOpMargin: AM=555, PM=251, EVE=256 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @316MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB101-2 @5.2MW, PB104-3 @5MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PB104-2 @5.5MW, PEDC U3 @70MW, PDPP3-E @8MW, PDPP3-H @8MW, PDPP1 U1 @4MW, PB101-1 @5.5MW [WEBSMS] | CVIS
6/17/2024 5:53:59 AM | [NSO Update] Luzon Grid-06/17/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15434MW, PK=10297MW, RR=426MW, NetOpMargin: AM=4710, PM=3957, EVE=2203 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Ilijan A @540MW, GNPD 2 @640MW, Masinloc 1 @300MW, Masinloc 2 @200MW, SLTEC 1 @115MW, SLTEC 2 @119MW, Limay 8 @60MW, Calaca 2 @270MW [WEBSMS] | CLUZ
6/17/2024 4:14:35 AM | [NSO Update] Luzon Grid-06/17/2024 04:14: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CLUZ
6/17/2024 4:14:20 AM | [NSO Update] Visayas Grid-06/17/2024 04:14: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CVIS
6/17/2024 4:14:07 AM | [NSO Update] Mindanao Grid-06/17/2024 04:19: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CMIN
6/17/2024 2:15:00 AM | Luzon Grid-06/17/2024 02:15: Malolos 150MVA T02 (Customer Owned) restored at 0206H (Planned Outage) [WEBSMS] | CLUZ
6/17/2024 1:31:42 AM | Luzon Grid-06/17/2024 01:31: San Gabriel offline at 0128H (Reserve Shutdown) [WEBSMS] | CLUZ
6/17/2024 12:35:24 AM | Luzon Grid-06/17/2024 00:35: Malolos 150MVA T02 (Customer Owned) de-energized at 0034H (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 11:35:02 PM | Visayas Grid-06/16/2024 23:35: Colon - Naga 138 kV Line 2 energized at 2333H (Planned Outage) [WEBSMS] | CVIS
6/16/2024 10:18:35 PM | Luzon Grid-06/16/2024 22:18: Dasmarinas-Las Pinas 230kV Line 1 de-energized at 2218H (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 8:23:09 PM | Luzon Grid-06/16/2024 20:23: Nagsaag-San Roque 230kV L2 loop in San Roque at 2021H (Unplanned Outage) [WEBSMS] | CLUZ
6/16/2024 8:20:50 PM | Luzon Grid-06/16/2024 20:20: Nagsaag-San Roque 230kV L2 tripped at 2017H, autoreclosed at Nagsaag (Unplanned Outage) [WEBSMS] | CLUZ
6/16/2024 6:37:26 PM | Mindanao Grid-06/16/2024 18:43: Tacurong SS 100MVA 138/69kV Power Transformer 3 energized at 1823H. (Planned Outage) [WEBSMS] | CMIN
6/16/2024 5:50:58 PM | [NSO Update] Mindanao Grid-06/16/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3108MW, PK=2046MW, RR=73MW, NetOpMargin: EVE=989 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/16/2024 5:50:00 PM | [NSO Update] Visayas Grid-06/16/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2592MW, PK=2055MW, RR=91MW, NetOpMargin: EVE=446 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @310MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB101-2 @5.2MW, PB104-3 @5MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PB104-2 @5.5MW, PEDC U3 @70MW, PDPP3-E @8MW, PDPP3-H @8MW, PDPP1 U1 @4MW [WEBSMS] | CVIS
6/16/2024 5:48:26 PM | [NSO Update] Luzon Grid-06/16/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14930MW, PK=11191MW, RR=339MW, NetOpMargin: EVE=3400 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Ilijan A @550MW, GNPD 2 @640MW, Masinloc 1 @250MW, Masinloc 2 @200MW, SLTEC 1 @115MW, SLTEC 2 @119MW, Limay 8 @60MW [WEBSMS] | CLUZ
6/16/2024 5:34:28 PM | Visayas Grid-06/16/2024 17:34: Colon-CVC 69 kV line energized at 1732H (Planned Outage) [WEBSMS] | CVIS
6/16/2024 5:25:19 PM | Luzon Grid-06/16/2024 17:25: EERI 1 shutdown at 1722H, on commissioning [WEBSMS] | CLUZ
6/16/2024 5:11:00 PM | Luzon Grid-06/16/2024 17:11: Santiago-Tuguegarao 230kV Line restored at 1710H (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 5:01:50 PM | Visayas Grid-06/16/2024 17:02: Calong-calong - Toledo BESS 69 kV Line energized at 1659H (Planned Outage) [WEBSMS] | CVIS
6/16/2024 4:29:53 PM | Visayas Grid-06/16/2024 16:30: Malitbog U2 cut-in at 1541H (Unplanned Outage) [WEBSMS] | CVIS
6/16/2024 4:04:39 PM | Mindanao Grid-06/16/2024 16:10: LAKE MAINIT (AGC) online at 1330H (Unplanned Outage) [WEBSMS] | CMIN
6/16/2024 3:53:36 PM | Luzon Grid-06/16/2024 15:53: Dasmarinas SS 600MVA T04 (T08) restored at 1553H (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 3:51:35 PM | Luzon Grid-06/16/2024 15:51: Dasmarinas SS 500kV Bus 1 restored at 1551H (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 3:34:41 PM | Mindanao Grid-06/16/2024 15:40: Tagoloan - SME 1387kV Line energized at 1531H. (Planned Outage) [WEBSMS] | CMIN
6/16/2024 3:22:09 PM | Luzon Grid-06/16/2024 15:22: Bantay SS 115kV Bus 2 restored at 1522H (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 2:58:26 PM | Mindanao Grid-06/16/2024 15:04: Tagoloan - Villanueva 138kV Line2 energized/looped at 1454H. (Planned Outage) [WEBSMS] | CMIN
6/16/2024 2:29:05 PM | Luzon Grid-06/16/2024 14:29: Naga-Labo 230kV line 2 restored at 1428H (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 1:21:29 PM | Luzon Grid-06/16/2024 13:21: Gumaca-Labo 230kV line 2 auto-tripped at 1311H, the auto-reclosing was successful at Gumaca side, the line was looped in Labo side at 1316H. (Unplanned Outage) [WEBSMS] | CLUZ
6/16/2024 1:12:13 PM | Luzon Grid-06/16/2024 13:12: Cabanatuan-Pantabangan 230kV Line was restored at 1312H. (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 12:42:43 PM | [NSO Update] Mindanao Grid-06/16/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3248MW, PK=1864MW, RR=73MW, NetOpMargin: PM=1311, EVE=1122 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/16/2024 12:42:40 PM | [NSO Update] Luzon Grid-06/16/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=16020MW, PK=10749MW, RR=356MW, NetOpMargin: PM=4915, EVE=3147 Highest Unit O/L: GNPD 1@668MW Derated Plant: Limay 8 @60MW, SLTEC 2 @119MW, Ilijan A @550MW, Masinloc 2 @200MW, GNPD 2 @640MW, Masinloc 1 @250MW, SLTEC 1 @115MW [WEBSMS] | CLUZ
6/16/2024 12:42:37 PM | [NSO Update] Visayas Grid-06/16/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2590MW, PK=1927MW, RR=86MW, NetOpMargin: PM=577, EVE=353 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @250MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB101-2 @5.2MW, PB104-3 @5MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PB104-2 @5.5MW, PEDC U3 @70MW, PDPP3-E @8MW, PDPP3-H @8MW, PDPP1 U1 @4MW [WEBSMS] | CVIS
6/16/2024 11:17:13 AM | Mindanao Grid-06/16/2024 11:23: Tagoloan - Manolo Fortich 138kV Line2 energized/looped at 1109H. (Planned Outage) [WEBSMS] | CMIN
6/16/2024 11:15:54 AM | Mindanao Grid-06/16/2024 11:21: Tagoloan SS 138kV Bus2 energized at 1108H. (Planned Outage) [WEBSMS] | CMIN
6/16/2024 11:15:04 AM | Mindanao Grid-06/16/2024 11:20: Tagoloan SS 100MVA 138/69kV Power Transformer 2 energized/looped at 1108H. (Planned Outage) [WEBSMS] | CMIN
6/16/2024 10:24:03 AM | Mindanao Grid-06/16/2024 10:29: LAKE MAINIT (AGC) Hydro shutdown at 1022H due to critical lake level (Unplanned Outage) [WEBSMS] | CMIN
6/16/2024 10:14:36 AM | Luzon Grid-06/16/2024 10:14: Dasmarinas-FCIE 115kV line was restored at 1005H. (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 8:12:02 AM | Visayas Grid-06/16/2024 08:12: Calong-calong - Toledo BESS 69 kV Line de-energized at 0810H (Planned Outage) [WEBSMS] | CVIS
6/16/2024 7:02:27 AM | Mindanao Grid-06/16/2024 07:08: Tacurong SS 100MVA 138/69kV Power Transformer 3 shutdown at 0646H. (Planned Outage) [WEBSMS] | CMIN
6/16/2024 6:42:52 AM | Visayas Grid-06/16/2024 06:43: Colon - Naga 138 kV Line 2 de-energized at 0623H (Planned Outage) [WEBSMS] | CVIS
6/16/2024 6:41:21 AM | Luzon Grid-06/16/2024 06:41: Naga-Labo 230kV line 2 was de-energized at 0638H. (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 6:22:10 AM | [NSO Update] Mindanao Grid-06/16/2024 06:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3256MW, PK=1824MW, RR=73MW, NetOpMargin: AM=1360, PM=1289, EVE=1174 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/16/2024 6:20:42 AM | [NSO Update] Visayas Grid-06/16/2024 06:20: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2756MW, PK=1951MW, RR=83MW, NetOpMargin: AM=723, PM=659, EVE=288 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @250MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB101-2 @5.2MW, PB104-3 @5MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PB104-2 @5.5MW, PEDC U3 @70MW, PDPP3-E @8MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/16/2024 6:13:14 AM | [NSO Update] Luzon Grid-06/16/2024 06:13: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=16388MW, PK=10618MW, RR=356MW, NetOpMargin: AM=5414, PM=4623, EVE=2921 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Limay 8 @60MW, SLTEC 2 @119MW, Ilijan A @550MW, Masinloc 2 @200MW, GNPD 2 @640MW, Masinloc 1 @250MW, SLTEC 1 @115MW, Calaca 2 @270MW [WEBSMS] | CLUZ
6/16/2024 5:52:32 AM | Luzon Grid-06/16/2024 05:52: Santiago-Tuguegarao 230kV Line de-energized at 0549H (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 5:44:55 AM | Luzon Grid-06/16/2024 05:45: Bantay SS 115kV Bus 2 de-energized at 0534H. (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 5:32:37 AM | Mindanao Grid-06/16/2024 05:38: Tagoloan SS 138kV Bus No. 2 de-energized at 0523H. (Planned Outage). [WEBSMS] | CMIN
6/16/2024 5:30:32 AM | Mindanao Grid-06/16/2024 05:36: Tagoloan SS 138/69kV 100MVA Power Transformer No. 2 de-energized at 0519H. (Planned Outage). [WEBSMS] | CMIN
6/16/2024 5:26:05 AM | Mindanao Grid-06/16/2024 05:31: Tagoloan-Manolo 138kV L2 de-energized/shutdown at 0517H. (Planned Outage). [WEBSMS] | CMIN
6/16/2024 5:22:06 AM | Mindanao Grid-06/16/2024 05:27: Tagoloan-SME 138kV Line (CO) de-energized/shutdown at 0512H. (Planned Outage). [WEBSMS] | CMIN
6/16/2024 5:20:51 AM | Mindanao Grid-06/16/2024 05:26: Tagoloan-Villanueva 138kV L2 de-energized/shutdown at 0511H. (Planned Outage). [WEBSMS] | CMIN
6/16/2024 5:12:44 AM | [NSO Update] Mindanao Grid-06/16/2024 05:18: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CMIN
6/16/2024 5:12:26 AM | [NSO Update] Visayas Grid-06/16/2024 05:12: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CVIS
6/16/2024 5:12:09 AM | [NSO Update] Luzon Grid-06/16/2024 05:12: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CLUZ
6/16/2024 5:07:06 AM | Luzon Grid-06/16/2024 05:07: Cabanatuan-Pantabangan 230kV Line de-energized at 0506H. (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 4:05:09 AM | Luzon Grid-06/16/2024 04:05: Dasmarinas SS 600MVA T04 (T08) and Dasmarinas SS 500kV Bus 1 de-energized at 0403H and 0404H, respectively. (Planned Outage) [WEBSMS] | CLUZ
6/16/2024 3:05:07 AM | Visayas Grid-06/16/2024 03:05: Colon-CVC 69 kV line de-energized at 0304H (Planned Outage) [WEBSMS] | CVIS
6/16/2024 12:18:30 AM | Visayas Grid-06/16/2024 00:18: Colon - Naga 138 kV Line 1 energized at 0018H (Planned Outage) [WEBSMS] | CVIS
6/15/2024 9:03:06 PM | Luzon Grid-06/15/2024 21:03: Quezon 300MVA T08 restored at 2100H. (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 7:25:51 PM | Luzon Grid-06/15/2024 19:25: San Jose-Angat 115kV line 4 restored at 1925H. (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 6:03:07 PM | Luzon Grid-06/15/2024 18:03: San Gabriel online at 1802H (Reserve Shutdown) [WEBSMS] | CLUZ
6/15/2024 5:52:52 PM | [NSO Update] Mindanao Grid-06/15/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3095MW, PK=2190MW, RR=73MW, NetOpMargin: EVE=832 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW [WEBSMS] | CMIN
6/15/2024 5:51:59 PM | [NSO Update] Visayas Grid-06/15/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2522MW, PK=2187MW, RR=91MW, NetOpMargin: EVE=243 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @240MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PB101-2 @5.2MW, PB101-1 @5.5MW, PB104-3 @5MW, PDPP1 U2 @4MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PB104-2 @5.5MW, PEDC U3 @70MW, PDPP3-E @8MW [WEBSMS] | CVIS
6/15/2024 5:50:20 PM | [NSO Update] Luzon Grid-06/15/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14009MW, PK=11625MW, RR=429MW, NetOpMargin: EVE=1955 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Limay 8 @60MW, SLTEC 2 @119MW, Ilijan A @550MW, Masinloc 2 @200MW, GNPD 2 @640MW, Masinloc 1 @200MW, SLTEC 1 @115MW [WEBSMS] | CLUZ
6/15/2024 4:15:24 PM | Mindanao Grid-06/15/2024 16:21: Baloi-Lugait 138kV Line energized/restored at 1614H. (Planned Outage). [WEBSMS] | CMIN
6/15/2024 3:54:49 PM | [NSO Update] Visayas Grid-06/15/2024 15:54: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1551H with power going to Luzon [WEBSMS] | CVIS
6/15/2024 3:54:32 PM | [NSO Update] Luzon Grid-06/15/2024 15:54: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1551H with power going to Luzon [WEBSMS] | CLUZ
6/15/2024 3:53:54 PM | [NSO Update] Visayas Grid-06/15/2024 15:54: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1541H from reverse power direction [WEBSMS] | CVIS
6/15/2024 3:53:36 PM | [NSO Update] Luzon Grid-06/15/2024 15:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1541H from reverse power direction [WEBSMS] | CLUZ
6/15/2024 3:06:52 PM | Luzon Grid-06/15/2024 15:06: Bantay 115kV Bus 1 restored at 1506H. (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 3:01:55 PM | Luzon Grid-06/15/2024 15:02: La Trinidad-Binga 230kV line 1 restored at 1501H. (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 2:25:22 PM | Luzon Grid-06/15/2024 14:25: Naga-Labo 230kV line 1 restored at 1424H. (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 12:54:22 PM | [NSO Update] Luzon Grid-06/15/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15785MW, PK=11842MW, RR=470MW, NetOpMargin: PM=3472, EVE=2722 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Limay 8 @60MW, SLTEC 2 @118MW, Ilijan A @550MW, Masinloc 2 @200MW, GNPD 2 @640MW, Masinloc 1 @200MW, SLTEC 1 @115MW, Calaca 1 @230MW [WEBSMS] | CLUZ
6/15/2024 12:45:56 PM | [NSO Update] Mindanao Grid-06/15/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3078MW, PK=2135MW, RR=73MW, NetOpMargin: PM=844, EVE=870 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/15/2024 12:37:34 PM | [NSO Update] Visayas Grid-06/15/2024 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2537MW, PK=2158MW, RR=91MW, NetOpMargin: PM=288, EVE=259 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @240MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-1 @5.5MW, PB104-3 @5MW, PDPP1 U2 @4MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PB104-1 @5MW, PB104-2 @5.5MW, PEDC U3 @70MW [WEBSMS] | CVIS
6/15/2024 11:40:50 AM | Luzon Grid-06/15/2024 11:40: Balsik PCB 9-01CB24BIK was energized at 1138H. (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 11:09:44 AM | Luzon Grid-06/15/2024 11:09: EERI 1 online at 1105H. (On test and commissioning) [WEBSMS] | CLUZ
6/15/2024 10:59:26 AM | Visayas Grid-06/15/2024 10:59: Leyte A - Malitbog Unit 1 cut-in at 1057H (Unplanned Outage) [WEBSMS] | CVIS
6/15/2024 10:32:55 AM | Visayas Grid-06/15/2024 10:33: Leyte A - Malitbog Unit 1 tripped at 1029H (Unplanned Outage) [WEBSMS] | CVIS
6/15/2024 9:20:33 AM | Mindanao Grid-06/15/2024 09:26: Bislig - Nabunturan 138kV Line energized/restored at 0918H. (Planned Outage). [WEBSMS] | CMIN
6/15/2024 9:14:18 AM | Visayas Grid-06/15/2024 09:14: Colon - CEBECO-VECO Consortium 69 kV Line energized at 0913H (Planned Outage) [WEBSMS] | CVIS
6/15/2024 9:09:57 AM | [NSO Update] Visayas Grid-06/15/2024 09:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0905H with power going to Visayas [WEBSMS] | CVIS
6/15/2024 9:09:09 AM | [NSO Update] Luzon Grid-06/15/2024 09:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0905H with power going to Visayas [WEBSMS] | CLUZ
6/15/2024 9:04:43 AM | Luzon Grid-06/15/2024 09:04: La Trinidad-Binga 230kV line 1 was de-energized at 0903H. (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 8:58:28 AM | [NSO Update] Visayas Grid-06/15/2024 08:58: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0855H from forward power direction [WEBSMS] | CVIS
6/15/2024 8:58:03 AM | [NSO Update] Luzon Grid-06/15/2024 08:58: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0855H from forward power direction [WEBSMS] | CLUZ
6/15/2024 8:20:10 AM | Mindanao Grid-06/15/2024 08:25: Baloi-Lugait 138kV Line de-energized/shutdown at 0804H. (Planned Outage). [WEBSMS] | CMIN
6/15/2024 8:07:29 AM | Luzon Grid-06/15/2024 08:07: Balsik PCB 9-01CB24BIK was de-energized at 0804H. (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 8:04:57 AM | Luzon Grid-06/15/2024 08:05: Quezon 300MVA T08 was de-energized at 0802H. (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 7:38:37 AM | Luzon Grid-06/15/2024 07:38: Bantay 115kV Bus 1 was de-energized at 0731H. (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 6:40:58 AM | Luzon Grid-06/15/2024 06:41: Naga-Labo 230kV line 1 was de-energized at 0638H. (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 6:40:39 AM | Visayas Grid-06/15/2024 06:40: Colon - Naga 138 kV Line 1 de-energized at 0614H (Planned Outage) [WEBSMS] | CVIS
6/15/2024 6:11:54 AM | Luzon Grid-06/15/2024 06:11: San Jose-Angat 115kV line 4 was de-energized at 0610H. (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 6:09:04 AM | Mindanao Grid-06/15/2024 06:14: Bislig - Nabunturan 138kV Line de-energized/shutdown at 0606H. (Planned Outage) [WEBSMS] | CMIN
6/15/2024 6:01:00 AM | [NSO Update] Mindanao Grid-06/15/2024 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3130MW, PK=2175MW, RR=73MW, NetOpMargin: AM=883, PM=812, EVE=821 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/15/2024 5:58:19 AM | [NSO Update] Visayas Grid-06/15/2024 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2515MW, PK=2097MW, RR=91MW, NetOpMargin: AM=327, PM=229, EVE=258 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @250MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-1 @5.5MW, PB104-3 @5MW, PDPP1 U2 @4MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PB104-1 @5MW, PB104-2 @5.5MW [WEBSMS] | CVIS
6/15/2024 5:56:58 AM | [NSO Update] Luzon Grid-06/15/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15955MW, PK=11198MW, RR=451MW, NetOpMargin: AM=4306, PM=3571, EVE=2456 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Limay 8 @60MW, SLTEC 2 @118MW, Ilijan A @550MW, Masinloc 2 @200MW, GNPD 2 @640MW, Masinloc 1 @200MW, SLTEC 1 @115MW [WEBSMS] | CLUZ
6/15/2024 4:53:01 AM | Luzon Grid-06/15/2024 04:53: Quezon-San Jose 230kV Line 3 restored at 0452H (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 4:07:35 AM | [NSO Update] Mindanao Grid-06/15/2024 04:13: Weather Advisory: Southwest Monsoon affecting the western sections of Visayas and Mindanao. [WEBSMS] | CMIN
6/15/2024 4:07:23 AM | [NSO Update] Visayas Grid-06/15/2024 04:07: Weather Advisory: Southwest Monsoon affecting the western sections of Visayas and Mindanao. [WEBSMS] | CVIS
6/15/2024 4:07:12 AM | [NSO Update] Luzon Grid-06/15/2024 04:07: Weather Advisory: Southwest Monsoon affecting the western sections of Visayas and Mindanao. [WEBSMS] | CLUZ
6/15/2024 3:23:51 AM | Luzon Grid-06/15/2024 03:23: Binan-Balibago 115kV Line energized at 0321H (Planned Outage) [WEBSMS] | CLUZ
6/15/2024 2:50:52 AM | Luzon Grid-06/15/2024 02:50: San Gabriel offline at 0238H (Reserve Shutdown) [WEBSMS] | CLUZ
6/15/2024 2:40:38 AM | Mindanao Grid-06/15/2024 02:46: WMPC DG4 shutdown at 0238H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/15/2024 2:22:25 AM | Mindanao Grid-06/15/2024 02:28: Naga Mindanao - Zamboanga 138kV Line1 Re-energized and looped at 0219H. (Planned Outage) [WEBSMS] | CMIN
6/15/2024 12:58:07 AM | Mindanao Grid-06/15/2024 01:03: MCC Unit 1 shutdown at 0053H (Reserve Shutdown) [WEBSMS] | CMIN
6/15/2024 12:28:18 AM | Mindanao Grid-06/15/2024 00:34: Naga MIndanao - Zamboanga 138kV Line1 de-energized/shutdown at 0019H (Planned Outage) [WEBSMS] | CMIN
6/15/2024 12:04:40 AM | Luzon Grid-06/15/2024 00:04: Dasmarinas SS PCB 9-03CB24DAS de-energized at 0004H (Planned Outage) [WEBSMS] | CLUZ
6/14/2024 11:46:07 PM | Mindanao Grid-06/14/2024 23:51: WMPC DG04 online at 2344H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/14/2024 11:20:31 PM | Luzon Grid-06/14/2024 23:20: Binan-Balibago 115kV Line de-energized at 2318H (Planned Outage) [WEBSMS] | CLUZ
6/14/2024 10:53:27 PM | Luzon Grid-06/14/2024 22:53: Quezon-San Jose 230kV Line 3 de-energized at 2253H (Planned Outage) [WEBSMS] | CLUZ
6/14/2024 7:36:30 PM | Visayas Grid-06/14/2024 19:36: Colon � CEBECO-VECO Consortium 69 kV Line de-energized at 1934H (Planned Outage) [WEBSMS] | CVIS
6/14/2024 7:11:32 PM | [NSO Update] Luzon Grid-06/14/2024 19:11: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1911H with power going to Luzon. [WEBSMS] | CLUZ
6/14/2024 7:11:30 PM | [NSO Update] Visayas Grid-06/14/2024 19:11: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1911H with power going to Luzon. [WEBSMS] | CVIS
6/14/2024 7:01:54 PM | [NSO Update] Visayas Grid-06/14/2024 19:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1901H from reverse power direction. [WEBSMS] | CVIS
6/14/2024 7:01:35 PM | [NSO Update] Luzon Grid-06/14/2024 19:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1901H from reverse power direction. [WEBSMS] | CLUZ
6/14/2024 5:52:56 PM | [NSO Update] Mindanao Grid-06/14/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3105MW, PK=2233MW, RR=73MW, NetOpMargin: EVE=799 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/14/2024 5:51:58 PM | [NSO Update] Visayas Grid-06/14/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2581MW, PK=2213MW, RR=91MW, NetOpMargin: EVE=276 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @250MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-1 @5.5MW, PB104-3 @5MW, PDPP1 U2 @4MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW [WEBSMS] | CVIS
6/14/2024 5:50:20 PM | [NSO Update] Luzon Grid-06/14/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14232MW, PK=11866MW, RR=429MW, NetOpMargin: EVE=1938 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Limay 8 @60MW, SLTEC 2 @118MW, Ilijan A @550MW, Masinloc 2 @200MW, GNPD 2 @640MW, Masinloc 1 @200MW, SLTEC 1 @115MW [WEBSMS] | CLUZ
6/14/2024 5:49:37 PM | Luzon Grid-06/14/2024 17:49: Bay-Makban Plant A 230kV Line 1 restored at 1749H (Planned Outage) [WEBSMS] | CLUZ
6/14/2024 5:41:16 PM | Luzon Grid-06/14/2024 17:41: Binga HEPP 230kV Overhead Line 1 restored at 1738H (Planned Outage). [WEBSMS] | CLUZ
6/14/2024 3:18:43 PM | Mindanao Grid-06/14/2024 15:24: WMPC DG04 shutdown at 1516H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/14/2024 2:26:49 PM | Mindanao Grid-06/14/2024 14:32: Agus6 SS Bus1 energized at 1419H. (Planned Outage) [WEBSMS] | CMIN
6/14/2024 2:20:30 PM | Luzon Grid-06/14/2024 14:20: Mexico 100MVAR Capacitor Bank 6 tripped at 1414H (Unplanned Outage) [WEBSMS] | CLUZ
6/14/2024 1:36:31 PM | Mindanao Grid-06/14/2024 13:42: LAKE MAINIT (AGC) online at 1334H (Unplanned Outage) [WEBSMS] | CMIN
6/14/2024 1:24:37 PM | Visayas Grid-06/14/2024 13:24: Calung-calung - Toledo Solar 69KV line de-energized at 1319H.(Planned Outage) [WEBSMS] | CVIS
6/14/2024 12:37:15 PM | [NSO Update] Luzon Grid-06/14/2024 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15787MW, PK=13335MW, RR=526MW, NetOpMargin: PM=1926, EVE=1783 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Limay 8 @60MW, SLTEC 2 @116MW, Ilijan A @540MW, Masinloc 2 @200MW, GNPD 2 @640MW, Masinloc 1 @200MW, SLTEC 1 @115MW [WEBSMS] | CLUZ
6/14/2024 12:33:43 PM | [NSO Update] Visayas Grid-06/14/2024 12:33: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2688MW, PK=2371MW, RR=91MW, NetOpMargin: PM=226, EVE=301 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @250MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-1 @5.5MW, PB104-2 @5.5MW, PB104-3 @5MW, PDPP1 U2 @4MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PB104-4 @5.5MW, TPC-Thermal @70MW [WEBSMS] | CVIS
6/14/2024 12:33:18 PM | [NSO Update] Mindanao Grid-06/14/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3144MW, PK=2456MW, RR=73MW, NetOpMargin: PM=615, EVE=726 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/14/2024 12:04:03 PM | Mindanao Grid-06/14/2024 12:09: Agus6 SS Bus1 de-energized/shutdown at 1201H. (Planned Outage) [WEBSMS] | CMIN
6/14/2024 12:01:46 PM | Luzon Grid-06/14/2024 12:01: Calaca - Malamig (Sta. Rosa) 230kV Line auto-tripped/auto-reclosed at 1157H (Unplanned Outage) [WEBSMS] | CLUZ
6/14/2024 11:59:28 AM | Luzon Grid-06/14/2024 11:59: San Gabriel online at 1157H (Reserve Shutdown) [WEBSMS] | CLUZ
6/14/2024 11:45:15 AM | Mindanao Grid-06/14/2024 11:51: Agus 6 HEP Unit 2 online at 1129H (Planned Outage). [WEBSMS] | CMIN
6/14/2024 10:05:44 AM | Mindanao Grid-06/14/2024 10:11: WMPC DG04 online at 1002H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/14/2024 9:45:26 AM | Luzon Grid-06/14/2024 09:45: EERI Unit 1 shutdown at 0943H. (Ongoing Testing and Commissioning) [WEBSMS] | CLUZ
6/14/2024 9:34:04 AM | Mindanao Grid-06/14/2024 09:39: LAKE MAINIT (AGC) Hydro shutdown at 0931H due to critical lake level (Unplanned Outage) [WEBSMS] | CMIN
6/14/2024 9:11:31 AM | Luzon Grid-06/14/2024 09:11: EERI Unit 1 online at 0909H. (Ongoing Testing and Commissioning) [WEBSMS] | CLUZ
6/14/2024 9:05:47 AM | [NSO Update] Visayas Grid-06/14/2024 09:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0903H with power going to Visayas. [WEBSMS] | CVIS
6/14/2024 9:05:43 AM | [NSO Update] Luzon Grid-06/14/2024 09:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0903H with power going to Visayas. [WEBSMS] | CLUZ
6/14/2024 8:30:15 AM | [NSO Update] Luzon Grid-06/14/2024 08:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0828H from forward power direction. [WEBSMS] | CLUZ
6/14/2024 8:29:52 AM | [NSO Update] Visayas Grid-06/14/2024 08:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0828H from forward power direction. [WEBSMS] | CVIS
6/14/2024 7:29:31 AM | Luzon Grid-06/14/2024 07:29: Bay-Makban Plant A 230kV Line 1 de-energized at 0729H. (Planned Outage) [WEBSMS] | CLUZ
6/14/2024 6:27:18 AM | Visayas Grid-06/14/2024 06:27: Colon-AYA 69 kV line energized at 0621H(Planned Outage) [WEBSMS] | CVIS
6/14/2024 6:11:30 AM | Mindanao Grid-06/14/2024 06:17: Agus6 U2 shutdown at 0603H. (Planned Outage) [WEBSMS] | CMIN
6/14/2024 6:02:23 AM | [NSO Update] Mindanao Grid-06/14/2024 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3153MW, PK=2297MW, RR=73MW, NetOpMargin: AM=783, PM=763, EVE=1005 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/14/2024 5:59:56 AM | [NSO Update] Visayas Grid-06/14/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2665MW, PK=2296MW, RR=91MW, NetOpMargin: AM=278, PM=221, EVE=245 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @250MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PDPP3-H @8MW, PB101-1 @5.5MW, PB104-2 @5.5MW, PB104-3 @5MW, PDPP1 U2 @4MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PB104-4 @5.5MW, TPC-Thermal @70MW [WEBSMS] | CVIS
6/14/2024 5:56:44 AM | [NSO Update] Luzon Grid-06/14/2024 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15823MW, PK=12554MW, RR=496MW, NetOpMargin: AM=2773, PM=1762, EVE=1528 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Limay 8 @60MW, SLTEC 2 @116MW, Ilijan A @540MW, Masinloc 2 @200MW, GNPD 2 @640MW [WEBSMS] | CLUZ
6/14/2024 4:23:59 AM | [NSO Update] Mindanao Grid-06/14/2024 04:29: Weather Update: Southwest Monsoon affecting the western section of Mindanao. [WEBSMS] | CMIN
6/14/2024 4:23:42 AM | [NSO Update] Visayas Grid-06/14/2024 04:23: Weather Update: Southwest Monsoon affecting the western section of Mindanao. [WEBSMS] | CVIS
6/14/2024 4:23:27 AM | [NSO Update] Luzon Grid-06/14/2024 04:23: Weather Update: Southwest Monsoon affecting the western section of Mindanao. [WEBSMS] | CLUZ
6/14/2024 3:54:38 AM | Visayas Grid-06/14/2024 03:54: Sangi - CEBECO III Toledo 34.5 kV Line energized at 0353H (Planned Outage) [WEBSMS] | CVIS
6/14/2024 3:44:46 AM | Visayas Grid-06/14/2024 03:44: Sangi - CEBECO III Pinamungahan 34.5 kV Line energized at 0343H (Planned Outage) [WEBSMS] | CVIS
6/14/2024 2:23:48 AM | Visayas Grid-06/14/2024 02:23: Sangi - CEBECO III Pinamungahan 34.5 kV Line de-energized at 0217H. (Planned Outage) [WEBSMS] | CVIS
6/14/2024 2:22:20 AM | Visayas Grid-06/14/2024 02:22: Sangi - CEBECO III Toledo 34.5 kV Line de-energized at 0211H. (Planned Outage) [WEBSMS] | CVIS
6/13/2024 9:14:06 PM | Luzon Grid-06/13/2024 21:14: SLTEC 1 online at 2112H (Unplanned Outage) [WEBSMS] | CLUZ
6/13/2024 7:59:59 PM | Visayas Grid-06/13/2024 20:00: Colon-AYA 69 kV line de-energized at 1959H (Planned Outage) [WEBSMS] | CVIS
6/13/2024 7:56:03 PM | [NSO Update] Visayas Grid-06/13/2024 19:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1947H with power going to Luzon [WEBSMS] | CVIS
6/13/2024 7:55:34 PM | [NSO Update] Luzon Grid-06/13/2024 19:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1947H with power going to Luzon [WEBSMS] | CLUZ
6/13/2024 7:42:11 PM | [NSO Update] Luzon Grid-06/13/2024 19:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1912H from reverse power direction [WEBSMS] | CLUZ
6/13/2024 7:41:33 PM | [NSO Update] Visayas Grid-06/13/2024 19:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1912H from reverse power direction [WEBSMS] | CVIS
6/13/2024 7:24:21 PM | Mindanao Grid-06/13/2024 19:30: WMPC DG05 shutdown at 1916H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/13/2024 6:39:48 PM | Luzon Grid-06/13/2024 18:39: Masinloc 1 online at 1838H (Unplanned Outage) [WEBSMS] | CLUZ
6/13/2024 5:54:54 PM | [NSO Update] Mindanao Grid-06/13/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3089MW, PK=2324MW, RR=73MW, NetOpMargin: EVE=693 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/13/2024 5:53:08 PM | [NSO Update] Visayas Grid-06/13/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2539MW, PK=2219MW, RR=91MW, NetOpMargin: EVE=229 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @250MW, CEDC U3 @75MW, GTEC @7MW, PEDC 3 @70MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @5MW, PB104-2 @5.5MW, PB104-3 @5MW, PDPP1 U2 @4MW, PDPP1 U3 @4MW, PDPP1 U5 @4MW, PB104-4 @5.5MW [WEBSMS] | CVIS
6/13/2024 5:51:49 PM | [NSO Update] Luzon Grid-06/13/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13541MW, PK=11938MW, RR=389MW, NetOpMargin: EVE=1215 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Limay 8 @60MW, SLTEC 2 @116MW, Ilijan A @500MW, Masinloc 2 @200MW, Masinloc 3 @300MW, GNPD 2 @640MW [WEBSMS] | CLUZ
6/13/2024 5:50:38 PM | Luzon Grid-06/13/2024 17:50: Bay-Makban Plant B 230kV Line 1 restored at 1750H (Planned Outage) [WEBSMS] | CLUZ
6/13/2024 4:54:12 PM | Luzon Grid-06/13/2024 16:54: Concepcion-Clark 230kV L1 restored at 1650H (Unplanned Outage) [WEBSMS] | CLUZ
6/13/2024 4:27:54 PM | Luzon Grid-06/13/2024 16:28: Concepcion-Clark 230kV L2 restored at 1627H (Planned Outage) [WEBSMS] | CLUZ
6/13/2024 4:05:13 PM | Mindanao Grid-06/13/2024 16:10: STEAG Unit 1 with 100MW load on emergency shutdown at 1600H. (Unplanned Outage) [WEBSMS] | CMIN
6/13/2024 3:29:34 PM | Luzon Grid-06/13/2024 15:29: Tayabas SS PCB 9Z-02CB08TAY energized at 1521H (Planned Outage) [WEBSMS] | CLUZ
6/13/2024 2:30:18 PM | Luzon Grid-06/13/2024 14:30: Concepcion-Clark 230kV L1 tripped at 1424H, frequency raise to 60.496hz. (Unplanned Outage) [WEBSMS] | CLUZ
6/13/2024 12:44:04 PM | [NSO Update] Luzon Grid-06/13/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15185MW, PK=13367MW, RR=496MW, NetOpMargin: PM=1322, EVE=809 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Limay 8 @60MW, SLTEC 2 @116MW, Ilijan A @500MW, Masinloc 2 @200MW, Masinloc 3 @300MW [WEBSMS] | CLUZ
6/13/2024 12:41:39 PM | [NSO Update] Visayas Grid-06/13/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2822MW, PK=2456MW, RR=91MW, NetOpMargin: PM=275, EVE=240 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @251MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/13/2024 12:39:37 PM | [NSO Update] Mindanao Grid-06/13/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3205MW, PK=2387MW, RR=73MW, NetOpMargin: PM=746, EVE=793 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/13/2024 11:53:09 AM | Mindanao Grid-06/13/2024 11:58: WMPC DG05 online at 1041H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/13/2024 10:32:51 AM | Mindanao Grid-06/13/2024 10:38: WMPC DG10 tripped at 1024H due to Lube Oil Low Pressure Stop. Declared FO. Unplanned Outage. [WEBSMS] | CMIN
6/13/2024 10:30:42 AM | Luzon Grid-06/13/2024 10:30: Mexico-Concepcion 230kV Line 1 restored at 1030H (Planned Outage) [WEBSMS] | CLUZ
6/13/2024 10:19:56 AM | Mindanao Grid-06/13/2024 10:25: WMPC DG10 online at 1017H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/13/2024 9:57:43 AM | [NSO Update] Visayas Grid-06/13/2024 09:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0920H with power going to Visayas. [WEBSMS] | CVIS
6/13/2024 9:46:44 AM | Luzon Grid-06/13/2024 09:46: Tayabas SS PCB 9Z-02CB08TAY de-energized at 0946H. (Planned Outage) [WEBSMS] | CLUZ
6/13/2024 9:24:32 AM | [NSO Update] Luzon Grid-06/13/2024 09:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0920H with power going to Visayas. [WEBSMS] | CLUZ
6/13/2024 9:12:09 AM | [NSO Update] Visayas Grid-06/13/2024 09:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0910H from forward power direction. [WEBSMS] | CVIS
6/13/2024 9:11:55 AM | [NSO Update] Luzon Grid-06/13/2024 09:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0910H from forward power direction. [WEBSMS] | CLUZ
6/13/2024 8:25:06 AM | Mindanao Grid-06/13/2024 08:30: AGUS 4 HEP Unit 3 with 40MW load shutdown at 0815H. PMS (GOMP). Planned Outage [WEBSMS] | CMIN
6/13/2024 8:23:25 AM | Mindanao Grid-06/13/2024 08:29: AGUS 4 HEP Unit 2 with 20MW load shutdown at 0808H. PMS (GOMP). Planned Outage [WEBSMS] | CMIN
6/13/2024 8:22:24 AM | Mindanao Grid-06/13/2024 08:28: AGUS 4 HEP Unit 1 with 20MW load shutdown at 0803H. PMS (GOMP). (Planned Outage) [WEBSMS] | CMIN
6/13/2024 8:01:26 AM | Luzon Grid-06/13/2024 08:01: Bay-Makban Plant B 230kV Line 1 de-energized at 0759H (Planned Outage) [WEBSMS] | CLUZ
6/13/2024 7:33:30 AM | Luzon Grid-06/13/2024 07:33: Dona Imelda SS 300MVA T01 restored at 0732H. (Planned Outage) [WEBSMS] | CLUZ
6/13/2024 6:18:06 AM | Luzon Grid-06/13/2024 06:18: Concepcion-Clark 230kV Line 2 de-energized at 0617H. (Planned Outage) [WEBSMS] | CLUZ
6/13/2024 5:45:19 AM | [NSO Update] Visayas Grid-06/13/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2639MW, PK=2316MW, RR=91MW, NetOpMargin: AM=231, PM=190, EVE=265 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @250MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-G @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/13/2024 5:41:03 AM | [NSO Update] Mindanao Grid-06/13/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3231MW, PK=2402MW, RR=73MW, NetOpMargin: AM=757, PM=593, EVE=796 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/13/2024 5:40:45 AM | Luzon Grid-06/13/2024 05:40: For info: San Jose 300MVA T03 was unlooped via high-side at 0534H after San Jose 300MVA T02 was restored at 0532H. [WEBSMS] | CLUZ
6/13/2024 5:38:09 AM | [NSO Update] Luzon Grid-06/13/2024 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15121MW, PK=12630MW, RR=476MW, NetOpMargin: AM=2015, PM=914, EVE=678 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MSLC2 @200MW, MSLC3 @300MW, ILIJAN A @500MW [WEBSMS] | CLUZ
6/13/2024 5:35:11 AM | Luzon Grid-06/13/2024 05:35: San Jose 300MVA T02 restored at 0532H (Planned Outage) [WEBSMS] | CLUZ
6/13/2024 5:21:03 AM | Luzon Grid-06/13/2024 05:21: Binan-San Pedro 115kV Line restored at 0520H (Planned Outage) [WEBSMS] | CLUZ
6/13/2024 5:15:43 AM | Luzon Grid-06/13/2024 05:15: SLTEC Unit 1 (114MW) tripped at 0511H (Unplanned Outage) [WEBSMS] | CLUZ
6/13/2024 5:05:05 AM | Luzon Grid-06/13/2024 05:05: Mexico-Concepcion 230kV Line 1 de-energized at 0504H (Planned Outage) [WEBSMS] | CLUZ
6/13/2024 4:10:17 AM | [NSO Update] Mindanao Grid-06/13/2024 04:16: Weather Update: Easterlies affecting the eastern section of Mindanao. [WEBSMS] | CMIN
6/13/2024 4:09:54 AM | [NSO Update] Visayas Grid-06/13/2024 04:09: Weather Update: Easterlies affecting the eastern section of Mindanao. [WEBSMS] | CVIS
6/13/2024 4:09:40 AM | [NSO Update] Luzon Grid-06/13/2024 04:09: Weather Update: Easterlies affecting the eastern section of Mindanao. [WEBSMS] | CLUZ
6/12/2024 11:54:58 PM | Luzon Grid-06/12/2024 23:55: Dona Imelda SS 300MVA T01 de-energized at 2354H (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 11:10:27 PM | Luzon Grid-06/12/2024 23:10: Binan-San Pedro 115kV Line de-energized at 2310H (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 10:09:47 PM | Luzon Grid-06/12/2024 22:09: San Jose 300MVA T02 de-energized at 2209H (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 10:09:12 PM | Luzon Grid-06/12/2024 22:09: For info: San Jose 300MVA T03 looped at 2206H in preparation for the de-energization of San Jose 300MVA T02. [WEBSMS] | CLUZ
6/12/2024 8:58:41 PM | [NSO Update] Luzon Grid-06/12/2024 20:58: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2057H with power going to Luzon. [WEBSMS] | CLUZ
6/12/2024 8:58:14 PM | [NSO Update] Visayas Grid-06/12/2024 20:58: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2057H with power going to Luzon. [WEBSMS] | CVIS
6/12/2024 8:49:36 PM | [NSO Update] Luzon Grid-06/12/2024 20:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2047H from reverse power direction. [WEBSMS] | CLUZ
6/12/2024 8:49:17 PM | [NSO Update] Visayas Grid-06/12/2024 20:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2047H from reverse power direction. [WEBSMS] | CVIS
6/12/2024 8:35:39 PM | Luzon Grid-06/12/2024 20:35: San Gabriel online at 2033H (Reserve Shutdown) [WEBSMS] | CLUZ
6/12/2024 8:30:26 PM | Luzon Grid-06/12/2024 20:30: For info: Sta Rita-San Lorenzo 230kV Bus 1 and Bus 2 Tie Breakers were unlooped at 2016H and 2017H, respectively. Batangas 300MVA T04 and T05 were back in parallel configuration at 2021H. This is in preparation for the synchronization of San Gabriel. [WEBSMS] | CLUZ
6/12/2024 6:42:13 PM | [NSO Update] Visayas Grid-06/12/2024 18:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1816H with power going to Visayas. [WEBSMS] | CVIS
6/12/2024 6:41:53 PM | [NSO Update] Luzon Grid-06/12/2024 18:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1816H with power going to Visayas. [WEBSMS] | CLUZ
6/12/2024 6:26:18 PM | Mindanao Grid-06/12/2024 18:32: WMPC DG4 tripped at 1819H due to turbo charger B bank problem [WEBSMS] | CMIN
6/12/2024 5:45:59 PM | [NSO Update] Mindanao Grid-06/12/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3267MW, PK=2193MW, RR=73MW, NetOpMargin: EVE=1001 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/12/2024 5:44:58 PM | [NSO Update] Visayas Grid-06/12/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2516MW, PK=2117MW, RR=91MW, NetOpMargin: EVE=308 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @248MW, CEDC U3 @75MW, GTEC @7MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @5MW, PB104-2 @5.5MW, PB104-3 @5MW, PDPP1 U2 @4MW, PEDC U3 @70MW [WEBSMS] | CVIS
6/12/2024 5:43:38 PM | Luzon Grid-06/12/2024 17:43: Bayombong-Santiago 230kV Line 2 restored at 1743H (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 5:41:50 PM | [NSO Update] Luzon Grid-06/12/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14519MW, PK=11151MW, RR=451MW, NetOpMargin: EVE=2916 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @200MW, GNPD 2 @640MW, MSLC2 @310MW, MSLC3 @320MW, ILIJAN A @500MW [WEBSMS] | CLUZ
6/12/2024 5:29:41 PM | Visayas Grid-06/12/2024 17:29: Colon-Magdugo 138 kV L1 energized at 1723H (Planned Outage) [WEBSMS] | CVIS
6/12/2024 5:02:25 PM | Luzon Grid-06/12/2024 17:02: Lumban-Gumaca 230kV Line 1 restored at 1701H (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 4:19:26 PM | Luzon Grid-06/12/2024 16:19: Naga-Daraga 230kV Line restored at 1618H (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 4:04:54 PM | Luzon Grid-06/12/2024 16:04: Calaca-Binan 230kV Line restored at 1604H (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 4:01:59 PM | Visayas Grid-06/12/2024 16:02: PGPP1 U2 re cut in at 1600H (Unplanned Outage) [WEBSMS] | CVIS
6/12/2024 3:54:53 PM | Visayas Grid-06/12/2024 15:54: PGPP1 U3 re cut in at 1553H (Unplanned Outage) [WEBSMS] | CVIS
6/12/2024 3:40:42 PM | Visayas Grid-06/12/2024 15:40: PGPP1 U1 re cut in at 1539H (Unplanned Outage) [WEBSMS] | CVIS
6/12/2024 2:35:56 PM | Mindanao Grid-06/12/2024 14:41: WMPC DG10 declared available at 1430H. From Unplanned Outage. [WEBSMS] | CMIN
6/12/2024 2:23:11 PM | Visayas Grid-06/12/2024 14:23: PGPP1 U2 tripped at 1419H, low vacuum (Unplanned Outage) [WEBSMS] | CVIS
6/12/2024 1:51:38 PM | Visayas Grid-06/12/2024 13:51: Pal 1 U2 cut in at 1349H (Unplanned Outage) [WEBSMS] | CVIS
6/12/2024 1:06:05 PM | Mindanao Grid-06/12/2024 13:11: LAKE MAINIT Hydro online at 1304H (Unplanned Outage) [WEBSMS] | CMIN
6/12/2024 12:49:28 PM | [NSO Update] Luzon Grid-06/12/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15389MW, PK=11983MW, RR=451MW, NetOpMargin: PM=2955, EVE=1587 Highest Unit O/L: GNPD 1@668MW Derated Plant: Masinloc 2 @310MW, Limay 8 @60MW, GNPD 2 @640MW, SLTEC 1 @117MW, SLTEC 2 @118MW, Ilijan A @500MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
6/12/2024 12:46:12 PM | [NSO Update] Visayas Grid-06/12/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2407MW, PK=2126MW, RR=89MW, NetOpMargin: PM=192, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @244MW, CEDC U3 @75MW, GTEC @7MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @5MW, PB104-2 @5.5MW, PB104-3 @5MW, PDPP1 U2 @4MW, PEDC U3 @70MW [WEBSMS] | CVIS
6/12/2024 12:46:01 PM | [NSO Update] Mindanao Grid-06/12/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3294MW, PK=2284MW, RR=73MW, NetOpMargin: PM=973, EVE=974 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/12/2024 11:19:12 AM | Visayas Grid-06/12/2024 11:19: Last feeder affected by Visayas First level ALD activation restored at 0931H (Unplanned Outage) [WEBSMS] | CVIS
6/12/2024 9:50:47 AM | Mindanao Grid-06/12/2024 09:56: LAKE MAINIT (AGC) Hydro with 4.7MW load shutdown at 0831H due to insufficient water supply (Unplanned Outage) [WEBSMS] | CMIN
6/12/2024 9:47:47 AM | Mindanao Grid-06/12/2024 09:53: WMPC DG04 online at 0945H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/12/2024 9:19:16 AM | Visayas Grid-06/12/2024 09:19: PGPP 1 units 1, 2 and 3 tripped at 0911H. Visayas ALD activated (Unplanned Outage) [WEBSMS] | CVIS
6/12/2024 8:49:39 AM | Visayas Grid-06/12/2024 08:49: SCBP cut in at 0845H (Unplanned Outage) [WEBSMS] | CVIS
6/12/2024 7:52:52 AM | Visayas Grid-06/12/2024 07:52: SCBP tripped at 0745H (Unplanned Outage) [WEBSMS] | CVIS
6/12/2024 7:06:41 AM | Luzon Grid-06/12/2024 07:06: Quezon-Marilao 230kV line and Marilao 230kV Bus 2 restored at 0705H (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 6:46:56 AM | Luzon Grid-06/12/2024 06:46: Naga-Daraga 230kV Line de-energized at 0646H (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 6:46:54 AM | Visayas Grid-06/12/2024 06:46: Colon-Magdugo 138kV Line 1 de-energized at 0645H (Planned Outage) [WEBSMS] | CVIS
6/12/2024 6:27:43 AM | Luzon Grid-06/12/2024 06:27: Lumban-Gumaca 230kV Line 1 de-energized at 0627H (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 6:09:57 AM | Luzon Grid-06/12/2024 06:10: Bayombong-Santiago 230kV L2 de-energized at 0607H (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 6:05:38 AM | [NSO Update] Visayas Grid-06/12/2024 06:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0601H from forward power direction [WEBSMS] | CVIS
6/12/2024 6:05:09 AM | [NSO Update] Luzon Grid-06/12/2024 06:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0601H from forward power direction [WEBSMS] | CLUZ
6/12/2024 6:00:56 AM | [NSO Update] Luzon Grid-06/12/2024 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15818MW, PK=10806MW, RR=435MW, NetOpMargin: AM=4577, PM=3703, EVE=2185 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 2 @310MW, Limay 8 @60MW, GNPD 2 @640MW, SLTEC 1 @117MW, SLTEC 2 @118MW, Ilijan A @500MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
6/12/2024 5:52:07 AM | Luzon Grid-06/12/2024 05:52: Calaca-Binan 230kV line was de-energized at 0551H. (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 5:44:11 AM | Luzon Grid-06/12/2024 05:44: Binan-Southwoods 115kV line was restored at 0543H. (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 5:38:47 AM | Luzon Grid-06/12/2024 05:38: For info: Batangas 300MVA T04 and T05 were unparalleled at 0532H. Sta Rita-San Lorenzo 230kV Bus 1 and Bus 2 Tie Breakers were closed at 0534H. [WEBSMS] | CLUZ
6/12/2024 5:36:27 AM | [NSO Update] Mindanao Grid-06/12/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3320MW, PK=2135MW, RR=73MW, NetOpMargin: AM=1112, PM=923, EVE=935 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/12/2024 5:33:46 AM | [NSO Update] Visayas Grid-06/12/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2599MW, PK=2087MW, RR=86MW, NetOpMargin: AM=426, PM=270, EVE=286 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @251MW, CEDC U3 @75MW, GTEC @7MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @5MW, PB104-2 @5MW, PB104-3 @5MW, PDPP1 U2 @4MW [WEBSMS] | CVIS
6/12/2024 4:48:02 AM | Luzon Grid-06/12/2024 04:48: San Gabriel shutdown at 0441H. (Reserved Shutdown) [WEBSMS] | CLUZ
6/12/2024 4:12:57 AM | [NSO Update] Mindanao Grid-06/12/2024 04:19: Weather Update: Easterlies affecting the eastern sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
6/12/2024 4:12:21 AM | [NSO Update] Visayas Grid-06/12/2024 04:12: Weather Update: Easterlies affecting the eastern sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
6/12/2024 4:11:59 AM | [NSO Update] Luzon Grid-06/12/2024 04:12: Weather Update: Easterlies affecting the eastern sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
6/12/2024 3:11:17 AM | Luzon Grid-06/12/2024 03:11: Quezon-Marilao 230kV line, and Marilao 230kV Bus 2 were de-energized at 0305H and 0306H respectively. (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 2:24:03 AM | Luzon Grid-06/12/2024 02:24: San Jose-Angat 115kV line 4 was energized at 0221H. (Unplanned Outage) [WEBSMS] | CLUZ
6/12/2024 1:47:15 AM | Luzon Grid-06/12/2024 01:47: Marilao 230kV Bus 1 was restored at 0142H. (Planned Outage) [WEBSMS] | CLUZ
6/12/2024 1:11:01 AM | Luzon Grid-06/12/2024 01:11: San Jose-Angat 115kV line 4 autotripped at 0106H. (Unplanned Outage) [WEBSMS] | CLUZ
6/12/2024 12:05:33 AM | Luzon Grid-06/12/2024 00:06: Marilao 230kV Bus 1 was de-energized at 0005H. (Planned Outage-Customer Owned) [WEBSMS] | CLUZ
6/11/2024 11:09:13 PM | Luzon Grid-06/11/2024 23:09: Binan-Southwoods 115kV line was de-energized at 2307H. (Planned Outage) [WEBSMS] | CLUZ
6/11/2024 10:23:31 PM | Luzon Grid-06/11/2024 22:24: Calaca Unit 2 online at 2212H. (Unplanned Outage) [WEBSMS] | CLUZ
6/11/2024 9:36:37 PM | Mindanao Grid-06/11/2024 21:42: WMPC DG04 shutdown at 2121H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/11/2024 8:40:46 PM | Mindanao Grid-06/11/2024 20:47: Mt. Apo Unit 3 online at 2028H from FO. (Unplanned Outage) [WEBSMS] | CMIN
6/11/2024 8:25:05 PM | Mindanao Grid-06/11/2024 20:31: WMPC DG08 shutdown at 1920H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/11/2024 6:17:50 PM | [NSO Update] Mindanao Grid-06/11/2024 18:24: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 1759H. Market operations will resume starting interval 1805H. [WEBSMS] | CMIN
6/11/2024 6:17:22 PM | [NSO Update] Visayas Grid-06/11/2024 18:17: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 1759H. Market operations will resume starting interval 1805H. [WEBSMS] | CVIS
6/11/2024 6:16:00 PM | [NSO Update] Luzon Grid-06/11/2024 18:16: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 1759H. Market operations will resume starting interval 1805H. [WEBSMS] | CLUZ
6/11/2024 6:08:58 PM | [NSO Update] Mindanao Grid-06/11/2024 18:15: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 1755H due to failure to generate RTD. [WEBSMS] | CMIN
6/11/2024 6:08:01 PM | [NSO Update] Visayas Grid-06/11/2024 18:08: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 1755H due to failure to generate RTD. [WEBSMS] | CVIS
6/11/2024 6:07:29 PM | [NSO Update] Luzon Grid-06/11/2024 18:08: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 1755H due to failure to generate RTD. [WEBSMS] | CLUZ
6/11/2024 6:03:22 PM | Luzon Grid-06/11/2024 18:03: EERI 1 shutdown at 1800H. (On test and commissioning) [WEBSMS] | CLUZ
6/11/2024 5:54:16 PM | [NSO Update] Luzon Grid-06/11/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13389MW, PK=11841MW, RR=428MW, NetOpMargin: EVE=1120 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, MSLC2 @310MW, ILIJAN @240MW [WEBSMS] | CLUZ
6/11/2024 5:50:22 PM | [NSO Update] Mindanao Grid-06/11/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3279MW, PK=2343MW, RR=73MW, NetOpMargin: EVE=863 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/11/2024 5:47:30 PM | [NSO Update] Visayas Grid-06/11/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2548MW, PK=2229MW, RR=91MW, NetOpMargin: EVE=227 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @238MW, CEDC U3 @75MW, GTEC @7MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @5MW, PB104-3 @5MW, PB104-2 @5.5MW, PDPP1 U2 @4MW, PEDC U3 @110MW [WEBSMS] | CVIS
6/11/2024 5:41:21 PM | Luzon Grid-06/11/2024 17:41: San Lorenzo Module 50 online at 1738H. (Unplanned Outage) [WEBSMS] | CLUZ
6/11/2024 5:07:28 PM | Luzon Grid-06/11/2024 17:08: Ilijan GT1-1 online at 1707H. (Unplanned Outage) [WEBSMS] | CLUZ
6/11/2024 5:05:47 PM | Luzon Grid-06/11/2024 17:06: Calaca Unit 2 tripped at 1701H from 300MW load. The lowest frequency was 59.393Hz. (Unplanned Outage) [WEBSMS] | CLUZ
6/11/2024 4:58:33 PM | Mindanao Grid-06/11/2024 17:04: WMPC DG01 shutdown at 1657H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/11/2024 3:28:19 PM | Luzon Grid-06/11/2024 15:28: Payocpoc PCB 8-02CB08PAY closed at 1526H. (Unplanned Outage-Customer Owned and Maintained Equipment) [WEBSMS] | CLUZ
6/11/2024 3:25:48 PM | Luzon Grid-06/11/2024 15:26: Ilijan ST1 online at 1522H. (Unplanned Outage) [WEBSMS] | CLUZ
6/11/2024 2:41:07 PM | Luzon Grid-06/11/2024 14:41: Payocpoc PCB 8-02CB08PAY tripped at 1429H. (Unplanned Outage-Customer Owned and Maintained Equipment) [WEBSMS] | CLUZ
6/11/2024 2:33:34 PM | Luzon Grid-06/11/2024 14:34: EERI 1 online at 1431H. (On test and commissioning) [WEBSMS] | CLUZ
6/11/2024 2:23:55 PM | Luzon Grid-06/11/2024 14:24: Ilijan GT1-2 online at 1422H. (Unplanned Outage) [WEBSMS] | CLUZ
6/11/2024 1:14:26 PM | Mindanao Grid-06/11/2024 13:20: WMPC DG01 online at 0312H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/11/2024 12:46:28 PM | [NSO Update] Luzon Grid-06/11/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14884MW, PK=12598MW, RR=496MW, NetOpMargin: PM=1790, EVE=1692 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, SLTEC 1 @115MW, SLTEC 2 @120MW, Calaca 1 @200MW [WEBSMS] | CLUZ
6/11/2024 12:42:52 PM | [NSO Update] Mindanao Grid-06/11/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3322MW, PK=2501MW, RR=73MW, NetOpMargin: PM=748, EVE=901 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/11/2024 12:42:45 PM | [NSO Update] Visayas Grid-06/11/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2752MW, PK=2349MW, RR=91MW, NetOpMargin: PM=312, EVE=335 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @235MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-E @10MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @5MW, PB104-3 @5MW, PB104-2 @5.5MW, PDPP1 U2 @4MW [WEBSMS] | CVIS
6/11/2024 9:51:40 AM | Mindanao Grid-06/11/2024 09:57: WMPC DG08 online at 0947H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/11/2024 9:38:17 AM | Mindanao Grid-06/11/2024 09:44: WMPC DG04 online at 0910H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/11/2024 7:47:24 AM | Luzon Grid-06/11/2024 07:47: Ilijan GT 2-2 online at 0746H (Unplanned Outage) [WEBSMS] | CLUZ
6/11/2024 6:47:15 AM | Luzon Grid-06/11/2024 06:47: Duhat 300MVA T02 restored at 0529H (Planned Outage) [WEBSMS] | CLUZ
6/11/2024 6:42:22 AM | Luzon Grid-06/11/2024 06:42: San Jose - Angat 115kV Line 4 restored at 0642H (Planned Outage) [WEBSMS] | CLUZ
6/11/2024 5:46:51 AM | [NSO Update] Mindanao Grid-06/11/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3342MW, PK=2335MW, RR=73MW, NetOpMargin: AM=934, PM=853, EVE=978 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/11/2024 5:44:58 AM | [NSO Update] Visayas Grid-06/11/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2827MW, PK=2182MW, RR=91MW, NetOpMargin: AM=554, PM=422, EVE=442 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @251MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-E @10MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, PDPP3-H @8MW, PB104-1 @5MW, PB104-3 @5MW [WEBSMS] | CVIS
6/11/2024 5:43:41 AM | [NSO Update] Luzon Grid-06/11/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14939MW, PK=11890MW, RR=472MW, NetOpMargin: AM=2577, PM=1566, EVE=1413 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Calaca 1 @200MW, Masinloc 2 @320MW, Masinloc 3 @280MW Limay 8 @60MW, GNPD 2 @640MW, SLTEC 1 @115MW, SLTEC 2 @120MW [WEBSMS] | CLUZ
6/11/2024 5:26:51 AM | Luzon Grid-06/11/2024 05:27: Ilijan B ST-2 online at 0522H. (Unplanned Outage) [WEBSMS] | CLUZ
6/11/2024 4:32:23 AM | [NSO Update] Mindanao Grid-06/11/2024 04:38: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 145 km West Northwest of Butuan City, Agusan del Norte or over the coastal waters of Garcia Hernandez, Bohol (9.5�N, 124.3�E). [WEBSMS] | CMIN
6/11/2024 4:32:09 AM | [NSO Update] Luzon Grid-06/11/2024 04:32: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 145 km West Northwest of Butuan City, Agusan del Norte or over the coastal waters of Garcia Hernandez, Bohol (9.5�N, 124.3�E). [WEBSMS] | CLUZ
6/11/2024 4:31:45 AM | [NSO Update] Visayas Grid-06/11/2024 04:32: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 145 km West Northwest of Butuan City, Agusan del Norte or over the coastal waters of Garcia Hernandez, Bohol (9.5�N, 124.3�E). [WEBSMS] | CVIS
6/11/2024 4:30:28 AM | [NSO Update] Visayas Grid-06/11/2024 04:30: undefined at 0300H Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 145 km West Northwest of Butuan City, Agusan del Norte or over the coastal waters of Garcia Hernandez, Bohol (9.5�N, 124.3�E). [WEBSMS] | CVIS
6/11/2024 4:08:01 AM | Luzon Grid-06/11/2024 04:08: Ilijan GT 2-1 online at 0405H (Unplanned Outage) [WEBSMS] | CLUZ
6/11/2024 4:05:52 AM | Luzon Grid-06/11/2024 04:06: San Jose - Angat 115kV Line 4 de-energized at 0404H (Unplanned Outage) [WEBSMS] | CLUZ
6/10/2024 9:52:50 PM | Mindanao Grid-06/10/2024 21:59: WMPC DG04 shutdown at 2146H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/10/2024 8:59:00 PM | Luzon Grid-06/10/2024 20:59: Ilijan - EERI 500kV Line 2 restored at 2029H. (Unplanned Outage) [WEBSMS] | CLUZ
6/10/2024 8:02:29 PM | Luzon Grid-06/10/2024 20:03: Ilijan - Tayabas 500kV line restored at 2002H. (Unplanned Outage) [WEBSMS] | CLUZ
6/10/2024 7:34:45 PM | Luzon Grid-06/10/2024 19:35: Ilijan - Dasmarinas 500kV Line looped at Ilijan side at 1933H. (Unplanned Outage). [WEBSMS] | CLUZ
6/10/2024 7:16:17 PM | Visayas Grid-06/10/2024 19:16: Daanbantayan SS 230 kV Bus 1 energized at 1912H (Planned Outage) [WEBSMS] | CVIS
6/10/2024 6:39:49 PM | Luzon Grid-06/10/2024 18:40: Laoag-Pagudpud Wind Farm 115kV Line (CO) restored at 1837H (Planned Outage) [WEBSMS] | CLUZ
6/10/2024 6:23:12 PM | [NSO Update] Mindanao Grid-06/10/2024 18:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3272MW, PK=2250MW, RR=73MW, NetOpMargin: EVE=949 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/10/2024 6:21:05 PM | [NSO Update] Visayas Grid-06/10/2024 18:21: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2606MW, PK=2125MW, RR=91MW, NetOpMargin: EVE=390 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @245MW, CEDC U3 @75MW, GTEC @7MW, PB104-2 @5.5MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, PDPP3-H @8MW, PDPP1 U2 @4MW, PB104-1 @5MW, PB104-3 @5MW [WEBSMS] | CVIS
6/10/2024 6:13:04 PM | [NSO Update] Luzon Grid-06/10/2024 18:13: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12667MW, PK=11368MW, RR=429MW, NetOpMargin: EVE=870 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, SLTEC 1 @115MW, SLTEC 2 @120MW, Calaca 1 @200MW [WEBSMS] | CLUZ
6/10/2024 5:52:44 PM | Luzon Grid-06/10/2024 17:53: San Gabriel online at 1746H. (From Reserve Shutdown) [WEBSMS] | CLUZ
6/10/2024 5:33:18 PM | Luzon Grid-06/10/2024 17:33: Affected ALD feeders of NGCP and MERALCO restored at 1726H AND 1729H, respectively. [WEBSMS] | CLUZ
6/10/2024 5:28:58 PM | Luzon Grid-06/10/2024 17:29: Iljan - Dasmarina 500kV Line tripped at Ilijan side at 1717H. (Unplanned Outage) [WEBSMS] | CLUZ
6/10/2024 5:23:06 PM | Luzon Grid-06/10/2024 17:23: For info: ALD occured at Meralco and NGCP at 1717H are due to tripping of Ilijan A and B with 1126MW. Lowest system frequency is 58.797Hz. [WEBSMS] | CLUZ
6/10/2024 5:18:18 PM | Luzon Grid-06/10/2024 17:18: Iljan - Tayabas 500kV Line tripped at 1717H. (Unplanned Outage) [WEBSMS] | CLUZ
6/10/2024 4:04:49 PM | Mindanao Grid-06/10/2024 16:11: WMPC DG08 shutdown at 1546H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/10/2024 2:37:42 PM | Mindanao Grid-06/10/2024 14:43: WMPC DG01 shutdown at 1434H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/10/2024 2:31:41 PM | [NSO Update] Visayas Grid-06/10/2024 14:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1427H with power going to Luzon [WEBSMS] | CVIS
6/10/2024 2:31:31 PM | [NSO Update] Luzon Grid-06/10/2024 14:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1427H with power going to Luzon [WEBSMS] | CLUZ
6/10/2024 2:18:31 PM | [NSO Update] Visayas Grid-06/10/2024 14:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1412H from reverse power direction. [WEBSMS] | CVIS
6/10/2024 2:14:30 PM | [NSO Update] Luzon Grid-06/10/2024 14:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1412H from reverse power direction. [WEBSMS] | CLUZ
6/10/2024 1:55:09 PM | Mindanao Grid-06/10/2024 14:01: WMPC DG04 online at 1347H as replacement power for WMPC DG10. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/10/2024 1:15:02 PM | [NSO Update] Visayas Grid-06/10/2024 13:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1313H with power going to Visayas. [WEBSMS] | CVIS
6/10/2024 1:14:25 PM | [NSO Update] Luzon Grid-06/10/2024 13:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1313H with power going to Visayas. [WEBSMS] | CLUZ
6/10/2024 1:12:08 PM | Mindanao Grid-06/10/2024 13:18: WMPC DG10 with 10MW load tripped at 1305H. Indication: Lube oil low pressure stop. (Unplanned Outage) [WEBSMS] | CMIN
6/10/2024 12:53:22 PM | [NSO Update] Luzon Grid-06/10/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15370MW, PK=12626MW, RR=496MW, NetOpMargin: PM=2248, EVE=885 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Ilijan A @550MW Calaca 1 @200MW [WEBSMS] | CLUZ
6/10/2024 12:50:20 PM | [NSO Update] Mindanao Grid-06/10/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3302MW, PK=2421MW, RR=73MW, NetOpMargin: PM=808, EVE=925 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/10/2024 12:50:13 PM | [NSO Update] Visayas Grid-06/10/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2752MW, PK=2357MW, RR=91MW, NetOpMargin: PM=304, EVE=235 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @230MW, CEDC U3 @75MW, GTEC @7MW, PB104-2 @5.5MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, PDPP3-H @8MW, PDPP1 U2 @4MW, PB104-1 @5MW [WEBSMS] | CVIS
6/10/2024 12:14:34 PM | [NSO Update] Luzon Grid-06/10/2024 12:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1213H from forward power direction. [WEBSMS] | CLUZ
6/10/2024 12:14:09 PM | [NSO Update] Visayas Grid-06/10/2024 12:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1213H from forward power direction. [WEBSMS] | CVIS
6/10/2024 12:05:25 PM | Luzon Grid-06/10/2024 12:05: EERI Unit 1 shutdown at 1201H (Ongoing Testing and Commissioning) [WEBSMS] | CLUZ
6/10/2024 11:54:04 AM | Luzon Grid-06/10/2024 11:54: San Jose-Angat 115kV line 2 restored at 1153H (Planned Outage) [WEBSMS] | CLUZ
6/10/2024 11:35:05 AM | Visayas Grid-06/10/2024 11:35: Malitbog U2 emergency cut-out at 1127H (Unplanned Outage) [WEBSMS] | CVIS
6/10/2024 10:55:51 AM | Luzon Grid-06/10/2024 10:56: Gumaca-Labo 230kV Line 2 restored at 1055H (Unplanned Outage) [WEBSMS] | CLUZ
6/10/2024 10:42:29 AM | Mindanao Grid-06/10/2024 10:48: WMPC DG08 Online at 1020H. Reactive Power Support (RPS) - System Voltage Requirement. [WEBSMS] | CMIN
6/10/2024 10:21:25 AM | Mindanao Grid-06/10/2024 10:27: WMPC DG08 online at 1020H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/10/2024 9:49:43 AM | Luzon Grid-06/10/2024 09:50: EERI Unit 1 online at 0938H (Ongoing Testing and Commissioning) [WEBSMS] | CLUZ
6/10/2024 9:36:43 AM | Mindanao Grid-06/10/2024 09:42: Mt. Apo 3 with 3MW load tripped at 0838H. Cause: for verification (Unplanned Outage) [WEBSMS] | CMIN
6/10/2024 9:20:03 AM | Mindanao Grid-06/10/2024 09:26: WMPC DG01 Online at 0900H. Reactive Power Support (RPS) - System Voltage Requirement. [WEBSMS] | CMIN
6/10/2024 8:52:49 AM | Luzon Grid-06/10/2024 08:53: Gumaca-Labo 230kV Line 2 de-energized at 0852H (Unplanned Outage) [WEBSMS] | CLUZ
6/10/2024 8:39:19 AM | Mindanao Grid-06/10/2024 08:45: WMPC DG10 Online at 0834H. Reactive Power Support (RPS) - System Voltage Requirement. [WEBSMS] | CMIN
6/10/2024 7:03:51 AM | Luzon Grid-06/10/2024 07:04: San Jose SS 115kV Bus 2 restored at 0656H (Planned Outage) [WEBSMS] | CLUZ
6/10/2024 6:39:00 AM | Visayas Grid-06/10/2024 06:39: Daanbantayan SS 230 kV Bus 1 de-energized at 0638H (Planned Outage) [WEBSMS] | CVIS
6/10/2024 6:14:14 AM | Luzon Grid-06/10/2024 06:14: Laoag-Pagudpud Wind Farm 115kV Line (CO) de-energized at 0609H (Planned Outage) [WEBSMS] | CLUZ
6/10/2024 5:53:09 AM | [NSO Update] Luzon Grid-06/10/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15809MW, PK=11793MW, RR=472MW, NetOpMargin: AM=3544, PM=1467, EVE=1005 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Ilijan A @550MW, Limay 2 @50MW [WEBSMS] | CLUZ
6/10/2024 5:40:14 AM | [NSO Update] Visayas Grid-06/10/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2825MW, PK=2240MW, RR=91MW, NetOpMargin: AM=494, PM=197, EVE=220 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @314MW, CEDC U3 @75MW, GTEC @7MW, PB104-3 @5MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, TGPP @116.5MW [WEBSMS] | CVIS
6/10/2024 5:38:51 AM | [NSO Update] Mindanao Grid-06/10/2024 05:45: Weather Advisory: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CMIN
6/10/2024 5:37:48 AM | [NSO Update] Mindanao Grid-06/10/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3325MW, PK=2366MW, RR=73MW, NetOpMargin: AM=886, PM=728, EVE=928 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/10/2024 4:10:54 AM | [NSO Update] Visayas Grid-06/10/2024 04:11: Weather Advisory: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CVIS
6/10/2024 4:10:25 AM | [NSO Update] Luzon Grid-06/10/2024 04:10: Weather Advisory: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CLUZ
6/10/2024 12:21:07 AM | Luzon Grid-06/10/2024 00:21: Angat 122.2MVA Main Transformer A, and San Jose-Angat 115kV line 2 were de-energized at 0012H and 0015H respectively. (Planned Outage) [WEBSMS] | CLUZ
6/9/2024 10:18:40 PM | Luzon Grid-06/09/2024 22:19: Concepcion-San Manuel 230kV line 2 was restored at 2218H. (Planned Outage) [WEBSMS] | CLUZ
6/9/2024 9:10:21 PM | Luzon Grid-06/09/2024 21:10: San Jose 115kV Bus 2 was de-energized at 2110H. (Planned Outage) [WEBSMS] | CLUZ
6/9/2024 8:18:21 PM | Mindanao Grid-06/09/2024 20:24: Mindanao Spot Peak for June 9, 2024, is 2,029.11MW at 1940H. The highest peak to date is 2,577.02 MW at 1333H on May 22, 2024. [WEBSMS] | CMIN
6/9/2024 8:14:41 PM | [NSO Update] Visayas Grid-06/09/2024 20:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2012H with power going to Luzon. [WEBSMS] | CVIS
6/9/2024 8:14:23 PM | [NSO Update] Luzon Grid-06/09/2024 20:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2012H with power going to Luzon. [WEBSMS] | CLUZ
6/9/2024 8:03:11 PM | [NSO Update] Luzon Grid-06/09/2024 20:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1958H from reverse power direction. [WEBSMS] | CLUZ
6/9/2024 8:02:57 PM | [NSO Update] Visayas Grid-06/09/2024 20:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1958H from reverse power direction. [WEBSMS] | CVIS
6/9/2024 7:50:19 PM | Luzon Grid-06/09/2024 19:50: Balsik-SBMA 230kV line was restored at 1948H. (Planned Outage) [WEBSMS] | CLUZ
6/9/2024 6:36:57 PM | Mindanao Grid-06/09/2024 18:43: Maco - UPSI Maco BESS 69kV line energized at 1836H. (Planned Outage) [WEBSMS] | CMIN
6/9/2024 6:31:05 PM | [NSO Update] Visayas Grid-06/09/2024 18:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1829H with power going to Visayas. [WEBSMS] | CVIS
6/9/2024 6:30:44 PM | [NSO Update] Luzon Grid-06/09/2024 18:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1829H with power going to Visayas. [WEBSMS] | CLUZ
6/9/2024 6:21:00 PM | [NSO Update] Visayas Grid-06/09/2024 18:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1818H from forward power direction. [WEBSMS] | CVIS
6/9/2024 6:20:16 PM | [NSO Update] Luzon Grid-06/09/2024 18:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1818H from forward power direction. [WEBSMS] | CLUZ
6/9/2024 5:55:46 PM | [NSO Update] Luzon Grid-06/09/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14382MW, PK=10517MW, RR=339MW, NetOpMargin: EVE=3526 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Ilijan A @550MW, SLTEC 1 @117MW, SLTEC 2 @121MW, Limay 2 @50MW [WEBSMS] | CLUZ
6/9/2024 5:32:21 PM | [NSO Update] Visayas Grid-06/09/2024 17:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2637MW, PK=2107MW, RR=91MW, NetOpMargin: EVE=440 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @306MW, CEDC U3 @75MW, GTEC @7MW, PB104-3 @5MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, TGPP @117MW [WEBSMS] | CVIS
6/9/2024 5:31:08 PM | [NSO Update] Mindanao Grid-06/09/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3263MW, PK=2055MW, RR=38MW, NetOpMargin: EVE=1170 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/9/2024 5:22:27 PM | Luzon Grid-06/09/2024 17:22: Binga - La Trinidad 230kV Line 1 was restored at 1722H. (Planned Outage) [WEBSMS] | CLUZ
6/9/2024 5:20:01 PM | Luzon Grid-06/09/2024 17:20: Muntinlupa-Binan 230kV Line 2 was restored at 1719H. (Planned Outage) [WEBSMS] | CLUZ
6/9/2024 5:09:33 PM | Visayas Grid-06/09/2024 17:09: Compostela - Daanbantayan 230 kV Line 2 energized at 1643H (Planned Outage) [WEBSMS] | CVIS
6/9/2024 5:03:52 PM | Mindanao Grid-06/09/2024 17:10: Maramag 75MVA 138kV Power Transformer No. 2 energized at 1700H. (Planned Outage) [WEBSMS] | CMIN
6/9/2024 5:02:38 PM | Mindanao Grid-06/09/2024 17:08: Kibawe - Davao 138kV L1 energized at 1700H (Planned Outage). [WEBSMS] | CMIN
6/9/2024 4:23:54 PM | Mindanao Grid-06/09/2024 16:30: Kibawe - Davao 138kV L1 energized at 1620H. (Planned Outage) [WEBSMS] | CMIN
6/9/2024 3:23:49 PM | Mindanao Grid-06/09/2024 15:29: Marawi 50MVA 138kV Power Transformer No. 1 energized at 1520H (Planned Outage) [WEBSMS] | CMIN
6/9/2024 2:42:10 PM | Luzon Grid-06/09/2024 14:42: San Gabriel shutdown at 1440H. (Reserve Shutdown) [WEBSMS] | CLUZ
6/9/2024 12:38:46 PM | [NSO Update] Mindanao Grid-06/09/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3308MW, PK=1881MW, RR=38MW, NetOpMargin: PM=1389, EVE=1181 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @28MW [WEBSMS] | CMIN
6/9/2024 12:37:36 PM | [NSO Update] Visayas Grid-06/09/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2607MW, PK=1998MW, RR=88MW, NetOpMargin: PM=522, EVE=431 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @306MW, CEDC U3 @75MW, GTEC @7MW, PB104-3 @5MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, TGPP @118.5MW [WEBSMS] | CVIS
6/9/2024 12:34:27 PM | [NSO Update] Luzon Grid-06/09/2024 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15546MW, PK=10535MW, RR=356MW, NetOpMargin: PM=4655, EVE=3182 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, MSLC2 @320MW, ILIJAN A @550MW [WEBSMS] | CLUZ
6/9/2024 11:42:25 AM | Luzon Grid-06/09/2024 11:42: Dasmarinas SS 230kV Bus 2 restored at 1142H (Planned Outage) [WEBSMS] | CLUZ
6/9/2024 11:39:03 AM | Mindanao Grid-06/09/2024 11:45: SEC1 online at 1042H from Forced Outage. [WEBSMS] | CMIN
6/9/2024 9:46:30 AM | Mindanao Grid-06/09/2024 09:52: Marawi 50MVA 138kV Power Transformer No. 1 de-energized at 0926H. (Planned Outage) [WEBSMS] | CMIN
6/9/2024 8:41:40 AM | Luzon Grid-06/09/2024 08:42: Muntinlupa-Binan 230kV Line 2 de-energized at 0840H (Planned Outage) [WEBSMS] | CLUZ
6/9/2024 8:03:27 AM | Mindanao Grid-06/09/2024 08:09: Kibawe - Davao 138kV L1 de-energized at 0802H. (Planned Outage) [WEBSMS] | CMIN
6/9/2024 6:59:25 AM | Mindanao Grid-06/09/2024 07:05: Maramag 75MVA 138kV Power Transformer No. 2 de-energized at 0647H. (Planned Outage) [WEBSMS] | CMIN
6/9/2024 6:43:40 AM | Luzon Grid-06/09/2024 06:44: Balsik-SBMA 230kV Line de-energized at 0643H (Planned Outage) [WEBSMS] | CLUZ
6/9/2024 6:36:26 AM | Mindanao Grid-06/09/2024 06:42: Maco - UPSI Maco BESS 69kV line de-energized at 0618H. (Planned Outage) [WEBSMS] | CMIN
6/9/2024 6:15:48 AM | Luzon Grid-06/09/2024 06:16: Binga - La Trinidad 230kV Line 1 de-energized at 0614H (Planned Outage) [WEBSMS] | CLUZ
6/9/2024 6:13:17 AM | Visayas Grid-06/09/2024 06:13: Compostela - Daanbantayan 230 kV Line 2 de-energized at 0612H (Planned Outage) [WEBSMS] | CVIS
6/9/2024 6:08:25 AM | [NSO Update] Mindanao Grid-06/09/2024 06:14: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3211MW, PK=1923MW, RR=38MW, NetOpMargin: AM=1249, PM=973, EVE=878 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @28MW [WEBSMS] | CMIN
6/9/2024 6:06:07 AM | [NSO Update] Visayas Grid-06/09/2024 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2690MW, PK=1823MW, RR=84MW, NetOpMargin: AM=783, PM=695, EVE=539 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @311MW, CEDC U3 @75MW, GTEC @7MW, PB104-3 @5MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, TGPP @116.5MW, PB104-1 @6MW, PB104-2 @6MW [WEBSMS] | CVIS
6/9/2024 6:02:20 AM | [NSO Update] Luzon Grid-06/09/2024 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15879MW, PK=10014MW, RR=356MW, NetOpMargin: AM=5509, PM=4628, EVE=3263 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, MSLC2 @320MW, ILIJAN A @550MW [WEBSMS] | CLUZ
6/9/2024 4:07:05 AM | [NSO Update] Mindanao Grid-06/09/2024 04:13: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CMIN
6/9/2024 4:06:28 AM | [NSO Update] Visayas Grid-06/09/2024 04:06: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CVIS
6/9/2024 4:06:01 AM | [NSO Update] Luzon Grid-06/09/2024 04:06: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CLUZ
6/9/2024 2:34:19 AM | Mindanao Grid-06/09/2024 02:40: SEC 1 tripped with 61.65MW at 0224H. The lowest frequency recorded is 59.6389Hz. (Unplanned Outage) [WEBSMS] | CMIN
6/9/2024 1:15:21 AM | Luzon Grid-06/09/2024 01:15: Dasmarinas SS 230kV Bus 2 de-energized at 0114H. (Planned Outage) [WEBSMS] | CLUZ
6/8/2024 11:24:46 PM | Luzon Grid-06/08/2024 23:25: San Gabriel online at 2322H. (From Reserve Shutdown) [WEBSMS] | CLUZ
6/8/2024 11:08:44 PM | Mindanao Grid-06/08/2024 23:14: Steag U2 online/synchronized back at 2254H. (Unplanned Outage) [WEBSMS] | CMIN
6/8/2024 11:00:13 PM | Mindanao Grid-06/08/2024 23:06: Steag U2 tripped with 85.23MW load at 2250H. The lowest frequency recorded is 59.378 Hz. (Unplanned outage) [WEBSMS] | CMIN
6/8/2024 9:16:51 PM | [NSO Update] Visayas Grid-06/08/2024 21:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2113H with power going to Luzon [WEBSMS] | CVIS
6/8/2024 9:16:23 PM | [NSO Update] Luzon Grid-06/08/2024 21:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2113H with power going to Luzon [WEBSMS] | CLUZ
6/8/2024 9:15:19 PM | [NSO Update] Visayas Grid-06/08/2024 21:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2102H from reverse power direction [WEBSMS] | CVIS
6/8/2024 9:14:33 PM | [NSO Update] Luzon Grid-06/08/2024 21:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2102H from reverse power direction [WEBSMS] | CLUZ
6/8/2024 7:53:52 PM | Mindanao Grid-06/08/2024 20:00: WMPC DG10 Shutdown at 1946H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
6/8/2024 6:42:51 PM | Mindanao Grid-06/08/2024 18:48: WMPC DG10 Online at 1839H. Reactive Power Support (RPS) - System Voltage Requirement. [WEBSMS] | CMIN
6/8/2024 6:42:17 PM | Luzon Grid-06/08/2024 18:42: Balsik-Olongapo 230kV line restored at 1842H. (Planned Outage) [WEBSMS] | CLUZ
6/8/2024 6:07:34 PM | Mindanao Grid-06/08/2024 18:13: Balo-i - IDPP 138kV Line energized/looped at 1804H. (Planned Outage) [WEBSMS] | CMIN
6/8/2024 6:02:46 PM | Visayas Grid-06/08/2024 18:03: Compostela-DaanBantayan 230 kV L1 energized at 1758H (Planned Outage) [WEBSMS] | CVIS
6/8/2024 5:59:57 PM | [NSO Update] Mindanao Grid-06/08/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3275MW, PK=2185MW, RR=73MW, NetOpMargin: EVE=1017 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/8/2024 5:58:33 PM | [NSO Update] Visayas Grid-06/08/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2522MW, PK=2157MW, RR=91MW, NetOpMargin: EVE=274 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, GTEC @7MW, PB104-3 @5MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, TGPP @116.5MW, PB104-1 @6MW [WEBSMS] | CVIS
6/8/2024 5:55:59 PM | [NSO Update] Luzon Grid-06/08/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13605MW, PK=10690MW, RR=429MW, NetOpMargin: EVE=2486 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, MSLC2 @320MW, ILIJAN A @550MW [WEBSMS] | CLUZ
6/8/2024 5:28:40 PM | Mindanao Grid-06/08/2024 17:34: Agus6 U2 Online at 1723H. Outside Management Control (OMC). (Planned Outage) [WEBSMS] | CMIN
6/8/2024 4:22:56 PM | Luzon Grid-06/08/2024 16:23: Bauang-Bakun 230kV line restored at 1621H. (Planned Outage) [WEBSMS] | CLUZ
6/8/2024 4:06:29 PM | Luzon Grid-06/08/2024 16:06: Tayabas PCB 9-02CB24TAY restored at 1606H. (Planned Outage) [WEBSMS] | CLUZ
6/8/2024 2:45:22 PM | [NSO Update] Luzon Grid-06/08/2024 14:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1443H with power going to Visayas [WEBSMS] | CLUZ
6/8/2024 2:44:39 PM | [NSO Update] Visayas Grid-06/08/2024 14:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1443H with power going to Visayas [WEBSMS] | CVIS
6/8/2024 2:24:07 PM | [NSO Update] Luzon Grid-06/08/2024 14:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1421H from forward power direction [WEBSMS] | CLUZ
6/8/2024 2:23:35 PM | [NSO Update] Visayas Grid-06/08/2024 14:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1421H from forward power direction [WEBSMS] | CVIS
6/8/2024 1:48:38 PM | Luzon Grid-06/08/2024 13:49: Balsik PCB 9-01CB08BIK was energized at 1348H. (Planned Outage) [WEBSMS] | CLUZ
6/8/2024 1:30:02 PM | Mindanao Grid-06/08/2024 13:36: Lake Mainit HEP (AGC) online at 1327H from OMC Outage. (Unplanned Outage) [WEBSMS] | CMIN
6/8/2024 1:10:28 PM | Luzon Grid-06/08/2024 13:10: Balsik PCB 9-01CB08BIK was de-energized at 1305H. (Planned Outage) [WEBSMS] | CLUZ
6/8/2024 12:45:44 PM | [NSO Update] Mindanao Grid-06/08/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3317MW, PK=2322MW, RR=73MW, NetOpMargin: PM=922, EVE=942 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/8/2024 12:44:10 PM | [NSO Update] Visayas Grid-06/08/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2653MW, PK=2220MW, RR=89MW, NetOpMargin: PM=344, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @116.5MW, LEYTE A @305MW, CEDC U3 @75MW, GTEC @7MW, PDPP3-H @8MW, PDPP3-G @10MW, PDPP3-E @10MW [WEBSMS] | CVIS
6/8/2024 12:39:58 PM | [NSO Update] Luzon Grid-06/08/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15233MW, PK=11638MW, RR=469MW, NetOpMargin: PM=3126, EVE=2563 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GNPD 2 @640MW, MSLC2 @320MW, ILIJAN A @540MW [WEBSMS] | CLUZ
6/8/2024 10:00:51 AM | Luzon Grid-06/08/2024 10:01: Tayabas PCB 9-02CB24TAY was de-energized at 1000H. (Planned Outage) [WEBSMS] | CLUZ
6/8/2024 9:40:41 AM | Luzon Grid-06/08/2024 09:41: EERI 1 online at 0933H. (Under test and commissioning) [WEBSMS] | CLUZ
6/8/2024 9:28:41 AM | [NSO Update] Luzon Grid-06/08/2024 09:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0926H with power going to Luzon. [WEBSMS] | CLUZ
6/8/2024 9:28:16 AM | [NSO Update] Visayas Grid-06/08/2024 09:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0926H with power going to Luzon. [WEBSMS] | CVIS
6/8/2024 9:22:20 AM | Mindanao Grid-06/08/2024 09:28: Agus6 U2 shutdown at 0908H. Outside Management Control (OMC). (Planned Outage) [WEBSMS] | CMIN
6/8/2024 9:18:26 AM | [NSO Update] Visayas Grid-06/08/2024 09:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0915H from forward power direction. [WEBSMS] | CVIS
6/8/2024 9:18:04 AM | [NSO Update] Luzon Grid-06/08/2024 09:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0915H from forward power direction. [WEBSMS] | CLUZ
6/8/2024 9:01:06 AM | Luzon Grid-06/08/2024 09:01: Concepcion-San Manuel 230kV line 2 was de-energized at 0859H. (Planned Outage) [WEBSMS] | CLUZ
6/8/2024 8:53:31 AM | Luzon Grid-06/08/2024 08:53: Nagsaag-San Jose 500kV line 2 was restored at 0852H. (Unplanned Outage) [WEBSMS] | CLUZ
6/8/2024 8:51:45 AM | Luzon Grid-06/08/2024 08:52: Bauang-Bakun 230kV line was de-energized at 0851H. (Planned Outage) [WEBSMS] | CLUZ
6/8/2024 8:33:41 AM | Mindanao Grid-06/08/2024 08:39: Lake Mainit (AGC) with 4.5MW load shutdown at 0830H due to low lake water elevation. (Unplanned Outage) [WEBSMS] | CMIN
6/8/2024 8:28:05 AM | Mindanao Grid-06/08/2024 08:34: Balo-i - IDPP 138kV Line De-energized/shutdown at 0821H. (Planned Outage) [WEBSMS] | CMIN
6/8/2024 6:37:18 AM | Luzon Grid-06/08/2024 06:37: Balsik-Olongapo 230kV line was de-energized at 0636H. (Planned Outage) [WEBSMS] | CLUZ
6/8/2024 6:25:22 AM | Visayas Grid-06/08/2024 06:25: Compostela-DaanBantayan 230 kV L1 de-energized at 0620H (Planned Outage) [WEBSMS] | CVIS
6/8/2024 5:38:38 AM | [NSO Update] Luzon Grid-06/08/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15246MW, PK=10530MW, RR=442MW, NetOpMargin: AM=4274, PM=3065, EVE=2713 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Ilijan A @540MW [WEBSMS] | CLUZ
6/8/2024 5:26:52 AM | [NSO Update] Visayas Grid-06/08/2024 05:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2643MW, PK=2077MW, RR=85MW, NetOpMargin: AM=481, PM=414, EVE=249 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @311MW, CEDC U3 @75MW, GTEC @7MW, PB104-3 @5MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, PDPP3-E @10MW, TGPP @116.5MW, PB104-1 @6MW, PB104-2 @6MW [WEBSMS] | CVIS
6/8/2024 5:24:53 AM | [NSO Update] Mindanao Grid-06/08/2024 05:31: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3327MW, PK=2224MW, RR=73MW, NetOpMargin: AM=1030, PM=915, EVE=856 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/8/2024 4:15:58 AM | [NSO Update] Luzon Grid-06/08/2024 04:16: Weather Update: Southwest Monsoon affecting the western sections of Luzon and Visayas. [WEBSMS] | CLUZ
6/8/2024 4:15:32 AM | [NSO Update] Mindanao Grid-06/08/2024 04:21: Weather Update: Southwest Monsoon affecting the western sections of Luzon and Visayas. [WEBSMS] | CMIN
6/8/2024 4:15:04 AM | [NSO Update] Visayas Grid-06/08/2024 04:15: Weather Update: Southwest Monsoon affecting the western sections of Luzon and Visayas. [WEBSMS] | CVIS
6/8/2024 3:38:08 AM | Luzon Grid-06/08/2024 03:38: For information: San Jose 9-03CB04SJO closed at 0335H, looping San Jose 500kV Ring Bus (Unplanned Outage). [WEBSMS] | CLUZ
6/7/2024 9:23:10 PM | Luzon Grid-06/07/2024 21:23: Bacnotan-San Esteban 230kV Line restored at 2118H (Planned Outage) [WEBSMS] | CLUZ
6/7/2024 9:18:25 PM | Mindanao Grid-06/07/2024 21:24: WMPC DG10 Shutdown at 2118H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/7/2024 7:37:05 PM | Luzon Grid-06/07/2024 19:37: San Manuel 230kV Bus 2 restored at 1936H (Planned Outage) [WEBSMS] | CLUZ
6/7/2024 6:56:16 PM | Luzon Grid-06/07/2024 18:56: San Jose-Nagsaag 500kV L2 de-energized at 1856H (Unplanned Outage). [WEBSMS] | CLUZ
6/7/2024 6:55:19 PM | Mindanao Grid-06/07/2024 19:01: WMPC DG04 Shutdown at 1855H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/7/2024 6:28:00 PM | Luzon Grid-06/07/2024 18:28: Bacnotan-San Esteban 230kV Line de-energized at 1826H (Planned Outage) [WEBSMS] | CLUZ
6/7/2024 5:51:39 PM | [NSO Update] Luzon Grid-06/07/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13412MW, PK=11265MW, RR=429MW, NetOpMargin: EVE=1718 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Ilijan A @500MW [WEBSMS] | CLUZ
6/7/2024 5:48:50 PM | [NSO Update] Visayas Grid-06/07/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2653MW, PK=2253MW, RR=91MW, NetOpMargin: EVE=309 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @306MW, CEDC U3 @75MW, GTEC @7MW, PB104-3 @5MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, PDPP3-E @10MW, TGPP @116.5MW [WEBSMS] | CVIS
6/7/2024 5:40:13 PM | [NSO Update] Mindanao Grid-06/07/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3221MW, PK=2307MW, RR=73MW, NetOpMargin: EVE=841 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/7/2024 4:47:51 PM | [NSO Update] Visayas Grid-06/07/2024 16:48: SO-initiated Market Intervention for Visayas has been lifted today at 1634H. Market operations will resume starting interval 1640H. [WEBSMS] | CVIS
6/7/2024 3:25:46 PM | Mindanao Grid-06/07/2024 15:31: WMPC DG08 Shutdown at 1523H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/7/2024 2:13:18 PM | [NSO Update] Visayas Grid-06/07/2024 14:13: SO-initiated Market Intervention for Visayas is issued today starting interval 1410H due to MLD implementation to prevent the overloading of Ubay-Maasin 138kV Line. [WEBSMS] | CVIS
6/7/2024 1:47:41 PM | Luzon Grid-06/07/2024 13:48: Naga-Tiwi C 230kV Line 2 tripped/reclosed at 1339H (Unplanned Outage) [WEBSMS] | CLUZ
6/7/2024 1:28:31 PM | Luzon Grid-06/07/2024 13:28: Masinloc 1 emergency shutdown at 1327H due to boiler tube leak (Unplanned Outage) [WEBSMS] | CLUZ
6/7/2024 1:20:56 PM | Mindanao Grid-06/07/2024 13:27: Agus 4 Unit 3 online at 1302H from OMC: Low forebay elevation. (Unplanned Outage) [WEBSMS] | CMIN
6/7/2024 12:48:42 PM | [NSO Update] Mindanao Grid-06/07/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3253MW, PK=2513MW, RR=73MW, NetOpMargin: PM=667, EVE=788 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @28MW [WEBSMS] | CMIN
6/7/2024 12:44:01 PM | [NSO Update] Luzon Grid-06/07/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15011MW, PK=12271MW, RR=496MW, NetOpMargin: PM=2244, EVE=1541 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @200MW, Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Ilijan A @500MW [WEBSMS] | CLUZ
6/7/2024 12:44:01 PM | [NSO Update] Visayas Grid-06/07/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2830MW, PK=2460MW, RR=91MW, NetOpMargin: PM=279, EVE=245 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, GTEC @7MW, PB104-3 @5MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, PDPP3-E @10MW, TGPP @116.5MW [WEBSMS] | CVIS
6/7/2024 12:09:29 PM | Mindanao Grid-06/07/2024 12:15: Therma 2 Unit 2 shutdown as DR at 1207H. Time of call at 1153H. [WEBSMS] | CMIN
6/7/2024 12:07:47 PM | Mindanao Grid-06/07/2024 12:13: Mapalad (IDPP) online as DR at 1134H. Time of call at 1123H. [WEBSMS] | CMIN
6/7/2024 11:57:11 AM | Mindanao Grid-06/07/2024 12:03: STEAG U2 synchronized back at 1147H from isolation due to the opening of PCB 7-02CB04STE. [WEBSMS] | CMIN
6/7/2024 11:47:24 AM | Mindanao Grid-06/07/2024 11:53: Therma 2 Unit 2 online as DR at 1130H. Time of call at 1116H. [WEBSMS] | CMIN
6/7/2024 11:24:02 AM | Mindanao Grid-06/07/2024 11:30: STEAG U2 with 100 MW gross gen was isolated at 1113H due to opening of PCB 7-02CB04STE. Details to Follow. [WEBSMS] | CMIN
6/7/2024 10:56:45 AM | [NSO Update] Luzon Grid-06/07/2024 10:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1055H with power going to Luzon [WEBSMS] | CLUZ
6/7/2024 10:56:42 AM | [NSO Update] Visayas Grid-06/07/2024 10:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1055H with power going to Luzon [WEBSMS] | CVIS
6/7/2024 10:46:53 AM | [NSO Update] Visayas Grid-06/07/2024 10:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1045H from reverse power direction [WEBSMS] | CVIS
6/7/2024 10:46:50 AM | [NSO Update] Luzon Grid-06/07/2024 10:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1045H from reverse power direction [WEBSMS] | CLUZ
6/7/2024 9:42:05 AM | Mindanao Grid-06/07/2024 09:48: WMPC DG04 online at 0940H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/7/2024 9:39:59 AM | Luzon Grid-06/07/2024 09:40: Kalayaan 4 with 142MW load tripped at 0934H. Lowest Frequency is 59.506Hz (Unplanned Outage) [WEBSMS] | CLUZ
6/7/2024 9:37:41 AM | Mindanao Grid-06/07/2024 09:43: Agusan Lake Mainit Hydro shutdown at 0932H due to low water elevation. (Unplanned Outage) [WEBSMS] | CMIN
6/7/2024 8:53:08 AM | Mindanao Grid-06/07/2024 08:59: WMPC DG10 online at 0852H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/7/2024 8:36:42 AM | Luzon Grid-06/07/2024 08:37: For Info: Luzon System Frequency reached 60.45H at 0829H due to tripping of Mexico-Arayat 69kV Line. [WEBSMS] | CLUZ
6/7/2024 8:22:22 AM | Luzon Grid-06/07/2024 08:22: Binga HEPP 230kV Overhead Line 1 de-energized at 0822H (Planned Outage) [WEBSMS] | CLUZ
6/7/2024 8:18:24 AM | [NSO Update] Luzon Grid-06/07/2024 08:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0817H with power going to Visayas [WEBSMS] | CLUZ
6/7/2024 8:18:19 AM | [NSO Update] Visayas Grid-06/07/2024 08:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0817H with power going to Visayas [WEBSMS] | CVIS
6/7/2024 8:07:54 AM | [NSO Update] Visayas Grid-06/07/2024 08:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0807H from forward power direction [WEBSMS] | CVIS
6/7/2024 8:07:50 AM | [NSO Update] Luzon Grid-06/07/2024 08:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0807H from forward power direction [WEBSMS] | CLUZ
6/7/2024 6:06:12 AM | Luzon Grid-06/07/2024 06:06: San Manuel 230kV Bus 2 de-energized at 0605H (Planned Outage) [WEBSMS] | CLUZ
6/7/2024 5:54:44 AM | [NSO Update] Mindanao Grid-06/07/2024 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3272MW, PK=2354MW, RR=73MW, NetOpMargin: AM=845, PM=562, EVE=741 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @28MW [WEBSMS] | CMIN
6/7/2024 5:52:26 AM | [NSO Update] Visayas Grid-06/07/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2744MW, PK=2229MW, RR=91MW, NetOpMargin: AM=424, PM=268, EVE=260 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, GTEC @7MW, PB104-1 @5.5MW, PB104-3 @5MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, PDPP3-E @10MW, PB104-2 @6MW, TGPP @116.5MW [WEBSMS] | CVIS
6/7/2024 5:49:04 AM | [NSO Update] Luzon Grid-06/07/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15369MW, PK=11159MW, RR=496MW, NetOpMargin: AM=3715, PM=1704, EVE=1746 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @200MW, Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Ilijan A @500MW [WEBSMS] | CLUZ
6/7/2024 4:30:24 AM | [NSO Update] Mindanao Grid-06/07/2024 04:36: Weather Update: Southwest Monsoon affecting the western sections of Luzon and Visayas. [WEBSMS] | CMIN
6/7/2024 4:30:13 AM | [NSO Update] Visayas Grid-06/07/2024 04:30: Weather Update: Southwest Monsoon affecting the western sections of Luzon and Visayas. [WEBSMS] | CVIS
6/7/2024 4:30:00 AM | [NSO Update] Luzon Grid-06/07/2024 04:30: Weather Update: Southwest Monsoon affecting the western sections of Luzon and Visayas. [WEBSMS] | CLUZ
6/6/2024 10:52:33 PM | Mindanao Grid-06/06/2024 22:58: Pulangi4 Unit 3 online at 2247H from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
6/6/2024 9:59:07 PM | Visayas Grid-06/06/2024 21:59: Carcon-Sangi 34.5kV line 2 energized at 2105H (Unplanned Outage) [WEBSMS] | CVIS
6/6/2024 9:15:06 PM | Mindanao Grid-06/06/2024 21:21: WMPC DG10 Shutdown at 2051H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/6/2024 8:39:20 PM | Visayas Grid-06/06/2024 20:39: Carcon SS 34.5kV bus 2 energized at 2030H (Unplanned Outage) [WEBSMS] | CVIS
6/6/2024 7:59:16 PM | Luzon Grid-06/06/2024 19:59: San Gabriel shutdown at 1958H (Reserve Shutdown) [WEBSMS] | CLUZ
6/6/2024 7:30:05 PM | Visayas Grid-06/06/2024 19:30: Carcon-2nd lift 34.5kV line tripped/restored at 1706H/1759H (Unplanned Outage). [WEBSMS] | CVIS
6/6/2024 6:57:24 PM | Mindanao Grid-06/06/2024 19:03: Pulangi 4 Unit 3 with 35MW load tripped at 1846H. Indication: Thrust bearing oil temperature high. No ALD activation, lowest frequency recorded at 59.89Hz. (Unplanned Outage) [WEBSMS] | CMIN
6/6/2024 6:50:07 PM | Mindanao Grid-06/06/2024 18:56: Baloi - Agus 5 138kV L energized at 1844H. (Planned Outage) [WEBSMS] | CMIN
6/6/2024 6:04:41 PM | [NSO Update] Mindanao Grid-06/06/2024 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3194MW, PK=2233MW, RR=73MW, NetOpMargin: EVE=888 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/6/2024 6:03:37 PM | [NSO Update] Visayas Grid-06/06/2024 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2560MW, PK=2172MW, RR=91MW, NetOpMargin: EVE=296 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @300MW, CEDC U3 @75MW, GTEC @7MW, Power Barge 104-1 @5.5MW, Power Barge 104-3 @5MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW, PDPP3-G @10MW, PDPP3-E @10MW [WEBSMS] | CVIS
6/6/2024 5:57:46 PM | [NSO Update] Luzon Grid-06/06/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14119MW, PK=11290MW, RR=462MW, NetOpMargin: EVE=2367 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @200MW, Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Ilijan A @500MW [WEBSMS] | CLUZ
6/6/2024 5:55:20 PM | Visayas Grid-06/06/2024 17:55: TPC 1A synchronized at 1740H (Unplanned Outage) [WEBSMS] | CVIS
6/6/2024 5:53:19 PM | Visayas Grid-06/06/2024 17:53: Carcon-Sangi 34.5kV line 3 restored at 1727H (Unplanned Outage) [WEBSMS] | CVIS
6/6/2024 5:51:46 PM | Visayas Grid-06/06/2024 17:51: Carcon-Sangi 34.5kV line 1 restored at 1733H (Unplanned Outage) [WEBSMS] | CVIS
6/6/2024 5:38:08 PM | Mindanao Grid-06/06/2024 17:44: WMPC DG4 Shutdown at 1733H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/6/2024 5:27:21 PM | Visayas Grid-06/06/2024 17:27: Carcon-Sangi 34.5kv line 1 tripped at 1706H (Unplanned Outage) [WEBSMS] | CVIS
6/6/2024 5:15:16 PM | Visayas Grid-06/06/2024 17:15: Carcon-Sangi 34.5kV line 3 tripped at 1706H. TPC 1A on islanding operation. (Unplanned Outage) [WEBSMS] | CVIS
6/6/2024 5:12:03 PM | Luzon Grid-06/06/2024 17:12: Santiago-NIA Baligatan HEPP 69kV Line (CO) restored at 1711H (Planned Outage) [WEBSMS] | CLUZ
6/6/2024 4:38:51 PM | Mindanao Grid-06/06/2024 16:44: Butuan - San Francisco 138kV L energized at 1637H. (Unplanned Outage) [WEBSMS] | CMIN
6/6/2024 4:34:17 PM | [NSO Update] Visayas Grid-06/06/2024 16:34: SO-initiated Market Intervention for Visayas has been lifted today at 1628H. Market operations will resume starting interval 1635H. [WEBSMS] | CVIS
6/6/2024 4:22:03 PM | [NSO Update] Visayas Grid-06/06/2024 16:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1557H with power going to Luzon [WEBSMS] | CVIS
6/6/2024 4:21:46 PM | [NSO Update] Luzon Grid-06/06/2024 16:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1557H with power going to Luzon [WEBSMS] | CLUZ
6/6/2024 4:20:55 PM | [NSO Update] Visayas Grid-06/06/2024 16:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1547H from reverse power direction [WEBSMS] | CVIS
6/6/2024 4:20:40 PM | [NSO Update] Luzon Grid-06/06/2024 16:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1547H from reverse power direction [WEBSMS] | CLUZ
6/6/2024 3:58:05 PM | Luzon Grid-06/06/2024 15:58: For Info: Luzon System Frequency reached 60.49H due to tripping of Malabon-Grace Park 115kV Line (Meralco Owned) at 1551H. [WEBSMS] | CLUZ
6/6/2024 3:49:55 PM | Luzon Grid-06/06/2024 15:50: EERI 1 shutdown at 1547H (On Commissioning Test) [WEBSMS] | CLUZ
6/6/2024 3:24:58 PM | Visayas Grid-06/06/2024 15:25: Carcon SS 34.5kV bus 2 de-energized at 1519H (Unplanned Outage). [WEBSMS] | CVIS
6/6/2024 3:20:46 PM | Visayas Grid-06/06/2024 15:20: Dumanjug 138KV Bus 2 energized at 1513H H (Planned Outage) [WEBSMS] | CVIS
6/6/2024 2:53:26 PM | Visayas Grid-06/06/2024 14:53: Carcon-Sangi 34.5kV line 2 de-energized at 1444H (Unplanned Outage). [WEBSMS] | CVIS
6/6/2024 1:28:34 PM | Mindanao Grid-06/06/2024 13:34: TM2 U1 Shutdown at 1318H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/6/2024 1:19:58 PM | [NSO Update] Visayas Grid-06/06/2024 13:20: SO-initiated Market Intervention for Visayas is issued today starting interval 1320H due to MLD implementation to prevent the overloading of Ubay-Maasin 138kV Line. [WEBSMS] | CVIS
6/6/2024 1:04:33 PM | [NSO Update] Mindanao Grid-06/06/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3228MW, PK=2605MW, RR=73MW, NetOpMargin: PM=551, EVE=712 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/6/2024 12:59:21 PM | [NSO Update] Visayas Grid-06/06/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2769MW, PK=2450MW, RR=91MW, NetOpMargin: PM=228, EVE=279 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @317MW, CEDC U3 @75MW, GTEC @7MW, Power Barge 104-1 @5.5MW, Power Barge 104-3 @5MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW [WEBSMS] | CVIS
6/6/2024 12:56:37 PM | [NSO Update] Visayas Grid-06/06/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2769MW, PK=2450MW, RR=91MW, NetOpMargin: PM=228, EVE=279 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @317MW, CEDC U3 @75MW, GTEC @7MW, Power Barge 104-1 @5.5MW, Power Barge 104-3 @5MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW (Total deration: 193.3MW) [WEBSMS] | CVIS
6/6/2024 12:44:52 PM | [NSO Update] Luzon Grid-06/06/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15144MW, PK=12900MW, RR=496MW, NetOpMargin: PM=1749, EVE=1737 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @290MW, GNPD 2 @640MW, MSLC1 @200MW, MSLC2 @320MW, ILIJAN A @500MW [WEBSMS] | CLUZ
6/6/2024 12:23:15 PM | Mindanao Grid-06/06/2024 12:29: Butuan - San Francisco 138kV L tripped at 1220H. (Unplanned Outage) [WEBSMS] | CMIN
6/6/2024 11:05:32 AM | Mindanao Grid-06/06/2024 11:11: TM2 Unit1 online at 1101H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/6/2024 9:49:35 AM | Mindanao Grid-06/06/2024 09:55: WMPC DG4 online at 0940H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/6/2024 8:58:43 AM | Luzon Grid-06/06/2024 08:59: EERI 1 online online at 0853H (On Commissioning Test) [WEBSMS] | CLUZ
6/6/2024 8:26:42 AM | Mindanao Grid-06/06/2024 08:32: AGUS2 Unit 1 shutdown at 0805H. PMS (GOMP) [WEBSMS] | CMIN
6/6/2024 8:23:45 AM | Luzon Grid-06/06/2024 08:24: San Juan-Calauan 230kV Line 1 restored at 0820H (Planned Outage) [WEBSMS] | CLUZ
6/6/2024 8:21:17 AM | Visayas Grid-06/06/2024 08:21: Dumanjug 138KV Bus de-energized @0806H. ( Planned Outage ) [WEBSMS] | CVIS
6/6/2024 8:20:55 AM | Mindanao Grid-06/06/2024 08:26: WMPC DG10 online at 0812H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/6/2024 8:19:03 AM | [NSO Update] Visayas Grid-06/06/2024 08:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0816H with power going to Visayas [WEBSMS] | CVIS
6/6/2024 8:17:52 AM | [NSO Update] Luzon Grid-06/06/2024 08:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0816H with power going to Visayas [WEBSMS] | CLUZ
6/6/2024 8:07:46 AM | [NSO Update] Visayas Grid-06/06/2024 08:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0806H from forward power direction [WEBSMS] | CVIS
6/6/2024 8:07:13 AM | [NSO Update] Luzon Grid-06/06/2024 08:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0806H from forward power direction [WEBSMS] | CLUZ
6/6/2024 6:15:30 AM | Mindanao Grid-06/06/2024 06:21: Baloi - Agus 5 138kV L de-energized at 0612H. (Planned Outage) [WEBSMS] | CMIN
6/6/2024 6:10:32 AM | Luzon Grid-06/06/2024 06:10: Santiago-NIA Baligatan HEPP 69kV Line (CO) de-energized at 0604H (Planned Outage) [WEBSMS] | CLUZ
6/6/2024 5:31:42 AM | [NSO Update] Mindanao Grid-06/06/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3239MW, PK=2488MW, RR=73MW, NetOpMargin: AM=678, PM=560, EVE=739 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/6/2024 5:29:03 AM | [NSO Update] Visayas Grid-06/06/2024 05:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2710MW, PK=2320MW, RR=91MW, NetOpMargin: AM=299, PM=215, EVE=240 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @317MW, CEDC U3 @75MW, GTEC @7MW, Power Barge 104-1 @5.5MW, Power Barge 104-3 @5MW, PDPP3-G @10MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW [WEBSMS] | CVIS
6/6/2024 5:27:16 AM | [NSO Update] Luzon Grid-06/06/2024 05:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15168MW, PK=11798MW, RR=494MW, NetOpMargin: AM=2877, PM=1862, EVE=1332 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @270MW, GNPD 2 @640MW, MSLC1 @200MW, MSLC2 @320MW, ILIJAN A @500MW [WEBSMS] | CLUZ
6/6/2024 4:03:31 AM | [NSO Update] Mindanao Grid-06/06/2024 04:09: Weather Update: Southwest Monsoon affecting the western sections of Luzon and Visayas. [WEBSMS] | CMIN
6/6/2024 4:03:19 AM | [NSO Update] Visayas Grid-06/06/2024 04:03: Weather Update: Southwest Monsoon affecting the western sections of Luzon and Visayas. [WEBSMS] | CVIS
6/6/2024 4:03:05 AM | [NSO Update] Luzon Grid-06/06/2024 04:03: Weather Update: Southwest Monsoon affecting the western sections of Luzon and Visayas. [WEBSMS] | CLUZ
6/6/2024 3:34:19 AM | Luzon Grid-06/06/2024 03:34: San Gabriel online at 0332H (Reserve Shutdown) [WEBSMS] | CLUZ
6/6/2024 12:25:28 AM | Visayas Grid-06/06/2024 00:25: Carcon-Sangi 34.5 kV L2 energized at 0022H, with clearance from MTD (Unplanned Outage) [WEBSMS] | CVIS
6/6/2024 12:13:24 AM | Visayas Grid-06/06/2024 00:13: Carcon-Sangi 34.5 kV L2 de-energized at 0007H, no PT supply (Unplanned Outage) [WEBSMS] | CVIS
6/5/2024 10:39:44 PM | Luzon Grid-06/05/2024 22:40: Pagbilao 2 online at 2239H (Unplanned Outage) [WEBSMS] | CLUZ
6/5/2024 10:12:04 PM | Luzon Grid-06/05/2024 22:12: San Juan-Calauan 230kV Line 1 de-energized at 2211H (Planned Outage) [WEBSMS] | CLUZ
6/5/2024 9:49:02 PM | Mindanao Grid-06/05/2024 21:55: WMPC DG10 Shutdown at 2146H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/5/2024 9:20:28 PM | Mindanao Grid-06/05/2024 21:26: WMPC DG4 Shutdown at 2116H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/5/2024 7:42:52 PM | [NSO Update] Visayas Grid-06/05/2024 19:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1941H with power going to Luzon [WEBSMS] | CVIS
6/5/2024 7:42:33 PM | [NSO Update] Luzon Grid-06/05/2024 19:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1941H with power going to Luzon [WEBSMS] | CLUZ
6/5/2024 7:41:49 PM | [NSO Update] Visayas Grid-06/05/2024 19:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1912H from reverse power direction [WEBSMS] | CVIS
6/5/2024 7:41:30 PM | [NSO Update] Luzon Grid-06/05/2024 19:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1912H from reverse power direction [WEBSMS] | CLUZ
6/5/2024 7:27:40 PM | Luzon Grid-06/05/2024 19:27: San Gabriel reserve shutdown at 1927H. [WEBSMS] | CLUZ
6/5/2024 6:09:58 PM | [NSO Update] Mindanao Grid-06/05/2024 18:16: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3199MW, PK=2388MW, RR=73MW, NetOpMargin: EVE=739 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/5/2024 6:08:45 PM | [NSO Update] Visayas Grid-06/05/2024 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2649MW, PK=2276MW, RR=91MW, NetOpMargin: EVE=282 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @300MW, CEDC U3 @75MW, GTEC @7MW, Power Barge 104-1 @5.5MW, PDPP3-G @10MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW, Power Barge 104-3 @5MW, LGPP @116.5MW, PGPP2-SOG 1 @18MW [WEBSMS] | CVIS
6/5/2024 6:07:07 PM | [NSO Update] Luzon Grid-06/05/2024 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13557MW, PK=10857MW, RR=478MW, NetOpMargin: EVE=2222 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @200MW, Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Ilijan A @500MW [WEBSMS] | CLUZ
6/5/2024 5:05:20 PM | Luzon Grid-06/05/2024 17:05: EERI 1 tripped at 1702H with 5MW load, on commissioing. [WEBSMS] | CLUZ
6/5/2024 4:59:15 PM | Mindanao Grid-06/05/2024 17:05: Agusan Lake Hydro (APC) online at 1655H. (Unplanned Outage) [WEBSMS] | CMIN
6/5/2024 4:58:10 PM | Luzon Grid-06/05/2024 16:58: EERI 1 online at 1656H, on commissioning . [WEBSMS] | CLUZ
6/5/2024 4:36:43 PM | Mindanao Grid-06/05/2024 16:42: Agus 5 Unit 2 online at 1633H. (Planned Outage) [WEBSMS] | CMIN
6/5/2024 3:49:41 PM | Mindanao Grid-06/05/2024 15:55: WMPC DG8 Shutdown at 1548H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/5/2024 2:48:50 PM | [NSO Update] Luzon Grid-06/05/2024 14:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1425H with power going to Visayas [WEBSMS] | CLUZ
6/5/2024 2:48:29 PM | [NSO Update] Visayas Grid-06/05/2024 14:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1425H with power going to Visayas [WEBSMS] | CVIS
6/5/2024 2:47:51 PM | [NSO Update] Luzon Grid-06/05/2024 14:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1415H from forward power direction [WEBSMS] | CLUZ
6/5/2024 2:47:31 PM | [NSO Update] Visayas Grid-06/05/2024 14:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1415H from forward power direction [WEBSMS] | CVIS
6/5/2024 1:02:03 PM | [NSO Update] Luzon Grid-06/05/2024 13:02: Update on System Advisory: The Luzon Grid Yellow Alert Notice issued today has been lifted effective 1300H. [WEBSMS] | CLUZ
6/5/2024 12:59:48 PM | [NSO Update] Luzon Grid-06/05/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14550MW, PK=13131MW, RR=536MW, NetOpMargin: PM=883, EVE=697 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Masinloc 1 @200MW, Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Ilijan A @500MW [WEBSMS] | CLUZ
6/5/2024 12:48:58 PM | Mindanao Grid-06/05/2024 12:55: WMPC DG8 Online at 1247H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/5/2024 12:41:25 PM | [NSO Update] Visayas Grid-06/05/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2856MW, PK=2503MW, RR=91MW, NetOpMargin: PM=261, EVE=246 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @313MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, Power Barge 104-1 @5.5MW, Power Barge 104-4 @6MW, PDPP3-G @10MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW, Power Barge 104-3 @5MW [WEBSMS] | CVIS
6/5/2024 12:39:43 PM | [NSO Update] Mindanao Grid-06/05/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3250MW, PK=2614MW, RR=73MW, NetOpMargin: PM=564, EVE=701 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/5/2024 12:02:33 PM | Visayas Grid-06/05/2024 12:02: Carcon-Sangi 34.5KV line 1 & Line 2 energized @ 1156H & 1158H respectively. ( Unplanned Outage ) [WEBSMS] | CVIS
6/5/2024 11:38:54 AM | Visayas Grid-06/05/2024 11:39: Carcon-Sangi 34.5KV line 1 & Line 2 auto tripped @1132H. ( Unplanned Outage ) [WEBSMS] | CVIS
6/5/2024 10:55:43 AM | Luzon Grid-06/05/2024 10:55: Kalayaan 4 with 125MW tripped at 1050H. Lowest system frequency was 59.83Hz. (Unplanned Outage) [WEBSMS] | CLUZ
6/5/2024 9:52:17 AM | Mindanao Grid-06/05/2024 09:58: WMPC DG4 Online at 0948H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/5/2024 8:58:54 AM | Visayas Grid-06/05/2024 08:59: Dumanjug 138KV Bus 1 de-energized @0837H. ( Planned Outage ) [WEBSMS] | CVIS
6/5/2024 8:50:00 AM | Mindanao Grid-06/05/2024 08:56: WMPC DG10 Online at 0846H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/5/2024 8:04:55 AM | Mindanao Grid-06/05/2024 08:10: Pulangi 4 Unit 2 shutdown at 0802H. PMS (Planned Outage) [WEBSMS] | CMIN
6/5/2024 8:03:12 AM | Mindanao Grid-06/05/2024 08:09: Agusan Lake Hydro (APC) shutdown at 0800H. Low Lake level elevation. (Unplanned Outage) [WEBSMS] | CMIN
6/5/2024 7:10:59 AM | Mindanao Grid-06/05/2024 07:17: GNPK UNIT 3 online at 0700H. (Unplanned Outage) [WEBSMS] | CMIN
6/5/2024 6:04:29 AM | Mindanao Grid-06/05/2024 06:10: Agus 5 Unit 2 shutdown at 0602H. P&E Request under MSRP Stage 1 Schedule III. (Planned Outage) [WEBSMS] | CMIN
6/5/2024 5:46:54 AM | [NSO Update] Luzon Grid-06/05/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=14733MW, PK=12772MW, RR=517MW, NetOpMargin: AM=1444, PM=183, EVE=626 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @200MW, Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Ilijan A @500MW [WEBSMS] | CLUZ
6/5/2024 5:41:52 AM | [NSO Update] Luzon Grid-06/05/2024 05:42: System Advisory: 05-Jun-2024, Luzon grid is on YELLOW Alert for interval hours 1400H-1600H and 1900H-2200H. Total capacity on forced outage is 1439.6MW. Total of de-rated capacity is 326MW. [WEBSMS] | CLUZ
6/5/2024 5:26:20 AM | [NSO Update] Mindanao Grid-06/05/2024 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3122MW, PK=2456MW, RR=73MW, NetOpMargin: AM=593, PM=423, EVE=579 Highest Unit O/L: GNPK 1,2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/5/2024 5:24:45 AM | [NSO Update] Visayas Grid-06/05/2024 05:24: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2786MW, PK=2506MW, RR=91MW, NetOpMargin: AM=189, PM=174, EVE=205 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @313MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, Power Barge 104-1 @5.5MW, Power Barge 104-4 @6MW, PDPP3-G @10MW, PDPP3-H @8MW, PDPP1 U5 @4.5MW, Power Barge 104-3 @5MW [WEBSMS] | CVIS
6/5/2024 4:05:03 AM | [NSO Update] Mindanao Grid-06/05/2024 04:11: Weather Update: Trough of a Low Pressure Area (LPA) affecting the eastern sections of Northern and Central Luzon. [WEBSMS] | CMIN
6/5/2024 4:04:31 AM | [NSO Update] Visayas Grid-06/05/2024 04:04: Weather Update: Trough of a Low Pressure Area (LPA) affecting the eastern sections of Northern and Central Luzon. [WEBSMS] | CVIS
6/5/2024 4:04:18 AM | [NSO Update] Luzon Grid-06/05/2024 04:04: Weather Update: Trough of a Low Pressure Area (LPA) affecting the eastern sections of Northern and Central Luzon. [WEBSMS] | CLUZ
6/5/2024 3:05:05 AM | Mindanao Grid-06/05/2024 03:11: GNPK Unit 3 (GN Power Kauswagan Ltd. Co. ) auto tripped at 0242H with a gross generation of 83.28 MW, caused by a Furnace Pressure Low-Low. Lowest system frequency recorded was 59.402Hz without ALD. Unplanned Outage. [WEBSMS] | CMIN
6/5/2024 12:26:51 AM | Mindanao Grid-06/05/2024 00:32: MCC Unit 1 online at 0018H from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
6/4/2024 10:30:00 PM | [NSO Update] Luzon Grid-06/04/2024 22:30: Update on System Advisory: The Luzon Grid Yellow Alert Notice issued today has been lifted effective 2226H. [WEBSMS] | CLUZ
6/4/2024 10:22:06 PM | Mindanao Grid-06/04/2024 22:28: WMPC DG 10 shutdown at 2216H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/4/2024 9:36:40 PM | [NSO Update] Visayas Grid-06/04/2024 21:36: Update on System Advisory: The Visayas Grid Yellow Alert Notice issued today has been lifted effective 2128H. [WEBSMS] | CVIS
6/4/2024 9:20:15 PM | Mindanao Grid-06/04/2024 21:26: WMPC DG 4 shutdown at 2116H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/4/2024 8:48:12 PM | Visayas Grid-06/04/2024 20:48: Calatrava-Cadiz 230kV Line 2 restored at 1905H. (Planned Outage) [WEBSMS] | CVIS
6/4/2024 7:05:50 PM | Visayas Grid-06/04/2024 19:05: Calatrava-Cadiz 230kV Line 2 restored at 1905H. (Planned Outage) [WEBSMS] | CVIS
6/4/2024 6:16:09 PM | [NSO Update] Mindanao Grid-06/04/2024 18:22: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3159MW, PK=2372MW, RR=73MW, NetOpMargin: EVE=714 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/4/2024 6:12:12 PM | [NSO Update] Visayas Grid-06/04/2024 18:12: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2708MW, PK=2598MW, RR=91MW, NetOpMargin: EVE=18 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @310MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, Power Barge 104-1 @5.5MW, Power Barge 104-4 @6MW, PDPP3-G @10MW, PDPP3-H @8MW, PDPP1 U2 @4MW, PDPP1 U5 @4.5MW, Power Barge 104-3 @5MW, PEDC 3 @120MW, PGPP1 @35MW [WEBSMS] | CVIS
6/4/2024 6:05:15 PM | [NSO Update] Visayas Grid-06/04/2024 18:05: System Advisory: 04-Jun-2024, Visayas grid is on YELLOW Alert for interval hours 1900H-2100H. Total capacity on forced outage is 373.6MW. Total of de-rated capacity is 313.8MW. [WEBSMS] | CVIS
6/4/2024 5:41:39 PM | [NSO Update] Luzon Grid-06/04/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=12851MW, PK=12277MW, RR=389MW, NetOpMargin: EVE=185 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @200MW, Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Ilijan A @537MW [WEBSMS] | CLUZ
6/4/2024 5:36:27 PM | Mindanao Grid-06/04/2024 17:42: Bunawan-Maco 138kV Line energized at 1727H, and looped at 1532H at the Bunawan SS side. From Unplanned Outage. [WEBSMS] | CMIN
6/4/2024 5:04:08 PM | [NSO Update] Visayas Grid-06/04/2024 17:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1654H with power going to Luzon [WEBSMS] | CVIS
6/4/2024 5:03:43 PM | [NSO Update] Luzon Grid-06/04/2024 17:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1654H with power going to Luzon [WEBSMS] | CLUZ
6/4/2024 5:02:17 PM | [NSO Update] Visayas Grid-06/04/2024 17:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1525H from forward power direction [WEBSMS] | CVIS
6/4/2024 5:01:56 PM | [NSO Update] Luzon Grid-06/04/2024 17:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1525H from forward power direction [WEBSMS] | CLUZ
6/4/2024 4:51:56 PM | Mindanao Grid-06/04/2024 16:57: WMPC DG 08 shutdown at 1617H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/4/2024 4:37:35 PM | Luzon Grid-06/04/2024 16:37: Concepcion-Clark 230kV Line 2 restored at 1632H (Unplanned Outage) [WEBSMS] | CLUZ
6/4/2024 4:29:59 PM | Luzon Grid-06/04/2024 16:30: QPPL online at 1629H (Unplanned Outage) [WEBSMS] | CLUZ
6/4/2024 4:05:59 PM | Luzon Grid-06/04/2024 16:06: Mexico-Concepcion 230kV Line 1 restored at 1605H (Unplanned Outage) [WEBSMS] | CLUZ
6/4/2024 3:54:31 PM | Mindanao Grid-06/04/2024 16:00: Bunawan-Maco 138kV Line auto tripped at 1542H. Unplanned Outage. Note: Advised for immediate line patrol. [WEBSMS] | CMIN
6/4/2024 3:43:22 PM | Luzon Grid-06/04/2024 15:43: Mexico-Concepcion 230kV Line 1 and Concepcion-Clark 230kV Line 2 tripped at 1538H (Unplanned Outage) [WEBSMS] | CLUZ
6/4/2024 3:02:19 PM | Mindanao Grid-06/04/2024 15:08: Bunawan SS 300MVA 230/138/13kV Power Transformer 2 successfully energized/restored at 1457H after clearance from MTD-B management. From Unplanned Outage. [WEBSMS] | CMIN
6/4/2024 2:29:51 PM | Mindanao Grid-06/04/2024 14:35: WMPC DG08 online at 1353H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/4/2024 2:09:13 PM | Mindanao Grid-06/04/2024 14:15: Bunawan SS 300MVA 230/138/13kV Power Transformer 2 autotripped at 1401H (For immediate investigation by MTD-B. Unplanned Outage) [WEBSMS] | CMIN
6/4/2024 1:55:48 PM | Mindanao Grid-06/04/2024 14:01: WMPC DG 08 shutdown at 1313H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/4/2024 12:55:15 PM | [NSO Update] Luzon Grid-06/04/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14009MW, PK=13289MW, RR=496MW, NetOpMargin: PM=224, EVE=184 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Masinloc 1 @210MW, Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Ilijan A @540MW [WEBSMS] | CLUZ
6/4/2024 12:47:38 PM | [NSO Update] Visayas Grid-06/04/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2905MW, PK=2584MW, RR=91MW, NetOpMargin: PM=229, EVE=232 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @317MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, Power Barge 104-1 @5.5MW, Power Barge 104-4 @6MW, PDPP3-G @5MW, PDPP3-H @8MW, PDPP1 U2 @4MW, PDPP1 U5 @4.5MW [WEBSMS] | CVIS
6/4/2024 12:46:06 PM | [NSO Update] Mindanao Grid-06/04/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3213MW, PK=2482MW, RR=73MW, NetOpMargin: PM=658, EVE=792 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW, GNPK3 @80MW [WEBSMS] | CMIN
6/4/2024 12:44:33 PM | Luzon Grid-06/04/2024 12:44: Dasmarinas-Ternate 115kV restored at 1243H (Unplanned Outage) [WEBSMS] | CLUZ
6/4/2024 11:40:45 AM | Luzon Grid-06/04/2024 11:40: Bay-Solarace 69kV Li & L2 restored at 1138H and 1140H (Unplanned Outage) [WEBSMS] | CLUZ
6/4/2024 10:54:03 AM | Mindanao Grid-06/04/2024 11:00: WMPC DG08 online at 1041H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/4/2024 10:45:27 AM | Luzon Grid-06/04/2024 10:45: EERI 1 shutdown at 1039H, on-commissioning. [WEBSMS] | CLUZ
6/4/2024 10:16:34 AM | Mindanao Grid-06/04/2024 10:22: Pulangi 4 Unit 3 online at 1005H. (Unplanned Outage) [WEBSMS] | CMIN
6/4/2024 10:05:47 AM | Luzon Grid-06/04/2024 10:06: Dasmarinas-Ternate 115kV de-energized at 1002H (Unplanned Outage) [WEBSMS] | CLUZ
6/4/2024 9:53:03 AM | Luzon Grid-06/04/2024 09:53: Bay-Solarace 69kV de-energized at 0938H (Unplanned Outage) [WEBSMS] | CLUZ
6/4/2024 9:22:34 AM | Luzon Grid-06/04/2024 09:22: ERRI 1 online at 0916H, on-commissioning. [WEBSMS] | CLUZ
6/4/2024 9:22:32 AM | Mindanao Grid-06/04/2024 09:28: WMPC DG04 online at 0920H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/4/2024 8:58:09 AM | Mindanao Grid-06/04/2024 09:04: WMPC DG10 online at 0840H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/4/2024 7:09:39 AM | [NSO Update] Mindanao Grid-06/04/2024 07:15: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3213MW, PK=2390MW, RR=73MW, NetOpMargin: AM=751, PM=624, EVE=747 Highest Unit O/L: GNPK 1,2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW, GNPK3 @80MW [WEBSMS] | CMIN
6/4/2024 6:05:05 AM | [NSO Update] Luzon Grid-06/04/2024 06:05: System Advisory: 04-June-2024 Luzon grid is on YELLOW Alert for interval hours 1400H-1700H and 1900H-2400H. Total capacity on forced outage is 1884.8MW. Total of de-rated capacity is 396MW. [WEBSMS] | CLUZ
6/4/2024 6:01:31 AM | [NSO Update] Visayas Grid-06/04/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2984MW, PK=2454MW, RR=91MW, NetOpMargin: AM=439, PM=284, EVE=237 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @313MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, Power Barge 104-1 @5.5MW, Power Barge 104-4 @6MW, PDPP3-E @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/4/2024 5:55:50 AM | [NSO Update] Luzon Grid-06/04/2024 05:56: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=14710MW, PK=12851MW, RR=496MW, NetOpMargin: AM=1363, PM=322, EVE=186 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @210MW, Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Ilijan A @500MW [WEBSMS] | CLUZ
6/4/2024 4:10:15 AM | [NSO Update] Mindanao Grid-06/04/2024 04:16: Weather update: Frontal System affecting Extreme Northern Luzon [WEBSMS] | CMIN
6/4/2024 4:09:53 AM | [NSO Update] Visayas Grid-06/04/2024 04:09: Weather update: Frontal System affecting Extreme Northern Luzon [WEBSMS] | CVIS
6/4/2024 4:06:32 AM | [NSO Update] Luzon Grid-06/04/2024 04:06: Weather update: Frontal System affecting Extreme Northern Luzon [WEBSMS] | CLUZ
6/4/2024 1:20:46 AM | Visayas Grid-06/04/2024 01:20: Carcon-Sangi 34.5KV line 2 energized at 0118H. (Unplanned Outage) [WEBSMS] | CVIS
6/4/2024 12:24:26 AM | Visayas Grid-06/04/2024 00:24: Carcon-Sangi 34.5KV line 2 tripped at 2358H. (Unplanned Outage) [WEBSMS] | CVIS
6/4/2024 12:17:26 AM | [NSO Update] Luzon Grid-06/04/2024 00:17: Update on System Advisory: Luzon Grid Yellow Alert Notice issued on June 03, 2024 has been lifted effective 0015H of June 04, 2024. [WEBSMS] | CLUZ
6/4/2024 12:08:52 AM | Mindanao Grid-06/04/2024 00:14: PULANGI 4 Unit 2 online at 0002H from outage OMC. (Unplanned Outage) [WEBSMS] | CMIN
6/3/2024 10:49:50 PM | Luzon Grid-06/03/2024 22:50: Sual Unit 1 online at 2248H (Unplanned Outage) [WEBSMS] | CLUZ
6/3/2024 10:44:14 PM | Mindanao Grid-06/03/2024 22:50: Update: Pulangi 4 Unit 3 with 40MW load tripped at 2235H. Indication: Main Transformer trip. No ALD activation, lowest frequency recorded at 59.784Hz. (Unplanned Outage) [WEBSMS] | CMIN
6/3/2024 10:38:21 PM | Mindanao Grid-06/03/2024 22:44: Pulangi 4 Unit 3 with 20MW load tripped at 2235H. Indication: Main Transformer trip. (Unplanned Outage) [WEBSMS] | CMIN
6/3/2024 9:50:16 PM | Mindanao Grid-06/03/2024 21:56: WMPC DG 10 shutdown at 2146H. End of MRU - System Voltage Requirement. at 2146H [WEBSMS] | CMIN
6/3/2024 9:15:13 PM | Luzon Grid-06/03/2024 21:15: Sual unit 1 tripped at 2111H (Unplanned Outage) [WEBSMS] | CLUZ
6/3/2024 9:05:53 PM | Luzon Grid-06/03/2024 21:06: Sual Unit 1 online at 2104H (Unplanned Outage) [WEBSMS] | CLUZ
6/3/2024 8:31:14 PM | Mindanao Grid-06/03/2024 20:37: WMPC DG 4 shutdown at 2021H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/3/2024 7:58:03 PM | Luzon Grid-06/03/2024 19:58: San Lorenzo Module 50 shutdown at 1956H (Unplanned Outage) [WEBSMS] | CLUZ
6/3/2024 7:08:15 PM | Visayas Grid-06/03/2024 19:08: Bohol sub grid MLD last feeder in at 1856H to avoid overloading of Leyte Bohol subcable (Unplanned Outage) [WEBSMS] | CVIS
6/3/2024 6:59:40 PM | [NSO Update] Visayas Grid-06/03/2024 18:59: SO-initiated Market Intervention for Visayas has been lifted today at 1856H. Market operations will resume starting interval 1905H. [WEBSMS] | CVIS
6/3/2024 5:51:30 PM | [NSO Update] Luzon Grid-06/03/2024 17:51: Update on System Advisory: 03-June-2024 Luzon grid is on YELLOW Alert for interval hours 1900H-2400H. Total capacity on forced outage is 2266.8MW. Total of de-rated capacity is 416MW. [WEBSMS] | CLUZ
6/3/2024 5:51:29 PM | Mindanao Grid-06/03/2024 17:57: WMPC DG08 shutdown at 1724H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/3/2024 5:42:16 PM | [NSO Update] Mindanao Grid-06/03/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3168MW, PK=2489MW, RR=73MW, NetOpMargin: EVE=606 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/3/2024 5:41:19 PM | [NSO Update] Visayas Grid-06/03/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2669MW, PK=2348MW, RR=90MW, NetOpMargin: EVE=232 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @317MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, Power Barge 104-1 @5.5MW, Power Barge 104-4 @6MW, PDPP3-E @10MW, PDPP3-H @8MW, PDPP3-G @10MW [WEBSMS] | CVIS
6/3/2024 5:38:45 PM | [NSO Update] Luzon Grid-06/03/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=13008MW, PK=12209MW, RR=471MW, NetOpMargin: EVE=328 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @190MW, Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Ilijan A @500MW [WEBSMS] | CLUZ
6/3/2024 5:37:50 PM | [NSO Update] Luzon Grid-06/03/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=13008MW, PK=12209MW, RR=471MW, NetOpMargin: EVE=328 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @190MW, Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Ilijan A @500MW [WEBSMS] | CLUZ
6/3/2024 5:36:57 PM | Mindanao Grid-06/03/2024 17:42: Agusan Lake Mainit Hydro online at 1702H. (Unplanned Outage) [WEBSMS] | CMIN
6/3/2024 4:21:22 PM | Luzon Grid-06/03/2024 16:21: Concepcion-Mexico 230kV Line 1 restored at 1620H (Unplanned Outage) [WEBSMS] | CLUZ
6/3/2024 4:04:02 PM | Luzon Grid-06/03/2024 16:04: Concepcion-Clark 230kV Line 2 restored at 1603H (Unplanned Outage) [WEBSMS] | CLUZ
6/3/2024 3:37:09 PM | Luzon Grid-06/03/2024 15:37: Concepcion-Mexico 230kV Line 1 and Concepcion-Clark 230kV Line 2 tripped at 1531H (Unplanned Outage) [WEBSMS] | CLUZ
6/3/2024 3:14:01 PM | [NSO Update] Visayas Grid-06/03/2024 15:14: SO-initiated Market Intervention for Visayas is issued today starting interval 1510H due to MLD implementation to prevent the overloading of Ubay-Maasin 138kV Line. [WEBSMS] | CVIS
6/3/2024 1:15:23 PM | [NSO Update] Mindanao Grid-06/03/2024 13:21: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3242MW, PK=2594MW, RR=73MW, NetOpMargin: PM=576, EVE=697 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/3/2024 1:13:56 PM | [NSO Update] Visayas Grid-06/03/2024 13:14: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2933MW, PK=2553MW, RR=86MW, NetOpMargin: PM=294, EVE=248 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @317MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-E @10MW, Power Barge 104-1 @5.5MW, Power Barge 104-3 @5MW, Power Barge 104-4 @6MW, PDPP3-H @8MW, PDPP3-G @10MW [WEBSMS] | CVIS
6/3/2024 1:08:14 PM | [NSO Update] Luzon Grid-06/03/2024 13:08: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14457MW, PK=13484MW, RR=491MW, NetOpMargin: PM=483, EVE=239 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @180MW, Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Ilijan A @500MW [WEBSMS] | CLUZ
6/3/2024 1:04:20 PM | [NSO Update] Luzon Grid-06/03/2024 13:04: Update on System Advisory: 03-June-2024 Luzon grid is on YELLOW Alert for interval hours 1400H-1600H and 1900H-2200H. Total capacity on forced outage is 2266.8MW. Total of de-rated capacity is 426MW. [WEBSMS] | CLUZ
6/3/2024 12:52:16 PM | Mindanao Grid-06/03/2024 12:58: WMPC DG08 online at 1250H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/3/2024 10:13:40 AM | Mindanao Grid-06/03/2024 10:19: WMPC DG04 online at 1009H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/3/2024 9:06:44 AM | Mindanao Grid-06/03/2024 09:12: PULANGI 4 Unit 2 online at 0901H from outage OMC. (Unplanned Outage) [WEBSMS] | CMIN
6/3/2024 8:55:09 AM | Mindanao Grid-06/03/2024 09:01: WMPC DG10 online at 0852H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/3/2024 8:05:16 AM | Mindanao Grid-06/03/2024 08:11: undefined at 0800H Agusan Lake Mainit Hydro shutdown at 0800H due to low water elevation. [WEBSMS] | CMIN
6/3/2024 7:20:37 AM | Visayas Grid-06/03/2024 07:20: Calatrava-Cadiz 230kV Line 2 de-energized at 0721H. (Planned Outage) [WEBSMS] | CVIS
6/3/2024 6:02:15 AM | Luzon Grid-06/03/2024 06:02: Binan 300MVA T01 restored at 0602H (Planned Outage) [WEBSMS] | CLUZ
6/3/2024 6:01:08 AM | [NSO Update] Mindanao Grid-06/03/2024 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3244MW, PK=2474MW, RR=73MW, NetOpMargin: AM=698, PM=554, EVE=743 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/3/2024 5:58:47 AM | [NSO Update] Visayas Grid-06/03/2024 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2808MW, PK=2456MW, RR=83MW, NetOpMargin: AM=269, PM=292, EVE=236 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @317MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-E @10MW, Power Barge 104-1 @5.5MW, Power Barge 104-3 @5MW, Power Barge 104-4 @6MW, PDPP3-H @8MW, PDPP3-G @10MW [WEBSMS] | CVIS
6/3/2024 5:52:32 AM | [NSO Update] Luzon Grid-06/03/2024 05:52: System Advisory: 03-June-2024 Luzon grid is on YELLOW Alert for interval hours 1500H-1600H and 2000H-2200H. Total capacity on forced outage is 2266.8MW. Total of de-rated capacity is 426MW. [WEBSMS] | CLUZ
6/3/2024 5:47:36 AM | [NSO Update] Luzon Grid-06/03/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=14414MW, PK=12465MW, RR=489MW, NetOpMargin: AM=1460, PM=856, EVE=439 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @180MW, Masinloc 2 @320MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Ilijan A @500MW [WEBSMS] | CLUZ
6/3/2024 4:27:14 AM | [NSO Update] Mindanao Grid-06/03/2024 04:33: Weather Update: Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CMIN
6/3/2024 4:27:06 AM | [NSO Update] Visayas Grid-06/03/2024 04:27: Weather Update: Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CVIS
6/3/2024 4:26:59 AM | [NSO Update] Luzon Grid-06/03/2024 04:27: Weather Update: Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CLUZ
6/3/2024 12:35:27 AM | [NSO Update] Luzon Grid-06/03/2024 00:35: 03-Jun-2024, ERC has lifted market suspension for Luzon grid today at 0035H. Market operations will resume starting interval 0040H. [WEBSMS] | CLUZ
6/2/2024 11:17:03 PM | Visayas Grid-06/02/2024 23:17: Cebu- Mandaue 138KV Line 1 & 2 in parallel operation @2308H. ( Planned Outage ) [WEBSMS] | CVIS
6/2/2024 11:02:46 PM | Luzon Grid-06/02/2024 23:03: Botolan-Labrador 230kV Line restored at 2300H (Planned Outage) [WEBSMS] | CLUZ
6/2/2024 9:51:36 PM | Luzon Grid-06/02/2024 21:51: Binan 300MVA T01 de-energized at 2151H (Planned Outage) [WEBSMS] | CLUZ
6/2/2024 7:54:19 PM | Luzon Grid-06/02/2024 19:54: Currimao-Laoag 115kV Line main protection at Laoag side commissioned at 1951H. [WEBSMS] | CLUZ
6/2/2024 7:44:58 PM | Luzon Grid-06/02/2024 19:45: Currimao-Laoag 115kV Line restored at 1943H, on commissioning of Main protection at Laoag side . [WEBSMS] | CLUZ
6/2/2024 7:36:15 PM | Mindanao Grid-06/02/2024 19:42: WMPC DG10 shutdown at 1920H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/2/2024 6:16:20 PM | Mindanao Grid-06/02/2024 18:22: Sultan Kudarat SS 138kV 100MVA Power Transformer #2 (7XF02SKU) energized/restored at 1805H. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
6/2/2024 6:12:16 PM | Mindanao Grid-06/02/2024 18:18: Kibawe-Sultan Kudarat (7LI1KIB-SKU) 138kV line energized at 1801H, and looped at 1803H at the SKU SS side. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
6/2/2024 6:01:31 PM | Luzon Grid-06/02/2024 18:01: Daraga 230kV Bus 2 restored at 1801H (Planned Outage) [WEBSMS] | CLUZ
6/2/2024 5:53:06 PM | [NSO Update] Luzon Grid-06/02/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13264MW, PK=11365MW, RR=294MW, NetOpMargin: EVE=1605 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @220MW, GNPD 2 @640MW, MSLC1 @180MW, MSLC2 @290MW, ILIJAN A@500MW [WEBSMS] | CLUZ
6/2/2024 5:50:52 PM | [NSO Update] Visayas Grid-06/02/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2670MW, PK=2186MW, RR=90MW, NetOpMargin: EVE=394 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @313MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-E @10MW, Power Barge 104-1 @5.5MW, Power Barge 104-3 @6MW, Power Barge 104-4 @6MW, PDPP3-H @8MW, PDPP3-G @10MW [WEBSMS] | CVIS
6/2/2024 5:47:59 PM | [NSO Update] Mindanao Grid-06/02/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3191MW, PK=2160MW, RR=73MW, NetOpMargin: EVE=958 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/2/2024 5:47:57 PM | Luzon Grid-06/02/2024 17:48: Botolan-Labrador 230kV Line de-energized at 1746H (Planned Outage) [WEBSMS] | CLUZ
6/2/2024 5:22:56 PM | Mindanao Grid-06/02/2024 17:28: Manolo-Maramag 138kV Line 2 energized/restored at 1713H, and looped at 1716H at the Maramag SS side. From Planned Outage/Non-GOMP. Note: (P&E requested shutdown). [WEBSMS] | CMIN
6/2/2024 5:19:25 PM | Luzon Grid-06/02/2024 17:19: San Juan-Calauan 230kV Line 2 restored at 1719H (Planned Outage) [WEBSMS] | CLUZ
6/2/2024 5:02:17 PM | Mindanao Grid-06/02/2024 17:08: Jasaan SS 138kV 100MVA Power Transformer 2 energized/restored at 1651H. From Planned Outage/GOMP. [WEBSMS] | CMIN
6/2/2024 4:50:14 PM | Mindanao Grid-06/02/2024 16:56: Maramag SS 138kV Bu #1 energized/restored at 1637H. From Planned Outage/Non-GOMP. Note: (P&E requested shutdown). [WEBSMS] | CMIN
6/2/2024 3:56:43 PM | Visayas Grid-06/02/2024 15:56: Magdugo-DaanLungsod 138 kV line energized at 1555H (Planned Outage) [WEBSMS] | CVIS
6/2/2024 3:34:22 PM | Mindanao Grid-06/02/2024 15:40: Davao - Bunawan 138kV Line 1 energized/restored at 1529H. From Planned Outage/Non-GOMP. (Note: P&E requested shutdown). [WEBSMS] | CMIN
6/2/2024 3:06:49 PM | Visayas Grid-06/02/2024 15:06: DaanLungsod SS 138 kV bus 2 energized at 1501H (Planned Outage) [WEBSMS] | CVIS
6/2/2024 2:12:57 PM | Luzon Grid-06/02/2024 14:13: Binga-La Trinidad 230kV Line 1 restored at 1411H (Planned Outage) [WEBSMS] | CLUZ
6/2/2024 1:11:46 PM | [NSO Update] Mindanao Grid-06/02/2024 13:17: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3234MW, PK=2119MW, RR=73MW, NetOpMargin: PM=1042, EVE=882 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/2/2024 1:10:36 PM | [NSO Update] Visayas Grid-06/02/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2873MW, PK=2012MW, RR=86MW, NetOpMargin: PM=775, EVE=308 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @317MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-E @10MW, Power Barge 104-1 @5.5MW, Power Barge 104-2 @5MW, Power Barge 104-3 @6MW, Power Barge 104-4 @6MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/2/2024 1:06:30 PM | [NSO Update] Luzon Grid-06/02/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14019MW, PK=11466MW, RR=311MW, NetOpMargin: PM=2242, EVE=939 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @180MW, Masinloc 2 @280MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Ilijan A @500MW, Sual 2 @600MW [WEBSMS] | CLUZ
6/2/2024 1:03:16 PM | Mindanao Grid-06/02/2024 13:09: WMPC DG10 online at 1259H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/2/2024 12:28:35 PM | Visayas Grid-06/02/2024 12:28: Daanbantayan-Tabango 230kV Line 2 energized at 1226H (Unplanned Outage) [WEBSMS] | CVIS
6/2/2024 12:02:23 PM | Visayas Grid-06/02/2024 12:02: Daanbantayan Ss 230kV bus 2 energized at 1156H (Unplanned Outage) [WEBSMS] | CVIS
6/2/2024 11:00:31 AM | Luzon Grid-06/02/2024 11:00: Mexico-San Rafael 230kV Line 1 restored at 1100H (Planned Outage) [WEBSMS] | CLUZ
6/2/2024 9:27:19 AM | Visayas Grid-06/02/2024 09:27: Daanbantayan Ss 230kV bus 2 de-energized at 0923H (Unplanned Outage) [WEBSMS] | CVIS
6/2/2024 9:02:18 AM | Visayas Grid-06/02/2024 09:02: Daanbantayan-Tabango 230kV Line 2 de-energized at 0854H (Unplanned Outage) [WEBSMS] | CVIS
6/2/2024 8:15:36 AM | Mindanao Grid-06/02/2024 08:21: Kibawe-Sultan Kudarat138kV line de-energized at 0801H (Planned Outage). [WEBSMS] | CMIN
6/2/2024 8:12:33 AM | Mindanao Grid-06/02/2024 08:18: Sultan Kudarat SS 100MVA Power Transformer 2 de-energized at 0750H (Planned Outage). [WEBSMS] | CMIN
6/2/2024 8:05:18 AM | Luzon Grid-06/02/2024 08:05: Binga-La Trinidad 230kV Line 1 de-energized at 0804H (Planned Outage) [WEBSMS] | CLUZ
6/2/2024 7:08:05 AM | Luzon Grid-06/02/2024 07:08: Daraga 230kV Bus 2 de-energized at 0707H (Planned Outage) [WEBSMS] | CLUZ
6/2/2024 7:04:54 AM | Luzon Grid-06/02/2024 07:05: San Juan-Calauan 230kV Line 2 de-energized at 0703H (Planned Outage) [WEBSMS] | CLUZ
6/2/2024 6:52:20 AM | Mindanao Grid-06/02/2024 06:58: Maramag SS 138kV Bus 1 de-energized at 0649H. (Planned Outage). [WEBSMS] | CMIN
6/2/2024 6:43:12 AM | Visayas Grid-06/02/2024 06:43: Magdugo-Daanlungsod 138kV Line de-energized at 0638H (Planned Outage) [WEBSMS] | CVIS
6/2/2024 6:35:26 AM | Mindanao Grid-06/02/2024 06:41: Manolo-Maramag 138kV Line 2 de-energized at 0633H. (Planned Outage). [WEBSMS] | CMIN
6/2/2024 6:11:31 AM | Mindanao Grid-06/02/2024 06:17: Jasaan SS 138kV 100MVA Power Transformer 2 de-energized at 0608H (Planned Outage). [WEBSMS] | CMIN
6/2/2024 6:02:58 AM | [NSO Update] Luzon Grid-06/02/2024 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14276MW, PK=10763MW, RR=351MW, NetOpMargin: AM=3162, PM=2377, EVE=832 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @200MW, Masinloc 2 @320MW, Pagbilao 1 @150MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Ilijan A @500MW, Sual 2 @600MW [WEBSMS] | CLUZ
6/2/2024 5:54:32 AM | Mindanao Grid-06/02/2024 06:00: Baloi - Villanueva 230kV Line 1 energized/restored at 0553H. (Planned Outage). [WEBSMS] | CMIN
6/2/2024 5:37:50 AM | [NSO Update] Visayas Grid-06/02/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2899MW, PK=1998MW, RR=83MW, NetOpMargin: AM=818, PM=629, EVE=333 Highest Unit O/L: THVI 1& 2@169MW Derated Plant: Leyte A @317MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-E @10MW, Power Barge 104-2 @6MW, Power Barge 104-3 @6MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/2/2024 5:37:41 AM | [NSO Update] Mindanao Grid-06/02/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3195MW, PK=2025MW, RR=73MW, NetOpMargin: AM=1097, PM=922, EVE=836 Highest Unit O/L: GNPK 1, 2, 3 &4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/2/2024 5:04:46 AM | Mindanao Grid-06/02/2024 05:10: Agusan Lake Mainit Hydro shutdown at 0502H due to low water elevation. [WEBSMS] | CMIN
6/2/2024 4:16:10 AM | Mindanao Grid-06/02/2024 04:22: Baloi - Villanueva 230kV Line 1 de-energized at 0414H. (Planned Outage). [WEBSMS] | CMIN
6/2/2024 4:08:59 AM | [NSO Update] Mindanao Grid-06/02/2024 04:14: Weather Advisory: Easterlies affecting the eastern sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
6/2/2024 4:08:46 AM | [NSO Update] Luzon Grid-06/02/2024 04:08: Weather Advisory: Easterlies affecting the eastern sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
6/2/2024 4:08:43 AM | [NSO Update] Visayas Grid-06/02/2024 04:08: Weather Advisory: Easterlies affecting the eastern sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
6/2/2024 4:00:10 AM | Luzon Grid-06/02/2024 04:00: Ilijan A GT 1-2 online at 0357H (Unplanned Outage) [WEBSMS] | CLUZ
6/2/2024 3:08:15 AM | Luzon Grid-06/02/2024 03:08: Sual 1 shutdown at 0305H (Unplanned Outage) [WEBSMS] | CLUZ
6/2/2024 2:34:12 AM | Mindanao Grid-06/02/2024 02:40: Power Source (PPEI) shutdown at 0215H. PMS(Non-GOMP). Unplanned Outage. [WEBSMS] | CMIN
6/2/2024 2:11:40 AM | [NSO Update] Luzon Grid-06/02/2024 02:11: Update on System Advisory: The Luzon Grid Yellow Alert Notice issued today has been lifted at 0207H. [WEBSMS] | CLUZ
6/2/2024 2:07:18 AM | Luzon Grid-06/02/2024 02:07: Ilijan A ST-1 online at 0206H. (Unplanned Outage) [WEBSMS] | CLUZ
6/2/2024 1:21:17 AM | Luzon Grid-06/02/2024 01:21: Duhat SS 300MVA T02 de-energized at 0120H (Customer Owned Planned Outage) [WEBSMS] | CLUZ
6/2/2024 1:05:50 AM | Luzon Grid-06/02/2024 01:06: Ilijan A GT 1-1 online at 0105H. (Unplanned Outage) [WEBSMS] | CLUZ
6/2/2024 12:59:41 AM | Luzon Grid-06/02/2024 00:59: Mexico-San Rafael 230kV Line 1 de-energized at 0059H. (Planned Outage) [WEBSMS] | CLUZ
6/2/2024 12:39:32 AM | [NSO Update] Luzon Grid-06/02/2024 00:39: Update on System Advisory: Luzon Grid Red Alert Notice issued June 1 is lifted at 0035H of June 2. Luzon Grid is still on Yellow Alert for intervals 0100H-0200H today. [WEBSMS] | CLUZ
6/2/2024 12:32:12 AM | Luzon Grid-06/02/2024 00:32: Quezon (Balintawak) SS 300MVA T07 (CO) restored at 0029H. (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 11:56:35 PM | Luzon Grid-06/01/2024 23:56: Manual Load Dropping (MLD) for MERALCO feeders were restored at 2347H. [WEBSMS] | CLUZ
6/1/2024 11:40:55 PM | Luzon Grid-06/01/2024 23:41: Manual Load Dropping (MLD) for NGCP feeders were restored at 2330H. [WEBSMS] | CLUZ
6/1/2024 9:18:01 PM | Mindanao Grid-06/01/2024 21:23: WMPC DG10 shutdown at 2117H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/1/2024 9:14:14 PM | Luzon Grid-06/01/2024 21:14: Ilijan B GT2-2 online at 2113H. (Unplanned Outage) [WEBSMS] | CLUZ
6/1/2024 7:54:29 PM | Luzon Grid-06/01/2024 19:54: Sta. Rita 20 online at 1949H. (Unplanned Outage) [WEBSMS] | CLUZ
6/1/2024 7:13:52 PM | Luzon Grid-06/01/2024 19:14: Ilijan B ST-2 online at 1913H. (Unplanned Outage) [WEBSMS] | CLUZ
6/1/2024 6:57:33 PM | Mindanao Grid-06/01/2024 19:03: Agusan Lake Mainit Hydro online at 1848H. (Unplanned Outage) [WEBSMS] | CMIN
6/1/2024 6:29:11 PM | Luzon Grid-06/01/2024 18:29: Taytay SS 300MVA T03 restored at 1822H (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 6:27:06 PM | Mindanao Grid-06/01/2024 18:33: Update: Lamsan Power Corp. with 13.25MW tripped at 1751H. Indication: Generator Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
6/1/2024 6:18:07 PM | Mindanao Grid-06/01/2024 18:24: Lamsan Power Corp. online at 1811H. From Forced outage. (Unplanned Outage) [WEBSMS] | CMIN
6/1/2024 6:14:58 PM | [NSO Update] Mindanao Grid-06/01/2024 18:20: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3181MW, PK=2374MW, RR=73MW, NetOpMargin: EVE=734 Highest Unit O/L: GNPK 1,2, 3 &4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/1/2024 6:13:22 PM | [NSO Update] Visayas Grid-06/01/2024 18:13: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2703MW, PK=2366MW, RR=91MW, NetOpMargin: EVE=246 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @313MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-E @10MW, Power Barge 104-2 @6MW, Power Barge 104-3 @6MW, PDPP3-H @8MW Remarks: [WEBSMS] | CVIS
6/1/2024 6:13:08 PM | Mindanao Grid-06/01/2024 18:19: Pulangi 4 U2 shutdown at 1811H. Low Water Forebay Elevation. Outside Management Control. (Unplanned outage) [WEBSMS] | CMIN
6/1/2024 6:12:29 PM | Luzon Grid-06/01/2024 18:12: Ilijan B GT2-1 online at 1811H. (Unplanned Outage) [WEBSMS] | CLUZ
6/1/2024 6:06:14 PM | [NSO Update] Luzon Grid-06/01/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=11261MW, PK=11843MW, RR=384MW, NetOpMargin: EVE=0 Highest Unit O/L: GNPD 1@668MW Derated Plant: Masinloc 1 @200MW, Masinloc 2 @320MW, Masinloc 3 @325MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Sual 1 @300MW, Sual 2 @620MW, Magat 1 @2MW, Magat 2 @2MW, Magat 3 @2MW, Magat 4 @2MW [WEBSMS] | CLUZ
6/1/2024 5:57:18 PM | Mindanao Grid-06/01/2024 18:03: Lamsan Power Corp. with 13.25MW tripped at 1751H. Details to follow (Unplanned Outage) [WEBSMS] | CMIN
6/1/2024 5:08:22 PM | Luzon Grid-06/01/2024 17:08: Binga - Nagsaag 230kV Line 2 auto-tripped/auto-reclosed at 1705H. (Unplanned Outage) [WEBSMS] | CLUZ
6/1/2024 4:54:31 PM | Mindanao Grid-06/01/2024 17:00: Baloi SS 230kV 300MVA Transformer #2 energized at 1651H. (Planned Outage). [WEBSMS] | CMIN
6/1/2024 4:53:38 PM | Mindanao Grid-06/01/2024 16:59: WMPC DG03 shutdown at 1652H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/1/2024 4:50:12 PM | Luzon Grid-06/01/2024 16:50: Bayombong - Santiago 230kV L1 restored at 1650H (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 3:57:05 PM | [NSO Update] Luzon Grid-06/01/2024 15:57: Update on System Advisory: 01-June-2024 Luzon Grid is on RED Alert for interval hours 1500H-2400H. Total capacity on forced outage is 3828.3MW. Total of de-rated capacity is 699MW. [WEBSMS] | CLUZ
6/1/2024 3:26:40 PM | Mindanao Grid-06/01/2024 15:32: WMPC DG08 shutdown at 1525H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/1/2024 2:55:52 PM | Luzon Grid-06/01/2024 14:56: June 01, 2024: Manual Load Dropping (MLD) for NGCP & Meralco feeders started at 1355H and 1407H, respectively. [WEBSMS] | CLUZ
6/1/2024 2:25:48 PM | Luzon Grid-06/01/2024 14:25: Bauang-Bacnotan 230kV Line restored at 1424H. (Unplanned Outage) [WEBSMS] | CLUZ
6/1/2024 1:54:08 PM | Luzon Grid-06/01/2024 13:54: Pagbilao Unit 1 online at 1353H (Unplanned Outage) [WEBSMS] | CLUZ
6/1/2024 1:30:23 PM | Mindanao Grid-06/01/2024 13:36: WMPC DG08 online at 1328H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/1/2024 1:05:37 PM | Luzon Grid-06/01/2024 13:05: Demand Control Imminent Warning (DCIW) is issued at 1305H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
6/1/2024 12:54:54 PM | [NSO Update] Luzon Grid-06/01/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=12691MW, PK=12634MW, RR=398MW, NetOpMargin: PM=0, EVE=0 Highest Unit O/L: GNPD 1@668MW Derated Plant: CLC2 @220MW, GNPD 2 @640MW, MSLC1 @230MW, MSLC2 @320MW, MSLC3 @325MW, SUAL 1 @300MW [WEBSMS] | CLUZ
6/1/2024 12:42:52 PM | [NSO Update] Mindanao Grid-06/01/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3217MW, PK=2483MW, RR=73MW, NetOpMargin: PM=662, EVE=684 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/1/2024 12:32:47 PM | [NSO Update] Visayas Grid-06/01/2024 12:32: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2950MW, PK=2446MW, RR=91MW, NetOpMargin: PM=412, EVE=316 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @308MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-E @10MW, PDPP3-H @8MW [WEBSMS] | CVIS
6/1/2024 12:25:07 PM | Luzon Grid-06/01/2024 12:25: Bauang-Bacnotan 230kV Line tripped at 1219H (Unplanned Outage) [WEBSMS] | CLUZ
6/1/2024 12:16:29 PM | Luzon Grid-06/01/2024 12:16: Sta. Rita SS 230kV Busbar 2 restored at 1215H (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 11:40:44 AM | [NSO Update] Luzon Grid-06/01/2024 11:40: Update on System Advisory: Luzon Grid is on RED Alert for interval hours 1400H-2400H and YELLOW Alert for interval hous 1200H-1300H. Total capacity on forced outage is 3822.3MW. Total of de-rated capacity is 642MW. [WEBSMS] | CLUZ
6/1/2024 11:36:51 AM | Luzon Grid-06/01/2024 11:37: System Advisory: ALD occurred at NGCP and Meralco due to the tripping Ilijan Blocks A & B (from 350MW each) at 1108H. Lowest system frequency is 58.910Hz. [WEBSMS] | CLUZ
6/1/2024 11:36:50 AM | Luzon Grid-06/01/2024 11:36: Affected ALD feeders of MERALCO and NGCP restored at 1120H AND 1121H, respectively. [WEBSMS] | CLUZ
6/1/2024 11:16:19 AM | Luzon Grid-06/01/2024 11:16: System Advisory: ALD occurred at NGCP and Meralco due to the tripping Ilijan Blocks A & B (from 350MW each) at 1108H. Lowest system frequency is 58.910Hz. [WEBSMS] | CLUZ
6/1/2024 11:00:53 AM | Mindanao Grid-06/01/2024 11:06: WMPC DG03 online at 1058H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/1/2024 11:00:19 AM | Mindanao Grid-06/01/2024 11:06: WMPC DG10 online at 1023H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
6/1/2024 9:27:25 AM | Mindanao Grid-06/01/2024 09:33: Agusan Lake Mainit Hydro shutdown at 0701H due to low water elevation. (Unplanned Outage) [WEBSMS] | CMIN
6/1/2024 8:12:14 AM | Luzon Grid-06/01/2024 08:12: Bolo-Sual 230kV Line 2 de-energized at 0812H (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 8:09:05 AM | Mindanao Grid-06/01/2024 08:14: Davao - Bunawan 138kV Line 1 de-energized at 0802H. (Planned Outage) [WEBSMS] | CMIN
6/1/2024 7:47:26 AM | Luzon Grid-06/01/2024 07:47: Quezon (Balintawak) SS 300MVA T07 (CO) de-energized at 0745H (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 7:03:35 AM | Luzon Grid-06/01/2024 07:03: Taytay SS 300MVA T03 de-energized at 0703H (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 6:47:33 AM | Mindanao Grid-06/01/2024 06:53: Baloi SS 230kV 300MVA Transformer #2 shutdown at 0631H. (Planned Outage). [WEBSMS] | CMIN
6/1/2024 6:39:56 AM | Luzon Grid-06/01/2024 06:40: Sta. Rita SS 230kV Busbar 2 de-energized at 0637H (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 6:28:08 AM | [NSO Update] Luzon Grid-06/01/2024 06:28: System Advisory: 01-June-2024, Luzon Grid is on YELLOW Alert for interval hours 2100H and 2200H. Total capacity on forced outage is 2622.3MW. Total of de-rated capacity is 860MW. [WEBSMS] | CLUZ
6/1/2024 6:26:08 AM | Luzon Grid-06/01/2024 06:26: Bayombong - Santiago 230kV L1 de-energized at 0620H (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 6:20:21 AM | [NSO Update] Luzon Grid-06/01/2024 06:20: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=13859MW, PK=11883MW, RR=311MW, NetOpMargin: AM=1665, PM=908, EVE=440 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @500MW, Masinloc 1 @230MW, Sual 2 @500MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Masinloc 2 @330MW, Sual 1 @300MW [WEBSMS] | CLUZ
6/1/2024 6:01:18 AM | [NSO Update] Visayas Grid-06/01/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2914MW, PK=2322MW, RR=89MW, NetOpMargin: AM=504, PM=324, EVE=282 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-E @10MW, Power Barge 104-2 @6MW, Power Barge 104-3 @6MW [WEBSMS] | CVIS
6/1/2024 5:59:55 AM | Luzon Grid-06/01/2024 06:00: Dona Imelda (Araneta) 230kV Bus 2energized at 0558H (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 5:54:54 AM | [NSO Update] Mindanao Grid-06/01/2024 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3247MW, PK=2267MW, RR=73MW, NetOpMargin: AM=907, PM=706, EVE=797 Highest Unit O/L: GNPK 1,2, 3 &4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
6/1/2024 5:53:14 AM | Luzon Grid-06/01/2024 05:53: Hermosa-Calaguiman 69kV Line energized at 0549H (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 5:44:50 AM | Luzon Grid-06/01/2024 05:44: Quezon (Balintawak) 300MVA T02 (Customer Owned) energized at 0504H (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 5:16:56 AM | [NSO Update] Mindanao Grid-06/01/2024 05:22: Weather Advisory: Easterlies affecting the eastern sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
6/1/2024 5:16:24 AM | [NSO Update] Luzon Grid-06/01/2024 05:16: Weather Advisory: Easterlies affecting the eastern sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
6/1/2024 5:16:22 AM | [NSO Update] Visayas Grid-06/01/2024 05:16: Weather Advisory: Easterlies affecting the eastern sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
6/1/2024 4:43:06 AM | Luzon Grid-06/01/2024 04:43: Hermosa-Calaguiman 69kV Line de-energized at 0442H (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 1:24:35 AM | Luzon Grid-06/01/2024 01:24: Dona Imelda (Araneta) 230kV Bus 2 de-energized at 0120H (Planned Outage) [WEBSMS] | CLUZ
6/1/2024 12:53:31 AM | Luzon Grid-06/01/2024 00:53: Sta. Rita Module 20 shutdown at 0046H (Unplanned Outage) [WEBSMS] | CLUZ
6/1/2024 12:19:19 AM | Luzon Grid-06/01/2024 00:19: Quezon (Balintawak) 300MVA T02 (Customer Owned) de-energized at 0012H (Planned Outage) [WEBSMS] | CLUZ
5/31/2024 11:38:03 PM | [NSO Update] Luzon Grid-05/31/2024 23:38: Update on System Advisory: The Luzon Grid Yellow Alert Notice issued today has been lifted at 2334H. [WEBSMS] | CLUZ
5/31/2024 11:07:12 PM | Visayas Grid-05/31/2024 23:07: Cebu - Mandaue 138 kV Line 1 is looped to Mandaue GIS at 2250H.(Unplanned Outage) [WEBSMS] | CVIS
5/31/2024 10:53:23 PM | [NSO Update] Luzon Grid-05/31/2024 22:53: Update on System Advisory: Luzon Grid Red Alert Notice issued today is lifted at 2213H. Luzon Grid is still on Yellow Alert for intervals 2300H-2400H. [WEBSMS] | CLUZ
5/31/2024 10:49:38 PM | Mindanao Grid-05/31/2024 22:55: WMPC DG10 shutdown at 2246H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/31/2024 9:46:52 PM | Mindanao Grid-05/31/2024 21:52: WMPC DG03 shutdown at 2144H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/31/2024 9:27:13 PM | Luzon Grid-05/31/2024 21:27: San Esteban 100MVA T2 commissioned at 2124H. [WEBSMS] | CLUZ
5/31/2024 8:34:16 PM | [NSO Update] Luzon Grid-05/31/2024 20:34: 31-May-2024, ERC has declared market suspension for Luzon grid effective 1905H interval. [WEBSMS] | CLUZ
5/31/2024 8:23:07 PM | Luzon Grid-05/31/2024 20:23: Correction: San Lorenzo 50 online at 2019H (Unplanned Outage) [WEBSMS] | CLUZ
5/31/2024 8:21:17 PM | Luzon Grid-05/31/2024 20:21: San Lorenzo 60 online at 2019H (Unplanned Outage) [WEBSMS] | CLUZ
5/31/2024 8:16:49 PM | [NSO Update] Visayas Grid-05/31/2024 20:16: Update on System Advisory: 31-May-2024, Visayas Grid YELLOW Alert Notice issued today is lifted at 2013H. [WEBSMS] | CVIS
5/31/2024 7:02:19 PM | [NSO Update] Luzon Grid-05/31/2024 19:02: System Advisory: 31-May-2024, Luzon Grid is on RED Alert for interval hours 2000H, 2100H and YELLOW Alert for interval hous 1800H, 1900H, 2200H-2400H. Total capacity on forced outage is 2561.3MW. Total of de-rated capacity is 603MW. [WEBSMS] | CLUZ
5/31/2024 7:01:37 PM | [NSO Update] Visayas Grid-05/31/2024 19:01: System Advisory: 31-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1900H. Total capacity on forced outage is 379.6MW. Total of de-rated capacity is 195.3MW. [WEBSMS] | CVIS
5/31/2024 6:53:15 PM | [NSO Update] Luzon Grid-05/31/2024 18:53: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=12542MW, PK=12293MW, RR=382MW, NetOpMargin: EVE=0 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @400MW, Masinloc 1 @250MW, Sual 2 @500MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Masinloc 2 @330MW, Limay 2 @50MW [WEBSMS] | CLUZ
5/31/2024 6:52:17 PM | [NSO Update] Mindanao Grid-05/31/2024 18:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3252MW, PK=2438MW, RR=73MW, NetOpMargin: EVE=741 Highest Unit O/L: GNPK 1, 2, 3 & 4 @138MW Derated Plant: Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @28MW [WEBSMS] | CMIN
5/31/2024 6:25:51 PM | [NSO Update] Visayas Grid-05/31/2024 18:25: [Correction] GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2661MW, PK=2396MW, RR=91MW, NetOpMargin: EVE=174 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @313MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-E @10MW, Power Barge 104-2 @6MW, Power Barge 104-3 @6MW [WEBSMS] | CVIS
5/31/2024 6:03:52 PM | [NSO Update] Visayas Grid-05/31/2024 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2715MW, PK=2396MW, RR=91MW, NetOpMargin: EVE=228 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @313MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-E @10MW, Power Barge 104-2 @6MW, Power Barge 104-3 @6MW [WEBSMS] | CVIS
5/31/2024 5:13:24 PM | Luzon Grid-05/31/2024 17:13: Tayabas PCB 9-04CB04TAY restored at 1711H (Planned Outage) [WEBSMS] | CLUZ
5/31/2024 5:10:03 PM | Luzon Grid-05/31/2024 17:10: Currimao-Laoag 115kV Line de-energized at 1707H (Planned Outage) [WEBSMS] | CLUZ
5/31/2024 5:04:28 PM | Mindanao Grid-05/31/2024 17:10: WMPC DG08 shutdown at 1645H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/31/2024 4:15:54 PM | Mindanao Grid-05/31/2024 16:21: WMPC DG01 shutdown at 1601H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/31/2024 3:43:08 PM | Mindanao Grid-05/31/2024 15:49: Baloi - Villanueva 230kV L1 (BLO.VLN1) energized/restored at 1539H, and looped at 1540H at the Baloi SS side. From Unplanned Outage. [WEBSMS] | CMIN
5/31/2024 3:40:01 PM | Mindanao Grid-05/31/2024 15:45: UPDATED: Baloi - Villanueva 230kV L1 (BLO.VLN1) auto-tripped at 1516H. (Unplanned Outage). [WEBSMS] | CMIN
5/31/2024 3:38:05 PM | Mindanao Grid-05/31/2024 15:43: Baloi - Villanueva 230V L1 (BLO.VLN.1) auto-tripped at 1516H. (Unplanned Outage). [WEBSMS] | CMIN
5/31/2024 1:56:36 PM | Mindanao Grid-05/31/2024 14:02: WMPC DG01 online at 1354H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/31/2024 12:54:53 PM | [NSO Update] Luzon Grid-05/31/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14303MW, PK=13105MW, RR=491MW, NetOpMargin: PM=707, EVE=428 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan A @400MW, Masinloc 1 @250MW, Sual 2 @500MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Masinloc 2 @330MW, Limay 2 @50MW [WEBSMS] | CLUZ
5/31/2024 12:51:24 PM | [NSO Update] Visayas Grid-05/31/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2916MW, PK=2578MW, RR=91MW, NetOpMargin: PM=248, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @308MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-G @10MW, PDPP3-E @10MW, Power Barge 104-2 @6MW, Power Barge 104-3 @6MW [WEBSMS] | CVIS
5/31/2024 12:43:23 PM | [NSO Update] Mindanao Grid-05/31/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3296MW, PK=2688MW, RR=73MW, NetOpMargin: PM=535, EVE=715 Highest Unit O/L: GNPK 1, 2, 3 & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @28MW [WEBSMS] | CMIN
5/31/2024 11:51:57 AM | Visayas Grid-05/31/2024 11:51: Cebu - Mandaue 138 kV Line 1 energized from Cebu SS at 1149H, for 12 hour soaking (Unplanned Outage) [WEBSMS] | CVIS
5/31/2024 11:43:25 AM | Mindanao Grid-05/31/2024 11:49: MT. APO 3 online at 1136H. (Unplanned Outage) [WEBSMS] | CMIN
5/31/2024 11:18:35 AM | Luzon Grid-05/31/2024 11:18: Ilijan GT1-2 online at 1116H. (Unplanned Outage) [WEBSMS] | CLUZ
5/31/2024 9:58:09 AM | Mindanao Grid-05/31/2024 10:04: Lake Mainit shutdown at 0946H due to Low Water Elevation. Outside Management Control. [WEBSMS] | CMIN
5/31/2024 9:52:26 AM | Mindanao Grid-05/31/2024 09:58: WMPC DG08 online at 0932H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/31/2024 9:50:49 AM | Mindanao Grid-05/31/2024 09:56: Mt Apo Unit 3 tripped at 0915H. Indication: Turbine Overspeed. (Unplanned Outage) [WEBSMS] | CMIN
5/31/2024 9:16:35 AM | Luzon Grid-05/31/2024 09:16: Ilijan GT1-2 tripped at 0909H from 176MW load. The lowest frequency recorded was 59.507Hz. (Unplanned Outage) [WEBSMS] | CLUZ
5/31/2024 8:56:26 AM | Mindanao Grid-05/31/2024 09:02: WMPC DG03 online at 0854H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/31/2024 8:13:19 AM | Mindanao Grid-05/31/2024 08:19: WMPC DG10 online at 0810H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/31/2024 8:10:05 AM | Luzon Grid-05/31/2024 08:10: Tayabas PCB 9-04CB04TAY was de-energized at 0805H. (Planned Outage) [WEBSMS] | CLUZ
5/31/2024 6:10:47 AM | [NSO Update] Luzon Grid-05/31/2024 06:10: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=14315MW, PK=12282MW, RR=479MW, NetOpMargin: AM=1554, PM=774, EVE=115 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan B @500MW, Masinloc 1 @250MW, Sual 2 @500MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @220MW, Masinloc 2 @320MW, Limay 2 @50MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
5/31/2024 6:08:15 AM | [NSO Update] Luzon Grid-05/31/2024 06:08: System Advisory: 31-May-2024, Luzon Grid is on YELLOW Alert for interval hours 1500H, 1600H, and 1900H-2200H. Total capacity on forced outage is 2070.3MW. Total of de-rated capacity is 528MW. [WEBSMS] | CLUZ
5/31/2024 6:02:02 AM | Luzon Grid-05/31/2024 06:02: San Jose SS 230kV Bus 2 restored at 0600H. (Planned Outage) [WEBSMS] | CLUZ
5/31/2024 5:44:20 AM | [NSO Update] Mindanao Grid-05/31/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3305MW, PK=2535MW, RR=73MW, NetOpMargin: AM=697, PM=619, EVE=770 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @28MW [WEBSMS] | CMIN
5/31/2024 5:43:02 AM | [NSO Update] Visayas Grid-05/31/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2880MW, PK=2398MW, RR=91MW, NetOpMargin: AM=391, PM=268, EVE=228 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @313MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-G @10MW, PDPP3-E @10MW, Power Barge 104-1 @6MW, Power Barge 104-2 @6MW, Power Barge 104-3 @6MW, Power Barge 104-4 @6MW [WEBSMS] | CVIS
5/31/2024 5:39:04 AM | Mindanao Grid-05/31/2024 05:44: AGUS 7 Unit 2 online at 0538H (Unplanned Outage) [WEBSMS] | CMIN
5/31/2024 4:58:00 AM | [NSO Update] Mindanao Grid-05/31/2024 05:03: Weather Update: Frontal System affecting Extreme Northern Luzon. [WEBSMS] | CMIN
5/31/2024 4:57:34 AM | [NSO Update] Visayas Grid-05/31/2024 04:57: Weather Update: Frontal System affecting Extreme Northern Luzon. [WEBSMS] | CVIS
5/31/2024 4:57:19 AM | [NSO Update] Luzon Grid-05/31/2024 04:57: Weather Update: Frontal System affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
5/31/2024 12:08:57 AM | [NSO Update] Luzon Grid-05/31/2024 00:09: Update on System Advisory: The Luzon Grid Yellow Alert Notice issued today has been lifted at 2355H. [WEBSMS] | CLUZ
5/30/2024 11:12:10 PM | [NSO Update] Luzon Grid-05/30/2024 23:12: Update on System Advisory: 30-May-2024, Luzon Grid is on YELLOW Alert for interval 2400H. Total capacity on forced outage is 2070.3MW. Total of de-rated capacity is 633MW. [WEBSMS] | CLUZ
5/30/2024 10:50:16 PM | Mindanao Grid-05/30/2024 22:56: WMPC DG10 shutdown at 2247H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/30/2024 10:33:20 PM | Mindanao Grid-05/30/2024 22:39: WMPC DG04 shutdown at 2232H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/30/2024 9:28:40 PM | Luzon Grid-05/30/2024 21:28: San Jose SS 230kV Bus 2 de-energized at 2127H. (Planned Outage) [WEBSMS] | CLUZ
5/30/2024 8:24:17 PM | Luzon Grid-05/30/2024 20:24: San Esteban 100MVA T02 energized at high side at 2020H (On-going Commissioning) [WEBSMS] | CLUZ
5/30/2024 7:17:49 PM | Mindanao Grid-05/30/2024 19:23: WMPC DG05 shutdown at 1916H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/30/2024 6:56:06 PM | Luzon Grid-05/30/2024 18:56: Nagsaag-San Roque HEPP 230kV Line 1 restored at 1855H. (Planned Outage) [WEBSMS] | CLUZ
5/30/2024 6:29:36 PM | Luzon Grid-05/30/2024 18:29: Nagsaag-San Roque HEPP 230kV Line 2 restored at 1829H. (Planned Outage) [WEBSMS] | CLUZ
5/30/2024 6:02:25 PM | [NSO Update] Luzon Grid-05/30/2024 18:02: Update on System Advisory: 30-May-2024, Luzon Grid is on YELLOW Alert for intervals 1900H-2300H. Total capacity on forced outage is 2070.3MW. Total of de-rated capacity is 1008MW. [WEBSMS] | CLUZ
5/30/2024 6:00:31 PM | [NSO Update] Luzon Grid-05/30/2024 18:00: 30-May-2024, ERC has lifted market suspension for Luzon grid today at 1800H. Market operations will resume starting interval 1805H. [WEBSMS] | CLUZ
5/30/2024 5:45:58 PM | Luzon Grid-05/30/2024 17:46: Nagsaag-San Roque HEPP 230kV Line 2 de-energized at 1745H (Planned Outage) [WEBSMS] | CLUZ
5/30/2024 5:42:20 PM | [NSO Update] Luzon Grid-05/30/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=12117MW, PK=11630MW, RR=389MW, NetOpMargin: EVE=98 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan B @465MW, Masinloc 1 @270MW, Sual 1 @460MW, Sual 2 @460MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @200MW, Masinloc 2 @330MW, Limay 2 @50MW, Masinloc 3 @92MW [WEBSMS] | CLUZ
5/30/2024 5:37:48 PM | [NSO Update] Visayas Grid-05/30/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2681MW, PK=2363MW, RR=91MW, NetOpMargin: EVE=227 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-G @10MW, PDPP1 U2 @4MW, PDPP1 U5 @4.5MW, PDPP3-E @10MW, Power Barge 104-1 @6MW, Power Barge 104-2 @6MW, Power Barge 104-3 @6MW, Power Barge 104-4 @7MW [WEBSMS] | CVIS
5/30/2024 5:32:29 PM | [NSO Update] Mindanao Grid-05/30/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3263MW, PK=2416MW, RR=73MW, NetOpMargin: EVE=774 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
5/30/2024 4:18:18 PM | Luzon Grid-05/30/2024 16:18: Bolo-Sual 230V Line 1 looped at 1617H. (Unplanned Outage) [WEBSMS] | CLUZ
5/30/2024 1:22:48 PM | [NSO Update] Mindanao Grid-05/30/2024 13:28: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3306MW, PK=2612MW, RR=73MW, NetOpMargin: PM=621, EVE=805 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
5/30/2024 1:20:23 PM | [NSO Update] Luzon Grid-05/30/2024 13:20: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=13786MW, PK=12680MW, RR=491MW, NetOpMargin: PM=614, EVE=186 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan B @400MW, Masinloc 1 @270MW, Sual 1 @460MW, Sual 2 @440MW, Limay 8 @60MW, GNPD 2 @640MW, Calaca 2 @200MW, Masinloc 2 @330MW [WEBSMS] | CLUZ
5/30/2024 1:14:05 PM | [NSO Update] Visayas Grid-05/30/2024 13:14: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2903MW, PK=2505MW, RR=91MW, NetOpMargin: PM=307, EVE=272 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-G @10MW, PDPP1 U2 @4MW, PDPP1 U5 @4.5MW, PDPP3-E @10MW, Power Barge 104-1 @6.5MW, Power Barge 104-2 @6MW, Power Barge 104-3 @6MW [WEBSMS] | CVIS
5/30/2024 12:43:34 PM | Luzon Grid-05/30/2024 12:43: Masinloc Unit 3 online at 1241H (Unplanned Outage) [WEBSMS] | CLUZ
5/30/2024 10:05:41 AM | Luzon Grid-05/30/2024 10:05: Bolo-Sual 230V Line 1 tripped at 1003H (Unplanned Outage) [WEBSMS] | CLUZ
5/30/2024 9:52:42 AM | Mindanao Grid-05/30/2024 09:58: WMPC DG04 online at 0948H. MRU - System Voltage Requirement. Time of call: 0946H. [WEBSMS] | CMIN
5/30/2024 8:55:50 AM | Mindanao Grid-05/30/2024 09:01: WMPC DG05 online at 0849H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/30/2024 8:42:45 AM | Mindanao Grid-05/30/2024 08:48: WMPC DG10 online at 0819H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/30/2024 8:21:49 AM | Luzon Grid-05/30/2024 08:21: Nagsaag-San Roque HEPP 230kV Line 1 de-energized at 0743H (Planned Outage) [WEBSMS] | CLUZ
5/30/2024 7:39:54 AM | Luzon Grid-05/30/2024 07:39: Nagsaag-San Roque HEPP 230kV Line 2 energized via Nagsaag side at 0736H (Extended Outage) [WEBSMS] | CLUZ
5/30/2024 7:13:52 AM | Mindanao Grid-05/30/2024 07:19: PULANGI 4 Unit 3 online at 0705H (Unplanned Outage) [WEBSMS] | CMIN
5/30/2024 7:08:27 AM | Luzon Grid-05/30/2024 07:08: Nagsaag-San Roque HEPP 230kV Line 2 de-energized at 0707H (Planned Outage) [WEBSMS] | CLUZ
5/30/2024 6:45:08 AM | [NSO Update] Mindanao Grid-05/30/2024 06:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3304MW, PK=2538MW, RR=73MW, NetOpMargin: AM=693, PM=596, EVE=791 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
5/30/2024 6:43:25 AM | [NSO Update] Visayas Grid-05/30/2024 06:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2940MW, PK=2398MW, RR=91MW, NetOpMargin: AM=451, PM=233, EVE=242 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-G @10MW, PDPP1 U2 @4MW, PDPP1 U5 @4.5MW, PDPP3-E @10MW, Power Barge 104-1 @6.5MW, Power Barge 104-2 @6MW, Power Barge 104-3 @6MW [WEBSMS] | CVIS
5/30/2024 6:40:05 AM | [NSO Update] Luzon Grid-05/30/2024 06:40: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=13409MW, PK=11890MW, RR=490MW, NetOpMargin: AM=1029, PM=622, EVE=336 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Ilijan B @410MW, Masinloc 1 @300MW, Sual 1 @450MW, Sual 2 @400MW, Limay 2 @50MW, Limay 4 @87MW, Limay 8 @60MW, GNPD 2 @640MW [WEBSMS] | CLUZ
5/30/2024 6:35:38 AM | [NSO Update] Luzon Grid-05/30/2024 06:35: System Advisory: 30-May-2024, Luzon Grid is on YELLOW Alert for intervals 1400H-1600H and 1900H-2200H. Total capacity on forced outage is 2405.3MW. Total of de-rated capacity is 749MW. [WEBSMS] | CLUZ
5/30/2024 4:33:26 AM | [NSO Update] Mindanao Grid-05/30/2024 04:39: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CMIN
5/30/2024 4:33:12 AM | [NSO Update] Visayas Grid-05/30/2024 04:33: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CVIS
5/30/2024 4:32:15 AM | [NSO Update] Luzon Grid-05/30/2024 04:32: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CLUZ
5/30/2024 4:11:47 AM | Mindanao Grid-05/30/2024 04:17: Davao - Toril 138kV Line 1 tripped and auto-reclosed at 0358H. (Unplanned Outage) [WEBSMS] | CMIN
5/29/2024 11:46:40 PM | Visayas Grid-05/29/2024 23:46: DaanBantayan SS 230 kV bus 1 energized at 2333H (Planned Outage) [WEBSMS] | CVIS
5/29/2024 10:50:40 PM | [NSO Update] Luzon Grid-05/29/2024 22:51: Update on System Advisory: The Luzon Grid Yellow Alert Notice issued today is lifted at 2225H. [WEBSMS] | CLUZ
5/29/2024 10:49:04 PM | Mindanao Grid-05/29/2024 22:55: WMPC DG10 Shutdown at 2246H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/29/2024 10:34:21 PM | Mindanao Grid-05/29/2024 22:40: WMPC DG3 Shutdown at 2148H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/29/2024 8:58:43 PM | [NSO Update] Luzon Grid-05/29/2024 20:59: Update on System Advisory: 29-May-2024, Luzon Grid is on YELLOW Alert for intervals 2200H-2300H. Total capacity on forced outage is Total: 2426.1MW. Total of de-rated capacity is 753MW. [WEBSMS] | CLUZ
5/29/2024 8:37:33 PM | Luzon Grid-05/29/2024 20:37: Masinloc 3 tripped at 2034H with a load 330MW, frequency dip at 59.344hz, No ALD (Unplanned Outage) [WEBSMS] | CLUZ
5/29/2024 6:33:35 PM | Visayas Grid-05/29/2024 18:33: Carcon-Sangi 34.5kV L3 energized at 1749H, emergency request (Unplanned Outage) [WEBSMS] | CVIS
5/29/2024 5:59:50 PM | [NSO Update] Luzon Grid-05/29/2024 18:00: Update on System Advisory: Luzon Grid Red Alert Notice issued today is lifted at 1800H. Luzon Grid is still on Yellow Alert for intervals 2000H-2200H. [WEBSMS] | CLUZ
5/29/2024 5:56:08 PM | [NSO Update] Luzon Grid-05/29/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=12015MW, PK=11246MW, RR=389MW, NetOpMargin: EVE=380 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan B @400MW, Masinloc 1 @320MW, Sual 1 @440MW, Sual 2 @370MW, Masinloc 2 @335MW, Limay 8 @60MW, Limay 2 @50MW, Limay 4 @87MW [WEBSMS] | CLUZ
5/29/2024 5:30:00 PM | [NSO Update] Visayas Grid-05/29/2024 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2670MW, PK=2342MW, RR=91MW, NetOpMargin: EVE=237 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-G @10MW, PDPP1 U2 @4MW, PDPP1 U5 @4.5MW, PDPP3 E @10MW [WEBSMS] | CVIS
5/29/2024 5:28:19 PM | [NSO Update] Mindanao Grid-05/29/2024 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3272MW, PK=2493MW, RR=73MW, NetOpMargin: EVE=706 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
5/29/2024 5:28:12 PM | Luzon Grid-05/29/2024 17:28: Nagsaag-San Roque HEPP 230kV Line 2 restored at 1727H (Planned Outage) [WEBSMS] | CLUZ
5/29/2024 5:01:10 PM | Mindanao Grid-05/29/2024 17:07: WMPC DG8 shutdown at 1700H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/29/2024 4:48:37 PM | Mindanao Grid-05/29/2024 16:54: WMPC DG5 SHUTDOWN at 1647H. From MRU -System Voltage Requirement. [WEBSMS] | CMIN
5/29/2024 4:42:56 PM | [NSO Update] Luzon Grid-05/29/2024 16:43: Weather Disturbance Alert Notice (WDAN) has been lifted today, May 29, 2024 at 1600H. Typhoon "AGHON" is now outside the Philippine Area of Responsibility (PAR). The center of the eye was estimated based on all available data 1,205 KM East Northeast of Extreme Northern Luzon (25.8�N, 132.2�E). [WEBSMS] | CLUZ
5/29/2024 4:41:28 PM | [NSO Update] Mindanao Grid-05/29/2024 16:47: Weather Disturbance Alert Notice (WDAN) has been lifted today, May 29, 2024 at 1600H. Typhoon "AGHON" is now outside the Philippine Area of Responsibility (PAR). The center of the eye was estimated based on all available data 1,205 KM East Northeast of Extreme Northern Luzon (25.8�N, 132.2�E). [WEBSMS] | CMIN
5/29/2024 4:41:14 PM | [NSO Update] Visayas Grid-05/29/2024 16:41: Weather Disturbance Alert Notice (WDAN) has been lifted today, May 29, 2024 at 1600H. Typhoon "AGHON" is now outside the Philippine Area of Responsibility (PAR). The center of the eye was estimated based on all available data 1,205 KM East Northeast of Extreme Northern Luzon (25.8�N, 132.2�E). [WEBSMS] | CVIS
5/29/2024 3:02:56 PM | Visayas Grid-05/29/2024 15:03: (Carcon-Sangi 34.5kV L3 de-energized at 1501H, emergency request Unplanned Outage) [WEBSMS] | CVIS
5/29/2024 2:47:42 PM | Visayas Grid-05/29/2024 14:47: Carcon-Sangi 34.5kV L2 energized at 1446H, emergency request (Unplanned Outage) [WEBSMS] | CVIS
5/29/2024 1:45:40 PM | Mindanao Grid-05/29/2024 13:51: WMPC DG5 Online at 1344H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/29/2024 1:04:06 PM | Luzon Grid-05/29/2024 13:04: Pagbilao 3 online at 1257H. (Unplanned Outage) [WEBSMS] | CLUZ
5/29/2024 12:56:11 PM | [NSO Update] Visayas Grid-05/29/2024 12:56: Update on System Advisory: 29-May-2024, Visayas Grid YELLOW Alert Notice issued today is lifted at 1300H. [WEBSMS] | CVIS
5/29/2024 12:52:25 PM | [NSO Update] Mindanao Grid-05/29/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3340MW, PK=2638MW, RR=73MW, NetOpMargin: PM=629, EVE=799 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
5/29/2024 12:50:47 PM | [NSO Update] Luzon Grid-05/29/2024 12:51: Update on System Advisory: 29-May-2024, Luzon Grid is on RED Alert for interval hours 1400H-1600H and 1900H-2200H and YELLOW Alert for intervals 1300H, 1700H-1800 and 2300H-2400H. Total capacity on forced outage is Total: 2511.1MW. Total of de-rated capacity is 910MW. [WEBSMS] | CLUZ
5/29/2024 12:31:16 PM | [NSO Update] Luzon Grid-05/29/2024 12:31: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=12950MW, PK=12749MW, RR=491MW, NetOpMargin: PM=0, EVE=0 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan B @360MW, Masinloc 1 @320MW, Sual 1 @420MW, Sual 2 @340MW, Masinloc 2 @335MW, Limay 8 @60MW, Ilijan A @540MW, Limay 2 @50MW, Limay 4 @87MW [WEBSMS] | CLUZ
5/29/2024 12:26:42 PM | [NSO Update] Visayas Grid-05/29/2024 12:26: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2886MW, PK=2490MW, RR=91MW, NetOpMargin: PM=305, EVE=240 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-G @10MW, PDPP1 U2 @4MW, PDPP1 U5 @4.5MW, PDPP3 E @10MW [WEBSMS] | CVIS
5/29/2024 11:49:14 AM | Luzon Grid-05/29/2024 11:49: Pagbilao - Pagbilao EHV 230kV Line 2 restored at 1148H. (Unplanned Outage) [WEBSMS] | CLUZ
5/29/2024 10:37:24 AM | Mindanao Grid-05/29/2024 10:43: WMPC DG8 Online at 1035H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/29/2024 9:27:54 AM | Visayas Grid-05/29/2024 09:28: Carcon-Sangi 34.5kV L2 de-energized at 0924H, emergency request (Unplanned Outage) [WEBSMS] | CVIS
5/29/2024 9:00:33 AM | Mindanao Grid-05/29/2024 09:06: WMPC DG03 online at 0850H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/29/2024 8:56:19 AM | Mindanao Grid-05/29/2024 09:02: Agus5 U2 online at 0848H. (Planned Outage) [WEBSMS] | CMIN
5/29/2024 8:55:38 AM | Mindanao Grid-05/29/2024 09:01: WMPC DG3 online at 0850H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/29/2024 8:42:37 AM | Visayas Grid-05/29/2024 08:42: DaanBantayan SS 230 kV bus 1 de-energized at 0837H (Planned Outage) [WEBSMS] | CVIS
5/29/2024 8:15:22 AM | Mindanao Grid-05/29/2024 08:21: WMPC DG10 Online at 0812H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/29/2024 8:14:25 AM | Mindanao Grid-05/29/2024 08:20: WMPC DG10 online at 0812H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/29/2024 7:12:36 AM | Luzon Grid-05/29/2024 07:12: Nagsaag-San Roque HEPP 230kV Line 2 de-energized at 0712H. (Planned Outage) [WEBSMS] | CLUZ
5/29/2024 6:26:55 AM | [NSO Update] Luzon Grid-05/29/2024 06:27: CORRECTION: System Advisory: 29-May-2024, Luzon Grid is on RED Alert for interval hours 1500H-1600H and YELLOW Alert for intervals 1400H, 1700H and 1900H-2300H. Total capacity on forced outage is 2490.3MW. Total of de-rated capacity is 687MW. [WEBSMS] | CLUZ
5/29/2024 6:07:21 AM | [NSO Update] Luzon Grid-05/29/2024 06:07: System Advisory: 29-May-2024, Luzon Grid is on RED Alert for interval hours 1500H-1600H and YELLOW Alert for intervals 1400H, 1700H and 1900H-2300H. Total capacity on forced outage is 2511.1MW. Total of de-rated capacity is 687MW. [WEBSMS] | CLUZ
5/29/2024 6:00:30 AM | [NSO Update] Luzon Grid-05/29/2024 06:00: GRID UPDATE AS OF 6:00 AM System Condition: RED ALERT CAP=13246MW, PK=11975MW, RR=401MW, NetOpMargin: AM=870, PM=0, EVE=265 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan B @400MW, Masinloc 1 @320MW, Sual 1 @420MW, Sual 2 @450MW, Masinloc 2 @335MW, Limay 8 @60MW (Total deration: 687MW) [WEBSMS] | CLUZ
5/29/2024 5:56:11 AM | [NSO Update] Visayas Grid-05/29/2024 05:56: System Advisory: 29-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1500H-1600H and 1900H. Total capacity on forced outage is 363.6MW. Total of de-rated capacity is 203.8MW. [WEBSMS] | CVIS
5/29/2024 5:53:00 AM | [NSO Update] Visayas Grid-05/29/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2929MW, PK=2356MW, RR=91MW, NetOpMargin: AM=482, PM=260, EVE=212 Highest Unit O/L: THVI 1& 2@169MW Derated Plant: Leyte A @312MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-G @10MW, PB104 U1 @5MW, PDPP1 U2 @4MW, PDPP1 U5 @4.5MW, PDPP3 E @10MW, PDPP3 G @10MW [WEBSMS] | CVIS
5/29/2024 5:20:53 AM | [NSO Update] Mindanao Grid-05/29/2024 05:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3339MW, PK=2448MW, RR=73MW, NetOpMargin: AM=818, PM=707, EVE=825 Highest Unit O/L: GNPK 1, 2, 3 & 4@138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW [WEBSMS] | CMIN
5/29/2024 4:18:10 AM | [NSO Update] Luzon Grid-05/29/2024 04:18: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "AGHON" {EWINIAR} was estimated based on all available data at 850 km East Northeast of Extreme Northern Luzon (23.1�N, 129.7�E) with maximum sustained winds of 130 km/h near the center and gustiness of up to 160 km/h. It is moving Northeastward at 20 km/h. Southwesterly Windflow affecting the western section of the country. [WEBSMS] | CLUZ
5/29/2024 4:17:56 AM | [NSO Update] Visayas Grid-05/29/2024 04:18: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "AGHON" {EWINIAR} was estimated based on all available data at 850 km East Northeast of Extreme Northern Luzon (23.1�N, 129.7�E) with maximum sustained winds of 130 km/h near the center and gustiness of up to 160 km/h. It is moving Northeastward at 20 km/h. Southwesterly Windflow affecting the western section of the country. [WEBSMS] | CVIS
5/29/2024 4:17:33 AM | [NSO Update] Mindanao Grid-05/29/2024 04:23: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "AGHON" {EWINIAR} was estimated based on all available data at 850 km East Northeast of Extreme Northern Luzon (23.1�N, 129.7�E) with maximum sustained winds of 130 km/h near the center and gustiness of up to 160 km/h. It is moving Northeastward at 20 km/h. Southwesterly Windflow affecting the western section of the country. [WEBSMS] | CMIN
5/29/2024 12:02:04 AM | [NSO Update] Luzon Grid-05/29/2024 00:02: Update on System Advisory: Luzon Grid Yellow Alert Notice issued today is lifted at 2359H. [WEBSMS] | CLUZ
5/28/2024 10:47:03 PM | Mindanao Grid-05/28/2024 22:53: WMPC DG10 shutdown at 2246H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/28/2024 9:28:59 PM | Mindanao Grid-05/28/2024 21:35: WMPC DG03 shutdown at 2127H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/28/2024 9:12:25 PM | [NSO Update] Luzon Grid-05/28/2024 21:12: Update on System Advisory: Luzon Grid Red Alert Notice issued today is lifted at 2105H. Luzon Grid still on Yellow Alert for intervals 2200H-2400H. [WEBSMS] | CLUZ
5/28/2024 8:00:51 PM | Luzon Grid-05/28/2024 20:01: Demand Control Imminent Warning (DCIW) is issued at 2001H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
5/28/2024 6:17:56 PM | Luzon Grid-05/28/2024 18:18: Nagsaag-San Roque HEPP 230kV Line 2 restored at 1817H (Planned Outage) [WEBSMS] | CLUZ
5/28/2024 6:02:28 PM | [NSO Update] Visayas Grid-05/28/2024 18:02: Update on System Advisory: Visayas Grid Yellow Alert Notice issued today is lifted at 1800H. [WEBSMS] | CVIS
5/28/2024 6:02:19 PM | Mindanao Grid-05/28/2024 18:08: Iligan-MCN 13.8kV line restored at 1745H. [WEBSMS] | CMIN
5/28/2024 5:49:42 PM | [NSO Update] Visayas Grid-05/28/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2655MW, PK=2286MW, RR=91MW, NetOpMargin: EVE=278 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @310MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-G @10MW, PB104 U1 @5MW, PDPP1 U2 @4MW, PDPP1 U5 @4.5MW, PB104 U2 @6MW [WEBSMS] | CVIS
5/28/2024 5:40:36 PM | [NSO Update] Luzon Grid-05/28/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=11983MW, PK=11352MW, RR=382MW, NetOpMargin: EVE=249 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan B @400MW, Masinloc 1 @320MW, Masinloc 2 @335MW, Sual 1 @420MW, Sual 2 @450MW, Limay 2 @50MW [WEBSMS] | CLUZ
5/28/2024 5:23:34 PM | [NSO Update] Mindanao Grid-05/28/2024 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3170MW, PK=2374MW, RR=73MW, NetOpMargin: EVE=722 Highest Unit O/L: GNPK 1,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW, GNPK 2 @104MW [WEBSMS] | CMIN
5/28/2024 4:35:18 PM | [NSO Update] Luzon Grid-05/28/2024 16:35: Weather Update: At 3:00 PM today, the center of Typhoon AGHON (EWINIAR) was estimated based on all available data at 520 km East of Basco, Batanes (19.9N, 126.9E) with maximum sustained winds of 130 km/h near the center and gustiness of up to 160 km/h. It is moving Northeastward at 30 km/h. Southwesterly Windflow affecting the western section of the country. [WEBSMS] | CLUZ
5/28/2024 4:32:11 PM | [NSO Update] Mindanao Grid-05/28/2024 16:38: Weather Update: At 3:00 PM today, the center of the eye of Typhoon AGHON (EWINIAR) was estimated based on all available data at 520 km East of Basco, Batanes (19.9N, 126.9E) with maximum sustained winds of 130 km/h near the center and gustiness of up to 160 km/h. It is moving Northeastward at 30 km/h. Southwesterly Windflow affecting the western section of the country. [WEBSMS] | CMIN
5/28/2024 4:31:49 PM | [NSO Update] Visayas Grid-05/28/2024 16:32: Weather Update: At 3:00 PM today, the center of the eye of Typhoon AGHON (EWINIAR) was estimated based on all available data at 520 km East of Basco, Batanes (19.9N, 126.9E) with maximum sustained winds of 130 km/h near the center and gustiness of up to 160 km/h. It is moving Northeastward at 30 km/h. Southwesterly Windflow affecting the western section of the country. [WEBSMS] | CVIS
5/28/2024 4:31:25 PM | [NSO Update] Luzon Grid-05/28/2024 16:31: Weather Update: At 3:00 PM today, the center of the eye of Typhoon AGHON (EWINIAR) was estimated based on all available data at 520 km East of Basco, Batanes (19.9N, 126.9E) with maximum sustained winds of 130 km/h near the center and gustiness of up to 160 km/h. It is moving Northeastward at 30 km/h. Southwesterly Windflow affecting the western section of the country. [WEBSMS] | CLUZ
5/28/2024 4:01:27 PM | Luzon Grid-05/28/2024 16:01: Demand Control Imminent Warning (DCIW) is issued at 1601H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
5/28/2024 3:56:52 PM | Mindanao Grid-05/28/2024 16:02: NACSUR with 10.7MW load isolated at 1517H due to outage of Placer-Surigao 69 kV feeder (Unplanned Outage) [WEBSMS] | CMIN
5/28/2024 3:35:50 PM | Visayas Grid-05/28/2024 15:36: GMC ILP of 2 MW cut off at 1509H. [WEBSMS] | CVIS
5/28/2024 3:20:14 PM | Mindanao Grid-05/28/2024 15:26: Iligan-MCN 13.8kV line tripped at 1510H due to phase-ABC fault , LD=1.15MW. Unplanned outage. [WEBSMS] | CMIN
5/28/2024 3:01:51 PM | Luzon Grid-05/28/2024 15:02: Demand Control Imminent Warning (DCIW) is issued at 1501H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
5/28/2024 2:58:49 PM | Mindanao Grid-05/28/2024 15:04: Baloi - Lugait 138kVL successfully energized/restored at 1447H. From Unplanned Outage. [WEBSMS] | CMIN
5/28/2024 2:57:03 PM | Mindanao Grid-05/28/2024 15:03: Baloi - Lugait 138kVL auto-tripped at 14:12:15H and auto-reclosed at 14:12:16H but failed to reclose. Unplanned Outage. [WEBSMS] | CMIN
5/28/2024 2:48:54 PM | Mindanao Grid-05/28/2024 14:54: WMPC DG08 shutdown at 1447H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/28/2024 2:05:28 PM | Luzon Grid-05/28/2024 14:05: Demand Control Imminent Warning (DCIW) is issued at 1401H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
5/28/2024 1:56:39 PM | Mindanao Grid-05/28/2024 14:02: PEAK POWER SAN FRANCISCO Unit 2 online at 1329H (Unplanned Outage) [WEBSMS] | CMIN
5/28/2024 1:55:50 PM | Mindanao Grid-05/28/2024 14:01: PEAK POWER SAN FRANCISCO Unit 2 tripped at 1317H. Cause: to be determined (Unplanned Outage) [WEBSMS] | CMIN
5/28/2024 1:53:31 PM | Mindanao Grid-05/28/2024 13:59: PEAK POWER SAN FRANCISCO Unit 1 isolated at 1133H isolated due to feeder outage of ASELCOs Alegria SS. (Unplanned Outage) [WEBSMS] | CMIN
5/28/2024 1:28:47 PM | Visayas Grid-05/28/2024 13:29: GMC implemented ILP at 1322H, to prevent Cebu-Mandaue 138 kV L2 overloading (Unplanned Outage) [WEBSMS] | CVIS
5/28/2024 1:15:13 PM | [NSO Update] Luzon Grid-05/28/2024 13:15: Update on System Advisory: 28-May-2024, Luzon Grid is on RED Alert for interval hours 1500H-1700H and 2100H and YELLOW Alert for intervals 1300H-1400H, 1800H-2000H and 2200H-2400H. Total capacity on forced outage is 2452.3MW. Total of de-rated capacity is 798MW. [WEBSMS] | CLUZ
5/28/2024 1:08:17 PM | [NSO Update] Visayas Grid-05/28/2024 13:08: Update on System Advisory: 28-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1600H and 1900H. Total capacity on forced outage is 375.6MW. Total of de-rated capacity is 204.3MW. [WEBSMS] | CVIS
5/28/2024 1:05:49 PM | [NSO Update] Luzon Grid-05/28/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=13277MW, PK=12869MW, RR=401MW, NetOpMargin: PM=7, EVE=14 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan B @215MW, Masinloc 1 @325MW, Sual 1 @420MW, Sual 2 @480MW [WEBSMS] | CLUZ
5/28/2024 12:50:18 PM | [NSO Update] Visayas Grid-05/28/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2885MW, PK=2527MW, RR=91MW, NetOpMargin: PM=268, EVE=212 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW, PDPP3-G @10MW, PB104 U1 @5MW [WEBSMS] | CVIS
5/28/2024 12:36:48 PM | Luzon Grid-05/28/2024 12:37: Lumban - Malaya 230kV Line 1 auto-tripped/auto-reclosed at 1232H. (Unplanned Outage) [WEBSMS] | CLUZ
5/28/2024 12:36:24 PM | [NSO Update] Mindanao Grid-05/28/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3240MW, PK=2625MW, RR=73MW, NetOpMargin: PM=543, EVE=679 Highest Unit O/L: GNPK 1, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW, GNPK 2 @104MW [WEBSMS] | CMIN
5/28/2024 12:27:04 PM | Luzon Grid-05/28/2024 12:27: Ilijan B GT2-2 online at 1226H. (Unplanned Outage) [WEBSMS] | CLUZ
5/28/2024 11:43:40 AM | Mindanao Grid-05/28/2024 11:49: Agus 6 Swyd - Baloi 138 kVL2 energized/restored at 1139H. From Planned Outage (Non-GOMP). Note: Approved P&E request shutdown. [WEBSMS] | CMIN
5/28/2024 11:27:37 AM | Mindanao Grid-05/28/2024 11:33: WMPC DG01 declared available at 1125H (Unplanned Outage) [WEBSMS] | CMIN
5/28/2024 11:20:15 AM | Mindanao Grid-05/28/2024 11:26: (Correction) SEDI (EEI) Unit 1 online at 1104H (Unplanned Outage) [WEBSMS] | CMIN
5/28/2024 11:19:30 AM | Mindanao Grid-05/28/2024 11:25: (Correction) SEDI (EEI) Unit 1 failed to synchronized at 1031H due to low pressure (Unplanned Outage) [WEBSMS] | CMIN
5/28/2024 11:15:14 AM | Mindanao Grid-05/28/2024 11:21: SEDI (EEI) online at 1104H (Unplanned Outage) [WEBSMS] | CMIN
5/28/2024 11:13:29 AM | Mindanao Grid-05/28/2024 11:19: SEDI (EEI) failed to synchronized at 1031H due to low pressure (Unplanned Outage) [WEBSMS] | CMIN
5/28/2024 11:07:45 AM | Luzon Grid-05/28/2024 11:08: Ilijan B ST-2 online at 1106H. (Unplanned Outage) [WEBSMS] | CLUZ
5/28/2024 10:20:48 AM | Luzon Grid-05/28/2024 10:21: Nagsaag-San Roque HEPP 230kV Line 1 energized at Nagsaag side at 1020H. (Planned Outage) [WEBSMS] | CLUZ
5/28/2024 9:54:16 AM | Mindanao Grid-05/28/2024 10:00: WMPC DG01 on forced outage at 0940H due to lube oil controller malfunction (Unplanned Outage) [WEBSMS] | CMIN
5/28/2024 9:51:42 AM | Mindanao Grid-05/28/2024 09:57: WMPC DG08 online at 0944H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/28/2024 9:34:28 AM | Luzon Grid-05/28/2024 09:34: Ilijan B GT2-1 online at 0933H. (Unplanned Outage) [WEBSMS] | CLUZ
5/28/2024 9:05:18 AM | Mindanao Grid-05/28/2024 09:11: WMPC DG03 online at 0903H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/28/2024 8:37:35 AM | Mindanao Grid-05/28/2024 08:43: Agus 6 Swyd - Baloi 138 kVL2 de-energized at 0827H. Planned Outage (Non-GOMP). Note: Approved P&E request shutdown. [WEBSMS] | CMIN
5/28/2024 8:35:57 AM | Mindanao Grid-05/28/2024 08:42: WMPC DG10 online at 0833H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/28/2024 7:18:26 AM | Luzon Grid-05/28/2024 07:18: Nagsaag-San Roque HEPP 230kV Line 1 and 2 de-energized at 0714H and 0718H, respectively. (Planned Outage) [WEBSMS] | CLUZ
5/28/2024 6:42:47 AM | [NSO Update] Luzon Grid-05/28/2024 06:43: System Advisory: 28-May-2024, Luzon Grid is on RED Alert for interval hours 1500H-1600H and 2100H-2200H and YELLOW Alert for intervals 1400H, 1700H, 1900H, 2000H and 2300H. Total capacity on forced outage is 3052.3MW. Total of de-rated capacity is 911MW. [WEBSMS] | CLUZ
5/28/2024 6:37:28 AM | [NSO Update] Luzon Grid-05/28/2024 06:37: GRID UPDATE AS OF 6:00 AM System Condition: RED ALERT CAP=13101MW, PK=11597MW, RR=400MW, NetOpMargin: AM=1104, PM=39, EVE=0 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: Ilijan A @400MW, Masinloc 1 @325MW, Sual 1 @420MW, Sual 2 @550MW, Magat 1 @2MW, Magat 2 @2MW, Magat 3 @2MW, Magat 4 @74MW, Limay 4 @60MW, Limay 8 @60MW [WEBSMS] | CLUZ
5/28/2024 6:23:19 AM | [NSO Update] Visayas Grid-05/28/2024 06:23: System Advisory: 28-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1500H-1600H. Total capacity on forced outage is 392.3MW. Total of de-rated capacity is 194.3MW. [WEBSMS] | CVIS
5/28/2024 6:21:22 AM | [NSO Update] Visayas Grid-05/28/2024 06:21: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2959MW, PK=2367MW, RR=91MW, NetOpMargin: AM=500, PM=281, EVE=228 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @310MW, CEDC U3 @75MW, GTEC @7MW, Nasulo @44.5MW [WEBSMS] | CVIS
5/28/2024 6:13:52 AM | [NSO Update] Mindanao Grid-05/28/2024 06:19: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3148MW, PK=2549MW, RR=73MW, NetOpMargin: AM=526, PM=495, EVE=579 Highest Unit O/L: GNPK 1, 2, & 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @32MW, AG1 @47MW, AG2 @60MW, AG4 @75MW, AG5 @23MW, AG6 @110MW, AG7 @21MW, PG4 @120MW [WEBSMS] | CMIN
5/28/2024 4:55:51 AM | Luzon Grid-05/28/2024 04:56: Ilijan GT1-1 online at 0455H (Unplanned Outage) [WEBSMS] | CLUZ
5/28/2024 4:33:05 AM | [NSO Update] Luzon Grid-05/28/2024 04:33: Weather Update:At 3:00 AM today,the center of the eye of Typhoon "AGHON"{EWINIAR} was estimated based on all available data at 290km East of Tuguegarao City,Cagayan (17.7�N, 124.5�E) w/ max.sustained winds of 130km/h near the center and gustiness of up to 160km/h. It is moving Northeastward at 10km/h. Southwesterly Windflow affecting the western sections of Central Luzon,Southern Luzon & Visayas. [WEBSMS] | CLUZ
5/28/2024 4:31:46 AM | [NSO Update] Visayas Grid-05/28/2024 04:31: Weather Update:At 3:00 AM today,the center of the eye of Typhoon "AGHON"{EWINIAR} was estimated based on all available data at 290km East of Tuguegarao City,Cagayan (17.7�N, 124.5�E) w/ max.sustained winds of 130km/h near the center and gustiness of up to 160km/h. It is moving Northeastward at 10km/h. Southwesterly Windflow affecting the western sections of Central Luzon,Southern Luzon & Visayas. [WEBSMS] | CVIS
5/28/2024 4:30:24 AM | [NSO Update] Mindanao Grid-05/28/2024 04:36: Weather Update:At 3:00 AM today,the center of the eye of Typhoon "AGHON" {EWINIAR} was estimated based on all available data at 290km East of Tuguegarao City,Cagayan (17.7�N, 124.5�E) with max. sustained winds of 130km/h near the center and gustiness of up to 160km/h. It is moving Northeastward at 10km/h. Southwesterly Windflow affecting the western sections of Central Luzon, Southern Luzon & Visayas. [WEBSMS] | CMIN
5/28/2024 3:59:02 AM | Visayas Grid-05/28/2024 03:59: Daanbantayan SS 230 kV Bus 1 energized at 0357H (Unplanned Outage) [WEBSMS] | CVIS
5/28/2024 3:17:54 AM | Mindanao Grid-05/28/2024 03:23: GN Power Unit 4 online at 0315H from F.O. (Unplanned Outage) [WEBSMS] | CMIN
5/28/2024 3:03:58 AM | Visayas Grid-05/28/2024 03:04: Daanbantayan SS 230 kV Bus 1 de-energized at 0301H (Unplanned Outage) [WEBSMS] | CVIS
5/28/2024 2:35:18 AM | Luzon Grid-05/28/2024 02:35: Ilijan ST1 online at 0234H. (Unplanned Outage) [WEBSMS] | CLUZ
5/28/2024 1:39:17 AM | Luzon Grid-05/28/2024 01:39: Mauban-Meralco 230kV line(Cutomer Owned) was energized at 0135H. (Unplanned Outage) [WEBSMS] | CLUZ
5/28/2024 1:07:36 AM | Luzon Grid-05/28/2024 01:07: Ilijan GT1-2 online at 0105H. (Unplanned Outage) [WEBSMS] | CLUZ
5/28/2024 12:16:04 AM | [NSO Update] Luzon Grid-05/28/2024 00:16: Update on System Advisory: Luzon Grid YELLOW ALERT NOTICE issued on May 27, 2024 has been lifted effective 0013H of May 28, 2024. [WEBSMS] | CLUZ
5/27/2024 11:05:58 PM | Luzon Grid-05/27/2024 23:06: Ilijan GT1-2 tripped at 2255H. (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 10:56:10 PM | Mindanao Grid-05/27/2024 23:02: WMPC DG10 shutdown at 2247H. MRU - System Voltage Requirement [WEBSMS] | CMIN
5/27/2024 10:50:26 PM | [NSO Update] Luzon Grid-05/27/2024 22:50: Update on System Advisory: Luzon Grid Red Alert Notice issued on 27-May-2024 is lifted today at 2248H. Luzon Grid still on Yellow Alert for intervals 2300H and 2400H. [WEBSMS] | CLUZ
5/27/2024 10:47:32 PM | Luzon Grid-05/27/2024 22:47: Ilijan GT1-2 online at 2246H. (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 10:34:37 PM | Mindanao Grid-05/27/2024 22:40: WMPC DG01 shutdown at 2216H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/27/2024 10:15:29 PM | Luzon Grid-05/27/2024 22:15: Manual Load Dropping (MLD) for NGCP feeders were restored at 2212H. [WEBSMS] | CLUZ
5/27/2024 10:07:45 PM | Luzon Grid-05/27/2024 22:08: Manual Load Dropping (MLD) of Meralco feeders were restored at 2201H. [WEBSMS] | CLUZ
5/27/2024 8:50:01 PM | Mindanao Grid-05/27/2024 20:56: WMPC DG08 shutdown at 2047H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/27/2024 8:34:48 PM | Luzon Grid-05/27/2024 20:35: System Advisory: May 27, 2024: Manual Load Dropping (MLD) for Meralco feeders started at 2031H. [WEBSMS] | CLUZ
5/27/2024 8:21:09 PM | Luzon Grid-05/27/2024 20:21: Lumban-Bay 230kV line 1 was restored at 2020H. (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 8:16:27 PM | Luzon Grid-05/27/2024 20:16: Lumban 230kV Bus 2 energized at 2015H. (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 7:59:38 PM | Luzon Grid-05/27/2024 19:59: Lumban-Bay 230kV line 1 and Lumban 230kV Bus 2 were de-energized at 1958H. (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 6:47:03 PM | Luzon Grid-05/27/2024 18:47: MPGC 1 online at 1842H (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 6:37:08 PM | Luzon Grid-05/27/2024 18:37: System Advisory: May 27, 2024: Manual Load Dropping (MLD) for NGCP feeders started at 1832H. [WEBSMS] | CLUZ
5/27/2024 6:12:03 PM | [NSO Update] Luzon Grid-05/27/2024 18:12: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=10675MW, PK=10764MW, RR=389MW, NetOpMargin: EVE=0 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca U2 @200MW, Masinloc 1 @325MW, Sual 1 @440MW, Sual 2 @580MW, Magat 1 @2MW, Magat 2 @2MW, Magat 3 @76MW, Magat 4 @2MW, Masinloc 3 @320MW [WEBSMS] | CLUZ
5/27/2024 5:54:55 PM | [NSO Update] Mindanao Grid-05/27/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2999MW, PK=2380MW, RR=73MW, NetOpMargin: EVE=546 Highest Unit O/L: GNPK 1, 2, & 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/27/2024 5:53:13 PM | [NSO Update] Visayas Grid-05/27/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2648MW, PK=2288MW, RR=91MW, NetOpMargin: EVE=269 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @310MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Nasulo @44.5MW, PDPP3-G @10MW [WEBSMS] | CVIS
5/27/2024 5:40:19 PM | Luzon Grid-05/27/2024 17:40: Demand Control Imminent Warning (DCIW) is issued at 1731H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
5/27/2024 5:30:57 PM | Luzon Grid-05/27/2024 17:31: San Lorenzo Module 50 shutdown at 1728H. (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 4:33:48 PM | Mindanao Grid-05/27/2024 16:39: AGUS 6 Unit 4 online at 1621H from FO. (Unplanned Outage) [WEBSMS] | CMIN
5/27/2024 4:23:48 PM | Luzon Grid-05/27/2024 16:24: San Jose PCB 8-05CB08SJO energized at 1622H (Planned Outage) [WEBSMS] | CLUZ
5/27/2024 4:12:18 PM | Luzon Grid-05/27/2024 16:12: SBPL online at 1610H. (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 4:02:45 PM | Luzon Grid-05/27/2024 16:03: Demand Control Imminent Warning (DCIW) is issued at 1601H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
5/27/2024 3:02:57 PM | Luzon Grid-05/27/2024 15:03: Demand Control Imminent Warning (DCIW) is issued at 1501H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
5/27/2024 2:57:54 PM | Luzon Grid-05/27/2024 14:58: May 27, 2024: Demand Control Imminent Warning (DCIW) is issued at 1321H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
5/27/2024 2:56:24 PM | Luzon Grid-05/27/2024 14:56: San Jose PCB 8-05CB08SJO de-energized at 1453H (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 2:49:43 PM | [NSO Update] Visayas Grid-05/27/2024 14:49: SO-initiated Market Intervention for Visayas has been lifted today at 1447H. Market operations will resume starting interval 1455H. [WEBSMS] | CVIS
5/27/2024 2:45:29 PM | Visayas Grid-05/27/2024 14:45: BOHECO 2 (CGP Garcia) MLD restored at 1437H. [WEBSMS] | CVIS
5/27/2024 2:36:44 PM | [NSO Update] Visayas Grid-05/27/2024 14:36: SO-initiated Market Intervention for Visayas is issued today starting interval 1425H due to MLD implementation to prevent the overloading of Ubay-Maasin 138kV Line. [WEBSMS] | CVIS
5/27/2024 2:35:24 PM | Visayas Grid-05/27/2024 14:35: BOHECO 2 (CGP Garcia) implemented 4.1MW MLD at 1422H to avoid overloading of 138kV Maasin-Ubay line. [WEBSMS] | CVIS
5/27/2024 2:29:41 PM | Mindanao Grid-05/27/2024 14:35: AGUS 5 Unit 1 with 22MW load tripped at 1407H. Indication: Over Speed-2nd stage, Vibration- 2nd stage, AVR Fault, 5P and 5C Lock-out relay trip. (Unplanned Outage) [WEBSMS] | CMIN
5/27/2024 1:01:33 PM | [NSO Update] Luzon Grid-05/27/2024 13:01: 27-May-2024, ERC has declared market suspension for Luzon grid effective 1305H interval. [WEBSMS] | CLUZ
5/27/2024 1:00:37 PM | [NSO Update] Luzon Grid-05/27/2024 13:00: Update on System Advisory: 27-May-2024, Luzon Grid is on RED Alert for interval hours 1400H-1700H and 1900H-2200H and YELLOW Alert for interval hours 1300H, 1800H, 2300H and 2400H. Total capacity on forced outage is 3946.3MW. Total of de-rated capacity is 794MW. [WEBSMS] | CLUZ
5/27/2024 12:57:04 PM | [NSO Update] Luzon Grid-05/27/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=11810MW, PK=11785MW, RR=491MW, NetOpMargin: PM=0, EVE=0 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca U2 @200MW, Masinloc 1 @325MW, Sual 1 @430MW, Sual 2 @580MW, Magat 1 @2MW, Magat 2 @2MW, Magat 3 @76MW, Magat 4 @2MW, Masinloc 3 @250MW [WEBSMS] | CLUZ
5/27/2024 12:39:03 PM | [NSO Update] Visayas Grid-05/27/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2853MW, PK=2505MW, RR=88MW, NetOpMargin: PM=260, EVE=233 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @310MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Power Barge 104-1 @6MW, Nasulo @42.5MW, PDPP3-E @10MW, PDPP3-G @10MW [WEBSMS] | CVIS
5/27/2024 12:32:09 PM | [NSO Update] Mindanao Grid-05/27/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3028MW, PK=2538MW, RR=73MW, NetOpMargin: PM=417, EVE=521 Highest Unit O/L: GNPK 1, 2 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/27/2024 12:28:19 PM | Mindanao Grid-05/27/2024 12:34: WMPC DG08 online at 1226H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/27/2024 12:18:18 PM | Mindanao Grid-05/27/2024 12:24: MPC (IDPP) U3 online at 1210H - REGULATORY REQUIREMENTS, EMISSION TEST : STACK EMISSION TEST. [WEBSMS] | CMIN
5/27/2024 12:17:20 PM | Mindanao Grid-05/27/2024 12:23: WMPC DG08 shutdown at 1214H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/27/2024 12:01:49 PM | Luzon Grid-05/27/2024 12:02: Late Entry: SBPL-Mauban 230kV L2 looped at 1358H in SBPL side, May 26, 2024 (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 11:27:26 AM | Mindanao Grid-05/27/2024 11:33: MPC (IDPP) shutdown at 1120H, End of REGULATORY REQUIREMENTS -EMISSION TEST - STACK EMISSION TEST. [WEBSMS] | CMIN
5/27/2024 10:03:39 AM | Mindanao Grid-05/27/2024 10:09: WMPC DG08 online at 0849H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/27/2024 9:52:41 AM | Mindanao Grid-05/27/2024 09:58: WMPC DG08 online at 0949H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/27/2024 9:15:44 AM | Mindanao Grid-05/27/2024 09:21: MPC (IDPP) online at 0908H - EMISSION TEST : STACK EMISSION TEST. [WEBSMS] | CMIN
5/27/2024 9:04:15 AM | Mindanao Grid-05/27/2024 09:10: WMPC DG01 online at 0843H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/27/2024 8:29:42 AM | Mindanao Grid-05/27/2024 08:35: WMPC DG10 online at 0814H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/27/2024 7:08:23 AM | Luzon Grid-05/27/2024 07:08: Masinloc 3 online at 0705H (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 6:45:53 AM | [NSO Update] Luzon Grid-05/27/2024 06:46: System Advisory: 27-May-2024, Luzon Grid is on RED Alert for interval hours 1700H-2200H and YELLOW Alert for interval hours 1400H-1600H and 2300H. Total capacity on forced outage is 4281.3MW. Total of de-rated capacity is 216MW. [WEBSMS] | CLUZ
5/27/2024 6:43:17 AM | [NSO Update] Mindanao Grid-05/27/2024 06:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2999MW, PK=2425MW, RR=73MW, NetOpMargin: AM=501, PM=398, EVE=518 Highest Unit O/L: GNPK 1, 2 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/27/2024 6:41:52 AM | [NSO Update] Visayas Grid-05/27/2024 06:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2963MW, PK=2299MW, RR=86MW, NetOpMargin: AM=578, PM=360, EVE=312 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @310MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Power Barge 104-1 @6MW, Nasulo @42.5MW, PDPP3-E @10MW, PDPP3-G @10MW [WEBSMS] | CVIS
5/27/2024 6:40:13 AM | [NSO Update] Luzon Grid-05/27/2024 06:40: GRID UPDATE AS OF 6:00 AM System Condition: RED ALERT CAP=12488MW, PK=10683MW, RR=511MW, NetOpMargin: AM=1294, PM=379, EVE=0 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Sual 1 @550MW, Calaca U2 @200MW, Masinloc 1 @325MW [WEBSMS] | CLUZ
5/27/2024 6:39:39 AM | Mindanao Grid-05/27/2024 06:45: Nagamin SS 138kV Bus 1 energized at 0628H. (Planned Outage) [WEBSMS] | CMIN
5/27/2024 5:41:13 AM | Mindanao Grid-05/27/2024 05:47: Matanao - Culaman 230kV L1 (7LI1MAT-CMA) energized/restored at 0534H and looped at 0536H, at the Matanao SS side. From Planned Outage/PO00AC (Non-GOMP). [WEBSMS] | CMIN
5/27/2024 5:31:14 AM | Luzon Grid-05/27/2024 05:31: Pagbilao EHV-Pagbilao 230kV Line 1 restored at 0530H (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 5:23:46 AM | Luzon Grid-05/27/2024 05:24: Kalayaan 4 with 100MW load tripped at 0521H. Lowest Frequency is 59.64Hz (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 5:01:52 AM | Luzon Grid-05/27/2024 05:02: Pagbilao EHV-Pagbilao 230kV Line 1 & 2 simultaneously tripped again at 0448H while Pagbilao Power Plant is normalizing their Bay 82 during closing of 8-02CB24PAG (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 4:45:52 AM | Luzon Grid-05/27/2024 04:46: Commissioning of New Main Protection and BFR of Daraga-Tiwi C 230kV Line completed at 0430H. Daraga-Tiwi C 230kV Line was energized and looped at 0330H (Planned Outage) [WEBSMS] | CLUZ
5/27/2024 4:29:55 AM | [NSO Update] Mindanao Grid-05/27/2024 04:35: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "AGHON" {EWINIAR} was estimated based on all available data at 95 km East of Baler, Aurora (15.6�N, 122.5�E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving North Northeastward at 10 km/h. Southwesterly Windflow affecting the western section of Southern Luzon and Visayas. [WEBSMS] | CMIN
5/27/2024 4:28:45 AM | [NSO Update] Visayas Grid-05/27/2024 04:28: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "AGHON" {EWINIAR} was estimated based on all available data at 95 km East of Baler, Aurora (15.6�N, 122.5�E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving North Northeastward at 10 km/h. Southwesterly Windflow affecting the western section of Southern Luzon and Visayas. [WEBSMS] | CVIS
5/27/2024 4:28:09 AM | [NSO Update] Luzon Grid-05/27/2024 04:28: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "AGHON" {EWINIAR} was estimated based on all available data at 95 km East of Baler, Aurora (15.6�N, 122.5�E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving North Northeastward at 10 km/h. Southwesterly Windflow affecting the western section of Southern Luzon and Visayas. [WEBSMS] | CLUZ
5/27/2024 12:52:48 AM | Luzon Grid-05/27/2024 00:53: Pagbilao EHV-Pagbilao 230kV L2 looped/restored at 0051H (Unplanned Outage) [WEBSMS] | CLUZ
5/27/2024 12:15:01 AM | Mindanao Grid-05/27/2024 00:21: Nagamin SS 138kV Bus 1 deenergized at 0006H (Planned Outage) [WEBSMS] | CMIN
5/27/2024 12:10:55 AM | Mindanao Grid-05/27/2024 00:16: LIBERTAD POWER shutdown at 0000H (Planned Outage) [WEBSMS] | CMIN
5/26/2024 11:38:09 PM | Mindanao Grid-05/26/2024 23:44: AGUS 6 Unit 4 emergency shutdown at 2333H due to unbalanced voltage (to inspect its potential transformer) (Unplanned Outage) [WEBSMS] | CMIN
5/26/2024 10:48:31 PM | Mindanao Grid-05/26/2024 22:54: WMPC DG05 shutdown at 2246H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/26/2024 9:49:27 PM | Mindanao Grid-05/26/2024 21:55: WMPC DG08 shutdown at 2148H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/26/2024 8:45:02 PM | Luzon Grid-05/26/2024 20:45: Pagbilao EHV-Pagbilao 230kV L1 looped/restored at 2042H (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 7:48:09 PM | Mindanao Grid-05/26/2024 19:54: PULANGI 4 Unit 1 online at 1806H (Planned Outage) [WEBSMS] | CMIN
5/26/2024 7:45:20 PM | Mindanao Grid-05/26/2024 19:51: WMPC DG08 online at 1830H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/26/2024 7:44:34 PM | Mindanao Grid-05/26/2024 19:50: WMPC DG05 online at 1755H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/26/2024 6:15:36 PM | Visayas Grid-05/26/2024 18:15: Dumanjug - Alcoy 69 kV Line de-energized/re-energized at 1731H/1810H [WEBSMS] | CVIS
5/26/2024 6:14:24 PM | [NSO Update] Luzon Grid-05/26/2024 18:14: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10926MW, PK=8983MW, RR=299MW, NetOpMargin: EVE=1644 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Sual 1 @550MW, Calaca U2 @190MW, Masinloc 1 @330MW [WEBSMS] | CLUZ
5/26/2024 6:06:52 PM | [NSO Update] Luzon Grid-05/26/2024 18:07: Update on System Advisory: The Luzon Grid Yellow Alert Notice issued today has been lifted effective 1800H. [WEBSMS] | CLUZ
5/26/2024 6:03:32 PM | Mindanao Grid-05/26/2024 18:09: Kibawe - Tacurong 138kV Line (7LI1KIB-TAC) energized at 1756H and looped at 1801H, at the Kibawe SS side. From Planned Outage/PO00AA (GOMP). [WEBSMS] | CMIN
5/26/2024 6:02:26 PM | Visayas Grid-05/26/2024 18:02: Carcon - Sangi 34.5 kV Line 1 energized at 1801H (Unplanned Outage) [WEBSMS] | CVIS
5/26/2024 5:47:08 PM | [NSO Update] Mindanao Grid-05/26/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2951MW, PK=2231MW, RR=73MW, NetOpMargin: EVE=647 Highest Unit O/L: GNPK 1, 2, & 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/26/2024 5:45:59 PM | [NSO Update] Visayas Grid-05/26/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2556MW, PK=2087MW, RR=91MW, NetOpMargin: EVE=378 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @310MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Power Barge 104-1 @6MW, Nasulo @44.5MW, PDPP3-E @10MW [WEBSMS] | CVIS
5/26/2024 5:38:20 PM | Mindanao Grid-05/26/2024 17:44: LAKE MAINIT Hydro online at 1719H (Unplanned Outage) [WEBSMS] | CMIN
5/26/2024 5:15:56 PM | [NSO Update] Mindanao Grid-05/26/2024 17:21: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm AGHON was estimated based on all available data over the coastal waters of Mauban, Quezon (14.4 N, 121.8 E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 130 km/h. It is moving Northeastward slowly. [WEBSMS] | CMIN
5/26/2024 5:15:45 PM | [NSO Update] Visayas Grid-05/26/2024 17:15: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm AGHON was estimated based on all available data over the coastal waters of Mauban, Quezon (14.4 N, 121.8 E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 130 km/h. It is moving Northeastward slowly. [WEBSMS] | CVIS
5/26/2024 5:15:31 PM | [NSO Update] Luzon Grid-05/26/2024 17:15: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm AGHON was estimated based on all available data over the coastal waters of Mauban, Quezon (14.4 N, 121.8 E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 130 km/h. It is moving Northeastward slowly. [WEBSMS] | CLUZ
5/26/2024 5:02:21 PM | Visayas Grid-05/26/2024 17:02: Dumanjug - Alcoy 69 kV Line energized at 1700H (Test and Commissioning) [WEBSMS] | CVIS
5/26/2024 4:57:44 PM | Visayas Grid-05/26/2024 16:57: Calong-Calong - Asturias 69 kV Line energized at 1657H (Planned Outage) [WEBSMS] | CVIS
5/26/2024 4:49:19 PM | Mindanao Grid-05/26/2024 16:55: PULANGI 4 Unit 3 online at 1619H (Planned Outage) [WEBSMS] | CMIN
5/26/2024 4:42:00 PM | Visayas Grid-05/26/2024 16:42: Dumanjug SS 100 MVA 138/69/13.8 kV TR1 re-energized at 1641H (Unplanned Outage) [WEBSMS] | CVIS
5/26/2024 3:43:38 PM | [NSO Update] Mindanao Grid-05/26/2024 15:49: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1520H with power going to Visayas [WEBSMS] | CMIN
5/26/2024 3:42:57 PM | Visayas Grid-05/26/2024 15:43: Dumanjug - Samboan 138 kV Line 2 energized at 1541H (Planned Outage) [WEBSMS] | CVIS
5/26/2024 3:42:53 PM | [NSO Update] Visayas Grid-05/26/2024 15:43: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1520H with power going to Visayas [WEBSMS] | CVIS
5/26/2024 3:20:38 PM | Mindanao Grid-05/26/2024 15:26: WMPC DG05 shutdownn at 1516H. End of MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/26/2024 1:36:52 PM | Luzon Grid-05/26/2024 13:37: Gumaca-Lumban 230kV L1 tripped/reclosed at 1333H (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 1:28:04 PM | [NSO Update] Mindanao Grid-05/26/2024 13:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2979MW, PK=2185MW, RR=73MW, NetOpMargin: PM=721, EVE=509 Highest Unit O/L: GNPK 1, 2, & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW, [WEBSMS] | CMIN
5/26/2024 1:26:38 PM | Luzon Grid-05/26/2024 13:26: Gumaca-Lumban 230kV L1 tripped/reclosed at 1324H (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 1:24:51 PM | Luzon Grid-05/26/2024 13:25: Masinloc 3 tripped at 1319H with a load of 335MW, frequency dip at 59.23hz, no ALD (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 1:20:50 PM | Luzon Grid-05/26/2024 13:21: Gumaca-Lumban 230kV L2 restored at 1320H (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 1:18:35 PM | [NSO Update] Visayas Grid-05/26/2024 13:18: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2675MW, PK=1964MW, RR=88MW, NetOpMargin: PM=623, EVE=201 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @310MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Power Barge 104-1 @6MW, Nasulo @42.5MW, PDPP3 - E @10MW [WEBSMS] | CVIS
5/26/2024 1:14:25 PM | [NSO Update] Luzon Grid-05/26/2024 13:14: System Advisory: 26-May-2024, Luzon Grid is on YELLOW Alert for interval hours 2100H-2200H and 2400H. Total capacity on forced outage is 3790.5MW. Total of de-rated capacity is 627MW. [WEBSMS] | CLUZ
5/26/2024 1:09:40 PM | Luzon Grid-05/26/2024 13:09: SBPL tripped at 1305H with of load 206MW, frequency dip at 59.46Hz (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 1:06:21 PM | [NSO Update] Luzon Grid-05/26/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=12222MW, PK=9175MW, RR=351MW, NetOpMargin: PM=2697, EVE=52 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Sual 1 @550MW, Calaca U2 @190MW, Masinloc 1 @325MW, Angat Main HEP @78MW, Masinloc 2 @340MW, SBPL @180MW [WEBSMS] | CLUZ
5/26/2024 1:04:13 PM | Luzon Grid-05/26/2024 13:04: Gumaca-Lumban 230kV L2 tripped at 1259H (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 12:46:20 PM | Luzon Grid-05/26/2024 12:46: Mauban-Meralco 230kV Line tripped at 1237H and Mauban-SBPL 230kV L2 unloped at SBPL at 1224H. (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 12:20:14 PM | Mindanao Grid-05/26/2024 12:26: WMPC DG08 shutdown at 1216H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/26/2024 12:19:14 PM | Mindanao Grid-05/26/2024 12:25: LAKE MAINIT Hydro shutdown at 1204H due to ANECO line clearing activity (Unplanned Outage) [WEBSMS] | CMIN
5/26/2024 12:10:08 PM | Mindanao Grid-05/26/2024 12:16: Nagamin - Zamboanga 138kV L1 energized at 1145H and successfully looped at 1151H, at Zamboanga SS side. From Planned Outage/ PO00AC/Non-GOMP. [WEBSMS] | CMIN
5/26/2024 11:41:31 AM | Luzon Grid-05/26/2024 11:41: 9-02CB04NGS restored at 1141H (Planned Outage) [WEBSMS] | CLUZ
5/26/2024 11:24:29 AM | Luzon Grid-05/26/2024 11:24: Pagbilao-Pagbilao 230kV L1 & L2 energized at 1107H and 1119H at Pagbilao substation, waiting for plant clearance for looping. (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 10:48:23 AM | Luzon Grid-05/26/2024 10:48: Tayabas-Pagbilao 500kV L2 autotripped/reclosed at 1043H (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 10:29:21 AM | Visayas Grid-05/26/2024 10:29: Carcon-Sangi 34.5KV line 1 de-energized at 1016H. ( Unplanned Outage ) [WEBSMS] | CVIS
5/26/2024 10:19:37 AM | Luzon Grid-05/26/2024 10:19: Tuguegarao 230kV Bus 1 restored at 1019H (Planned Outage) [WEBSMS] | CLUZ
5/26/2024 10:14:15 AM | Mindanao Grid-05/26/2024 10:20: PULANGI 4 Unit 1 shutdown at 1007H (Planned Outage) [WEBSMS] | CMIN
5/26/2024 10:13:36 AM | Mindanao Grid-05/26/2024 10:19: PULANGI 4 Unit 3 shutdown at 1003H (Planned Outage) [WEBSMS] | CMIN
5/26/2024 10:03:27 AM | Mindanao Grid-05/26/2024 10:09: WMPC DG05 online at 0957H. MRU - System Voltage Requirement (replacement power for WMPC DG04 which tripped at 0949H). [WEBSMS] | CMIN
5/26/2024 10:00:29 AM | Mindanao Grid-05/26/2024 10:06: WMPC DG04 with 10MW tripped at 0949H. Cause: Turbo charger shock pulse alarm (Unplanned Outage) [WEBSMS] | CMIN
5/26/2024 9:53:06 AM | Luzon Grid-05/26/2024 09:53: Pagbilao 3 tripped at 0926H with a load of 420MW, lowest frequency dip is 59.35Hz, no ALD (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 9:41:21 AM | Luzon Grid-05/26/2024 09:41: Simultaneous tripping of Pagbilao-Pagbilao Plant 230kV L1 & L2 and Pagbilao 3 with a load 420MW at 0926H (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 9:38:06 AM | Luzon Grid-05/26/2024 09:38: Simultaneous tripping of Pagbilao-Pagbilao Plant 230kV L1 & L2 and Pagbilao 3 with a load 420MW (Unplanned Outage). [WEBSMS] | CLUZ
5/26/2024 9:21:41 AM | Luzon Grid-05/26/2024 09:21: Nagsaag-Casecnan 230kV line 1 restored at 0921H (Planned Outage) [WEBSMS] | CLUZ
5/26/2024 7:54:37 AM | Luzon Grid-05/26/2024 07:54: Lumban-Lumban BESS 69kV tripped/restored at 0436H/0751H (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 7:44:45 AM | Mindanao Grid-05/26/2024 07:50: Kibawe - Tacurong 138kV Line (7LI1KIB-TAC) de-energized at 0743H. Planned Outage/PO00AA (GOMP). Note: This is an MD6 (MOM) GOMP-approved shutdown request. [WEBSMS] | CMIN
5/26/2024 7:28:57 AM | Mindanao Grid-05/26/2024 07:34: Matanao - Culaman 230kV L1 (7LI1MAT-CMA) de-energized at 0719H. Planned Outage/PO00AC (Non GOMP). Note: This is MSO-NPD approved shutdown request. [WEBSMS] | CMIN
5/26/2024 7:07:07 AM | Luzon Grid-05/26/2024 07:07: Bay-Lumban 230kV L1 restored at 0707H (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 6:52:29 AM | Luzon Grid-05/26/2024 06:52: Bay-Lumban 230kV L1 tripped at 0647H (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 6:42:34 AM | Visayas Grid-05/26/2024 06:42: Dumanjug-Samboan 138KV line 2 de-energized @0640H. ( Planned Outage ) [WEBSMS] | CVIS
5/26/2024 6:32:11 AM | [NSO Update] Luzon Grid-05/26/2024 06:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13146MW, PK=9609MW, RR=350MW, NetOpMargin: AM=3186, PM=1881, EVE=782 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @190MW, MSLC1 @325MW, MSLC2 @340MW, SUAL 1 @550MW [WEBSMS] | CLUZ
5/26/2024 6:23:15 AM | Visayas Grid-05/26/2024 06:23: 69KV Calong-Calong - Asturias line de-energized at 0610H. ( Planned Outage ) [WEBSMS] | CVIS
5/26/2024 6:16:20 AM | Luzon Grid-05/26/2024 06:16: 9-02CB04NGS de-energized at 0614H (Planned Outage) [WEBSMS] | CLUZ
5/26/2024 6:01:33 AM | [NSO Update] Mindanao Grid-05/26/2024 06:07: Weather Update: At 3:00 AM today, the center of Tropical Storm "AGHON" was estimated based on all available data over the coastal waters of Pagbilao, Quezon (13.8�N, 121.8�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving Northwestward at 10 km/h. [WEBSMS] | CMIN
5/26/2024 6:01:14 AM | [NSO Update] Visayas Grid-05/26/2024 06:01: Weather Update: At 3:00 AM today, the center of Tropical Storm "AGHON" was estimated based on all available data over the coastal waters of Pagbilao, Quezon (13.8�N, 121.8�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving Northwestward at 10 km/h. [WEBSMS] | CVIS
5/26/2024 6:00:51 AM | Luzon Grid-05/26/2024 06:01: Nagsaag-Casecnan 230kV line 1 was de-energized at 0553H. (Planned Outage) [WEBSMS] | CLUZ
5/26/2024 6:00:45 AM | [NSO Update] Luzon Grid-05/26/2024 06:00: Weather Update: At 3:00 AM today, the center of Tropical Storm "AGHON" was estimated based on all available data over the coastal waters of Pagbilao, Quezon (13.8�N, 121.8�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving Northwestward at 10 km/h. [WEBSMS] | CLUZ
5/26/2024 5:59:35 AM | [NSO Update] Mindanao Grid-05/26/2024 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3001MW, PK=2081MW, RR=73MW, NetOpMargin: AM=847, PM=818, EVE=615 Highest Unit O/L: GNPK 1, 2, & 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/26/2024 5:57:30 AM | [NSO Update] Visayas Grid-05/26/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2722MW, PK=1863MW, RR=86MW, NetOpMargin: AM=773, PM=680, EVE=346 Highest Unit O/L: THVI 1 and 2 @169MW Derated Plant: Leyte A @310MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Power Barge 104-1 @6MW, Nasulo @42.5MW, PDPP3 - E @10MW [WEBSMS] | CVIS
5/26/2024 5:35:47 AM | Luzon Grid-05/26/2024 05:36: Pagbilao EHV-Pagbilao Plant 230kV line 2 was restored at 0525H.(Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 5:30:05 AM | Luzon Grid-05/26/2024 05:30: Pagbilao Unit 1 tripped at 0518H while on load stabilization. (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 5:27:54 AM | Luzon Grid-05/26/2024 05:28: Pagbilao Unit 2 tripped at 0449H while attempting to synchronize from house load. (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 5:16:40 AM | Luzon Grid-05/26/2024 05:16: Pagbilao Unit 3 synchronized at 0512H from house load. (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 5:15:07 AM | Luzon Grid-05/26/2024 05:15: Pagbilao Unit 1 synchronized at 0447H from house load. (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 5:10:16 AM | Luzon Grid-05/26/2024 05:10: System Advisory: Additional info: The lowest system frequency during the ALD occurrence at 0436H was 58.714Hz. [WEBSMS] | CLUZ
5/26/2024 5:06:09 AM | Luzon Grid-05/26/2024 05:06: System Advisory: The NGCP and Meralco ALD affected feeders were restored at 0451H. [WEBSMS] | CLUZ
5/26/2024 5:00:18 AM | Luzon Grid-05/26/2024 05:00: System Advisory: ALD occurred at NGCP and Meralco due to the de-synchronization of Pagbilao Units 1, 2, and 3 at 0436H. Pagbilao EHV-Pagbilao Plant 230kV line 1 auto-tripped/reclosed while Pagbilao EHV-Pagbilao Plant 230kV line 2 tripped at the same time. [WEBSMS] | CLUZ
5/26/2024 4:59:22 AM | Luzon Grid-05/26/2024 04:59: System Advisory: ALD occurred at NGCP and Meralco due to the de-synchronization of Pagbilao Units 1, 2, and 3(on-house load) at 0436H. Pagbilao EHV-Pagbilao Plant 230kV line 1 auto-tripped/auto-reclosed while Pagbilao EHV-Pagbilao Plant 230kV line 2 tripped at the same time. [WEBSMS] | CLUZ
5/26/2024 4:33:44 AM | Luzon Grid-05/26/2024 04:33: Tuguegarao 230kV Bus 1 de-energized at 0432H (Planned Outage). [WEBSMS] | CLUZ
5/26/2024 4:05:38 AM | Mindanao Grid-05/26/2024 04:11: Baloi SS 138kV Bus 1 energized at 0401H. (Planned Outage) [WEBSMS] | CMIN
5/26/2024 2:01:16 AM | Mindanao Grid-05/26/2024 02:07: PULANGI 4 HEP Unit 3 online at 0141H from FO. (Unplanned Outage) [WEBSMS] | CMIN
5/26/2024 1:37:59 AM | Visayas Grid-05/26/2024 01:38: TVI Unit # 2 re-on line at 0124H. ( Unplanned Outage ) [WEBSMS] | CVIS
5/26/2024 1:24:35 AM | Mindanao Grid-05/26/2024 01:30: PULANGI 4 HEP Unit 3 tripped at 0100H. Indication: 64 GB Stator Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
5/26/2024 1:21:53 AM | Luzon Grid-05/26/2024 01:22: Kalayaan Unit 3(-156MW) tripped as pump at 0118H. The system frequency reached 60.468Hz. (Unplanned Outage) [WEBSMS] | CLUZ
5/26/2024 1:01:13 AM | Mindanao Grid-05/26/2024 01:07: PULANGI 4 HEP Unit 3 online at 0040. (Planned Outage) [WEBSMS] | CMIN
5/26/2024 1:00:55 AM | [NSO Update] Visayas Grid-05/26/2024 01:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0055H with power going to Luzon [WEBSMS] | CVIS
5/26/2024 1:00:15 AM | [NSO Update] Luzon Grid-05/26/2024 01:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0055H with power going to Luzon [WEBSMS] | CLUZ
5/26/2024 12:45:05 AM | Mindanao Grid-05/26/2024 00:51: Nagamin - Zamboanga 138kV L1 de-energized at 0034H. (Planned Outage) [WEBSMS] | CMIN
5/26/2024 12:43:48 AM | Mindanao Grid-05/26/2024 00:49: Maramag-Pulangi 4 138kV L3 energized at 0023H. (Planned Outage) [WEBSMS] | CMIN
5/26/2024 12:42:25 AM | [NSO Update] Visayas Grid-05/26/2024 00:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0040H from reverse power direction [WEBSMS] | CVIS
5/26/2024 12:41:21 AM | [NSO Update] Luzon Grid-05/26/2024 00:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0040H from reverse power direction [WEBSMS] | CLUZ
5/26/2024 12:06:01 AM | Mindanao Grid-05/26/2024 00:12: WMPC DG08 online at 0003H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/26/2024 12:05:12 AM | Mindanao Grid-05/26/2024 00:11: WMPC DG04 online at 0001H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/25/2024 11:20:02 PM | Mindanao Grid-05/25/2024 23:26: Baloi SS 138kV Bus 1 de-energized at 2317H. (Planned Outage) [WEBSMS] | CMIN
5/25/2024 10:18:38 PM | Mindanao Grid-05/25/2024 22:24: WMPC DG10 shutdown at 2217H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/25/2024 9:32:51 PM | [NSO Update] Visayas Grid-05/25/2024 21:33: Update on System Advisory: The Visayas Grid Yellow Alert Notice issued today has been lifted effective 2121H. [WEBSMS] | CVIS
5/25/2024 9:03:20 PM | Visayas Grid-05/25/2024 21:03: Dumanjug SS 100 MVA 138/69/13.8 kV TR1 de-energized at 2100H (Unplanned Outage) [WEBSMS] | CVIS
5/25/2024 7:58:31 PM | Mindanao Grid-05/25/2024 20:04: AGUS 5 HEP Unit 2 shutdown at 1952H due to low forebay elevation. (Unplanned Outage) [WEBSMS] | CMIN
5/25/2024 6:20:34 PM | [NSO Update] Visayas Grid-05/25/2024 18:20: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2431MW, PK=2174MW, RR=90MW, NetOpMargin: EVE=166 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @307MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Power Barge 104-1 @6MW, Nasulo @44.5MW [WEBSMS] | CVIS
5/25/2024 6:15:35 PM | [NSO Update] Visayas Grid-05/25/2024 18:15: System Advisory: 25-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1900H-2100H. Total capacity on forced outage is 574.6MW. Total of de-rated capacity is 198.3MW. [WEBSMS] | CVIS
5/25/2024 5:48:39 PM | Visayas Grid-05/25/2024 17:48: KSPC U1 cut-in at 1746H (Unplanned Outage) [WEBSMS] | CVIS
5/25/2024 5:38:56 PM | [NSO Update] Luzon Grid-05/25/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12223MW, PK=10875MW, RR=389MW, NetOpMargin: EVE=959 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @180MW, MSLC1 @330MW, MSLC2 @340MW, SUAL 1 @550MW, SUAL 2 @570MW [WEBSMS] | CLUZ
5/25/2024 5:37:26 PM | [NSO Update] Mindanao Grid-05/25/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2948MW, PK=2300MW, RR=73MW, NetOpMargin: EVE=575 Highest Unit O/L: GNPK 1, 2, & 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/25/2024 5:35:27 PM | [NSO Update] Luzon Grid-05/25/2024 17:35: Weather Update: At 3:00 PM today, the center of Tropical Depression AGHON was estimated based on all available data over the coastal waters of Sibuyan Island (12.7 N, 122.8 E) with maximum sustained winds of 45 km/h near the center and gustiness of up to 70 km/h. It is moving West Northwestward at 20 km/h. [WEBSMS] | CLUZ
5/25/2024 5:35:09 PM | [NSO Update] Visayas Grid-05/25/2024 17:35: Weather Update: At 3:00 PM today, the center of Tropical Depression AGHON was estimated based on all available data over the coastal waters of Sibuyan Island (12.7 N, 122.8 E) with maximum sustained winds of 45 km/h near the center and gustiness of up to 70 km/h. It is moving West Northwestward at 20 km/h. [WEBSMS] | CVIS
5/25/2024 5:34:55 PM | [NSO Update] Mindanao Grid-05/25/2024 17:40: Weather Update: At 3:00 PM today, the center of Tropical Depression AGHON was estimated based on all available data over the coastal waters of Sibuyan Island (12.7 N, 122.8 E) with maximum sustained winds of 45 km/h near the center and gustiness of up to 70 km/h. It is moving West Northwestward at 20 km/h. [WEBSMS] | CMIN
5/25/2024 5:01:42 PM | Mindanao Grid-05/25/2024 17:07: WMPC DG04 shutdown at 1659H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/25/2024 5:00:57 PM | Luzon Grid-05/25/2024 17:01: Ilijan GT1-2 shutdown at 1659H. (Unplanned Outage) [WEBSMS] | CLUZ
5/25/2024 4:51:58 PM | Luzon Grid-05/25/2024 16:52: Ilijan GT2-1 shutdown at 1646H. (Unplanned Outage) [WEBSMS] | CLUZ
5/25/2024 4:46:22 PM | Luzon Grid-05/25/2024 16:46: Tayabas PCB 9-02CB24TAY was energized at 1645H. (Planned Outage) [WEBSMS] | CLUZ
5/25/2024 4:39:36 PM | Luzon Grid-05/25/2024 16:39: Ilijan Block A ST1 and Ilijan Block B ST2 shutdown at 1636H. (Unplanned Outage due to gas supply trouble) [WEBSMS] | CLUZ
5/25/2024 4:20:32 PM | Mindanao Grid-05/25/2024 16:26: Zamboanga SS 138kV Bus 2 energized at 1618H. (Planned Outage) [WEBSMS] | CMIN
5/25/2024 3:59:33 PM | Mindanao Grid-05/25/2024 16:05: Davao SS 150 MVA Transformer No. 1 energized at 1554H (Planned Outage) [WEBSMS] | CMIN
5/25/2024 3:32:22 PM | Visayas Grid-05/25/2024 15:32: Dumanjug - Samboan 138 kV Line 1 energized at 1531H (Planned Outage) [WEBSMS] | CVIS
5/25/2024 2:18:01 PM | Luzon Grid-05/25/2024 14:18: Tayabas PCB 9-02CB24TAY was de-energized at 1411H. (Planned Outage) [WEBSMS] | CLUZ
5/25/2024 1:38:58 PM | Mindanao Grid-05/25/2024 13:44: AGUS 1 HEP Unit 2 online at 1311H from PMS- GOMP. (Planned Outage) [WEBSMS] | CMIN
5/25/2024 1:17:41 PM | Mindanao Grid-05/25/2024 13:23: WMPC DG04 online at 1314H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/25/2024 1:01:37 PM | [NSO Update] Luzon Grid-05/25/2024 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13802MW, PK=11938MW, RR=441MW, NetOpMargin: PM=1422, EVE=671 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @300MW, Sual 2 @570MW, Calaca U2 @180MW, Masinloc 1 @330MW, Ilijan B @300MW, Angat Main HEP @78MW, Sual 1 @550MW [WEBSMS] | CLUZ
5/25/2024 12:43:51 PM | [NSO Update] Visayas Grid-05/25/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2426MW, PK=2135MW, RR=91MW, NetOpMargin: PM=200, EVE=182 Highest Unit O/L: THVI 1@169MW Derated Plant: Leyte A @307MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Power Barge 104-2 @6MW [WEBSMS] | CVIS
5/25/2024 12:40:02 PM | [NSO Update] Luzon Grid-05/25/2024 12:40: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1225H with power going to Visayas. [WEBSMS] | CLUZ
5/25/2024 12:39:27 PM | [NSO Update] Visayas Grid-05/25/2024 12:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1225H with power going to Visayas. [WEBSMS] | CVIS
5/25/2024 12:37:09 PM | [NSO Update] Mindanao Grid-05/25/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2987MW, PK=2285MW, RR=73MW, NetOpMargin: PM=629, EVE=631 Highest Unit O/L: GNPK 1, 2, 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/25/2024 12:17:52 PM | [NSO Update] Luzon Grid-05/25/2024 12:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1215H from forward power direction. [WEBSMS] | CLUZ
5/25/2024 12:17:29 PM | [NSO Update] Visayas Grid-05/25/2024 12:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1215H from forward power direction. [WEBSMS] | CVIS
5/25/2024 10:46:50 AM | Mindanao Grid-05/25/2024 10:52: WMPC DG10 online at 1045H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/25/2024 9:50:00 AM | [NSO Update] Visayas Grid-05/25/2024 09:50: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0940H with power going to Luzon. [WEBSMS] | CVIS
5/25/2024 9:49:56 AM | [NSO Update] Luzon Grid-05/25/2024 09:50: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0940H with power going to Luzon. [WEBSMS] | CLUZ
5/25/2024 9:36:00 AM | Luzon Grid-05/25/2024 09:36: San Rafael - Cabanatuan 230kv Line restored at 0935H (Planned Outage) [WEBSMS] | CLUZ
5/25/2024 9:16:26 AM | [NSO Update] Luzon Grid-05/25/2024 09:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0909H from forward power direction. [WEBSMS] | CLUZ
5/25/2024 9:15:41 AM | [NSO Update] Visayas Grid-05/25/2024 09:15: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0909H from forward power direction. [WEBSMS] | CVIS
5/25/2024 9:09:35 AM | Mindanao Grid-05/25/2024 09:15: Zamboanga SS 138kV BUS #2 de-energized at 0905H. Planned Outage. [WEBSMS] | CMIN
5/25/2024 8:38:01 AM | Visayas Grid-05/25/2024 08:38: PGPP 1 unit 1 re-online at 0834H (Unplanned Outage) [WEBSMS] | CVIS
5/25/2024 8:05:41 AM | Visayas Grid-05/25/2024 08:05: THVI unit 2 auto-tripped 0752H load. (Unplanned Outage) [WEBSMS] | CVIS
5/25/2024 7:36:51 AM | Luzon Grid-05/25/2024 07:37: San Esteban - Laoag 230kv Line 2 restored at 0736H (Planned Outage) [WEBSMS] | CLUZ
5/25/2024 7:17:29 AM | Visayas Grid-05/25/2024 07:17: Sogongon unit # 2 re-online at 0715H. (Unplanned Outage) [WEBSMS] | CVIS
5/25/2024 7:14:08 AM | Visayas Grid-05/25/2024 07:14: Amlan-PGPP1 138KV Line 1 energized at Amlan SS side at 0709H (Unplanned Outage) [WEBSMS] | CVIS
5/25/2024 6:48:37 AM | Visayas Grid-05/25/2024 06:48: Dumanjug-Samboan 138KV Line 1 de-energized at 0642H (Planned Outage) [WEBSMS] | CVIS
5/25/2024 6:47:48 AM | Mindanao Grid-05/25/2024 06:53: Davao SS 150MVA Transformer No. 1 de-energized at 0642H. (Planned Outage) [WEBSMS] | CMIN
5/25/2024 6:35:27 AM | [NSO Update] Mindanao Grid-05/25/2024 06:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3004MW, PK=2179MW, RR=73MW, NetOpMargin: AM=752, PM=504, EVE=481 Highest Unit O/L: GNPK 1, 2, 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/25/2024 6:34:35 AM | Mindanao Grid-05/25/2024 06:40: Nagamin SS 138kV Bus no. 1 energized at 0634H. (Planned Outage) [WEBSMS] | CMIN
5/25/2024 6:31:53 AM | [NSO Update] Visayas Grid-05/25/2024 06:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2505MW, PK=1995MW, RR=86MW, NetOpMargin: AM=424, PM=353, EVE=271 Highest Unit O/L: THVI 1 & 2 @ 169M Derated Plant: Leyte A @300MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Power Barge 104-2 @6MW, PGPP1 @35.5MW [WEBSMS] | CVIS
5/25/2024 6:31:27 AM | Visayas Grid-05/25/2024 06:31: PGPP 1 unit 3 re-online at 0628H (Unplanned Outage) [WEBSMS] | CVIS
5/25/2024 6:26:27 AM | Mindanao Grid-05/25/2024 06:32: PULANGI 4 Unit 3 with 20.5MW load shutdown at 0605H. (Unplanned Outage) [WEBSMS] | CMIN
5/25/2024 6:25:59 AM | [NSO Update] Luzon Grid-05/25/2024 06:26: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14388MW, PK=12086MW, RR=400MW, NetOpMargin: AM=1902, PM=1326, EVE=704 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @300MW, Sual 2 @570MW, Calaca U2 @180MW, Masinloc 1 @330MW, Ilijan B @300MW, Angat Main HEP @78MW, Sual 1 @550MW [WEBSMS] | CLUZ
5/25/2024 6:13:39 AM | Mindanao Grid-05/25/2024 06:19: Maramag-Pulangi 4 138kV L3, de-energized at 0605H. Planned Outage. [WEBSMS] | CMIN
5/25/2024 5:56:14 AM | Visayas Grid-05/25/2024 05:56: PGPP 2 OKOY re-on line @ 0554H.( Unplanned Outage ) [WEBSMS] | CVIS
5/25/2024 5:27:32 AM | Visayas Grid-05/25/2024 05:27: Sogongon unit # 1 re-online at 0523H. [WEBSMS] | CVIS
5/25/2024 4:52:12 AM | [NSO Update] Mindanao Grid-05/25/2024 04:58: Weather Update: At 3:00 AM today, the center of Tropical Depression "AGHON" was estimated based on all available data in the vicinity of Santa Rita, Samar (11.5�N, 125.1�E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving Northwestward at 30 km/h. [WEBSMS] | CMIN
5/25/2024 4:51:48 AM | [NSO Update] Visayas Grid-05/25/2024 04:51: Weather Update: At 3:00 AM today, the center of Tropical Depression "AGHON" was estimated based on all available data in the vicinity of Santa Rita, Samar (11.5�N, 125.1�E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving Northwestward at 30 km/h. [WEBSMS] | CVIS
5/25/2024 4:51:23 AM | [NSO Update] Luzon Grid-05/25/2024 04:51: Weather Update: At 3:00 AM today, the center of Tropical Depression "AGHON" was estimated based on all available data in the vicinity of Santa Rita, Samar (11.5�N, 125.1�E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving Northwestward at 30 km/h. [WEBSMS] | CLUZ
5/25/2024 4:39:13 AM | Visayas Grid-05/25/2024 04:39: PGPP I total plant tripping, Sogongon U#1 & 2 and OKOY tripped at 0428H with total load of 169.5 MW. ( Unplanned Outage ) [WEBSMS] | CVIS
5/25/2024 4:18:41 AM | Luzon Grid-05/25/2024 04:18: San Esteban - Laoag 230kv Line 2 de-energized at 0418H (Planned Outage) [WEBSMS] | CLUZ
5/25/2024 4:09:17 AM | Luzon Grid-05/25/2024 04:09: San Rafael - Cabanatuan 230kv Line de-energized at 0409H (Planned Outage) [WEBSMS] | CLUZ
5/25/2024 4:08:33 AM | Mindanao Grid-05/25/2024 04:14: PULANGI 4 Unit 1 online at 0407H (Unplanned Outage) [WEBSMS] | CMIN
5/25/2024 2:51:07 AM | Mindanao Grid-05/25/2024 02:57: GNPK Unit 4 emergency shutdown at 0248H due to suspected tube leak at boiler (Unplanned Outage) [WEBSMS] | CMIN
5/25/2024 1:19:55 AM | Luzon Grid-05/25/2024 01:20: Ilijan Block B GT2-2 shutdown at 0117H (Unplanned Outage) [WEBSMS] | CLUZ
5/25/2024 12:50:57 AM | [NSO Update] Luzon Grid-05/25/2024 00:51: 25-May-2024, ERC has lifted market suspension for Luzon grid today at 0050H. Market operations will resume starting interval 0055H. [WEBSMS] | CLUZ
5/25/2024 12:37:39 AM | Luzon Grid-05/25/2024 00:37: Ilijan Block A GT1-1 shutdown at 0031H (Unplanned Outage) [WEBSMS] | CLUZ
5/25/2024 12:18:44 AM | Mindanao Grid-05/25/2024 00:24: Naga Mindanao 138kV Bus 1 de-energized/shutdown at 0003H. (Planned Outage) [WEBSMS] | CMIN
5/24/2024 11:30:48 PM | [NSO Update] Luzon Grid-05/24/2024 23:30: Update on System Advisory: Luzon Grid Yellow Alert notice issued today is lifted at 2325H [WEBSMS] | CLUZ
5/24/2024 11:24:28 PM | Mindanao Grid-05/24/2024 23:30: MANOLO FORTICH 2 Unit 3 online at 2242H (Unplanned Outage) [WEBSMS] | CMIN
5/24/2024 11:23:32 PM | Mindanao Grid-05/24/2024 23:29: MANOLO FORTICH 2 Unit 2 online at 2233H (Unplanned Outage) [WEBSMS] | CMIN
5/24/2024 10:29:11 PM | [NSO Update] Visayas Grid-05/24/2024 22:29: 24-May-2024, ERC has lifted market suspension for Visayas grid today at 2229H. Market operations will resume starting interval 2235H. [WEBSMS] | CVIS
5/24/2024 10:18:17 PM | Mindanao Grid-05/24/2024 22:24: WMPC DG10 shutdown at 2216H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/24/2024 10:04:43 PM | Luzon Grid-05/24/2024 22:04: Daraga-Tiwi C 230kV Line de-energized at 2204H. (Planned Outage) [WEBSMS] | CLUZ
5/24/2024 9:30:21 PM | [NSO Update] Visayas Grid-05/24/2024 21:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2125H with power going to Luzon [WEBSMS] | CVIS
5/24/2024 9:29:38 PM | [NSO Update] Luzon Grid-05/24/2024 21:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2125H with power going to Luzon [WEBSMS] | CLUZ
5/24/2024 9:18:43 PM | [NSO Update] Luzon Grid-05/24/2024 21:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2115H from reverse power direction [WEBSMS] | CLUZ
5/24/2024 9:17:59 PM | [NSO Update] Visayas Grid-05/24/2024 21:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2115H from reverse power direction [WEBSMS] | CVIS
5/24/2024 8:54:53 PM | Mindanao Grid-05/24/2024 21:00: MANOLO FORTICH 1 Unit 4 online at 2052H (Unplanned Outage) [WEBSMS] | CMIN
5/24/2024 7:15:55 PM | [NSO Update] Visayas Grid-05/24/2024 19:16: The Visayas Grid is on "BLUE ALERT" due to Tropical Depression �AGHON� is forecast to move generally west northwestward to northwestward from today until tomorrow while slowly intensifying. On the track forecast, AGHON is forecast to make landfall over the southern portion of Eastern Samar or Dinagat Islands by tomorrow morning as a tropical storm. [WEBSMS] | CVIS
5/24/2024 6:58:39 PM | [NSO Update] Visayas Grid-05/24/2024 18:58: Update on System Advisory: Visayas Grid Yellow Alert notice issued today is lifted at 1854H [WEBSMS] | CVIS
5/24/2024 6:52:05 PM | [NSO Update] Luzon Grid-05/24/2024 18:52: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=13073MW, PK=12148MW, RR=419MW, NetOpMargin: EVE=506 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @400MW, SLTEC 1 @117MW, SLTEC 2 @119MW, Masinloc 1 @330MW, Limay 4 @60MW, Calaca 2 @120MW, Angat Main HEP @78MW, Sual 1 @450MW, Sual 2 @540MW [WEBSMS] | CLUZ
5/24/2024 6:46:56 PM | [NSO Update] Visayas Grid-05/24/2024 18:47: GRID UPDATE AS OF Invalid date System Condition: NORMAL CAP=2578MW, PK=2214MW, RR=91MW, Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @302MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Power Barge 104-2 @6MW [WEBSMS] | CVIS
5/24/2024 6:44:24 PM | [NSO Update] Mindanao Grid-05/24/2024 18:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3080MW, PK=2220MW, RR=73MW, NetOpMargin: EVE=787 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/24/2024 6:39:54 PM | [NSO Update] Mindanao Grid-05/24/2024 18:45: The Visayas Grid is on "BLUE ALERT" due to Tropical Depression �AGHON� is forecast to move generally west northwestward to northwestward from today until tomorrow while slowly intensifying. On the track forecast, AGHON is forecast to make landfall over the southern portion of Eastern Samar or Dinagat Islands by tomorrow morning as a tropical storm. [WEBSMS] | CMIN
5/24/2024 6:39:25 PM | [NSO Update] Luzon Grid-05/24/2024 18:39: The Visayas Grid is on "BLUE ALERT" due to Tropical Depression �AGHON� is forecast to move generally west northwestward to northwestward from today until tomorrow while slowly intensifying. On the track forecast, AGHON is forecast to make landfall over the southern portion of Eastern Samar or Dinagat Islands by tomorrow morning as a tropical storm. [WEBSMS] | CLUZ
5/24/2024 6:38:18 PM | [NSO Update] Luzon Grid-05/24/2024 18:38: The Visayas Grid is on "BLUE ALERT" due to The Visayas Grid is on "BLUE ALERT" due to Tropical Depression �AGHON� is forecast to move generally west northwestward to northwestward from today until tomorrow while slowly intensifying. On the track forecast, AGHON is forecast to make landfall over the southern portion of Eastern Samar or Dinagat Islands by tomorrow morning as a tropical storm. [WEBSMS] | CLUZ
5/24/2024 6:37:27 PM | [NSO Update] Luzon Grid-05/24/2024 18:37: The Visayas Grid is on "BLUE ALERT" due to The Visayas Grid is on "BLUE ALERT" due to Tropical Depression �AGHON� is forecast to move generally west northwestward to northwestward from today until tomorrow while slowly intensifying. On the track forecast, AGHON is forecast to make landfall over the southern portion of Eastern Samar or Dinagat Islands by tomorrow morning as a tropical storm. [WEBSMS] | CLUZ
5/24/2024 4:36:53 PM | Luzon Grid-05/24/2024 16:37: Calaca Unit 2 online at 1635H. (Unplanned Outage) [WEBSMS] | CLUZ
5/24/2024 4:03:48 PM | Mindanao Grid-05/24/2024 16:09: WMPC DG4 Shutdown at 1601H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/24/2024 3:47:14 PM | Luzon Grid-05/24/2024 15:47: Calaca 2 with 220MW load tripped at 1543H. Lowest system frequency was 59.410Hz. (Unplanned Outage) [WEBSMS] | CLUZ
5/24/2024 1:20:33 PM | [NSO Update] Luzon Grid-05/24/2024 13:20: Update on System Advisory: 24-May-2024, Luzon Grid is on YELLOW Alert for interval hour 1400H-2300H. Total capacity on forced outage is 1661.5MW. Total of de-rated capacity is 683MW. [WEBSMS] | CLUZ
5/24/2024 1:19:43 PM | [NSO Update] Visayas Grid-05/24/2024 13:19: Update on System Advisory: 24-May-2024, Visayas Grid is on YELLOW Alert for interval hours 2100H-2200H. Total capacity on forced outage is 485.3MW. Total of de-rated capacity is 200.3MW. [WEBSMS] | CVIS
5/24/2024 1:13:40 PM | [NSO Update] Luzon Grid-05/24/2024 13:13: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14331MW, PK=13691MW, RR=441MW, NetOpMargin: PM=199, EVE=252 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @400MW, SLTEC 1 @117MW, SLTEC 2 @119MW, Masinloc 1 @330MW, Limay 4 @60MW, Calaca 2 @190MW, Angat Main HEP @78MW, Sual 1 @450MW [WEBSMS] | CLUZ
5/24/2024 1:06:01 PM | [NSO Update] Visayas Grid-05/24/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2681MW, PK=2312MW, RR=91MW, NetOpMargin: PM=278, EVE=12 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @302MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Power Barge 104-2 @6MW [WEBSMS] | CVIS
5/24/2024 1:01:04 PM | [NSO Update] Mindanao Grid-05/24/2024 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3109MW, PK=2462MW, RR=73MW, NetOpMargin: PM=574, EVE=593 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/24/2024 12:50:35 PM | Mindanao Grid-05/24/2024 12:56: Bunawan - Nabunturan 138kV Line energized/looped at 1245H. (Unplanned Outage) [WEBSMS] | CMIN
5/24/2024 11:44:59 AM | Luzon Grid-05/24/2024 11:45: Naga-Tiwi C 230kV line 1 was restored at 1144H. (Unplanned Outage) [WEBSMS] | CLUZ
5/24/2024 11:39:14 AM | Luzon Grid-05/24/2024 11:39: Naga-Tiwi C 230kV line 1 auto-tripped at 1131H. (Unplanned Outage) [WEBSMS] | CLUZ
5/24/2024 10:06:48 AM | Mindanao Grid-05/24/2024 10:12: WMPC DG04 online at 0930H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/24/2024 9:35:03 AM | Mindanao Grid-05/24/2024 09:41: WMPC DG4 Online at 0930H. MRU _ System Voltage Requirement. [WEBSMS] | CMIN
5/24/2024 9:33:48 AM | Mindanao Grid-05/24/2024 09:39: WMPC DG4 online at 0930H. [WEBSMS] | CMIN
5/24/2024 8:27:20 AM | [NSO Update] Luzon Grid-05/24/2024 08:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0823H with power going to Visayas. [WEBSMS] | CLUZ
5/24/2024 8:26:49 AM | [NSO Update] Visayas Grid-05/24/2024 08:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0823H with power going to Visayas. [WEBSMS] | CVIS
5/24/2024 8:25:04 AM | [NSO Update] Luzon Grid-05/24/2024 08:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0813H from forward power direction. [WEBSMS] | CLUZ
5/24/2024 8:24:28 AM | [NSO Update] Visayas Grid-05/24/2024 08:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0813H from forward power direction. [WEBSMS] | CVIS
5/24/2024 7:46:02 AM | Mindanao Grid-05/24/2024 07:52: Naga Mindanao SS 138kV SVC energized at 0742H. (Planned Outage) [WEBSMS] | CMIN
5/24/2024 7:39:51 AM | Mindanao Grid-05/24/2024 07:45: Naga Mindanao 138kV Bus 2 energized at 0738H. (Planned Outage) [WEBSMS] | CMIN
5/24/2024 7:31:19 AM | Mindanao Grid-05/24/2024 07:37: Kibawe - Tacurong 138kV Line re-energize/loop at 0726H. (Unplanned Outage) [WEBSMS] | CMIN
5/24/2024 7:23:44 AM | Mindanao Grid-05/24/2024 07:29: Kibawe - Tacurong 138kV Line tripped at 0709H. (Unplanned Outage) [WEBSMS] | CMIN
5/24/2024 6:41:17 AM | [NSO Update] Visayas Grid-05/24/2024 06:41: System Advisory: 24-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1300H-2200H. Total capacity on forced outage is 485.3MW. Total of de-rated capacity is 200.3MW. [WEBSMS] | CVIS
5/24/2024 6:38:27 AM | [NSO Update] Luzon Grid-05/24/2024 06:38: System Advisory: 24-May-2024, Luzon Grid is on YELLOW Alert for interval hour 1400H-1600H and 1900H-2300H. Total capacity on forced outage is 1661.5MW. Total of de-rated capacity is 624MW. [WEBSMS] | CLUZ
5/24/2024 6:28:22 AM | [NSO Update] Visayas Grid-05/24/2024 06:28: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2882MW, PK=2533MW, RR=91MW, NetOpMargin: AM=258, PM=124, EVE=28 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @302MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Power Barge 104-2 @6MW [WEBSMS] | CVIS
5/24/2024 6:26:33 AM | [NSO Update] Luzon Grid-05/24/2024 06:26: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=14749MW, PK=13238MW, RR=340MW, NetOpMargin: AM=1171, PM=459, EVE=138 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: Calaca 2 @ 150MW, GNPD 1 @ 600MW, Masinloc 1 @ 330MW, SLTEC 1 @ 117MW, SLTEC 2 @ 119MW, Ilijan A @ 400MW, Limay 4 @ 30MW [WEBSMS] | CLUZ
5/24/2024 6:09:19 AM | Mindanao Grid-05/24/2024 06:15: Bunawan-Nabunturan 138 kV Line auto-tripped at 0547H and reclosed at Nabunturan side only. Unplanned Outage [WEBSMS] | CMIN
5/24/2024 5:51:25 AM | Visayas Grid-05/24/2024 05:51: KSPC unit # 1 auto tripped at 0547H with load of 99MW. ( Unplanned Outage ) [WEBSMS] | CVIS
5/24/2024 5:43:27 AM | [NSO Update] Mindanao Grid-05/24/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3132MW, PK=2609MW, RR=73MW, NetOpMargin: AM=451, PM=354, EVE=509 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/24/2024 5:23:39 AM | [NSO Update] Luzon Grid-05/24/2024 05:23: Weather Disturbance Alert Notice (WDAN) is issued at 0500H. Tropical Depression �AGHON� has entered the Philippine Area of Responsibility (PAR). The center of the eye was estimated based on all available data at 350 km East of Hinatuan, Surigao del Sur (8.3�N, 129.5�E) with maximum sustained winds of 45 km/h near the center and gustiness of up to 55 km/h. It is moving West Northwestward at 30km/h [WEBSMS] | CLUZ
5/24/2024 5:15:37 AM | [NSO Update] Mindanao Grid-05/24/2024 05:21: Weather Disturbance Alert Notice (WDAN) is issued at 0500H. Tropical Depression �AGHON� has entered the Philippine Area of Responsibility (PAR). The center of the eye was estimated based on all available data at 350 km East of Hinatuan, Surigao del Sur (8.3�N, 129.5�E) with maximum sustained winds of 45 km/h near the center and gustiness of up to 55 km/h. It is moving West Northwestward at 30 km/h. [WEBSMS] | CMIN
5/24/2024 5:15:21 AM | [NSO Update] Visayas Grid-05/24/2024 05:15: Weather Disturbance Alert Notice (WDAN) is issued at 0500H. Tropical Depression �AGHON� has entered the Philippine Area of Responsibility (PAR). The center of the eye was estimated based on all available data at 350 km East of Hinatuan, Surigao del Sur (8.3�N, 129.5�E) with maximum sustained winds of 45 km/h near the center and gustiness of up to 55 km/h. It is moving West Northwestward at 30km/h [WEBSMS] | CVIS
5/24/2024 1:09:32 AM | [NSO Update] Luzon Grid-05/24/2024 01:09: Update on System Advisory: Luzon Grid Yellow Alert notice issued today is lifted at 0107H. [WEBSMS] | CLUZ
5/24/2024 12:52:25 AM | [NSO Update] Luzon Grid-05/24/2024 00:52: Update on System Advisory: Luzon Grid Red Alert notice issued on 23-May-2024 is lifted today at 0050H. Luzon Grid still on Yellow Alert for interval 0100H. [WEBSMS] | CLUZ
5/24/2024 12:47:19 AM | [NSO Update] Visayas Grid-05/24/2024 00:47: Update on System Advisory: Visayas Grid Yellow Alert notice issued on 23-May-2024 is lifted today at 0045H. [WEBSMS] | CVIS
5/24/2024 12:27:52 AM | [NSO Update] Visayas Grid-05/24/2024 00:27: Update on System Advisory: 23-May-2024, Visayas Grid is on YELLOW Alert for interval hour 2400H. Total capacity on forced outage is 383.8MW. Total of de-rated capacity is 200.3MW. [WEBSMS] | CVIS
5/24/2024 12:26:27 AM | [NSO Update] Luzon Grid-05/24/2024 00:26: Update on System Advisory: 23-May-2024, Luzon Grid is on RED Alert for interval hour 2400H and YELLOW Alert for interval hour 0100H of 24-May-2024. Total capacity on forced outage is 2688.5MW. Total of de-rated capacity is 1176MW. [WEBSMS] | CLUZ
5/24/2024 12:06:22 AM | Mindanao Grid-05/24/2024 00:12: NagaMin SS 138 kV Bus 2 de-energized at 0004H. Planned Outage [WEBSMS] | CMIN
5/24/2024 12:03:10 AM | Mindanao Grid-05/24/2024 00:09: Naga Mindanao SS 138kV SVC De-energized/shutdown at 0002H. (Planned Outage) [WEBSMS] | CMIN
5/24/2024 12:00:42 AM | Luzon Grid-05/24/2024 00:00: Affected MLD issued at 1925H in feeders of MERALCO and NGCP restored at 2355H and 2345H, respectively. [WEBSMS] | CLUZ
5/23/2024 11:41:05 PM | Luzon Grid-05/23/2024 23:41: Sual 1 online at 2337H (Unplanned Outage) [WEBSMS] | CLUZ
5/23/2024 11:20:48 PM | [NSO Update] Visayas Grid-05/23/2024 23:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2318H with power going to Luzon. [WEBSMS] | CVIS
5/23/2024 11:20:33 PM | [NSO Update] Luzon Grid-05/23/2024 23:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2318H with power going to Luzon. [WEBSMS] | CLUZ
5/23/2024 10:59:21 PM | Mindanao Grid-05/23/2024 23:05: WMPC DG06 shutdown at 2256H. End of MRU Operation- System Voltage Requirement. [WEBSMS] | CMIN
5/23/2024 10:37:06 PM | [NSO Update] Visayas Grid-05/23/2024 22:37: Update on System Advisory: Visayas Grid Red Alert notice issued today is lifted at 2229H. Visayas Grid still on Yellow Alert for interval 2300H. [WEBSMS] | CVIS
5/23/2024 10:14:14 PM | [NSO Update] Visayas Grid-05/23/2024 22:14: Update on System Advisory: 23-May-2024, Visayas Grid is on RED Alert for interval hour 2200H and YELLOW Alert for interval hour 2300H. Total capacity on forced outage is 383.8MW. Total of de-rated capacity is 200.3MW. [WEBSMS] | CVIS
5/23/2024 9:17:52 PM | Mindanao Grid-05/23/2024 21:23: WMPC DG07 shutdown at 2116H. End of MRU Operation- System Voltage Requirement. [WEBSMS] | CMIN
5/23/2024 9:15:17 PM | Visayas Grid-05/23/2024 21:15: VECO last feeder in at 2113H. [WEBSMS] | CVIS
5/23/2024 8:28:32 PM | [NSO Update] Luzon Grid-05/23/2024 20:28: Update on System Advisory: 23-May-2024, Luzon Grid is on RED Alert for interval hours 2100H-2300H and YELLOW Alert for interval hour 2400H. Total capacity on forced outage is 2618.5MW. Total of de-rated capacity is 1176MW. [WEBSMS] | CLUZ
5/23/2024 8:14:48 PM | Visayas Grid-05/23/2024 20:14: CEBECO 1 feeder restored at 1945H (Unplanned Outage) [WEBSMS] | CVIS
5/23/2024 8:13:45 PM | Visayas Grid-05/23/2024 20:13: CEBECO 3 feeder restored at 1944H (Unplanned Outage) [WEBSMS] | CVIS
5/23/2024 7:49:13 PM | Mindanao Grid-05/23/2024 19:55: WMPC DG04 shutdown at 1947H. End of MRU Operation- System Voltage Requirement. [WEBSMS] | CMIN
5/23/2024 7:29:33 PM | Luzon Grid-05/23/2024 19:29: Demand Control Imminent Warning (DCIW) is re-issued at 1907H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency [WEBSMS] | CLUZ
5/23/2024 6:31:27 PM | Visayas Grid-05/23/2024 18:31: VECO total ILP implemented at 14MW. [WEBSMS] | CVIS
5/23/2024 6:29:45 PM | Visayas Grid-05/23/2024 18:29: CEBECO1/CEBECO2/VECO/CEBECO3 implemented MLD at 1745H/1800H/1815H/1817H with a load of 6MW/3MW/16.1MW/1.4MW due to Visayas gen deficiency. [WEBSMS] | CVIS
5/23/2024 6:09:13 PM | [NSO Update] Luzon Grid-05/23/2024 18:09: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=12284MW, PK=12271MW, RR=429MW, NetOpMargin: EVE=0 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: GMEC 1 & 2 @ 260MW, Masinloc 1 @ 340MW, SLTEC 1 @ 117MW, SLTEC 2 @ 119MW, Limay 4 @ 30MW, Ilijan A @ 420MW [WEBSMS] | CLUZ
5/23/2024 5:56:58 PM | [NSO Update] Visayas Grid-05/23/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=2436MW, PK=2443MW, RR=91MW, NetOpMargin: EVE=0 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Power Barge 101-2 @1MW [WEBSMS] | CVIS
5/23/2024 5:54:49 PM | [NSO Update] Mindanao Grid-05/23/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3085MW, PK=2519MW, RR=73MW, NetOpMargin: EVE=493 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.1MW, MA2 @32MW [WEBSMS] | CMIN
5/23/2024 5:12:48 PM | Mindanao Grid-05/23/2024 17:18: WMPC DG03 shutdown at 1709H. End of MRU Operation- System Voltage Requirement. [WEBSMS] | CMIN
5/23/2024 4:06:07 PM | Visayas Grid-05/23/2024 16:06: VECO implemented ILP at 1600H, gen deficiency (Unplanned Outage) [WEBSMS] | CVIS
5/23/2024 3:47:09 PM | Luzon Grid-05/23/2024 15:47: Calaca 2 online at 1543H (Unplanned Outage) [WEBSMS] | CLUZ
5/23/2024 2:39:41 PM | [NSO Update] Luzon Grid-05/23/2024 14:39: Correction: System Advisory: 23-May-2024, Luzon Grid is on RED Alert for interval hours 1400H-1600H and 1900H-2200H, and YELLOW Alert for interval hours 1300H, 1700H-1800H, 2300H& 2400H. Total capacity on forced outage is 2708.5MW. Total of de-rated capacity is 407MW. [WEBSMS] | CLUZ
5/23/2024 2:35:26 PM | Luzon Grid-05/23/2024 14:35: Dasmarinas-TMC II (Ternate) 115kV restored at 1431H (Planned Outage) [WEBSMS] | CLUZ
5/23/2024 2:32:57 PM | Mindanao Grid-05/23/2024 14:38: WMPC DG08 shutdown at 1431H. End of MRU Operation - System Voltage Requirement. [WEBSMS] | CMIN
5/23/2024 2:29:07 PM | Visayas Grid-05/23/2024 14:29: MECO (Gaisano Metro) implemented 0.8 MW ILP at 1325H [WEBSMS] | CVIS
5/23/2024 2:26:49 PM | Visayas Grid-05/23/2024 14:26: MECO (Sheraton) implemented 1.5 MW ILP at 1330H [WEBSMS] | CVIS
5/23/2024 2:24:04 PM | Visayas Grid-05/23/2024 14:24: GMC implemented additional 1.5 MW ILP at 1312H [WEBSMS] | CVIS
5/23/2024 2:18:33 PM | Visayas Grid-05/23/2024 14:18: MECO (Gaisano Grand Mall) implemented 1.7 MW ILP at 1315H [WEBSMS] | CVIS
5/23/2024 2:15:00 PM | Visayas Grid-05/23/2024 14:15: MECO (Gaisano Island Mall) implemented 1.4 MW ILP at 1312H [WEBSMS] | CVIS
5/23/2024 2:09:28 PM | Visayas Grid-05/23/2024 14:09: MECO (JPark) ILP cut off at 1212H [WEBSMS] | CVIS
5/23/2024 1:57:45 PM | [NSO Update] Visayas Grid-05/23/2024 13:57: Correction: Update on System Advisory: 23-May-2024, Visayas Grid is on RED Alert for interval hours 1400H-2100H and YELLOW Alert for interval hours 1300H, 2200H, and 2300H. Total capacity on forced outage is 388.8MW. Total of de-rated capacity is 200.3MW. [WEBSMS] | CVIS
5/23/2024 1:28:16 PM | [NSO Update] Visayas Grid-05/23/2024 13:28: Update on System Advisory: 23-May-2024, Visayas Grid is on RED Alert for interval hours 1400H-2100H and YELLOW Alert for interval hours 1300H, 2200H, and 2300H. Total capacity on forced outage is 375.8MW. Total of de-rated capacity is 200.3MW. [WEBSMS] | CVIS
5/23/2024 1:21:54 PM | [NSO Update] Luzon Grid-05/23/2024 13:21: System Advisory: 23-May-2024, Luzon Grid is on RED Alert for interval hours 1400H-1600H and 1900H-2200H, and YELLOW Alert for interval hours 1300H, 1700H-1800H, 2300H& 2400H. Total capacity on forced outage is 2528.5MW. Total of de-rated capacity is 407MW. [WEBSMS] | CLUZ
5/23/2024 1:21:24 PM | [NSO Update] Luzon Grid-05/23/2024 13:21: Updated System Advisory: 23-May-2024, Luzon Grid is on RED Alert for interval hours 1400H-1600H and 1900H-2200H, and YELLOW Alert for interval hours 1300H, 1700H-1800H, 2300H& 2400H. Total capacity on forced outage is 2528.5MW. Total of de-rated capacity is 407MW. [WEBSMS] | CLUZ
5/23/2024 1:19:44 PM | Luzon Grid-05/23/2024 13:19: SCPC 3 online at 1310H (Unplanned Outage) [WEBSMS] | CLUZ
5/23/2024 1:18:39 PM | [NSO Update] Visayas Grid-05/23/2024 13:18: 23-May-2024, ERC has declared market suspension for Visayas grid effective 1305H interval. [WEBSMS] | CVIS
5/23/2024 1:18:04 PM | [NSO Update] Luzon Grid-05/23/2024 13:18: 23-May-2024, ERC has declared market suspension for Luzon grid effective 1305H interval. [WEBSMS] | CLUZ
5/23/2024 1:17:34 PM | Luzon Grid-05/23/2024 13:17: May 23, 2024: Demand Control Imminent Warning (DCIW) is issued at 1315H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
5/23/2024 1:14:28 PM | [NSO Update] Luzon Grid-05/23/2024 13:14: Update on System Advisory: 23-May-2024, Luzon Grid is on RED Alert for interval hours 1400H-1600H and 1900H-2200H, and YELLOW Alert for interval hours 1300H, 1700H, 1800H, 2300H, and 2400H. Total capacity on forced outage is 2528.5MW. Total of de-rated capacity is 407MW. [WEBSMS] | CLUZ
5/23/2024 1:07:30 PM | [NSO Update] Mindanao Grid-05/23/2024 13:13: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3128MW, PK=2730MW, RR=38MW, NetOpMargin: PM=360, EVE=477 Highest Unit O/L: GNPK 1, 2, 3 &4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/23/2024 1:01:02 PM | [NSO Update] Visayas Grid-05/23/2024 13:01: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=2717MW, PK=2657MW, RR=91MW, NetOpMargin: PM=0, EVE=0 Highest Unit O/L: THVI 1& 2 @168MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Power Barge 101-2 @1MW [WEBSMS] | CVIS
5/23/2024 12:58:18 PM | [NSO Update] Luzon Grid-05/23/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=13441MW, PK=13438MW, RR=491MW, NetOpMargin: PM=0, EVE=0 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @420MW, SLTEC 1 @117MW, SLTEC 2 @118MW, Masinloc 1 @340MW, Limay 4 @30MW, GMEC 1 @240MW, GMEC 2 @240MW [WEBSMS] | CLUZ
5/23/2024 12:31:53 PM | Luzon Grid-05/23/2024 12:31: San Jose - Tayabas 500kV Line 2 energized at 1230H (On Commissioning) [WEBSMS] | CLUZ
5/23/2024 11:39:25 AM | Luzon Grid-05/23/2024 11:39: Olongapo-Subic 230kV Line auto-tripped/auto-reclosed at 1136H (Unplanned Outage) [WEBSMS] | CLUZ
5/23/2024 11:10:17 AM | Mindanao Grid-05/23/2024 11:16: TM2 Unit 1 online at 1054H - SO Dispatched. [WEBSMS] | CMIN
5/23/2024 10:33:02 AM | Mindanao Grid-05/23/2024 10:38: WMPC DG04 online at 1030H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/23/2024 10:29:07 AM | Visayas Grid-05/23/2024 10:29: GMC implemented 2.0 MW ILP at 1020H to prevent overloading of Cebu-Mandaue line 2. [WEBSMS] | CVIS
5/23/2024 10:26:51 AM | Visayas Grid-05/23/2024 10:26: MECO (JPark) implemented 2.2 MW ILP at 1020H to prevent overloading of Cebu-Mandaue line 2. [WEBSMS] | CVIS
5/23/2024 10:12:40 AM | Mindanao Grid-05/23/2024 10:18: WMPC DG07 online at 1010H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/23/2024 9:56:18 AM | Luzon Grid-05/23/2024 09:56: Calaca Unit 2 (80MW) tripped at 0952H. Lowest system frequency dipped to 59.696Hz. [WEBSMS] | CLUZ
5/23/2024 9:50:47 AM | Mindanao Grid-05/23/2024 09:56: WMPC DG08 online at 0949H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/23/2024 9:49:53 AM | Mindanao Grid-05/23/2024 09:55: WMPC DG08 online at 0949H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/23/2024 9:19:07 AM | Luzon Grid-05/23/2024 09:19: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0916H (Planned Outage) [WEBSMS] | CLUZ
5/23/2024 9:08:30 AM | Mindanao Grid-05/23/2024 09:14: Correction: WMPC DG06 online at 0903H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/23/2024 9:05:24 AM | Mindanao Grid-05/23/2024 09:11: WMPC DG6 online at 0903H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/23/2024 9:04:48 AM | Mindanao Grid-05/23/2024 09:10: WMPC DG06 online at 0906H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/23/2024 8:43:46 AM | [NSO Update] Visayas Grid-05/23/2024 08:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0835H with power going to Visayas. [WEBSMS] | CVIS
5/23/2024 8:43:17 AM | [NSO Update] Luzon Grid-05/23/2024 08:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0835H with power going to Visayas. [WEBSMS] | CLUZ
5/23/2024 8:26:59 AM | [NSO Update] Luzon Grid-05/23/2024 08:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0825H from forward power direction. [WEBSMS] | CLUZ
5/23/2024 8:26:24 AM | [NSO Update] Visayas Grid-05/23/2024 08:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0825H from forward power direction. [WEBSMS] | CVIS
5/23/2024 8:26:04 AM | Mindanao Grid-05/23/2024 08:31: WMPC DG10 online at 0823H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/23/2024 6:20:39 AM | [NSO Update] Mindanao Grid-05/23/2024 06:26: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3139MW, PK=2521MW, RR=38MW, NetOpMargin: AM=580, PM=546, EVE=610 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/23/2024 6:19:09 AM | [NSO Update] Visayas Grid-05/23/2024 06:19: GRID UPDATE AS OF 6:00 AM System Condition: RED ALERT CAP=2769MW, PK=2484MW, RR=91MW, NetOpMargin: AM=194, PM=25, EVE=0 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW [WEBSMS] | CVIS
5/23/2024 6:15:11 AM | [NSO Update] Luzon Grid-05/23/2024 06:15: GRID UPDATE AS OF 6:00 AM System Condition: RED ALERT CAP=14109MW, PK=12882MW, RR=510MW, NetOpMargin: AM=718, PM=0, EVE=0 Highest Unit O/L: GNPD 2 @668MW Derated Plant: Ilijan A @400MW, SLTEC 1 @117MW, SLTEC 2 @118MW, Masinloc 1 @330MW, Limay 4 @60MW, Limay 8 @60MW, Sual 2 @550MW, GNPD 1 @600MW, Angat Main @78MW [WEBSMS] | CLUZ
5/23/2024 6:10:33 AM | [NSO Update] Visayas Grid-05/23/2024 06:10: System Advisory: 23-May-2024, Visayas Grid is on RED Alert for interval hours 1500H, 1600H, and 1900H, and YELLOW Alert for interval hours 1300H, 1400H, 1700H, 1800H, 2000H, 2100H, and 2200H. Total capacity on forced outage is 356.8MW. Total of de-rated capacity is 196.3MW. [WEBSMS] | CVIS
5/23/2024 6:06:47 AM | [NSO Update] Luzon Grid-05/23/2024 06:06: System Advisory: 23-May-2024, Luzon Grid is on RED Alert for interval hours 1400H-1700H and 1900H-2200H, and YELLOW Alert for interval hours 1300H, 1800H, 2300H, and 2400H. Total capacity on forced outage is 1953.5MW. Total of de-rated capacity is 572MW. [WEBSMS] | CLUZ
5/23/2024 5:24:09 AM | Visayas Grid-05/23/2024 05:24: Dumanjug SS 138kV Bus 1 energized at 0231H(Unplanned Outage) [WEBSMS] | CVIS
5/23/2024 5:13:54 AM | Luzon Grid-05/23/2024 05:13: Calaca Unit 2 online at 0510H (Unplanned Outage) [WEBSMS] | CLUZ
5/23/2024 4:47:25 AM | [NSO Update] Mindanao Grid-05/23/2024 04:53: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
5/23/2024 4:47:14 AM | [NSO Update] Visayas Grid-05/23/2024 04:47: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
5/23/2024 4:47:03 AM | [NSO Update] Luzon Grid-05/23/2024 04:47: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
5/23/2024 3:02:09 AM | Luzon Grid-05/23/2024 03:02: Calaca 2 tripped with 15MW load at 0258H (Unplanned Outage) [WEBSMS] | CLUZ
5/23/2024 2:58:04 AM | Luzon Grid-05/23/2024 02:58: Calaca 2 online at 0255H (Unplanned Outage) [WEBSMS] | CLUZ
5/23/2024 2:37:22 AM | Luzon Grid-05/23/2024 02:37: Binan - Muntinlupa 230kV Line 2 restored at 0233H (Unplanned Outage) [WEBSMS] | CLUZ
5/23/2024 1:34:37 AM | [NSO Update] Luzon Grid-05/23/2024 01:34: System Advisory: The Luzon grid Yellow Alert Notice issued today has been lifted effective 0121H. [WEBSMS] | CLUZ
5/23/2024 12:40:11 AM | Visayas Grid-05/23/2024 00:40: Dumanjug SS 138kV Bus 1 de-energized at 0036H (Unplanned Outage) [WEBSMS] | CVIS
5/23/2024 12:32:17 AM | Visayas Grid-05/23/2024 00:32: Dumanjug SS 138kV Bus 2 energized at 0021H (Unplanned Outage) [WEBSMS] | CVIS
5/23/2024 12:20:49 AM | [NSO Update] Luzon Grid-05/23/2024 00:20: Update on System Advisory: 22-May-2024, Luzon Grid YELLOW Alert has been extended until interval hours 2400H (22-May) and 0100H (23-May). Total capacity on forced outage is 2453.5MW. Total of de-rated capacity is 795MW. [WEBSMS] | CLUZ
5/23/2024 12:13:49 AM | Luzon Grid-05/23/2024 00:13: Bay-Solarace 69kV lines 1 and 2 restored at 2345H and 2346H respectively. (Planned Outage) [WEBSMS] | CLUZ
5/22/2024 11:56:21 PM | Luzon Grid-05/22/2024 23:56: Affected ALD feeders of MERALCO and NGCP restored at 2349H AND 2351H, respectively. [WEBSMS] | CLUZ
5/22/2024 11:55:24 PM | Luzon Grid-05/22/2024 23:55: ALD occurred at NGCP and MERALCO area due to tripping Sual 1 with 540MW at 2341H. Lowest system frequency was 59.018Hz. [WEBSMS] | CLUZ
5/22/2024 11:54:06 PM | Luzon Grid-05/22/2024 23:54: Affected ALD feeders of MERALCO and NGCP restored at 2349H AND 2351H, respectively. [WEBSMS] | CLUZ
5/22/2024 11:46:25 PM | Luzon Grid-05/22/2024 23:46: ALD occurred at NGCP and MERALCO area due to tripping Sual 1 with 540MW at 2341H. Lowest system frequency was 59.018Hz. [WEBSMS] | CLUZ
5/22/2024 10:52:29 PM | Mindanao Grid-05/22/2024 22:58: WMPC DG10 shutdown at 2246H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 10:48:10 PM | Mindanao Grid-05/22/2024 22:54: WMPC DG10 shutdown at 2246H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 10:39:55 PM | [NSO Update] Visayas Grid-05/22/2024 22:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2224H with power going to Luzon [WEBSMS] | CVIS
5/22/2024 10:39:41 PM | [NSO Update] Luzon Grid-05/22/2024 22:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2224H with power going to Luzon [WEBSMS] | CLUZ
5/22/2024 10:38:33 PM | [NSO Update] Visayas Grid-05/22/2024 22:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2207H from reverse power direction [WEBSMS] | CVIS
5/22/2024 10:38:14 PM | [NSO Update] Luzon Grid-05/22/2024 22:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2207H from reverse power direction [WEBSMS] | CLUZ
5/22/2024 10:30:02 PM | [NSO Update] Visayas Grid-05/22/2024 22:30: System Advisory: The Visayas Grid Yellow Alert Notice issued today has been lifted at 2224H. [WEBSMS] | CVIS
5/22/2024 10:05:17 PM | Mindanao Grid-05/22/2024 22:11: WMPC DG01 shutdown at 2201H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 9:30:28 PM | Luzon Grid-05/22/2024 21:30: Bacman - Palayan Binary Plant 230kV Tie Line restored at 2128H (Planned Outage) [WEBSMS] | CLUZ
5/22/2024 9:16:55 PM | Luzon Grid-05/22/2024 21:16: Calaca 2 with 30MW tripped at 2112H. (Unplanned Outage) [WEBSMS] | CLUZ
5/22/2024 9:16:09 PM | [NSO Update] Luzon Grid-05/22/2024 21:16: Update on System Advisory: 22-May-2024, Luzon Grid is on YELLOW Alert for interval hours 2200H and 2300H. Total capacity on forced outage is 1806.5MW. Total of de-rated capacity is 482MW. [WEBSMS] | CLUZ
5/22/2024 9:08:10 PM | Luzon Grid-05/22/2024 21:08: Calaca Unit 2 online at 2104H (Unplanned Outage) [WEBSMS] | CLUZ
5/22/2024 8:09:02 PM | Luzon Grid-05/22/2024 20:09: Bay-Solarace 69kV lines 1 and 2 de-energized at 2105H and 2107H respectively. (Planned Outage) [WEBSMS] | CLUZ
5/22/2024 7:35:37 PM | Mindanao Grid-05/22/2024 19:41: PEAK POWER SAN FRANCISCO Unit 1 declared not available at 1900H. Reason: Hotspot at CT terminal. [WEBSMS] | CMIN
5/22/2024 6:00:30 PM | [NSO Update] Mindanao Grid-05/22/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3085MW, PK=2498MW, RR=73MW, NetOpMargin: EVE=514 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/22/2024 5:59:30 PM | [NSO Update] Visayas Grid-05/22/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2652MW, PK=2442MW, RR=91MW, NetOpMargin: EVE=118 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @300MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW [WEBSMS] | CVIS
5/22/2024 5:58:19 PM | [NSO Update] Luzon Grid-05/22/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=13687MW, PK=12287MW, RR=469MW, NetOpMargin: EVE=931 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @330MW, SLTEC 1 @117MW, SLTEC 2 @119MW, ILIJAN A @400MW [WEBSMS] | CLUZ
5/22/2024 5:18:53 PM | Mindanao Grid-05/22/2024 17:24: WMPC DG08 shutdown at 1715H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 5:17:39 PM | Mindanao Grid-05/22/2024 17:23: WMPC DG03 shutdown at 1643H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 5:16:57 PM | Mindanao Grid-05/22/2024 17:22: WMPC DG07 shutdown at 1630H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 5:03:05 PM | Mindanao Grid-05/22/2024 17:08: WMPC DG03 shutdown at 1643H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 5:02:43 PM | Visayas Grid-05/22/2024 17:02: MECO ( Portion of Basak last Fdr. ) MLD restored @1700H. [WEBSMS] | CVIS
5/22/2024 4:51:51 PM | Visayas Grid-05/22/2024 16:51: MECO ( Portion of Basak FDR. ) MLD restored @1647H. [WEBSMS] | CVIS
5/22/2024 4:41:56 PM | Mindanao Grid-05/22/2024 16:47: WMPC DG07 shutdown at 1640H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 4:31:23 PM | Visayas Grid-05/22/2024 16:31: Correction: MLD implemented at 1452H, MECO ( Portion of Pajo Fdr. ) MLD restored at 1500H, GMC ILP restored at 1611H. [WEBSMS] | CVIS
5/22/2024 4:13:33 PM | Visayas Grid-05/22/2024 16:13: MECO ( Portion of Basak Fdr. ) MLD restored at 1452H, MECO ( Portion of Pajo Fdr. ) MLD restored at 1500H, GMC ILP restored at 1611H. [WEBSMS] | CVIS
5/22/2024 4:12:13 PM | Luzon Grid-05/22/2024 16:12: Mexico - Quezon 230kV Line restored at 1611H. (Unplanned Outage) [WEBSMS] | CLUZ
5/22/2024 3:50:34 PM | Luzon Grid-05/22/2024 15:50: Mexico - Quezon 230kV Line tripped at 1548H. (Unplanned Outage) [WEBSMS] | CLUZ
5/22/2024 3:49:56 PM | [NSO Update] Visayas Grid-05/22/2024 15:49: SO-initiated Market Intervention for Visayas has been lifted today at 1544H. Market operations will resume starting interval 1550H. [WEBSMS] | CVIS
5/22/2024 3:27:43 PM | Luzon Grid-05/22/2024 15:27: Binan - Muntinlupa 230kV Line 2 auto-tripped at 1526H. (Unplanned Outage) [WEBSMS] | CLUZ
5/22/2024 3:23:26 PM | Luzon Grid-05/22/2024 15:23: For info: The Luzon System Frequency reached 60.503Hz at 1518H during the auto-tripping of the Malabon-Malinta 115kV line(Customer Owned) affecting voltage sensitive loads. [WEBSMS] | CLUZ
5/22/2024 2:26:13 PM | Mindanao Grid-05/22/2024 14:32: NEW BATAAN Hydro with 0.5MW load isolated at 1235H due to NORDECO feeder outage (Unplanned Outage) [WEBSMS] | CMIN
5/22/2024 2:18:22 PM | Mindanao Grid-05/22/2024 14:24: WMPC DG07 dispatched as MRU-System Voltage Requirement at 1415H (converted from energy to MRU). [WEBSMS] | CMIN
5/22/2024 1:32:01 PM | Mindanao Grid-05/22/2024 13:37: WMPC DG04 with 10MW gross generation and running as MRU tripped at 1327H with indication HT high temperature stop. Unplanned Outage [WEBSMS] | CMIN
5/22/2024 1:23:08 PM | Visayas Grid-05/22/2024 13:23: MECO (Part Basak Feeder 1 ) implemented 3.1MW MLD at 1318H to prevent overloading of Cebu-Mandaue Line 2 [WEBSMS] | CVIS
5/22/2024 1:18:07 PM | Mindanao Grid-05/22/2024 13:24: WMPC DG03 online at 1315H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 1:12:20 PM | Visayas Grid-05/22/2024 13:12: GMC U3 implemented additional 1.4 MW ILP at 1300H to prevent overloading of Cebu-Mandaue line 2 [WEBSMS] | CVIS
5/22/2024 1:10:24 PM | [NSO Update] Luzon Grid-05/22/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14840MW, PK=13549MW, RR=531MW, NetOpMargin: PM=761, EVE=609 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 330MW, SLTEC 1 @ 117MW, SLTEC 2 @ 118MW, Ilijan A @ 400MW [WEBSMS] | CLUZ
5/22/2024 1:03:46 PM | [NSO Update] Mindanao Grid-05/22/2024 13:09: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3130MW, PK=2691MW, RR=38MW, NetOpMargin: PM=400, EVE=482 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/22/2024 1:02:10 PM | Mindanao Grid-05/22/2024 13:08: (Correction) WMPC DG08 online at 1258H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 1:01:19 PM | Mindanao Grid-05/22/2024 13:07: WMPC DG01 online at 1258H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 12:58:53 PM | [NSO Update] Visayas Grid-05/22/2024 12:58: System Advisory: 22-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1400H-2100H. Total capacity on forced outage is 346.3MW. Total of de-rated capacity is 207.3MW. [WEBSMS] | CVIS
5/22/2024 12:56:21 PM | [NSO Update] Visayas Grid-05/22/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2946MW, PK=2652MW, RR=91MW, NetOpMargin: PM=202, EVE=126 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @295MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4.5MW, Panay Diesel 1-2 @4.5MW [WEBSMS] | CVIS
5/22/2024 12:49:03 PM | [NSO Update] Visayas Grid-05/22/2024 12:49: SO-initiated Market Intervention for Visayas is issued today starting interval 1245H due to MLD implementation to prevent the overloading of Cebu-Mandaue 138kV Line 2. [WEBSMS] | CVIS
5/22/2024 12:48:51 PM | Visayas Grid-05/22/2024 12:48: MECO (Part Pajo Feeder 2) implemented 5.8MW MLD at 1242H to prevent overloading of Cebu-Mandaue Line 2 [WEBSMS] | CVIS
5/22/2024 12:48:08 PM | Mindanao Grid-05/22/2024 12:54: MT. APO 3 online at 1246H (Unplanned Outage) [WEBSMS] | CMIN
5/22/2024 12:25:07 PM | Visayas Grid-05/22/2024 12:25: Malitbog U1 cut in at 1153H (Unplanned Outage) [WEBSMS] | CVIS
5/22/2024 12:22:36 PM | Visayas Grid-05/22/2024 12:22: MECO (Part Pajo Feeder 2) MLD restored at 1215H. [WEBSMS] | CVIS
5/22/2024 12:12:57 PM | [NSO Update] Visayas Grid-05/22/2024 12:12: SO initiated Market Intervention for Visayas has been lifted today at 1206H. Market operations will resume starting interval 1215H. [WEBSMS] | CVIS
5/22/2024 12:08:04 PM | Visayas Grid-05/22/2024 12:08: MECO (MCIAA Terminal 2) ILP cut off at 1153H. [WEBSMS] | CVIS
5/22/2024 12:05:14 PM | Visayas Grid-05/22/2024 12:05: MECO (Part Pajo Feeder 2) implemented 2.5 MLD at 1151H to prevent overloading of Cebu-Mandaue Line 2 [WEBSMS] | CVIS
5/22/2024 12:03:12 PM | Visayas Grid-05/22/2024 12:03: MECO (Part Pajo Feeder 2) implemented 2.5 MLD 2 MW ILP to prevent overloading of Cebu-Mandaue Line 2 [WEBSMS] | CVIS
5/22/2024 11:59:05 AM | [NSO Update] Visayas Grid-05/22/2024 11:59: SO-initiated Market Intervention for Visayas is issued today starting interval 1155H due to MLD implementation to prevent the overloading of Cebu-Mandaue 138kV Line 2. [WEBSMS] | CVIS
5/22/2024 11:06:51 AM | Visayas Grid-05/22/2024 11:06: Dumanjug SS 138kV Bus 2 de-energized at 1103H (Unplanned Outage) [WEBSMS] | CVIS
5/22/2024 10:40:14 AM | Visayas Grid-05/22/2024 10:40: MECO (MCIAA Terminal 2) implemented 2 MW ILP at 1033H. [WEBSMS] | CVIS
5/22/2024 10:17:45 AM | Visayas Grid-05/22/2024 10:17: GMC Implemented ILP of 2.0 MW at 1003H to prevent overloading of Cebu-Mandaue line 2 [WEBSMS] | CVIS
5/22/2024 10:05:18 AM | Mindanao Grid-05/22/2024 10:11: WMPC DG01 online at 1000H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 9:57:52 AM | Mindanao Grid-05/22/2024 10:03: MT. APO 3 with 3MW load tripped at 0948H. Cause: for verification (Unplanned Outage) [WEBSMS] | CMIN
5/22/2024 8:54:03 AM | [NSO Update] Visayas Grid-05/22/2024 08:54: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0850H with power going to Visayas [WEBSMS] | CVIS
5/22/2024 8:53:34 AM | [NSO Update] Luzon Grid-05/22/2024 08:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0850H with power going to Visayas [WEBSMS] | CLUZ
5/22/2024 8:46:05 AM | Mindanao Grid-05/22/2024 08:51: WMPC DG04 online at 0841H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 8:45:01 AM | Mindanao Grid-05/22/2024 08:50: WMPC DG10 online at 0820H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/22/2024 8:42:43 AM | [NSO Update] Visayas Grid-05/22/2024 08:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0840H from forward power direction [WEBSMS] | CVIS
5/22/2024 8:41:24 AM | [NSO Update] Luzon Grid-05/22/2024 08:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0840H from forward power direction [WEBSMS] | CLUZ
5/22/2024 6:35:12 AM | [NSO Update] Visayas Grid-05/22/2024 06:35: Correction: System Advisory: 22-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1400H-1600H and 1900H. Total capacity on forced outage is 327.8MW. Total of de-rated capacity is 204.3MW. [WEBSMS] | CVIS
5/22/2024 6:15:28 AM | [NSO Update] Visayas Grid-05/22/2024 06:15: System Advisory: 22-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1400H-1600H and 1900H. Total capacity on forced outage is 339.3MW. Total of de-rated capacity is 204.3MW. [WEBSMS] | CVIS
5/22/2024 6:13:35 AM | [NSO Update] Luzon Grid-05/22/2024 06:13: Correction: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=15011MW, PK=12794MW, RR=513MW, NetOpMargin: AM=1704, PM=659, EVE=610 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 330MW, SLTEC 1 @ 117MW, SLTEC 2 @ 118MW, Ilijan A @ 400MW [WEBSMS] | CLUZ
5/22/2024 6:10:13 AM | [NSO Update] Luzon Grid-05/22/2024 06:10: Correction: System Advisory: 22-May-2024, Luzon Grid is on YELLOW Alert for interval hour 1400H-1600H and 2100H. Total capacity on forced outage is 1626.3MW. Total of de-rated capacity is 285MW. [WEBSMS] | CLUZ
5/22/2024 6:03:06 AM | [NSO Update] Luzon Grid-05/22/2024 06:03: System Advisory: 22-May-2024, Luzon Grid is on YELLOW Alert for interval hour 1600H. Total capacity on forced outage is 1626.3MW. Total of de-rated capacity is 285MW. [WEBSMS] | CLUZ
5/22/2024 5:55:11 AM | [NSO Update] Luzon Grid-05/22/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=15161MW, PK=12794MW, RR=513MW, NetOpMargin: AM=1854, PM=809, EVE=760 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 330MW, SLTEC 1 @ 117MW, SLTEC 2 @ 118MW, Ilijan A @ 400MW [WEBSMS] | CLUZ
5/22/2024 5:53:30 AM | [NSO Update] Visayas Grid-05/22/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2801MW, PK=2518MW, RR=91MW, NetOpMargin: AM=193, PM=244, EVE=216 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @298MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4.5MW, Panay Diesel 1-2 @4.5MW [WEBSMS] | CVIS
5/22/2024 5:51:41 AM | [NSO Update] Mindanao Grid-05/22/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3138MW, PK=2463MW, RR=38MW, NetOpMargin: AM=636, PM=458, EVE=563 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/22/2024 4:53:55 AM | Luzon Grid-05/22/2024 04:53: Binga-La Trinidad 230kV L2 restored at 0452H (Unplanned Outage) [WEBSMS] | CLUZ
5/22/2024 4:52:11 AM | Luzon Grid-05/22/2024 04:52: Binga-Nagsaag 230kV L2 restored at 0450H (Unplanned Outage) [WEBSMS] | CLUZ
5/22/2024 4:46:41 AM | Luzon Grid-05/22/2024 04:46: Binga Ambuklao 230kV L2 restored at 0445H (Unplanned Outage) [WEBSMS] | CLUZ
5/22/2024 4:39:14 AM | Luzon Grid-05/22/2024 04:39: Binga-Binga HEPP Tie Line 1 restored at 0438H (Unplanned Outage) [WEBSMS] | CLUZ
5/22/2024 4:31:14 AM | [NSO Update] Luzon Grid-05/22/2024 04:31: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CLUZ
5/22/2024 4:30:27 AM | [NSO Update] Visayas Grid-05/22/2024 04:30: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CVIS
5/22/2024 4:30:15 AM | [NSO Update] Mindanao Grid-05/22/2024 04:36: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CMIN
5/22/2024 4:28:07 AM | Luzon Grid-05/22/2024 04:28: Binga 230kV Bus 2 restored at 0427H (Unplanned Outage) [WEBSMS] | CLUZ
5/22/2024 4:20:56 AM | Mindanao Grid-05/22/2024 04:26: Tagoloan- Manolo 138 kV L2 (7LI2TAG-MNO) energized at 0418H from Planned Outage. [WEBSMS] | CMIN
5/22/2024 4:18:01 AM | Mindanao Grid-05/22/2024 04:23: Tagoloan-SS 138/69 kV, 100 MVA Transformer T2 (7XF02TAG) energized at 0416 from Planned Outage. [WEBSMS] | CMIN
5/22/2024 4:12:42 AM | Mindanao Grid-05/22/2024 04:18: Tagoloan SS 138 kV Bus 2 (7BS02TAG) energized at 0411H from Planned Outage [WEBSMS] | CMIN
5/22/2024 3:49:39 AM | Luzon Grid-05/22/2024 03:49: Bay-Solarace 69kV Line 1 restored at 0348H (Planned Outage). [WEBSMS] | CLUZ
5/22/2024 2:23:36 AM | Mindanao Grid-05/22/2024 02:29: Tagoloan SS 138 kV Bus 2 (7BS02TAG) de-energized at 0220H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
5/22/2024 2:07:23 AM | Mindanao Grid-05/22/2024 02:13: Tagoloan-SS 138/69 kV, 100 MVA Transformer T2 (7XF02TAG) de-energized at 0204H. Planned Outage Non-GOMP. [WEBSMS] | CMIN
5/22/2024 2:03:29 AM | Mindanao Grid-05/22/2024 02:09: Tagoloan- Manolo 138 kV L2 (7LI2TAG-MNO) de-energized at 0203H. Planned Outage Non-GOMP. [WEBSMS] | CMIN
5/22/2024 12:00:39 AM | Luzon Grid-05/22/2024 00:00: Bay-Solarace 69kV Line 2 restored at 2358H (Planned Outage) [WEBSMS] | CLUZ
5/21/2024 10:59:26 PM | [NSO Update] Visayas Grid-05/21/2024 22:59: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2258H with power going to Luzon. [WEBSMS] | CVIS
5/21/2024 10:59:13 PM | [NSO Update] Luzon Grid-05/21/2024 22:59: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2258H with power going to Luzon. [WEBSMS] | CLUZ
5/21/2024 10:58:45 PM | Mindanao Grid-05/21/2024 23:04: WMPC DG10 shutdown at 2246H. End of MRU operation [WEBSMS] | CMIN
5/21/2024 10:52:29 PM | [NSO Update] Luzon Grid-05/21/2024 22:52: System Advisory: Luzon Grid Yellow Alert notice issued today has been lifted at 2251H. [WEBSMS] | CLUZ
5/21/2024 10:41:26 PM | [NSO Update] Visayas Grid-05/21/2024 22:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2240H from reverse power direction. [WEBSMS] | CVIS
5/21/2024 10:41:08 PM | [NSO Update] Luzon Grid-05/21/2024 22:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2240H from reverse power direction. [WEBSMS] | CLUZ
5/21/2024 9:22:17 PM | Mindanao Grid-05/21/2024 21:28: WMPC DG07 shutdown at 2117H. End of MRU operation [WEBSMS] | CMIN
5/21/2024 9:20:11 PM | [NSO Update] Visayas Grid-05/21/2024 21:20: System Advisory: Visayas Grid Yellow Alert notice issued today has been lifted at 2119H. [WEBSMS] | CVIS
5/21/2024 7:33:11 PM | Luzon Grid-05/21/2024 19:33: Bay-Solarace 69kV Line 1 & 2 de-energized at 1931 and 1932H respectively (Planned Outage) [WEBSMS] | CLUZ
5/21/2024 6:47:17 PM | Luzon Grid-05/21/2024 18:47: Santiago-Tugugarao 230kV Line restored at 1846H (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 6:31:02 PM | Luzon Grid-05/21/2024 18:31: Santiago-Magat 230kV L1 restored at 1829H (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 6:29:27 PM | Luzon Grid-05/21/2024 18:29: Bayombong-Santiago 230kV L2 restored at 1828H (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 6:26:39 PM | Luzon Grid-05/21/2024 18:26: Ambuklao-Bayombong 230kV restored at 1824H (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 6:11:31 PM | Luzon Grid-05/21/2024 18:11: Gamu-Tuguegarao 230kV Line restored at 1810H (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 6:05:21 PM | Luzon Grid-05/21/2024 18:05: Santiago-Gamu 230kV Line restored at 1805H (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 6:02:36 PM | Luzon Grid-05/21/2024 18:02: Santiago-Magat 230kV L2 restored at 1800H (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 6:01:09 PM | [NSO Update] Luzon Grid-05/21/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=13425MW, PK=12282MW, RR=467MW, NetOpMargin: EVE=676 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 315MW, SLTEC 1 @ 117MW, SLTEC 2 @ 118MW, Ilijan A @ 400MW [WEBSMS] | CLUZ
5/21/2024 5:56:55 PM | Luzon Grid-05/21/2024 17:57: Bayombong-Santiago 230kV L1 restored at 1755H (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 5:55:56 PM | [NSO Update] Visayas Grid-05/21/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2703MW, PK=2494MW, RR=91MW, NetOpMargin: EVE=118 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @288MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW [WEBSMS] | CVIS
5/21/2024 5:53:33 PM | [NSO Update] Mindanao Grid-05/21/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3087MW, PK=2446MW, RR=73MW, NetOpMargin: EVE=568 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/21/2024 5:52:00 PM | [NSO Update] Mindanao Grid-05/21/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: CAP=3087MW, PK=2446MW, RR=73MW, NetOpMargin: EVE=568 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/21/2024 5:50:26 PM | Luzon Grid-05/21/2024 17:50: Ambuklao-Bayombong 230kV L1 restored at 1749H (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 5:49:07 PM | Luzon Grid-05/21/2024 17:49: Ambukalo-AHEP 230kV L1 restored at 1745H (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 5:48:42 PM | Mindanao Grid-05/21/2024 17:54: WMPC DG01 shutdown at 1747H. End of MRU operation [WEBSMS] | CMIN
5/21/2024 5:44:57 PM | Visayas Grid-05/21/2024 17:45: MECO ( Gaisano Metro ) ILP restored at 1730H. Last Feeder MECO (Gaisano Grand Mall Basak) ILP restored at 1740H. [WEBSMS] | CVIS
5/21/2024 5:41:14 PM | Luzon Grid-05/21/2024 17:41: Binga-Ambuklao 230kV L1restored at 1740H (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 5:39:24 PM | [NSO Update] Mindanao Grid-05/21/2024 17:45: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 1731H. Market operations will resume starting interval 1740H. [WEBSMS] | CMIN
5/21/2024 5:39:03 PM | [NSO Update] Visayas Grid-05/21/2024 17:39: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 1731H. Market operations will resume starting interval 1740H. [WEBSMS] | CVIS
5/21/2024 5:38:42 PM | [NSO Update] Luzon Grid-05/21/2024 17:38: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today at 1731H. Market operations will resume starting interval 1740H. [WEBSMS] | CLUZ
5/21/2024 5:36:07 PM | [NSO Update] Mindanao Grid-05/21/2024 17:42: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 1735H due to failure to generate RTD. [WEBSMS] | CMIN
5/21/2024 5:35:53 PM | [NSO Update] Visayas Grid-05/21/2024 17:36: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 1735H due to failure to generate RTD. [WEBSMS] | CVIS
5/21/2024 5:35:25 PM | [NSO Update] Luzon Grid-05/21/2024 17:35: MO-initiated Market Intervention is issued today for Luzon, Visayas, & Mindanao Grid starting interval 1735H due to failure to generate RTD. [WEBSMS] | CLUZ
5/21/2024 5:30:05 PM | Visayas Grid-05/21/2024 17:30: MECO (Gaisano Island Mall) ILP restored at 1720H. GMC ILP restored at 1722H. [WEBSMS] | CVIS
5/21/2024 5:25:02 PM | Luzon Grid-05/21/2024 17:25: Binga 230kV Bus 2, Binga Ambuklao 230kV L1 & L2 tripped at 1714H resulted in isolation of Cagayan, highest frequency reach at 60.552hZ(Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 5:20:24 PM | Mindanao Grid-05/21/2024 17:26: WMPC DG08 shutdown at 1716H. End of MRU operation [WEBSMS] | CMIN
5/21/2024 5:15:47 PM | Visayas Grid-05/21/2024 17:16: GMC ILP restored at 1708H. MECO (JPark Hotel) ILP restored at 1711H. [WEBSMS] | CVIS
5/21/2024 5:04:51 PM | Visayas Grid-05/21/2024 17:05: MECO (Mactan Newtown Portion) restored ILP at 1702H. [WEBSMS] | CVIS
5/21/2024 4:55:48 PM | [NSO Update] Visayas Grid-05/21/2024 16:56: SO initiated Market Intervention for Visayas has been lifted today at 1646H. Market operations will resume starting interval 1655H. [WEBSMS] | CVIS
5/21/2024 4:39:45 PM | [NSO Update] Visayas Grid-05/21/2024 16:39: SO-initiated Market Intervention for Visayas is issued today starting interval 1635H due to MLD implementation to prevent the overloading of Cebu-Mandaue 138kV Line 2. [WEBSMS] | CVIS
5/21/2024 4:37:26 PM | Visayas Grid-05/21/2024 16:37: MECO (Mactan Newtown Portion) implemented MLD of 4.0 MW load at 1634H to prevent overloading of Cebu-Mandaue 138 kV line 2 due to abnormal sound of EAUC U#4. [WEBSMS] | CVIS
5/21/2024 4:30:30 PM | Visayas Grid-05/21/2024 16:30: GMC Implemented ILP of 2.0 MW at 1624H to prevent overloading of C-M line 2 due to abnormal sound of EAUC U#4. [WEBSMS] | CVIS
5/21/2024 4:29:47 PM | Visayas Grid-05/21/2024 16:30: MECO ( Gaisano Metro ) Implemented ILP of 4.2 MW at 1621H to prevent overloading of C-M line 2 due to abnormal sound of EAUC U#4. [WEBSMS] | CVIS
5/21/2024 4:18:13 PM | Visayas Grid-05/21/2024 16:18: GMC ILP portion restored at 1615H. [WEBSMS] | CVIS
5/21/2024 4:07:21 PM | Visayas Grid-05/21/2024 16:07: MECO (Plantation Bay) ILP restored at 1556H. [WEBSMS] | CVIS
5/21/2024 3:39:31 PM | Visayas Grid-05/21/2024 15:39: MECO (portion of Basak Feeder) energized @1533H. [WEBSMS] | CVIS
5/21/2024 3:19:24 PM | Mindanao Grid-05/21/2024 15:25: Baloi-Agus5 138 kV Line energized at 1518H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
5/21/2024 2:10:57 PM | [NSO Update] Visayas Grid-05/21/2024 14:11: SO initiated Market Intervention for Visayas has been lifted today at 1401H. Market operations will resume starting interval 1410H. [WEBSMS] | CVIS
5/21/2024 1:52:59 PM | Visayas Grid-05/21/2024 13:53: MECO (portion of Basak Feeder) implemented ILP at 0941H restored at 1350H [WEBSMS] | CVIS
5/21/2024 1:49:40 PM | Visayas Grid-05/21/2024 13:49: MECO (Gaisano Island Mall) implemented ILP of 1.0 MW at 1346H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/21/2024 1:46:46 PM | [NSO Update] Visayas Grid-05/21/2024 13:46: SO-initiated Market Intervention for Visayas is issued today starting interval 1335H due to MLD implementation to prevent the overloading of Cebu-Mandaue 138kV Line 2. [WEBSMS] | CVIS
5/21/2024 1:41:31 PM | Visayas Grid-05/21/2024 13:41: MECO (portion of Basak Feeder) implemented ILP of 3.2 MW and MLD of 1.3 MW at 1333H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/21/2024 1:32:36 PM | Mindanao Grid-05/21/2024 13:38: WMPC DG08 online at 1330H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/21/2024 1:22:31 PM | Visayas Grid-05/21/2024 13:22: MECO (J-Park) implemented ILP of 1.9 MW at 1321H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/21/2024 1:14:32 PM | Visayas Grid-05/21/2024 13:14: GMC implemented additional ILP of 2 MW at 1312H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/21/2024 1:10:55 PM | Visayas Grid-05/21/2024 13:11: MECO (Plantation Bay) implemented ILP of 1.9 MW at 1308H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/21/2024 12:59:29 PM | Visayas Grid-05/21/2024 12:59: MECO (Gaisano Grand Mall) implemented ILP of 1.8 MW at 1255H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/21/2024 12:53:34 PM | [NSO Update] Mindanao Grid-05/21/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3133MW, PK=2651MW, RR=38MW, NetOpMargin: PM=443, EVE=506 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/21/2024 12:50:46 PM | [NSO Update] Visayas Grid-05/21/2024 12:50: System Advisory: 21-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1400H-2100H. Total capacity on forced outage is 320.8MW. Total of de-rated capacity is 218.3MW. [WEBSMS] | CVIS
5/21/2024 12:46:55 PM | [NSO Update] Visayas Grid-05/21/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2976MW, PK=2674MW, RR=91MW, NetOpMargin: PM=211, EVE=119 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @285MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW [WEBSMS] | CVIS
5/21/2024 12:42:03 PM | [NSO Update] Luzon Grid-05/21/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14543MW, PK=13547MW, RR=486MW, NetOpMargin: PM=510, EVE=653 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: Ilijan A @400MW, SLTEC 1 @117MW, SLTEC 2 @118MW, Masinloc 1 @315MW, Limay 4 @60MW, Limay 8 @60MW [WEBSMS] | CLUZ
5/21/2024 12:30:09 PM | Luzon Grid-05/21/2024 12:30: Laoag - Balaoi Wind Farm 115kV Line 1 (CO) restored at 1230H (Planned Outage) [WEBSMS] | CLUZ
5/21/2024 11:25:08 AM | Luzon Grid-05/21/2024 11:25: Ilijan A GT 1-2 online at 1018H (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 11:22:31 AM | Mindanao Grid-05/21/2024 11:28: MPC DG10 is online back at 1117H from unplanned outage. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/21/2024 11:17:47 AM | Mindanao Grid-05/21/2024 11:23: WMPC DG10 tripped at 1110H as the emergency stop button was accidentally activated due to vibration. [WEBSMS] | CMIN
5/21/2024 11:06:36 AM | Mindanao Grid-05/21/2024 11:12: WMPC DG07 online at 1104H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/21/2024 10:02:31 AM | Visayas Grid-05/21/2024 10:02: GMC implemented ILP of 2 MW at 0958H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/21/2024 9:53:29 AM | Visayas Grid-05/21/2024 09:53: MECO (portion of Basak Feeder) implemented ILP of 3.3 MW at 0941H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/21/2024 9:13:09 AM | Mindanao Grid-05/21/2024 09:19: WMPC DG10 is online back at 0910H from unplanned outage. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/21/2024 9:10:50 AM | Mindanao Grid-05/21/2024 09:16: WMPC DG01 online at 0907H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/21/2024 8:59:41 AM | Mindanao Grid-05/21/2024 09:05: WMPC DG10 tripped at 0855H. Indication: HT water low pressure stop [WEBSMS] | CMIN
5/21/2024 8:56:57 AM | [NSO Update] Luzon Grid-05/21/2024 08:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0854H with power going to Visayas. [WEBSMS] | CLUZ
5/21/2024 8:56:46 AM | [NSO Update] Visayas Grid-05/21/2024 08:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0854H with power going to Visayas. [WEBSMS] | CVIS
5/21/2024 8:47:58 AM | [NSO Update] Visayas Grid-05/21/2024 08:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0844H from forward power direction. [WEBSMS] | CVIS
5/21/2024 8:47:11 AM | [NSO Update] Luzon Grid-05/21/2024 08:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0844H from forward power direction. [WEBSMS] | CLUZ
5/21/2024 8:45:54 AM | Mindanao Grid-05/21/2024 08:51: Baloi-Agus5 138 kV Line de-energized at 0835H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
5/21/2024 8:31:41 AM | Mindanao Grid-05/21/2024 08:37: WMPC DG10 online at 0828H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/21/2024 7:43:18 AM | Luzon Grid-05/21/2024 07:43: Bay-Solarace 69kV lines 1 and 2 restored at 0741H and 0743H respectively. (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 6:22:38 AM | Mindanao Grid-05/21/2024 06:28: Balo-i SS 138kV Bus 1 energized at 0618H from Planned Outage [WEBSMS] | CMIN
5/21/2024 6:13:04 AM | [NSO Update] Luzon Grid-05/21/2024 06:13: Correction: System Advisory: 21-May-2024, Luzon Grid is on YELLOW Alert for interval hours 1400H-1600H and 2000H-2200H. Total capacity on forced outage is 1575.8MW. Total of de-rated capacity is 500MW. [WEBSMS] | CLUZ
5/21/2024 6:01:52 AM | [NSO Update] Visayas Grid-05/21/2024 06:02: System Advisory: 21-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1500H-1600H and 1900H-2100H. Total capacity on forced outage is 305.8MW. Total of de-rated capacity is 208.3MW. [WEBSMS] | CVIS
5/21/2024 5:59:45 AM | [NSO Update] Visayas Grid-05/21/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2918MW, PK=2609MW, RR=91MW, NetOpMargin: AM=218, PM=268, EVE=190 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @295MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW [WEBSMS] | CVIS
5/21/2024 5:57:11 AM | [NSO Update] Luzon Grid-05/21/2024 05:57: System Advisory: 21-May-2024, Luzon Grid is on YELLOW Alert for interval hours 1400H-1600H and 2000H-2200H. Total capacity on forced outage is 1635.8MW. Total of de-rated capacity is 500MW. [WEBSMS] | CLUZ
5/21/2024 5:53:46 AM | [NSO Update] Luzon Grid-05/21/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=14823MW, PK=12901MW, RR=507MW, NetOpMargin: AM=1415, PM=653, EVE=813 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: Ilijan A @200MW, SLTEC 1 @117MW, SLTEC 2 @118MW, Masinloc 1 @315MW, Limay 4 @60MW, Limay 8 @60MW (Total deration: 500MW) [WEBSMS] | CLUZ
5/21/2024 5:50:53 AM | [NSO Update] Mindanao Grid-05/21/2024 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3141MW, PK=2480MW, RR=38MW, NetOpMargin: AM=622, PM=472, EVE=524 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/21/2024 5:21:29 AM | Luzon Grid-05/21/2024 05:21: Muntinlupa 115kV Bus 2 restored at 0520H (Planned Outage) [WEBSMS] | CLUZ
5/21/2024 4:51:53 AM | Luzon Grid-05/21/2024 04:52: Laoag - Balaoi Wind Farm 115kV Line 1 (CO) de-energized at 0450H (Planned Outage) [WEBSMS] | CLUZ
5/21/2024 4:05:20 AM | [NSO Update] Luzon Grid-05/21/2024 04:05: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CLUZ
5/21/2024 4:05:07 AM | [NSO Update] Visayas Grid-05/21/2024 04:05: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CVIS
5/21/2024 4:04:46 AM | [NSO Update] Mindanao Grid-05/21/2024 04:10: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CMIN
5/21/2024 2:57:11 AM | Luzon Grid-05/21/2024 02:57: Bay-Makban Ormat 69kV line and Bay-Makban E 69kV line were energized at 0255H and 0254H respectively (Unplanned Outage) [WEBSMS] | CLUZ
5/21/2024 2:37:54 AM | Luzon Grid-05/21/2024 02:38: For info: Sta Rita Module 40 completed the fuel changeover from fuel oil to natural gas at 0232H [WEBSMS] | CLUZ
5/21/2024 1:49:43 AM | Luzon Grid-05/21/2024 01:49: For info: Sta Rita Module 20 completed the fuel changeover from oil to gas at 0143H. [WEBSMS] | CLUZ
5/21/2024 1:19:08 AM | [NSO Update] Luzon Grid-05/21/2024 01:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0117H with power going to Luzon. [WEBSMS] | CLUZ
5/21/2024 1:18:43 AM | [NSO Update] Visayas Grid-05/21/2024 01:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0117H with power going to Luzon. [WEBSMS] | CVIS
5/21/2024 1:11:21 AM | [NSO Update] Luzon Grid-05/21/2024 01:11: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0107H from reverse power direction. [WEBSMS] | CLUZ
5/21/2024 1:10:50 AM | [NSO Update] Visayas Grid-05/21/2024 01:11: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0107H from reverse power direction. [WEBSMS] | CVIS
5/21/2024 1:03:56 AM | Mindanao Grid-05/21/2024 01:10: Balo-i SS 100MVA 138/69kV Power Transformer 3 energized at 0101H. (Planned Outage) [WEBSMS] | CMIN
5/21/2024 12:20:09 AM | Luzon Grid-05/21/2024 00:20: Muntinlupa 115kV Bus 2 was de-energized at 0014H. (Planned Outage) [WEBSMS] | CLUZ
5/20/2024 11:47:52 PM | Mindanao Grid-05/20/2024 23:53: Balo-i SS 138kV Bus 1 De-energized/shutdown at 2346H. (Planned Outage) [WEBSMS] | CMIN
5/20/2024 11:20:07 PM | Luzon Grid-05/20/2024 23:20: (Correction of Transmission Line Name) Mexico-San Rafael 230kV line 1 auto-tripped/auto-reclosed at 2238H. (Unplanned Outage) [WEBSMS] | CLUZ
5/20/2024 11:17:42 PM | Mindanao Grid-05/20/2024 23:23: WMPC DG10 shutdown at 2316H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/20/2024 10:46:58 PM | Luzon Grid-05/20/2024 22:47: Mexico-San Rafael 230kV line auto-tripped/auto-reclosed at 2238H. (Unplanned Outage) [WEBSMS] | CLUZ
5/20/2024 10:04:47 PM | Luzon Grid-05/20/2024 22:05: Bay-Makban Ormat 69kV line and Bay-Makban E 69kV line were de-energized at 2200H and 2201H respectively. (Unplanned Outage) [WEBSMS] | CLUZ
5/20/2024 9:53:21 PM | Mindanao Grid-05/20/2024 21:59: NEW BATAAN Hydro online at 2135H (Unplanned Outage) [WEBSMS] | CMIN
5/20/2024 9:51:22 PM | Luzon Grid-05/20/2024 21:51: Bay-Solarace 69kV lines 1 and 2 were de-energized at 2147H and 2148H respectively. (Unplanned Outage) [WEBSMS] | CLUZ
5/20/2024 9:49:53 PM | [NSO Update] Visayas Grid-05/20/2024 21:50: System Advisory: Visayas Grid Yellow Alert notice issued today has been lifted at 2146H. [WEBSMS] | CVIS
5/20/2024 9:47:16 PM | Mindanao Grid-05/20/2024 21:53: WMPC DG01 shutdown at 2146H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/20/2024 9:45:46 PM | Mindanao Grid-05/20/2024 21:51: NEW BATAAN Hydro with 0.5MW load tripped at 1932H due to recloser tripping (Unplanned Outage) [WEBSMS] | CMIN
5/20/2024 9:44:20 PM | [NSO Update] Luzon Grid-05/20/2024 21:44: System Advisory: Luzon Grid Yellow Alert notice issued today has been lifted at 2142H. [WEBSMS] | CLUZ
5/20/2024 8:52:36 PM | Mindanao Grid-05/20/2024 20:58: NEW BATAAN Hydro online at 1920H (Unplanned Outage) [WEBSMS] | CMIN
5/20/2024 8:17:49 PM | Mindanao Grid-05/20/2024 20:23: WMPC DG07 shutdown at 2016H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/20/2024 6:14:11 PM | Mindanao Grid-05/20/2024 18:20: WMPC DG07 online at 1812H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/20/2024 6:08:52 PM | Mindanao Grid-05/20/2024 18:14: MT. APO 3 online at 1805H (Unplanned Outage) [WEBSMS] | CMIN
5/20/2024 5:49:37 PM | [NSO Update] Luzon Grid-05/20/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=12878MW, PK=11977MW, RR=479MW, NetOpMargin: EVE=422 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: MASINLOC 1 @315MW, SLTEC 1@117MW, SLTEC 2@118MW, ILIJAN A @250MW [WEBSMS] | CLUZ
5/20/2024 5:40:28 PM | [NSO Update] Visayas Grid-05/20/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2699MW, PK=2486MW, RR=91MW, NetOpMargin: EVE=121 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @292MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW, Panay Diesel 3-G @8MW, TGPP @81.2MW [WEBSMS] | CVIS
5/20/2024 5:26:43 PM | Visayas Grid-05/20/2024 17:26: MECO (Portion of Tambuli Resort) ILP cut off at 1711H. Last fdr. restored, Meco (JPark) ILP cut off at 1715H. [WEBSMS] | CVIS
5/20/2024 5:23:40 PM | [NSO Update] Mindanao Grid-05/20/2024 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3087MW, PK=2508MW, RR=73MW, NetOpMargin: EVE=506 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/20/2024 5:21:40 PM | Mindanao Grid-05/20/2024 17:27: Balo-i - Agus2 138kV Line 1 energized/looped at 1716H. (Planned Outage) [WEBSMS] | CMIN
5/20/2024 5:15:55 PM | Mindanao Grid-05/20/2024 17:21: WMPC DG3 shutdown at 1713H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/20/2024 5:14:33 PM | Mindanao Grid-05/20/2024 17:20: WMPC DG03 shutdown at 1713H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/20/2024 5:10:18 PM | Mindanao Grid-05/20/2024 17:16: WMPC DG7 Shutdown at 1700H. From MRU _ System Voltage Requirement. [WEBSMS] | CMIN
5/20/2024 5:03:41 PM | Visayas Grid-05/20/2024 17:03: MECO (Punta Rizal) ILP cut off at 1701H. [WEBSMS] | CVIS
5/20/2024 5:01:43 PM | Visayas Grid-05/20/2024 17:01: MECO (GMC U3) ILP cut off at 1653H. [WEBSMS] | CVIS
5/20/2024 4:45:25 PM | Visayas Grid-05/20/2024 16:45: MECO (Knowles Electronics) ILP cut off at 1640H. [WEBSMS] | CVIS
5/20/2024 3:49:22 PM | Mindanao Grid-05/20/2024 15:54: MT. APO 3 with 2.2MW load tripped at 1541H. Indication: No brine flow (Unplanned Outage) [WEBSMS] | CMIN
5/20/2024 3:38:44 PM | Visayas Grid-05/20/2024 15:38: MECO (Gaisano Island Mall) ILP cut off at 1455H. MECO (MCIAA TERMINAL 2) ILP cut-off 1502H. [WEBSMS] | CVIS
5/20/2024 3:10:24 PM | Mindanao Grid-05/20/2024 15:15: Agus5 U2 online at 1502H. From P&E request shutdown. Non-GOMP. (Planned Outage) [WEBSMS] | CMIN
5/20/2024 3:06:45 PM | Luzon Grid-05/20/2024 15:06: Ambuklao - Ambuklao HEPP 230kV Tie Line restored at 1504H (Planned Outage) [WEBSMS] | CLUZ
5/20/2024 3:00:32 PM | Mindanao Grid-05/20/2024 15:05: NEW BATAAN Hydro shutdown at 1419H due to insufficient water supply (Unplanned Outage). [WEBSMS] | CMIN
5/20/2024 2:52:15 PM | Mindanao Grid-05/20/2024 14:57: WMPC DG08 shutdown at 1451H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/20/2024 2:08:19 PM | Visayas Grid-05/20/2024 14:08: MECO (Portion of Tambuli Resort) implemented ILP of 4.0 MW at 1400H to prevent overloading of Cebu - Mandaue 138 kV Line 2(Unplanned Outage) [WEBSMS] | CVIS
5/20/2024 1:38:34 PM | Visayas Grid-05/20/2024 13:38: MECO (Sheraton and Dusit Thani) implemented ILP restored at 1335H [WEBSMS] | CVIS
5/20/2024 1:33:28 PM | Visayas Grid-05/20/2024 13:33: MECO (J-Park) implemented ILP of 2.1 MW at 1330H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/20/2024 1:17:52 PM | Visayas Grid-05/20/2024 13:18: MECO (Knowles) implemented ILP of 3.4 MW at 1311H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/20/2024 1:07:56 PM | Visayas Grid-05/20/2024 13:08: GMC implemented ILP of 1.8 MW at 1258H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/20/2024 12:48:16 PM | [NSO Update] Mindanao Grid-05/20/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3133MW, PK=2670MW, RR=73MW, NetOpMargin: PM=390, EVE=489 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/20/2024 12:47:15 PM | [NSO Update] Visayas Grid-05/20/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2984MW, PK=2643MW, RR=91MW, NetOpMargin: PM=249, EVE=139 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @292MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW, Panay Diesel 3-G @8MW, TGPP @81.2MW [WEBSMS] | CVIS
5/20/2024 12:45:05 PM | [NSO Update] Luzon Grid-05/20/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14561MW, PK=13458MW, RR=531MW, NetOpMargin: PM=572, EVE=509 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 300MW, SLTEC 1 @ 117MW, SLTEC 2 @ 118MW, Ilijan A @ 250MW [WEBSMS] | CLUZ
5/20/2024 11:08:37 AM | Mindanao Grid-05/20/2024 11:13: WMPC DG08 online at 1105H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/20/2024 11:07:05 AM | Visayas Grid-05/20/2024 11:07: MECO (Gaisano Grand Mall) implemented ILP of 1.4 MW at 1103H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/20/2024 10:59:52 AM | Luzon Grid-05/20/2024 11:00: Laoag-EDC Burgos Wind Farm 115kV Line (CO) restored at 1057H (Planned Outage) [WEBSMS] | CLUZ
5/20/2024 10:59:05 AM | Mindanao Grid-05/20/2024 11:04: WMPC DG03 online at 1052H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/20/2024 10:53:20 AM | Visayas Grid-05/20/2024 10:53: MECO (MCIA Terminal 2) implemented ILP of 2.4 MW at 1049H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/20/2024 10:03:34 AM | Mindanao Grid-05/20/2024 10:08: WMPC DG07 online at 1000H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/20/2024 10:03:32 AM | Mindanao Grid-05/20/2024 10:08: Balo-i - Agus 2 138kV Line 1 De-energized/shutdown at 1001H. (Planned Outage) [WEBSMS] | CMIN
5/20/2024 9:22:42 AM | Visayas Grid-05/20/2024 09:22: MECO started ILP implementation at 0913H (Sheraton and Dusit Thani) with 3.7 MW load to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/20/2024 9:18:15 AM | Visayas Grid-05/20/2024 09:18: MECO started ILP implementation at 0913H (Sheraton and Ducit Thani) with 3.7 MW load [WEBSMS] | CVIS
5/20/2024 9:09:59 AM | Mindanao Grid-05/20/2024 09:15: WMPC DG01 online at 0905H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/20/2024 8:27:04 AM | Mindanao Grid-05/20/2024 08:32: WMPC DG10 online at 0825H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/20/2024 6:59:41 AM | Visayas Grid-05/20/2024 06:59: LGPP U2 cut-out at 0656H (Unplanned Outage) [WEBSMS] | CVIS
5/20/2024 6:58:47 AM | Mindanao Grid-05/20/2024 07:03: AGUS 5 Unit 2 shutdown at 0652H. Note: with shutdown schedule at 0800H, however, early shutdown implemented due to low forebay elevation. [WEBSMS] | CMIN
5/20/2024 6:51:55 AM | [NSO Update] Luzon Grid-05/20/2024 06:52: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0644H with power going to Visayas [WEBSMS] | CLUZ
5/20/2024 6:51:36 AM | [NSO Update] Visayas Grid-05/20/2024 06:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0644H with power going to Visayas [WEBSMS] | CVIS
5/20/2024 6:50:54 AM | [NSO Update] Luzon Grid-05/20/2024 06:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0634H from forward power direction [WEBSMS] | CLUZ
5/20/2024 6:49:52 AM | [NSO Update] Luzon Grid-05/20/2024 06:50: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=14648MW, PK=12076MW, RR=511MW, NetOpMargin: AM=2061, PM=692, EVE=953 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @250MW, SLTEC 1 @117MW, SLTEC 2 @118MW, Masinloc 1 @300MW [WEBSMS] | CLUZ
5/20/2024 6:47:56 AM | [NSO Update] Visayas Grid-05/20/2024 06:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0634H from forward power direction [WEBSMS] | CVIS
5/20/2024 6:33:11 AM | Luzon Grid-05/20/2024 06:33: Ambuklao-Ambuklao HEPP 230kV Tie Line de-energized at 0632H (Planned Outage) [WEBSMS] | CLUZ
5/20/2024 6:31:23 AM | [NSO Update] Visayas Grid-05/20/2024 06:31: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2926MW, PK=2478MW, RR=91MW, NetOpMargin: AM=357, PM=236, EVE=106 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @300MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW, Panay Diesel 3-G @8MW, TGPP @81.2MW [WEBSMS] | CVIS
5/20/2024 6:25:23 AM | [NSO Update] Visayas Grid-05/20/2024 06:25: System Advisory: 20-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1400H-2100H. Total capacity on forced outage is 305.8MW. Total of de-rated capacity is 247.6MW. [WEBSMS] | CVIS
5/20/2024 6:24:44 AM | [NSO Update] Luzon Grid-05/20/2024 06:24: System Advisory: 20-May-2024, Luzon Grid is on YELLOW Alert for interval hours 1500H and 1600H. Total capacity on forced outage is 1635.8MW. Total of de-rated capacity is 405MW. [WEBSMS] | CLUZ
5/20/2024 5:28:23 AM | Luzon Grid-05/20/2024 05:28: Kalayaan 4 as pump with a laod of -160MW tripped at 0525H. Highest Frequency is 60.37Hz (Unplanned Outage) [WEBSMS] | CLUZ
5/20/2024 5:21:35 AM | [NSO Update] Mindanao Grid-05/20/2024 05:26: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3142MW, PK=2480MW, RR=73MW, NetOpMargin: AM=590, PM=482, EVE=560 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/20/2024 4:12:40 AM | Luzon Grid-05/20/2024 04:12: Laoag - EDC Burgos Wind Farm 115kV Line (CO) de-energized at 0409H (Planned Outage) [WEBSMS] | CLUZ
5/20/2024 4:06:21 AM | [NSO Update] Mindanao Grid-05/20/2024 04:11: Weather Update: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
5/20/2024 4:06:04 AM | [NSO Update] Visayas Grid-05/20/2024 04:06: Weather Update: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
5/20/2024 4:05:52 AM | [NSO Update] Luzon Grid-05/20/2024 04:05: Weather Update: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
5/20/2024 2:48:48 AM | Luzon Grid-05/20/2024 02:49: Binan-San Pedro 115kV Line restored at 0248H (Planned Outage) [WEBSMS] | CLUZ
5/20/2024 2:47:37 AM | Luzon Grid-05/20/2024 02:47: Binan-Southwoods 115kV Line restored at 0246H (Planned Outage) [WEBSMS] | CLUZ
5/20/2024 12:52:33 AM | Mindanao Grid-05/20/2024 00:57: Matanao - Digos Solar Power Plant (DSP) 69kV Line energized at 0048H. (Planned Outage) [WEBSMS] | CMIN
5/20/2024 12:06:30 AM | [NSO Update] Visayas Grid-05/20/2024 00:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2333H with power going to Luzon [WEBSMS] | CVIS
5/20/2024 12:06:13 AM | [NSO Update] Luzon Grid-05/20/2024 00:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2333H with power going to Luzon [WEBSMS] | CLUZ
5/20/2024 12:05:13 AM | [NSO Update] Visayas Grid-05/20/2024 00:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2322H from reverse power direction [WEBSMS] | CVIS
5/20/2024 12:04:54 AM | [NSO Update] Luzon Grid-05/20/2024 00:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2322H from reverse power direction [WEBSMS] | CLUZ
5/19/2024 11:19:37 PM | Mindanao Grid-05/19/2024 23:24: Maco-Nabunturan 138 kV Line (7LI1MAC-NAB) energized at 2313H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
5/19/2024 10:58:11 PM | Mindanao Grid-05/19/2024 23:03: WMPC DG10 Shutdown at 2246H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/19/2024 10:28:06 PM | Luzon Grid-05/19/2024 22:28: Binan-Southwoods 115kV Line de-energized at 2221H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 10:25:06 PM | Luzon Grid-05/19/2024 22:25: Binan-San Pedro 115kV Line de-energized at 2219H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 10:24:15 PM | Visayas Grid-05/19/2024 22:24: TGPP U1 cut in at 2203H (Planned Outage) [WEBSMS] | CVIS
5/19/2024 9:28:54 PM | [NSO Update] Visayas Grid-05/19/2024 21:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2127H with power going to Visayas [WEBSMS] | CVIS
5/19/2024 9:28:37 PM | [NSO Update] Luzon Grid-05/19/2024 21:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2127H with power going to Visayas [WEBSMS] | CLUZ
5/19/2024 9:22:27 PM | [NSO Update] Visayas Grid-05/19/2024 21:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2117H from forward power direction [WEBSMS] | CVIS
5/19/2024 9:22:03 PM | [NSO Update] Luzon Grid-05/19/2024 21:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2117H from forward power direction [WEBSMS] | CLUZ
5/19/2024 9:21:22 PM | [NSO Update] Visayas Grid-05/19/2024 21:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1932H with power going to Luzon [WEBSMS] | CVIS
5/19/2024 9:21:04 PM | [NSO Update] Luzon Grid-05/19/2024 21:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1932H with power going to Luzon [WEBSMS] | CLUZ
5/19/2024 8:26:18 PM | Luzon Grid-05/19/2024 20:26: Binan-Muntinlupa 230kV Line 4 restored at 2024H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 8:02:22 PM | Mindanao Grid-05/19/2024 20:07: 7XF02NAB_Nabunturan SS Power Transformer #2,100 MVA energized at 1959H. Planned Outage /GOMP. [WEBSMS] | CMIN
5/19/2024 7:45:54 PM | Luzon Grid-05/19/2024 19:46: San Jose-Balsik 500kV Line restored at 1943H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 6:08:52 PM | Mindanao Grid-05/19/2024 18:13: Matanao - Digos Solar Power Plant (DSP) 69kV Line de-energized at 1803H. (Planned Outage) [WEBSMS] | CMIN
5/19/2024 6:00:22 PM | [NSO Update] Visayas Grid-05/19/2024 18:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1757H from forward power direction [WEBSMS] | CVIS
5/19/2024 6:00:03 PM | [NSO Update] Luzon Grid-05/19/2024 18:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1757H from forward power direction [WEBSMS] | CLUZ
5/19/2024 5:58:57 PM | [NSO Update] Mindanao Grid-05/19/2024 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3023MW, PK=2354MW, RR=73MW, NetOpMargin: EVE=596 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/19/2024 5:57:19 PM | [NSO Update] Visayas Grid-05/19/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2606MW, PK=2292MW, RR=91MW, NetOpMargin: EVE=222 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @305MW [WEBSMS] | CVIS
5/19/2024 5:57:04 PM | Visayas Grid-05/19/2024 17:57: Samboan SS 50 MVA TR2 energized at 1755H (Planned Outage) [WEBSMS] | CVIS
5/19/2024 5:55:43 PM | [NSO Update] Luzon Grid-05/19/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13035MW, PK=10370MW, RR=339MW, NetOpMargin: EVE=2326 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @325MW, SLTEC 1 @117MW, SLTEC 2 @118MW, ILIJAN A @250MW [WEBSMS] | CLUZ
5/19/2024 5:55:26 PM | Visayas Grid-05/19/2024 17:55: Amlan-Samboan 138kV Line 2 energized @1750H. (Planned Outage) [WEBSMS] | CVIS
5/19/2024 5:15:19 PM | Luzon Grid-05/19/2024 17:15: Binan-Muntinlupa 230kV Line 4 de-energized at 1715H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 5:15:03 PM | Mindanao Grid-05/19/2024 17:20: Lamsan Power Corp. with 15.3MW load isolated by the tripping of Sultan Kudarat - Midsayap 69kV Line, restored at 1705H. (Unplanned Outage.) [WEBSMS] | CMIN
5/19/2024 5:05:40 PM | Mindanao Grid-05/19/2024 17:10: Agus 1 unit 1 online at 1656H (Planned Outage) [WEBSMS] | CMIN
5/19/2024 5:04:36 PM | Luzon Grid-05/19/2024 17:04: Lumban-Bay 230kV Line 2 restored at 1703H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 5:03:31 PM | Visayas Grid-05/19/2024 17:03: Mandaue - Guizo and Mandaue - Paknaan 69 kV Lines energized at 1658H and 1659H (Planned Outage) [WEBSMS] | CVIS
5/19/2024 4:58:17 PM | Luzon Grid-05/19/2024 16:58: Daraga SS 230kV Bus 1 restored at 1657H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 4:02:36 PM | Luzon Grid-05/19/2024 16:02: Pantabangan-Nagsaag 230kV Line restored at 1600H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 1:51:56 PM | [NSO Update] Luzon Grid-05/19/2024 13:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14138MW, PK=11163MW, RR=351MW, NetOpMargin: PM=2624, EVE=1030 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 325MW, Masinloc 2 @ 340MW, Masinloc 3 @ 300, SLTEC 1 @ 117MW, SLTEC 2 @ 118MW, Ilijan A @ 250MW [WEBSMS] | CLUZ
5/19/2024 1:49:31 PM | [NSO Update] Mindanao Grid-05/19/2024 13:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3073MW, PK=2207MW, RR=73MW, NetOpMargin: PM=793, EVE=565 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/19/2024 1:47:03 PM | [NSO Update] Visayas Grid-05/19/2024 13:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2733MW, PK=2205MW, RR=91MW, NetOpMargin: PM=436, EVE=171 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 298MW [WEBSMS] | CVIS
5/19/2024 10:41:25 AM | Mindanao Grid-05/19/2024 10:46: WMPC DG10 Online at 1037H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/19/2024 10:32:50 AM | Visayas Grid-05/19/2024 10:32: Magdugo-Colon 138 kV Line 1 looped at 1031H (Unplanned Outage) [WEBSMS] | CVIS
5/19/2024 10:13:07 AM | Visayas Grid-05/19/2024 10:13: Magdugo-Colon 138 kV line 1 opened in Magdugo side at 1004H (Unplanned Outage) [WEBSMS] | CVIS
5/19/2024 10:12:46 AM | Luzon Grid-05/19/2024 10:12: Binan 300MVA T02 restored at 1012H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 10:05:25 AM | Luzon Grid-05/19/2024 10:05: Binan 230kV Bus 2 restored at 1003H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 8:35:29 AM | Luzon Grid-05/19/2024 08:35: San Jose 500kV ring bus loop at 0833H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 8:13:56 AM | [NSO Update] Visayas Grid-05/19/2024 08:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0807H with power going to Luzon. [WEBSMS] | CVIS
5/19/2024 8:13:35 AM | [NSO Update] Luzon Grid-05/19/2024 08:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0807H with power going to Luzon. [WEBSMS] | CLUZ
5/19/2024 8:03:14 AM | Mindanao Grid-05/19/2024 08:08: 7XF02NAB_Nabunturan SS Power Transformer #2,100 MVA de-energized at 0759H. Planned Outage /GOMP. [WEBSMS] | CMIN
5/19/2024 7:38:45 AM | [NSO Update] Visayas Grid-05/19/2024 07:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0736H from forward power direction. [WEBSMS] | CVIS
5/19/2024 7:38:24 AM | [NSO Update] Luzon Grid-05/19/2024 07:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0736H from forward power direction. [WEBSMS] | CLUZ
5/19/2024 6:52:44 AM | Mindanao Grid-05/19/2024 06:57: Maco-Nabunturan 138 kV (Line_7LI1MAC-NAB) de-energized at 0650H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
5/19/2024 6:41:27 AM | [NSO Update] Mindanao Grid-05/19/2024 06:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3127MW, PK=1998MW, RR=73MW, NetOpMargin: AM=1055, PM=900, EVE=685 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/19/2024 6:35:53 AM | Visayas Grid-05/19/2024 06:36: Samboan SS 50 MVA TR2 de-energized at 0635H (Planned Outage) [WEBSMS] | CVIS
5/19/2024 6:34:34 AM | Luzon Grid-05/19/2024 06:34: Daraga SS 230kV Bus 1de-energized at 0633H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 6:30:31 AM | [NSO Update] Visayas Grid-05/19/2024 06:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2783MW, PK=2068MW, RR=91MW, NetOpMargin: AM=625, PM=478, EVE=177 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW, Tongonan GPP @79.5MW, Power Barge 104-3 @5MW [WEBSMS] | CVIS
5/19/2024 6:26:52 AM | [NSO Update] Luzon Grid-05/19/2024 06:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14566MW, PK=10607MW, RR=350MW, NetOpMargin: AM=3609, PM=2533, EVE=1042 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @325MW, MSLC2 @340MW, MSLC3 @300MW, SLTEC 1 @117MW, SLTEC 2 @118MW, ILIJAN A @350MW [WEBSMS] | CLUZ
5/19/2024 6:25:02 AM | [NSO Update] Luzon Grid-05/19/2024 06:25: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14566MW, PK=10607MW, RR=350MW, NetOpMargin: AM=3609, PM=2533, EVE=1042 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @325MW, MSLC2 @340MW, MSLC3 @300MW, SLTEC 1 @117MW, SLTEC 2 @118MW, ILIJAN A @350MW [WEBSMS] | CLUZ
5/19/2024 5:56:58 AM | Luzon Grid-05/19/2024 05:57: Lumban-Bay 230kV Line 2 de-energized at 0555H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 5:36:15 AM | Visayas Grid-05/19/2024 05:36: Mandaue - Guizo and Mandaue - Paknaan 69 kV Lines de-energized at 0534H and 0535H (Planned Outage) [WEBSMS] | CVIS
5/19/2024 5:17:40 AM | Mindanao Grid-05/19/2024 05:22: WMPC DG10 Shutdown at 0516H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/19/2024 5:14:20 AM | Luzon Grid-05/19/2024 05:14: San Jose PCB 9-07CB04SJO and 9-08CB04SJO de-energized at 0512H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 5:10:56 AM | Luzon Grid-05/19/2024 05:11: San Jose-Balsik 500kV Line de-energized at 0510H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 4:46:03 AM | Mindanao Grid-05/19/2024 04:51: Naga Mindanao SS SVC energized at 0444H. (Planned Outage) [WEBSMS] | CMIN
5/19/2024 4:43:23 AM | Mindanao Grid-05/19/2024 04:48: Naga Mindanao SS 138kV Bus 2 energized at 0442H. (Planned Outage) [WEBSMS] | CMIN
5/19/2024 4:40:43 AM | [NSO Update] Mindanao Grid-05/19/2024 04:45: Weather Update: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
5/19/2024 4:40:14 AM | [NSO Update] Visayas Grid-05/19/2024 04:40: Weather Update: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
5/19/2024 4:39:27 AM | [NSO Update] Luzon Grid-05/19/2024 04:39: Weather Update: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
5/19/2024 4:14:59 AM | Luzon Grid-05/19/2024 04:15: Pantabangan-Nagsaag 230kV Line de-energized at 0411H (Planned Outage) [WEBSMS] | CLUZ
5/19/2024 3:01:43 AM | Mindanao Grid-05/19/2024 03:06: Balo-i SS 138kV Bus 1 energized at 0258H. (Planned Outage) [WEBSMS] | CMIN
5/19/2024 1:42:18 AM | Mindanao Grid-05/19/2024 01:47: Balo-i - Luga-it 138kV Line energized/looped at 0140H. (Planned Outage) [WEBSMS] | CMIN
5/19/2024 12:09:53 AM | Mindanao Grid-05/19/2024 00:14: Naga Mindanao SS 138kV Bus 2 de-energized/shutdown at 0008H. (Planned Outage) [WEBSMS] | CMIN
5/19/2024 12:07:46 AM | Mindanao Grid-05/19/2024 00:12: Naga Mindanao SS 138kV SVC De-energized/shutdown at 0005H. (Planned Outage) [WEBSMS] | CMIN
5/18/2024 11:52:15 PM | Mindanao Grid-05/18/2024 23:57: Matanao - Digos Solar Power Plant (DSP) 69kV Line 1 energized at 2346H. (Planned Outage) [WEBSMS] | CMIN
5/18/2024 11:39:00 PM | Mindanao Grid-05/18/2024 23:44: Baloi-i SS 138kV Bus 1 de-energized/shutdown at 2336H. (Planned Outage) [WEBSMS] | CMIN
5/18/2024 11:34:56 PM | Luzon Grid-05/18/2024 23:35: Binan 230kV Bus 2 de-energized at 2334H (Planned Outage) [WEBSMS] | CLUZ
5/18/2024 11:32:14 PM | Luzon Grid-05/18/2024 23:32: Binan 300MVA T02 de-energized at 2332H (Planned Outage) [WEBSMS] | CLUZ
5/18/2024 11:21:54 PM | Visayas Grid-05/18/2024 23:22: Daanbantayan SS 230 kV bus 1 energized 2319H (Planned Outage) [WEBSMS] | CVIS
5/18/2024 11:18:14 PM | [NSO Update] Visayas Grid-05/18/2024 23:18: Luzon Grid-05/18/2024 13:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2314H with power going to Luzon. [WEBSMS] | CVIS
5/18/2024 11:17:31 PM | [NSO Update] Luzon Grid-05/18/2024 23:17: Luzon Grid-05/18/2024 13:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2314H with power going to Luzon. [WEBSMS] | CLUZ
5/18/2024 11:12:48 PM | Luzon Grid-05/18/2024 23:12: SCPC 1 online at 2311H (Planned Outage) [WEBSMS] | CLUZ
5/18/2024 11:09:05 PM | [NSO Update] Visayas Grid-05/18/2024 23:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2301H from reverse power direction [WEBSMS] | CVIS
5/18/2024 11:08:00 PM | [NSO Update] Luzon Grid-05/18/2024 23:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2301H from reverse power direction [WEBSMS] | CLUZ
5/18/2024 10:08:20 PM | Mindanao Grid-05/18/2024 22:13: WMPC DG1 Shutdown at 2201H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/18/2024 10:07:26 PM | Luzon Grid-05/18/2024 22:07: SCPC 3 manually tripped at 2154H from 30MW load (Unplanned Outage) [WEBSMS] | CLUZ
5/18/2024 8:00:35 PM | [NSO Update] Visayas Grid-05/18/2024 20:00: System Advisory: Visayas Grid Yellow Alert notice issued today has been lifted at 1958H. [WEBSMS] | CVIS
5/18/2024 6:53:32 PM | Luzon Grid-05/18/2024 18:53: SCPC 3 synchronized at 1852H (Unplanned Outage) [WEBSMS] | CLUZ
5/18/2024 6:04:34 PM | [NSO Update] Mindanao Grid-05/18/2024 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3048MW, PK=2389MW, RR=73MW, NetOpMargin: EVE=587 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/18/2024 6:02:53 PM | [NSO Update] Visayas Grid-05/18/2024 18:02: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2673MW, PK=2374MW, RR=91MW, NetOpMargin: EVE=207 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @300MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW, Tongonan GPP @79.5MW, Power Barge 104-3 @5MW [WEBSMS] | CVIS
5/18/2024 5:55:31 PM | [NSO Update] Luzon Grid-05/18/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12627MW, PK=11491MW, RR=429MW, NetOpMargin: EVE=707 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @325MW, MSLC2 @340MW, MSLC3 @240MW, SLTEC 1 @116MW, SLTEC 2 @116MW, ILIJAN A @250MW [WEBSMS] | CLUZ
5/18/2024 5:45:13 PM | Luzon Grid-05/18/2024 17:45: Binga-La Trinidad 230kV L2 restored at 1738H (Planned Outage) [WEBSMS] | CLUZ
5/18/2024 5:34:56 PM | Luzon Grid-05/18/2024 17:35: SCPC 1 synchronized at 1726H but tripped at 1732H (Unplanned Outage) [WEBSMS] | CLUZ
5/18/2024 4:32:17 PM | Luzon Grid-05/18/2024 16:32: Balsik-San Jose 500kV Line looped/restored at 1631H (Unplanned Outage) [WEBSMS] | CLUZ
5/18/2024 4:25:43 PM | Luzon Grid-05/18/2024 16:25: SCPC 1 & 3 with a total load of 300MW (150MW each) on houseload due to SIPS activation caused by unlooping of Balsik-San Jose 500kV Line at 1612H. Lowest Frequency is 59.31Hz (Unplanned Outage) [WEBSMS] | CLUZ
5/18/2024 4:22:49 PM | Mindanao Grid-05/18/2024 16:27: General Santos - Tacurong 138kV Line1 energized/looped at 1619H. (Unplanned Outage) [WEBSMS] | CMIN
5/18/2024 3:50:16 PM | Mindanao Grid-05/18/2024 15:55: WMPC DG07 shutdown at 1536H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/18/2024 3:45:43 PM | Mindanao Grid-05/18/2024 15:50: WMPC DG07 shutdown at 1337H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/18/2024 3:45:16 PM | Mindanao Grid-05/18/2024 15:50: General Santos - Tacurong 138kV Line 2 energized/looped at 1540H. (Unplanned Outage) [WEBSMS] | CMIN
5/18/2024 3:42:50 PM | Mindanao Grid-05/18/2024 15:47: General Santos - Tacurong 138kV Line 1 and Line 2 simultaneously tripped at 1529H. (Unplanned Outage) [WEBSMS] | CMIN
5/18/2024 1:39:17 PM | Mindanao Grid-05/18/2024 13:44: WMPC DG7 Online at 1337H. MRU -System Voltage Requirement. [WEBSMS] | CMIN
5/18/2024 1:38:10 PM | [NSO Update] Visayas Grid-05/18/2024 13:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1331H with power going to Visayas. [WEBSMS] | CVIS
5/18/2024 1:37:55 PM | [NSO Update] Luzon Grid-05/18/2024 13:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1331H with power going to Visayas. [WEBSMS] | CLUZ
5/18/2024 1:25:03 PM | [NSO Update] Visayas Grid-05/18/2024 13:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1318H from forward power direction [WEBSMS] | CVIS
5/18/2024 1:24:47 PM | [NSO Update] Luzon Grid-05/18/2024 13:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1318H from forward power direction [WEBSMS] | CLUZ
5/18/2024 1:23:19 PM | Mindanao Grid-05/18/2024 13:28: Balo-i - Luga-it 138kV Line De-energized/shutdown at 1320H. (Planned Outage) [WEBSMS] | CMIN
5/18/2024 12:55:03 PM | [NSO Update] Luzon Grid-05/18/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14089MW, PK=12388MW, RR=441MW, NetOpMargin: PM=1260, EVE=965 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @325MW, MSLC2 @340MW, MSLC3 @240MW, SLTEC 1 @116MW, SLTEC 2 @118MW, ILIJAN A @250MW [WEBSMS] | CLUZ
5/18/2024 12:54:45 PM | [NSO Update] Mindanao Grid-05/18/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3092MW, PK=2450MW, RR=73MW, NetOpMargin: PM=570, EVE=567 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/18/2024 12:53:35 PM | [NSO Update] Visayas Grid-05/18/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2748MW, PK=2440MW, RR=91MW, NetOpMargin: PM=217, EVE=189 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @295MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW, Tongonan GPP @78.5MW, Power Barge 104-3 @5MW [WEBSMS] | CVIS
5/18/2024 12:48:40 PM | [NSO Update] Luzon Grid-05/18/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14089MW, PK=12388MW, RR=441MW, NetOpMargin: PM=1260, EVE=965 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @325MW, MSLC2 @340MW, MSLC3 @240MW, SLTEC 1 @116MW, SLTEC 2 @118MW, ILIJAN A @250MW [WEBSMS] | CLUZ
5/18/2024 11:39:49 AM | Luzon Grid-05/18/2024 11:39: Correction: Nagsaag SS PCB 9Z-03CB24NGS restored at 1139H (Planned Outage) [WEBSMS] | CLUZ
5/18/2024 11:32:58 AM | Luzon Grid-05/18/2024 11:33: Nagsaag SS PCB 9Z-03CB24NGS de-energized at 1130H (Planned Outage) [WEBSMS] | CLUZ
5/18/2024 11:13:12 AM | Mindanao Grid-05/18/2024 11:18: WMPC DG1 Online at 1111H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/18/2024 11:06:02 AM | Visayas Grid-05/18/2024 11:06: Calongcalong SS 50 MVA TR2 energized at 1105H (Planned Outage) [WEBSMS] | CVIS
5/18/2024 9:42:00 AM | Mindanao Grid-05/18/2024 09:46: WMPC DG10 online at 0938H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/18/2024 9:41:08 AM | Mindanao Grid-05/18/2024 09:46: WMPC DG10 Online at 0938H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/18/2024 8:23:19 AM | Mindanao Grid-05/18/2024 08:28: AGUS1 Unit 1 shutdown at 0809H. PMS (Non-GOMP) [WEBSMS] | CMIN
5/18/2024 8:05:57 AM | Visayas Grid-05/18/2024 08:06: Calongcalong SS 50 MVA TR2 de-energized at 0805H (Planned Outage) [WEBSMS] | CVIS
5/18/2024 7:00:06 AM | Luzon Grid-05/18/2024 07:00: Balsik SS PCB 9Z-01CB24BIK restored at 0614H (Planned Outage) [WEBSMS] | CLUZ
5/18/2024 6:37:54 AM | Visayas Grid-05/18/2024 06:37: Daan Bantayan SS 230 kV bus 1 de-energized 0637H (Planned Outage) [WEBSMS] | CVIS
5/18/2024 6:32:31 AM | [NSO Update] Visayas Grid-05/18/2024 06:32: System Advisory: 18-May-2024, Visayas Grid is on YELLOW Alert for interval hour 1900H. Total capacity on forced outage is 338.8MW. Total of de-rated capacity is 239.6MW. [WEBSMS] | CVIS
5/18/2024 6:16:57 AM | Luzon Grid-05/18/2024 06:17: Balsik SS PCB 9Z-01CB24BIK de-energized at 0614H (Planned Outage) [WEBSMS] | CLUZ
5/18/2024 6:08:11 AM | Luzon Grid-05/18/2024 06:08: Binga-La Trinidad 230kV L2 de-energized at 0604H (Planned Outage) [WEBSMS] | CLUZ
5/18/2024 5:59:02 AM | [NSO Update] Luzon Grid-05/18/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14474MW, PK=11377MW, RR=440MW, NetOpMargin: AM=2657, PM=1292, EVE=976 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @325MW, MSLC2 @340MW, MSLC3 @240MW, SLTEC 1 @116MW, SLTEC 2 @116MW, ILIJAN A @250MW, [WEBSMS] | CLUZ
5/18/2024 5:43:26 AM | [NSO Update] Mindanao Grid-05/18/2024 05:48: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today, 18 May 2024, at 0534H. Market operations will resume starting interval 0545H. [WEBSMS] | CMIN
5/18/2024 5:42:50 AM | [NSO Update] Visayas Grid-05/18/2024 05:42: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today, 18 May 2024, at 0534H. Market operations will resume starting interval 0545H. [WEBSMS] | CVIS
5/18/2024 5:41:28 AM | [NSO Update] Luzon Grid-05/18/2024 05:41: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today, 18 May 2024, at 0534H. Market operations will resume starting interval 0545H [WEBSMS] | CLUZ
5/18/2024 5:39:08 AM | [NSO Update] Mindanao Grid-05/18/2024 05:44: MO-initiated Market Intervention is issued today, 18 May 2024, for Luzon, Visayas, & Mindanao Grid starting interval 0540H due to failure to generate RTD. [WEBSMS] | CMIN
5/18/2024 5:38:42 AM | [NSO Update] Luzon Grid-05/18/2024 05:38: MO-initiated Market Intervention is issued today, 18 May 2024, for Luzon, Visayas, & Mindanao Grid starting interval 0540H due to failure to generate RTD. [WEBSMS] | CLUZ
5/18/2024 5:38:33 AM | [NSO Update] Visayas Grid-05/18/2024 05:38: MO-initiated Market Intervention is issued today, 18 May 2024, for Luzon, Visayas, & Mindanao Grid starting interval 0540H due to failure to generate RTD. [WEBSMS] | CVIS
5/18/2024 5:33:16 AM | [NSO Update] Mindanao Grid-05/18/2024 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3106MW, PK=2330MW, RR=73MW, NetOpMargin: AM=703, PM=623, EVE=569 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/18/2024 5:12:23 AM | Luzon Grid-05/18/2024 05:12: San Jose-Tayabas 500kV Line 2 de-energized at 0512H. (Planned Outage) [WEBSMS] | CLUZ
5/18/2024 4:40:05 AM | Luzon Grid-05/18/2024 04:40: Currimao - Laoag 115kV Line restored at 0440H. (Unplanned Outage) [WEBSMS] | CLUZ
5/18/2024 4:02:06 AM | [NSO Update] Luzon Grid-05/18/2024 04:02: Weather Advisory: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
5/18/2024 4:02:02 AM | [NSO Update] Visayas Grid-05/18/2024 04:02: Weather Advisory: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
5/18/2024 4:01:59 AM | [NSO Update] Mindanao Grid-05/18/2024 04:06: Weather Advisory: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
5/18/2024 1:26:58 AM | Mindanao Grid-05/18/2024 01:31: Manolo 1 Unit 3 online at 0048H. (Unplanned Outage) [WEBSMS] | CMIN
5/18/2024 1:26:02 AM | Mindanao Grid-05/18/2024 01:31: Manolo 1 Unit 1 online at 0047H. (Unplanned outage) [WEBSMS] | CMIN
5/18/2024 12:54:27 AM | Mindanao Grid-05/18/2024 00:59: Matanao - Digos Solar 69kV line energized at 0046H. (From Planned Outage) [WEBSMS] | CMIN
5/18/2024 12:35:01 AM | [NSO Update] Luzon Grid-05/18/2024 00:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0030H with power going to Luzon. [WEBSMS] | CLUZ
5/18/2024 12:34:35 AM | [NSO Update] Visayas Grid-05/18/2024 00:34: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0030H with power going to Luzon. [WEBSMS] | CVIS
5/18/2024 12:22:35 AM | [NSO Update] Luzon Grid-05/18/2024 00:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0020H from reverse power direction. [WEBSMS] | CLUZ
5/18/2024 12:21:58 AM | [NSO Update] Visayas Grid-05/18/2024 00:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0020H from reverse power direction. [WEBSMS] | CVIS
5/17/2024 11:39:15 PM | Luzon Grid-05/17/2024 23:39: Ilijan GT1-2 shutdown at 2337H (Unplanned Outage) [WEBSMS] | CLUZ
5/17/2024 10:50:15 PM | Mindanao Grid-05/17/2024 22:55: WMPC DG10 shutdown at 2246H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/17/2024 10:02:42 PM | Mindanao Grid-05/17/2024 22:07: WMPC DG01 shutdown at 2202H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/17/2024 9:37:51 PM | Luzon Grid-05/17/2024 21:37: MPGC 1 with 150MW tripped at 2135H. Lowest system frequency was 59.631Hz. (Unplanned Outage) [WEBSMS] | CLUZ
5/17/2024 9:36:06 PM | [NSO Update] Visayas Grid-05/17/2024 21:36: System Advisory: Visayas Grid Yellow Alert notice issued today has been lifted at 2133H. [WEBSMS] | CVIS
5/17/2024 7:47:21 PM | Mindanao Grid-05/17/2024 19:52: WMPC DG08 shutdown at 1946H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/17/2024 7:41:00 PM | Luzon Grid-05/17/2024 19:41: Currimao - Laoag 115kV Line tripped at 1931H. (Unplanned Outage) [WEBSMS] | CLUZ
5/17/2024 7:01:48 PM | Mindanao Grid-05/17/2024 19:06: SPC Mati with 9MW load tripped at 1820H. Isolated by the tripping of Maco - Banaybanay 69kV Line. (Unplanned Outage). [WEBSMS] | CMIN
5/17/2024 6:47:24 PM | Mindanao Grid-05/17/2024 18:52: FDC Unit 1 online at 1841H (Unplanned Outage) [WEBSMS] | CMIN
5/17/2024 6:34:49 PM | [NSO Update] Luzon Grid-05/17/2024 18:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13635MW, PK=12233MW, RR=469MW, NetOpMargin: EVE=934 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @350MW, SLTEC 1 @116MW, SLTEC 2 @116MW, Bakun HEPP @10MW, Masinloc 1 @325MW, Masinloc 2 @335MW [WEBSMS] | CLUZ
5/17/2024 6:07:24 PM | Mindanao Grid-05/17/2024 18:12: Matanao - Digos Solar 69kV line de-energized at 1804H. (Planned Outage) [WEBSMS] | CMIN
5/17/2024 5:53:51 PM | [NSO Update] Visayas Grid-05/17/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2731MW, PK=2435MW, RR=91MW, NetOpMargin: EVE=205 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @302MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW [WEBSMS] | CVIS
5/17/2024 5:44:22 PM | [NSO Update] Mindanao Grid-05/17/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2967MW, PK=2416MW, RR=73MW, NetOpMargin: EVE=478 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/17/2024 5:19:21 PM | Visayas Grid-05/17/2024 17:19: MECO (Gaisano Metro) ILP cut off at 1707H. [WEBSMS] | CVIS
5/17/2024 5:15:58 PM | Visayas Grid-05/17/2024 17:16: MECO (Gaisano Island Mall) ILP cut off at 1654H. [WEBSMS] | CVIS
5/17/2024 4:42:03 PM | Visayas Grid-05/17/2024 16:42: MECO (Gaisano Grand Mall Basak) ILP cut off at 1639H. [WEBSMS] | CVIS
5/17/2024 4:28:46 PM | Visayas Grid-05/17/2024 16:28: MECO F#5 (MCIAA Terminal 2) ILP cut off at 1625H. [WEBSMS] | CVIS
5/17/2024 4:25:25 PM | Visayas Grid-05/17/2024 16:25: MECO (Sheraton) ILP cut off at 1618H. [WEBSMS] | CVIS
5/17/2024 4:23:26 PM | Visayas Grid-05/17/2024 16:23: MECO (JPark) ILP cut off at 1615H. [WEBSMS] | CVIS
5/17/2024 4:21:56 PM | Visayas Grid-05/17/2024 16:21: GMC ILP cut off at 1617H. [WEBSMS] | CVIS
5/17/2024 4:08:41 PM | [NSO Update] Visayas Grid-05/17/2024 16:08: SO initiated Market Intervention for Visayas has been lifted today at 1557H. Market operations will resume starting interval 1605H. [WEBSMS] | CVIS
5/17/2024 4:04:25 PM | Visayas Grid-05/17/2024 16:04: MECO (Mactan Newtown Portion) MLD of 1.8 MW load at 1258H restored at 1556H. [WEBSMS] | CVIS
5/17/2024 3:16:04 PM | Visayas Grid-05/17/2024 15:16: MECO (Part of MECO feeder) MLD restored at 1500H. [WEBSMS] | CVIS
5/17/2024 3:13:53 PM | Visayas Grid-05/17/2024 15:13: MECO (Sheraton) implemented ILP of 1.5 MW load at 1457H [WEBSMS] | CVIS
5/17/2024 3:02:46 PM | Visayas Grid-05/17/2024 15:02: MECO (Gaisano Metro) implemented ILP of 0.8 MW load at 1432H [WEBSMS] | CVIS
5/17/2024 2:37:02 PM | Visayas Grid-05/17/2024 14:37: MECO (Mactan Newtown) portion of Feeder#4 MLD restored at 1415H. [WEBSMS] | CVIS
5/17/2024 2:33:05 PM | Visayas Grid-05/17/2024 14:33: MECO implemented 3.2MW MLD part of Pajo Feeder at 1403H. (Unplanned Outage) [WEBSMS] | CVIS
5/17/2024 1:45:42 PM | Visayas Grid-05/17/2024 13:45: MECO F#5 (MCIAA Terminal 2) implemented ILP of 1.8 MW load at 1341H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/17/2024 1:15:50 PM | [NSO Update] Mindanao Grid-05/17/2024 13:20: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3013MW, PK=2580MW, RR=73MW, NetOpMargin: PM=360, EVE=478 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/17/2024 1:14:17 PM | [NSO Update] Luzon Grid-05/17/2024 13:14: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14904MW, PK=13572MW, RR=531MW, NetOpMargin: PM=801, EVE=1150 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @350MW, SLTEC 1 @114MW, SLTEC 2 @117MW, Bakun HEPP @10MW, Masinloc 1 @325MW, Masinloc 2 @335MW [WEBSMS] | CLUZ
5/17/2024 1:12:21 PM | Visayas Grid-05/17/2024 13:12: MECO (JPark Hotel) implemented ILP of 2.2 MW load at 1308H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/17/2024 1:11:28 PM | [NSO Update] Visayas Grid-05/17/2024 13:11: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=3018MW, PK=2625MW, RR=91MW, NetOpMargin: PM=302, EVE=197 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @302MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW, Panay Diesel 3-G @8MW [WEBSMS] | CVIS
5/17/2024 1:11:27 PM | Mindanao Grid-05/17/2024 13:16: WMPC DG07 online at 1245H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/17/2024 1:10:43 PM | Mindanao Grid-05/17/2024 13:15: WMPC DG03 online at 1045H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/17/2024 1:09:40 PM | [NSO Update] Visayas Grid-05/17/2024 13:09: System Advisory: 17-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1600H, 1900H, 2000H, and 2100H. Total capacity on forced outage is 324.3MW. Total of de-rated capacity is 206.3MW. [WEBSMS] | CVIS
5/17/2024 1:04:21 PM | Visayas Grid-05/17/2024 13:04: MECO (Mactan Newtown Portion) implemented ILP of 1.8 MW load at 1258H to prevent overloading of Cebu-Mandaue 138 kV line 2 [WEBSMS] | CVIS
5/17/2024 12:22:26 PM | Mindanao Grid-05/17/2024 12:27: Manolo 1 Unit 2 & 4 shutdown at 1208H. Comprehensive assessment of 138kV Equipment. (Unplanned Outage) [WEBSMS] | CMIN
5/17/2024 11:59:34 AM | Visayas Grid-05/17/2024 11:59: COLON-NAGA 138kV line 2 energized at 1155H. ( Planned Outage ) [WEBSMS] | CVIS
5/17/2024 11:09:22 AM | Visayas Grid-05/17/2024 11:09: MECO (Gaisano Grand Mall Basak) implemented ILP of 1.7 MW load at 1105H to prevent overloading of Cebu-Mandaue 138 kV line 2 [WEBSMS] | CVIS
5/17/2024 10:42:46 AM | Visayas Grid-05/17/2024 10:42: MECO (Gaizano Island Mall) implemented ILP of 1.0 MW load at 1038H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/17/2024 10:37:33 AM | [NSO Update] Visayas Grid-05/17/2024 10:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1032H with power going to Visayas. [WEBSMS] | CVIS
5/17/2024 10:37:17 AM | [NSO Update] Luzon Grid-05/17/2024 10:36: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1032H with power going to Visayas. [WEBSMS] | CLUZ
5/17/2024 10:35:47 AM | [NSO Update] Luzon Grid-05/17/2024 10:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1021H from forward power direction. [WEBSMS] | CLUZ
5/17/2024 10:35:26 AM | [NSO Update] Visayas Grid-05/17/2024 10:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1021H from forward power direction. [WEBSMS] | CVIS
5/17/2024 10:17:15 AM | Mindanao Grid-05/17/2024 10:22: WMPC DG08 online at 1012H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/17/2024 10:03:00 AM | Visayas Grid-05/17/2024 10:03: GMC implemented ILP of 2.0 MW load at 0958H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/17/2024 9:21:02 AM | Visayas Grid-05/17/2024 09:21: VECO ( GIS 1&4 ) implemented load transfer of 5.8MW at 0911H to prevent overloading of Cebu-LapuLapu 138kV line2. [WEBSMS] | CVIS
5/17/2024 9:18:31 AM | Mindanao Grid-05/17/2024 09:23: WMPC DG01 online at 0916H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/17/2024 9:15:56 AM | Visayas Grid-05/17/2024 09:15: MECO (Mactan Newtown) portion of Feeder#4 implemented MLD instead of ILP of 3.2mW at 0851H to prevent overloading of Cebu-Lapulapu 138kV line 2 due to non availability of EAUC U 1 & 4. [WEBSMS] | CVIS
5/17/2024 9:15:47 AM | [NSO Update] Visayas Grid-05/17/2024 09:15: SO-initiated Market Intervention for Visayas is issued today starting interval 0855H due to MLD implementation to prevent the overloading of Cebu-Mandaue 138kV Line 2. [WEBSMS] | CVIS
5/17/2024 9:01:27 AM | Visayas Grid-05/17/2024 09:01: COLON-NAGA 138kV line 2 de-energized at 0847H. ( Planned Outage ) [WEBSMS] | CVIS
5/17/2024 8:58:10 AM | Luzon Grid-05/17/2024 08:58: San Jose 750MVA TO5 de-energized at 0852H (Planned Outage) [WEBSMS] | CLUZ
5/17/2024 8:23:15 AM | Mindanao Grid-05/17/2024 08:28: WMPC DG10 online at 0819H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/17/2024 5:47:09 AM | [NSO Update] Mindanao Grid-05/17/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3057MW, PK=2445MW, RR=73MW, NetOpMargin: AM=540, PM=341, EVE=454 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @32MW [WEBSMS] | CMIN
5/17/2024 5:45:57 AM | [NSO Update] Visayas Grid-05/17/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2840MW, PK=2479MW, RR=91MW, NetOpMargin: AM=270, PM=179, EVE=253 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @307MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW, Panay Diesel 3-G @8MW [WEBSMS] | CVIS
5/17/2024 5:43:48 AM | [NSO Update] Luzon Grid-05/17/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15285MW, PK=12656MW, RR=491MW, NetOpMargin: AM=2138, PM=962, EVE=1113 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 320MW, Masinloc 2 @ 335MW, SLTEC 1 @ 112MW, SLTEC 2 @ 115MW, Ilijan A @ 350MW [WEBSMS] | CLUZ
5/17/2024 4:08:21 AM | [NSO Update] Mindanao Grid-05/17/2024 04:13: Weather Advisory: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
5/17/2024 4:08:07 AM | [NSO Update] Visayas Grid-05/17/2024 04:08: Weather Advisory: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
5/17/2024 4:07:52 AM | [NSO Update] Luzon Grid-05/17/2024 04:07: Weather Advisory: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
5/17/2024 12:07:43 AM | [NSO Update] Visayas Grid-05/17/2024 00:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0006H with power going to Luzon. [WEBSMS] | CVIS
5/17/2024 12:07:28 AM | [NSO Update] Luzon Grid-05/17/2024 00:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0006H with power going to Luzon. [WEBSMS] | CLUZ
5/16/2024 11:55:40 PM | [NSO Update] Visayas Grid-05/16/2024 23:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2351H from reverse power direction. [WEBSMS] | CVIS
5/16/2024 11:54:47 PM | [NSO Update] Luzon Grid-05/16/2024 23:54: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2351H from reverse power direction. [WEBSMS] | CLUZ
5/16/2024 11:15:57 PM | Mindanao Grid-05/16/2024 23:20: WMPC DG10 shutdown at 2246H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/16/2024 11:14:57 PM | Mindanao Grid-05/16/2024 23:19: WMPC DG01 shutdown at 2301H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/16/2024 9:00:34 PM | [NSO Update] Visayas Grid-05/16/2024 21:00: System Advisory: Visayas Grid Yellow Alert notice issued today has been lifted at 2058H. [WEBSMS] | CVIS
5/16/2024 8:00:54 PM | Luzon Grid-05/16/2024 20:01: QPPL shutdown at 2000H. (Unplanned Outage) [WEBSMS] | CLUZ
5/16/2024 7:48:35 PM | Luzon Grid-05/16/2024 19:48: Bay-Calamba 230kV line 1 was restored at 1945H. (Unplanned Outage) [WEBSMS] | CLUZ
5/16/2024 6:39:36 PM | Mindanao Grid-05/16/2024 18:44: WMPC DG07 shutdown at 1716H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/16/2024 6:22:54 PM | [NSO Update] Luzon Grid-05/16/2024 18:23: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14043MW, PK=12202MW, RR=469MW, NetOpMargin: EVE=1372 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 315MW, Masinloc 2 @ 335MW, SLTEC 1 @ 113MW, SLTEC 2 @ 115MW, Ilijan A @ 350MW [WEBSMS] | CLUZ
5/16/2024 6:20:11 PM | [NSO Update] Luzon Grid-05/16/2024 18:20: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14043MW, PK=12202MW, RR=469MW, NetOpMargin: EVE=1372 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 315MW, Masinloc 2 @ 335MW, SLTEC 1 @ 113MW, SLTEC 2 @ 115MW, Ilijan A @ 350MW [WEBSMS] | CLUZ
5/16/2024 6:07:36 PM | Visayas Grid-05/16/2024 18:07: MECO implemented ILP to prevent overloading of Cebu - Mandaue 138 kV Line 2 lifted at 1727H [WEBSMS] | CVIS
5/16/2024 5:55:21 PM | [NSO Update] Mindanao Grid-05/16/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2968MW, PK=2447MW, RR=73MW, NetOpMargin: EVE=448 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @36MW [WEBSMS] | CMIN
5/16/2024 5:53:06 PM | [NSO Update] Visayas Grid-05/16/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2720MW, PK=2437MW, RR=91MW, NetOpMargin: EVE=191 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @287MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW, Panay Diesel 3-G @8MW [WEBSMS] | CVIS
5/16/2024 4:48:22 PM | Mindanao Grid-05/16/2024 16:53: WMPC DG08 shutdown at 1646H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/16/2024 4:17:00 PM | Visayas Grid-05/16/2024 16:17: GMC implemented ILP to prevent overloading of Cebu - Mandaue 138 kV Line 2 lifted at 1604H [WEBSMS] | CVIS
5/16/2024 1:45:20 PM | Visayas Grid-05/16/2024 13:45: MECO (MEPZ 2 Acoland) implemented ILP of 4.6 MW load at 1342H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/16/2024 1:44:54 PM | Luzon Grid-05/16/2024 13:45: Santiago-NIA Baligatan HEPP 69kV Line restored at 1344H (Planned Outage) [WEBSMS] | CLUZ
5/16/2024 1:39:40 PM | Visayas Grid-05/16/2024 13:39: MECO (Gaizano Mall Basak) implemented ILP of 2.3 MW load at 1336H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/16/2024 1:33:58 PM | Visayas Grid-05/16/2024 13:33: MECO (Gaizano Island Mall) implemented ILP of 1.2 MW load at 1331H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/16/2024 1:19:00 PM | Visayas Grid-05/16/2024 13:19: MECO (Cebu Light) implemented ILP of 1.2 MW load at 1309H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/16/2024 1:16:36 PM | Visayas Grid-05/16/2024 13:16: ECO (KNOWLES Electronic) implemented ILP of 2.0 MW load at 1301H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/16/2024 1:11:13 PM | [NSO Update] Visayas Grid-05/16/2024 13:11: Update on System Advisory: 16-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1500H-1600H and 1900H-2000H. Total capacity on forced outage is 305.8MW. Total of de-rated capacity is 215.3MW. [WEBSMS] | CVIS
5/16/2024 1:02:54 PM | [NSO Update] Visayas Grid-05/16/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=3028MW, PK=2659MW, RR=91MW, NetOpMargin: PM=278, EVE=168 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @293MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW, Panay Diesel 3-G @8MW [WEBSMS] | CVIS
5/16/2024 12:56:58 PM | [NSO Update] Mindanao Grid-05/16/2024 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3021MW, PK=2590MW, RR=73MW, NetOpMargin: PM=358, EVE=485 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @36MW [WEBSMS] | CMIN
5/16/2024 12:51:08 PM | [NSO Update] Luzon Grid-05/16/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15389MW, PK=13551MW, RR=491MW, NetOpMargin: PM=1347, EVE=1243 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 315MW, Masinloc 2 @ 335MW, SLTEC 1 @ 113MW, SLTEC 2 @ 115MW, Ilijan A @ 350MW [WEBSMS] | CLUZ
5/16/2024 12:46:35 PM | Mindanao Grid-05/16/2024 12:51: WMPC DG03 online at 1238H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/16/2024 12:20:48 PM | Visayas Grid-05/16/2024 12:20: MECO (MCIAA Terminal 2) implemented ILP restored @1213H. [WEBSMS] | CVIS
5/16/2024 12:01:07 PM | Luzon Grid-05/16/2024 12:01: Bay-Calamba 230kV Line 1 tripped at 1156H (Unplanned Outage) [WEBSMS] | CLUZ
5/16/2024 11:51:48 AM | Mindanao Grid-05/16/2024 11:56: WMPC DG07 online at 1135H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/16/2024 11:09:11 AM | Visayas Grid-05/16/2024 11:09: GMC implemented additional ILP of 1.0 MW load at 1049H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/16/2024 11:00:30 AM | Visayas Grid-05/16/2024 11:00: MECO (Sheraton Hotel) implemented ILP of 1.5 MW load at 1052H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/16/2024 10:30:35 AM | Visayas Grid-05/16/2024 10:30: MECO (MCIAA Terminal 2) implemented ILP of 2.0 MW load at 1027H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/16/2024 10:05:31 AM | Visayas Grid-05/16/2024 10:05: GMC implemented ILP of 2.0 MW load at 0950H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/16/2024 9:39:36 AM | Visayas Grid-05/16/2024 09:39: MECO (JPark Hotel) implemented ILP of 2.5 MW load at 0933H to prevent overloading of Cebu-Mandaue 138 kV line 2. [WEBSMS] | CVIS
5/16/2024 8:50:56 AM | Mindanao Grid-05/16/2024 08:55: WMPC DG01 online at 0846H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/16/2024 8:12:56 AM | Mindanao Grid-05/16/2024 08:17: WMPC DG10 online at 0801H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/16/2024 6:16:03 AM | Mindanao Grid-05/16/2024 06:20: Pulangi4 U1 shutdown at 0417H. Low Water Forebay Elevation. Outside Management Control (OMC). [WEBSMS] | CMIN
5/16/2024 6:11:01 AM | [NSO Update] Luzon Grid-05/16/2024 06:11: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0607H with power going to Visayas. [WEBSMS] | CLUZ
5/16/2024 6:10:47 AM | [NSO Update] Visayas Grid-05/16/2024 06:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0607H with power going to Visayas. [WEBSMS] | CVIS
5/16/2024 6:04:52 AM | [NSO Update] Visayas Grid-05/16/2024 06:04: System Advisory: 16-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1600H and 1900H. Total capacity on forced outage is 318.8MW. Total of de-rated capacity is 196.3MW. [WEBSMS] | CVIS
5/16/2024 6:01:55 AM | [NSO Update] Visayas Grid-05/16/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=3072MW, PK=2551MW, RR=91MW, NetOpMargin: AM=430, PM=308, EVE=205 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @307MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW [WEBSMS] | CVIS
5/16/2024 5:59:58 AM | [NSO Update] Mindanao Grid-05/16/2024 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3046MW, PK=2534MW, RR=73MW, NetOpMargin: AM=439, PM=410, EVE=530 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @48.9MW, MA2 @36MW [WEBSMS] | CMIN
5/16/2024 5:58:21 AM | [NSO Update] Luzon Grid-05/16/2024 05:58: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0554H from forward power direction. [WEBSMS] | CLUZ
5/16/2024 5:57:51 AM | [NSO Update] Luzon Grid-05/16/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15780MW, PK=12791MW, RR=516MW, NetOpMargin: AM=2473, PM=1418, EVE=1244 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 315MW, Masinloc 2 @ 335MW, SLTEC 1 @ 113MW, SLTEC 2 @ 115MW, Ilijan A @ 350MW [WEBSMS] | CLUZ
5/16/2024 5:57:08 AM | [NSO Update] Luzon Grid-05/16/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15780MW, PK=12791MW, RR=516MW, NetOpMargin: AM=2473, PM=1418, EVE=1244 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 315MW, Masinloc 2 @ 335MW, SLTEC 1 @ 113MW, SLTEC 2 @ 115MW, Ilijan A @ 350MW [WEBSMS] | CLUZ
5/16/2024 5:56:34 AM | [NSO Update] Visayas Grid-05/16/2024 05:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0554H from forward power direction. [WEBSMS] | CVIS
5/16/2024 4:29:49 AM | [NSO Update] Mindanao Grid-05/16/2024 04:35: Weather Advisory: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
5/16/2024 4:29:32 AM | [NSO Update] Visayas Grid-05/16/2024 04:29: Weather Advisory: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
5/16/2024 4:29:14 AM | [NSO Update] Luzon Grid-05/16/2024 04:29: Weather Advisory: Shear Line affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
5/16/2024 4:04:30 AM | Luzon Grid-05/16/2024 04:04: Santiago-NIA Baligatan HEPP 69kV Line de-energized at 0402H (Planned Outage) [WEBSMS] | CLUZ
5/16/2024 2:52:16 AM | Luzon Grid-05/16/2024 02:52: For information: Sta Rita 20 completed the fuel changeover from gas to oil at 0234H. [WEBSMS] | CLUZ
5/16/2024 1:53:34 AM | Mindanao Grid-05/16/2024 01:58: Matanao -Digos Solar Plant 69 kV Line energized at 0152H. Planned Outage. [WEBSMS] | CMIN
5/16/2024 1:42:33 AM | Luzon Grid-05/16/2024 01:42: Sta Rita 40 changeover from gas to oil at 0134H. [WEBSMS] | CLUZ
5/16/2024 1:37:07 AM | [NSO Update] Visayas Grid-05/16/2024 01:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0134H with power going to Luzon. [WEBSMS] | CVIS
5/16/2024 1:36:09 AM | [NSO Update] Luzon Grid-05/16/2024 01:36: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0134H with power going to Luzon. [WEBSMS] | CLUZ
5/16/2024 1:20:02 AM | [NSO Update] Visayas Grid-05/16/2024 01:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0116H from reverse power direction. [WEBSMS] | CVIS
5/16/2024 1:18:48 AM | [NSO Update] Luzon Grid-05/16/2024 01:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0116H from reverse power direction. [WEBSMS] | CLUZ
5/15/2024 11:15:01 PM | [NSO Update] Visayas Grid-05/15/2024 23:15: System Advisory: Visayas Grid Yellow Alert notice issued today has been lifted at 2149H. [WEBSMS] | CVIS
5/15/2024 10:26:39 PM | Mindanao Grid-05/15/2024 22:31: WMPC DG10 shutdown at 2216H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/15/2024 9:59:45 PM | Mindanao Grid-05/15/2024 22:04: WMPC DG08 shutdown at 21246H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/15/2024 6:19:22 PM | Mindanao Grid-05/15/2024 18:24: Matanao -Digos Solar Plant 69 kV Line de-energized at 1817H. Planned Outage. [WEBSMS] | CMIN
5/15/2024 6:16:29 PM | [NSO Update] Luzon Grid-05/15/2024 18:16: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14518MW, PK=12138MW, RR=493MW, NetOpMargin: EVE=1886 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @400MW, SLTEC 1 @114MW, SLTEC 2 @116MW, Bakun HEPP @7MW, Masinloc 1 @300MW, Masinloc 2 @270MW [WEBSMS] | CLUZ
5/15/2024 6:15:06 PM | [NSO Update] Mindanao Grid-05/15/2024 18:20: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2997MW, PK=2435MW, RR=73MW, NetOpMargin: EVE=489 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @36MW [WEBSMS] | CMIN
5/15/2024 6:13:09 PM | [NSO Update] Luzon Grid-05/15/2024 18:13: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14518MW, PK=12138MW, RR=493MW, NetOpMargin: EVE=1886 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @400MW, SLTEC 1 @114MW, SLTEC 2 @116MW, Bakun HEPP @7MW, Masinloc 1 @300MW, Masinloc 2 @270MW [WEBSMS] | CLUZ
5/15/2024 6:11:57 PM | [NSO Update] Luzon Grid-05/15/2024 18:12: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14518MW, PK=12138MW, RR=493MW, NetOpMargin: EVE=1886 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @400MW, SLTEC 1 @114MW, SLTEC 2 @116MW, Bakun HEPP @7MW, Masinloc 1 @300MW, Masinloc 2 @270MW [WEBSMS] | CLUZ
5/15/2024 6:05:36 PM | [NSO Update] Visayas Grid-05/15/2024 18:05: Update on System Advisory: 15-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1800H-2200H. Total capacity on forced outage is 351.3MW. Total of de-rated capacity is 210.3MW. [WEBSMS] | CVIS
5/15/2024 6:02:12 PM | [NSO Update] Visayas Grid-05/15/2024 18:02: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2706MW, PK=2503MW, RR=91MW, NetOpMargin: EVE=111 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @293MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-E @11MW [WEBSMS] | CVIS
5/15/2024 5:48:44 PM | Mindanao Grid-05/15/2024 17:53: WMPC DG03 shutdown at 1747H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/15/2024 3:02:03 PM | Mindanao Grid-05/15/2024 15:07: Agus 5 Unit 1 online at 1458H from OMC due to low forebay elevation (Unplanned Outage) [WEBSMS] | CMIN
5/15/2024 2:10:33 PM | Mindanao Grid-05/15/2024 14:15: WMPC DG01 shutdown at 1409H. MRU - System Voltage Requirement [WEBSMS] | CMIN
5/15/2024 2:09:17 PM | Mindanao Grid-05/15/2024 14:14: WMPC DG05 shutdown at 1408H. MRU - System Voltage Requirement [WEBSMS] | CMIN
5/15/2024 1:33:04 PM | Mindanao Grid-05/15/2024 13:38: WMPC DG05 online at 1319H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/15/2024 1:15:02 PM | Mindanao Grid-05/15/2024 13:20: WMPC DG01 online at 1311H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/15/2024 1:04:38 PM | [NSO Update] Visayas Grid-05/15/2024 13:04: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2968MW, PK=2646MW, RR=91MW, NetOpMargin: PM=230, EVE=205 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @298MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-G @8MW [WEBSMS] | CVIS
5/15/2024 12:59:58 PM | Mindanao Grid-05/15/2024 13:05: Update: Lamsan Baggase-Fired Power Plant tripped with 15.42MW Load at 1145H. Indication: For further investigation. (Unplanned Outage) [WEBSMS] | CMIN
5/15/2024 12:59:56 PM | [NSO Update] Mindanao Grid-05/15/2024 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3043MW, PK=2618MW, RR=73MW, NetOpMargin: PM=352, EVE=541 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @36MW [WEBSMS] | CMIN
5/15/2024 12:53:56 PM | [NSO Update] Luzon Grid-05/15/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15193MW, PK=13169MW, RR=531MW, NetOpMargin: PM=1493, EVE=1780 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @400MW, SLTEC 1 @116MW, SLTEC 2 @118MW, Bakun HEPP @7MW, Masinloc 1 @300MW, Masinloc 2 @270MW [WEBSMS] | CLUZ
5/15/2024 12:32:20 PM | Mindanao Grid-05/15/2024 12:37: Lugait SS 75MVA Transformer No. 1 energized at 1229H. (Planned Outage) [WEBSMS] | CMIN
5/15/2024 12:22:16 PM | Mindanao Grid-05/15/2024 12:27: Minergy Coal U3 online at 0038H (Unplanned Outage) [WEBSMS] | CMIN
5/15/2024 12:13:58 PM | Mindanao Grid-05/15/2024 12:19: Lugait - Opol 138kV line energized at 1204H. (Planned Outage) [WEBSMS] | CMIN
5/15/2024 12:13:07 PM | Mindanao Grid-05/15/2024 12:18: IDPP - Lugait 138kV line energized at 1200H. (Planned Outage) [WEBSMS] | CMIN
5/15/2024 12:12:13 PM | Mindanao Grid-05/15/2024 12:17: Lamsan Baggase-Fired Power Plant tripped with 15.42MW Load at 1145H. Indication: Over voltage. (Unplanned Outage) [WEBSMS] | CMIN
5/15/2024 11:56:07 AM | Mindanao Grid-05/15/2024 12:01: Baloi - Lugait 138kV line energized at 1153H. (Planned Outage) [WEBSMS] | CMIN
5/15/2024 11:41:15 AM | Mindanao Grid-05/15/2024 11:46: WMPC DG03 online at 1102H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/15/2024 9:49:18 AM | Visayas Grid-05/15/2024 09:49: CEDC Unit #1 cut-in at 0937H initial 8.0MW (Unplanned Outage) [WEBSMS] | CVIS
5/15/2024 9:32:39 AM | Mindanao Grid-05/15/2024 09:37: WMPC DG08 online at 0926H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/15/2024 9:23:22 AM | Mindanao Grid-05/15/2024 09:28: WMPC DG01 running as MRU tripped at 0919H. Indication: HT low pressure stop. (Unplanned Outage) [WEBSMS] | CMIN
5/15/2024 9:02:19 AM | Mindanao Grid-05/15/2024 09:07: WMPC DG01 online at 0900H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/15/2024 8:31:10 AM | Mindanao Grid-05/15/2024 08:36: WMPC DG10 online at 0821H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/15/2024 8:26:15 AM | [NSO Update] Luzon Grid-05/15/2024 08:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0824H with power going to Visayas. [WEBSMS] | CLUZ
5/15/2024 8:25:54 AM | [NSO Update] Visayas Grid-05/15/2024 08:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0824H with power going to Visayas. [WEBSMS] | CVIS
5/15/2024 8:09:16 AM | [NSO Update] Luzon Grid-05/15/2024 08:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0805H from forward power direction. [WEBSMS] | CLUZ
5/15/2024 8:08:03 AM | [NSO Update] Visayas Grid-05/15/2024 08:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0805H from forward power direction. [WEBSMS] | CVIS
5/15/2024 7:43:46 AM | Mindanao Grid-05/15/2024 07:48: IDPP - Lugait 138kV line de-energized at 0737H (Planned Outage) [WEBSMS] | CMIN
5/15/2024 7:11:58 AM | Mindanao Grid-05/15/2024 07:17: Baloi - Lugait 138kV line de-energized at 0710H. (Planned Outage) [WEBSMS] | CMIN
5/15/2024 7:08:08 AM | Mindanao Grid-05/15/2024 07:13: Lugait - Opol 138kV line de-energized at 0704H. (Planned Outage) [WEBSMS] | CMIN
5/15/2024 6:31:37 AM | Mindanao Grid-05/15/2024 06:36: Lugait SS 75MVA Transformer No. 2 de-energized at 0624H. (Planned Outage) [WEBSMS] | CMIN
5/15/2024 6:28:59 AM | Mindanao Grid-05/15/2024 06:34: Lugait SS 75MVA Transformer No. 1 de-energized at 0623H.(Planned Outage) [WEBSMS] | CMIN
5/15/2024 6:25:16 AM | [NSO Update] Visayas Grid-05/15/2024 06:25: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2810MW, PK=2494MW, RR=91MW, NetOpMargin: AM=225, PM=239, EVE=127 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @298MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 1-5 @4MW, Panay Diesel 3-G @8MW [WEBSMS] | CVIS
5/15/2024 6:23:19 AM | [NSO Update] Visayas Grid-05/15/2024 06:23: System Advisory: 15-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1400H-2100H. Total capacity on forced outage is 404MW. Total of de-rated capacity is 209.3MW. [WEBSMS] | CVIS
5/15/2024 6:17:29 AM | [NSO Update] Mindanao Grid-05/15/2024 06:22: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3004MW, PK=2451MW, RR=73MW, NetOpMargin: AM=480, PM=300, EVE=452 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @48.9MW, MA2 @36MW [WEBSMS] | CMIN
5/15/2024 6:16:04 AM | [NSO Update] Luzon Grid-05/15/2024 06:16: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15478MW, PK=13134MW, RR=516MW, NetOpMargin: AM=1828, PM=696, EVE=1173 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @400MW, SLTEC 1 @116MW, SLTEC 2 @118MW, Bakun HEPP @7MW, Masinloc 1 @300MW, Masinloc 2 @270MW [WEBSMS] | CLUZ
5/15/2024 5:48:46 AM | Luzon Grid-05/15/2024 05:49: QPPL online at 0547H. (Unplanned Outage) [WEBSMS] | CLUZ
5/15/2024 4:31:01 AM | [NSO Update] Mindanao Grid-05/15/2024 04:36: Weather Update: Shear Line affecting the eastern section of Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
5/15/2024 4:30:46 AM | [NSO Update] Visayas Grid-05/15/2024 04:30: Weather Update: Shear Line affecting the eastern section of Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
5/15/2024 4:30:20 AM | [NSO Update] Luzon Grid-05/15/2024 04:30: Weather Update: Shear Line affecting the eastern section of Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
5/15/2024 2:37:34 AM | Luzon Grid-05/15/2024 02:37: Quezon (Balintawak) SS 300MVA T08 (Customer Owned) restored at 0234H (Planned Outage) [WEBSMS] | CLUZ
5/15/2024 2:11:59 AM | [NSO Update] Luzon Grid-05/15/2024 02:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0210H with power going to Luzon [WEBSMS] | CLUZ
5/15/2024 2:10:58 AM | [NSO Update] Visayas Grid-05/15/2024 02:11: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0210H with power going to Luzon [WEBSMS] | CVIS
5/15/2024 2:03:48 AM | [NSO Update] Luzon Grid-05/15/2024 02:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0200H from reverse power direction [WEBSMS] | CLUZ
5/15/2024 2:02:22 AM | [NSO Update] Visayas Grid-05/15/2024 02:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0200H from reverse power direction [WEBSMS] | CVIS
5/15/2024 1:03:49 AM | Visayas Grid-05/15/2024 01:04: CEDC Unit#1 cut-out @ 0100H. ( Planned Outage ) [WEBSMS] | CVIS
5/15/2024 12:59:50 AM | Visayas Grid-05/15/2024 01:00: 138KV Dumanjug 100MVA TR#1 energized @0059H. ( Planned Outage ) [WEBSMS] | CVIS
5/15/2024 12:07:20 AM | Luzon Grid-05/15/2024 00:07: Quezon (Balintawak) SS 300MVA T08 (Customer Owend) de-energized at 0006H. (Planned Outage) [WEBSMS] | CLUZ
5/15/2024 12:01:52 AM | [NSO Update] Luzon Grid-05/15/2024 00:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2353H with power going to Visayas [WEBSMS] | CLUZ
5/15/2024 12:01:32 AM | [NSO Update] Visayas Grid-05/15/2024 00:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2353H with power going to Visayas [WEBSMS] | CVIS
5/14/2024 11:23:19 PM | Mindanao Grid-05/14/2024 23:28: The New Power Circuit Breaker at Maramag SS (7Z-07CB24MRM) energized at 2314H with approved energization permit No. ENRP-2024-04-0090. [WEBSMS] | CMIN
5/14/2024 11:16:18 PM | Mindanao Grid-05/14/2024 23:21: Pulangi 4 Unit 1 online at 2314H from OMC. [WEBSMS] | CMIN
5/14/2024 11:07:25 PM | [NSO Update] Visayas Grid-05/14/2024 23:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2304H from reverse power direction [WEBSMS] | CVIS
5/14/2024 11:07:09 PM | [NSO Update] Luzon Grid-05/14/2024 23:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2304H from reverse power direction [WEBSMS] | CLUZ
5/14/2024 11:01:42 PM | Mindanao Grid-05/14/2024 23:06: WMPC DG10 shutdown at 2247H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/14/2024 11:00:41 PM | Mindanao Grid-05/14/2024 23:05: WMPC DG01 shutdown at 2236H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/14/2024 10:50:48 PM | [NSO Update] Luzon Grid-05/14/2024 22:50: System Advisory: The Luzon Grid Yellow Alert notice issued today has been lifted at 2233H. [WEBSMS] | CLUZ
5/14/2024 9:49:06 PM | [NSO Update] Visayas Grid-05/14/2024 21:49: System Advisory: Visayas Grid Yellow Alert notice issued today has been lifted at 2148H. [WEBSMS] | CVIS
5/14/2024 6:39:58 PM | Visayas Grid-05/14/2024 18:40: PGPP 1 and PGPP 2 (Okoy, Sog 1 and Sog 2) total plant isolated at 169 MW during Dumanjug 138 kV bus multiple tripping (Unplanned Outage) [WEBSMS] | CVIS
5/14/2024 6:35:50 PM | Mindanao Grid-05/14/2024 18:40: Maramag-Kibawe 138 kV Line 1 re-energized at 1832H. Planned Outage/Non -GOMP. [WEBSMS] | CMIN
5/14/2024 6:22:26 PM | Visayas Grid-05/14/2024 18:22: Dumanjug-Colon/Samboan 138 kV Line 1 looped at 1804H/1806H (Unplanned Outage) [WEBSMS] | CVIS
5/14/2024 6:10:45 PM | Mindanao Grid-05/14/2024 18:15: Matanao -Digos Solar Plant 69 kV Line de-energized at 1806H. Planned Outage. [WEBSMS] | CMIN
5/14/2024 6:06:37 PM | [NSO Update] Visayas Grid-05/14/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2567MW, PK=2471MW, RR=91MW, NetOpMargin: EVE=4 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 292MW [WEBSMS] | CVIS
5/14/2024 6:04:18 PM | [NSO Update] Mindanao Grid-05/14/2024 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2905MW, PK=2451MW, RR=73MW, NetOpMargin: EVE=381 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @36MW [WEBSMS] | CMIN
5/14/2024 6:02:03 PM | Visayas Grid-05/14/2024 18:02: Dumanjug-Colon 138 kV Line 1 and Dumanjug-Samboan 138 kV Line 1 isolated from Dumanjug side at 1745H, upon energization of new TR2 100 MVA (Unplanned Outage) [WEBSMS] | CVIS
5/14/2024 6:00:31 PM | [NSO Update] Luzon Grid-05/14/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=13877MW, PK=12122MW, RR=472MW, NetOpMargin: EVE=1282 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 300MW, Masinloc 2 @ 340MW, SLTEC 1 @ 116MW, SLTEC 2 @ 118MW, Ilijan A @ 400MW [WEBSMS] | CLUZ
5/14/2024 5:48:14 PM | Luzon Grid-05/14/2024 17:48: Concepcion-Clark 230kV Line 1 looped at Clark side at 1746H. (Planned Outage) [WEBSMS] | CLUZ
5/14/2024 5:10:44 PM | Visayas Grid-05/14/2024 17:10: Lapulapu GIS last ILP off line at 1705H (Unplanned Outage) [WEBSMS] | CVIS
5/14/2024 5:07:19 PM | Mindanao Grid-05/14/2024 17:12: Agus 6 Swyd 100MVA Transformer 3 re-energized at 1701H (Unplanned Outage). [WEBSMS] | CMIN
5/14/2024 5:03:50 PM | Mindanao Grid-05/14/2024 17:08: WMPC DG08 shutdown at 1701H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/14/2024 3:59:34 PM | Mindanao Grid-05/14/2024 16:04: Mt. Apo U3 online at 1552H. (Unplanned Outage) [WEBSMS] | CMIN
5/14/2024 3:21:12 PM | Mindanao Grid-05/14/2024 15:26: WMPC DG02 online at 1455H. (Unplanned Outage) [WEBSMS] | CMIN
5/14/2024 3:19:25 PM | Mindanao Grid-05/14/2024 15:24: WMPC DG09 with 9.1MW load tripped at 1435H. Indication: HT cooler high temp (Unplanned Outage) [WEBSMS] | CMIN
5/14/2024 3:18:33 PM | Mindanao Grid-05/14/2024 15:23: WMPC DG02 with 7.8MW load tripped at 1443H. Indication: HT cooler high temp (Unplanned Outage) [WEBSMS] | CMIN
5/14/2024 3:03:16 PM | Mindanao Grid-05/14/2024 15:08: WMPC DG01 online at 1453H. MRU - System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
5/14/2024 2:58:09 PM | Mindanao Grid-05/14/2024 15:03: WMPC DG01 tripped at 1443H, Indication: HT cooler high temp. MRU -System Voltage requirement. (Unplanned Outage) [WEBSMS] | CMIN
5/14/2024 1:28:09 PM | [NSO Update] Mindanao Grid-05/14/2024 13:33: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2964MW, PK=2596MW, RR=73MW, NetOpMargin: PM=295, EVE=421 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW [WEBSMS] | CMIN
5/14/2024 1:27:09 PM | [NSO Update] Visayas Grid-05/14/2024 13:27: System Advisory: 14-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1500H-2100H. Total capacity on forced outage is 377.8MW. Total of de-rated capacity is 201.3MW. [WEBSMS] | CVIS
5/14/2024 1:16:10 PM | [NSO Update] Visayas Grid-05/14/2024 13:16: System Advisory: 14-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1500H-2100H. [WEBSMS] | CVIS
5/14/2024 1:14:57 PM | [NSO Update] Visayas Grid-05/14/2024 13:15: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2995MW, PK=2653MW, RR=91MW, NetOpMargin: PM=250, EVE=128 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @300MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW [WEBSMS] | CVIS
5/14/2024 1:05:44 PM | [NSO Update] Luzon Grid-05/14/2024 13:05: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14788MW, PK=13811MW, RR=491MW, NetOpMargin: PM=486, EVE=343 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @280MW, SLTEC 1 @116MW, SLTEC 2 @118MW, ILIJAN A @400MW [WEBSMS] | CLUZ
5/14/2024 9:58:44 AM | Mindanao Grid-05/14/2024 10:03: WMPC DG08 online at 0955H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/14/2024 9:57:51 AM | Mindanao Grid-05/14/2024 10:02: WMPC DG01 online at 0845H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/14/2024 8:51:42 AM | Luzon Grid-05/14/2024 08:51: Bacnotan-CIP II 69kV Line restored at 0849H (Planned Outage) [WEBSMS] | CLUZ
5/14/2024 8:38:25 AM | [NSO Update] Visayas Grid-05/14/2024 08:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0835H with power going to Visayas [WEBSMS] | CVIS
5/14/2024 8:37:49 AM | [NSO Update] Luzon Grid-05/14/2024 08:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0835H with power going to Visayas [WEBSMS] | CLUZ
5/14/2024 8:26:18 AM | [NSO Update] Visayas Grid-05/14/2024 08:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0825H from forward power direction [WEBSMS] | CVIS
5/14/2024 8:26:04 AM | [NSO Update] Luzon Grid-05/14/2024 08:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0825H from forward power direction [WEBSMS] | CLUZ
5/14/2024 8:07:37 AM | Mindanao Grid-05/14/2024 08:12: WMPC DG10 cut-in at 0800H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/14/2024 6:42:46 AM | [NSO Update] Luzon Grid-05/14/2024 06:42: Correction: System Advisory: 14-May-2024, Luzon Grid is on YELLOW Alert for interval hours 1400H-1700H, 2100H, and 2200H. Total capacity on forced outage is 1253.1MW. Total of de-rated capacity is 279MW. [WEBSMS] | CLUZ
5/14/2024 6:30:53 AM | [NSO Update] Visayas Grid-05/14/2024 06:31: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=3038MW, PK=2561MW, RR=91MW, NetOpMargin: AM=386, PM=140, EVE=167 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @307MW, CEDC U3 @75MW, GTEC Calbayog Bunker @7MW, Panay Diesel 3-G @8MW [WEBSMS] | CVIS
5/14/2024 6:28:57 AM | [NSO Update] Luzon Grid-05/14/2024 06:29: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=15081MW, PK=12621MW, RR=491MW, NetOpMargin: AM=1969, PM=601, EVE=732 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @200MW, SLTEC 1 @116MW, SLTEC 2 @118MW, ILIJAN A @400MW [WEBSMS] | CLUZ
5/14/2024 6:24:07 AM | [NSO Update] Visayas Grid-05/14/2024 06:24: System Advisory: 14-May-2024, Visayas Grid is on YELLOW Alert for interval hours 1400H-1600H and 1900H-2100H. Total capacity on forced outage is 350.8MW. Total of de-rated capacity is 199.3MW. [WEBSMS] | CVIS
5/14/2024 6:23:32 AM | [NSO Update] Luzon Grid-05/14/2024 06:23: System Advisory: 14-May-2024, Luzon Grid is on YELLOW Alert for interval hours 1400H-1700H, 2100H, and 2200H. Total capacity on forced outage is 953.1MW. Total of de-rated capacity is 279MW. [WEBSMS] | CLUZ
5/14/2024 6:14:10 AM | Mindanao Grid-05/14/2024 06:19: Maramag-Kibawe 138 kV Line 1 de-energized at 0610H. Planned Outage/Non -GOMP. [WEBSMS] | CMIN
5/14/2024 5:50:55 AM | Luzon Grid-05/14/2024 05:51: Dasmarinas SS 115kV Bus 2 restored at 0549H (Unplanned Outage) [WEBSMS] | CLUZ
5/14/2024 5:44:41 AM | Luzon Grid-05/14/2024 05:44: Binan-Balibago 115kV Line restored at 0542H (Planned Outage) [WEBSMS] | CLUZ
5/14/2024 5:27:32 AM | [NSO Update] Mindanao Grid-05/14/2024 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2988MW, PK=2438MW, RR=73MW, NetOpMargin: AM=477, PM=297, EVE=394 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW [WEBSMS] | CMIN
5/14/2024 4:49:29 AM | Luzon Grid-05/14/2024 04:49: Bacnotan-CIP II 69kV Line de-energized at 0445H (Planned Outage) [WEBSMS] | CLUZ
5/14/2024 4:25:07 AM | Luzon Grid-05/14/2024 04:25: Dasmarinas SS 115kV Bus 2 de-energized at 0420H (Unplanned Outage) [WEBSMS] | CLUZ
5/14/2024 4:18:31 AM | [NSO Update] Mindanao Grid-05/14/2024 04:23: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
5/14/2024 4:18:15 AM | [NSO Update] Visayas Grid-05/14/2024 04:18: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
5/14/2024 4:18:07 AM | [NSO Update] Luzon Grid-05/14/2024 04:18: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
5/14/2024 3:11:56 AM | Luzon Grid-05/14/2024 03:12: Dasmarinas SS 115kV Bus 2 restored at 0310H (Planned Outage) [WEBSMS] | CLUZ
5/14/2024 1:14:50 AM | Mindanao Grid-05/14/2024 01:19: Matanao - DSP 69kV Line energized at 0107H. (Planned Outage) [WEBSMS] | CMIN
5/14/2024 1:08:32 AM | Luzon Grid-05/14/2024 01:08: Dasmarinas SS 115kV Bus 2 de-energized at 0107H (Planned Outage) [WEBSMS] | CLUZ
5/14/2024 12:42:46 AM | Luzon Grid-05/14/2024 00:43: Binan-Balibago 115kV Line de-energized at 0040H (Planned Outage) [WEBSMS] | CLUZ
5/13/2024 11:03:13 PM | Mindanao Grid-05/13/2024 23:08: WMPC dg10 Shutdown at 2301H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/13/2024 10:50:41 PM | [NSO Update] Visayas Grid-05/13/2024 22:50: System Advisory: The Visayas Grid Yellow Alert notice issued today has been lifted at 2245H. [WEBSMS] | CVIS
5/13/2024 10:35:07 PM | [NSO Update] Luzon Grid-05/13/2024 22:35: System Advisory: The Luzon Grid Yellow Alert notice issued today has been lifted at 2230H. [WEBSMS] | CLUZ
5/13/2024 10:06:04 PM | Mindanao Grid-05/13/2024 22:11: WMPC DG6 Shutdown at 2156H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/13/2024 9:55:26 PM | Luzon Grid-05/13/2024 21:55: Nagsaag-Casecnan 230kV L1 tripped/reclosed at 2152H (Unplanned Outage) [WEBSMS] | CLUZ
5/13/2024 9:05:48 PM | [NSO Update] Visayas Grid-05/13/2024 21:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2103H from reverse power direction. [WEBSMS] | CVIS
5/13/2024 9:05:31 PM | [NSO Update] Luzon Grid-05/13/2024 21:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2103H from reverse power direction. [WEBSMS] | CLUZ
5/13/2024 8:59:45 PM | [NSO Update] Luzon Grid-05/13/2024 20:59: System Advisory Update: 13-May-2024, Luzon Grid is on YELLOW Alert for interval hours 2100H-2200H. Total capacity on forced outage is 1762.9MW. Total of de-rated capacity is 294MW. [WEBSMS] | CLUZ
5/13/2024 7:48:49 PM | Luzon Grid-05/13/2024 19:49: MPGC 3 online at 1947H (On- Commissioning) [WEBSMS] | CLUZ
5/13/2024 6:49:25 PM | [NSO Update] Visayas Grid-05/13/2024 18:49: Correction: System Advisory: 13-May-2024, Visayas Grid is on YELLOW Alert for interval hour 1900H-2200H. Total capacity on forced outage is 320.3MW. Total of de-rated capacity is 243.3MW. [WEBSMS] | CVIS
5/13/2024 6:47:21 PM | [NSO Update] Mindanao Grid-05/13/2024 18:52: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today, 13 May 2024, at 1839H. Market operations will resume starting interval 1845H. [WEBSMS] | CMIN
5/13/2024 6:46:59 PM | [NSO Update] Visayas Grid-05/13/2024 18:47: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today, 13 May 2024, at 1839H. Market operations will resume starting interval 1845H. [WEBSMS] | CVIS
5/13/2024 6:46:41 PM | [NSO Update] Luzon Grid-05/13/2024 18:46: MO-initiated Market Intervention for the Luzon, Visayas and Mindanao Grid has been lifted today, 13 May 2024, at 1839H. Market operations will resume starting interval 1845H. [WEBSMS] | CLUZ
5/13/2024 6:43:52 PM | [NSO Update] Visayas Grid-05/13/2024 18:44: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2701MW, PK=2486MW, RR=91MW, NetOpMargin: EVE=124 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 266MW [WEBSMS] | CVIS
5/13/2024 6:38:40 PM | [NSO Update] Visayas Grid-05/13/2024 18:38: System Advisory: 13-May-2024, Visayas Grid is on YELLOW Alert for interval hour 1900H-2200H. Total capacity on forced outage is 320.3MW. Total of de-rated capacity is 215.3MW. [WEBSMS] | CVIS
5/13/2024 6:36:51 PM | [NSO Update] Luzon Grid-05/13/2024 18:37: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW CAP=13386MW, PK=12063MW, RR=464MW, NetOpMargin: EVE=859 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 2 @ 340MW, SLPGC 1 @ 130MW, Ilijan A @ 400MW [WEBSMS] | CLUZ
5/13/2024 6:26:38 PM | [NSO Update] Mindanao Grid-05/13/2024 18:31: MO-initiated Market Intervention is issued today, 13 May 2024, for Luzon, Visayas, & Mindanao Grid starting interval 1810H due to RTD generation failure. [WEBSMS] | CMIN
5/13/2024 6:26:22 PM | [NSO Update] Visayas Grid-05/13/2024 18:26: MO-initiated Market Intervention is issued today, 13 May 2024, for Luzon, Visayas, & Mindanao Grid starting interval 1810H due to RTD generation failure. [WEBSMS] | CVIS
5/13/2024 6:26:00 PM | [NSO Update] Luzon Grid-05/13/2024 18:26: MO-initiated Market Intervention is issued today, 13 May 2024, for Luzon, Visayas, & Mindanao Grid starting interval 1810H due to RTD generation failure. [WEBSMS] | CLUZ
5/13/2024 6:23:04 PM | [NSO Update] Mindanao Grid-05/13/2024 18:28: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2925MW, PK=2416MW, RR=73MW, NetOpMargin: EVE=436 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @36MW [WEBSMS] | CMIN
5/13/2024 6:16:53 PM | Mindanao Grid-05/13/2024 18:21: Matanao Digos Solar(DSP) shutdown at 1813H. (Planned Outage) [WEBSMS] | CMIN
5/13/2024 6:08:31 PM | [NSO Update] Visayas Grid-05/13/2024 18:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1749H with power going to Visayas. [WEBSMS] | CVIS
5/13/2024 6:08:13 PM | [NSO Update] Luzon Grid-05/13/2024 18:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1749H with power going to Visayas. [WEBSMS] | CLUZ
5/13/2024 6:02:55 PM | Visayas Grid-05/13/2024 18:03: Compostela SS 230kV Bus 1 energized at 1746H (Planned Outage) [WEBSMS] | CVIS
5/13/2024 5:45:24 PM | [NSO Update] Visayas Grid-05/13/2024 17:45: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) Pole 2 auto-blocked at 1736H from forward power direction. Lala-Dumanjug 350kV HVDC currently operating on monopolar mode (Pole 1). [WEBSMS] | CVIS
5/13/2024 5:45:06 PM | [NSO Update] Mindanao Grid-05/13/2024 17:50: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) Pole 2 auto-blocked at 1736H from forward power direction. Lala-Dumanjug 350kV HVDC currently operating on monopolar mode (Pole 1). [WEBSMS] | CMIN
5/13/2024 5:41:38 PM | [NSO Update] Visayas Grid-05/13/2024 17:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1738H from forward power direction. [WEBSMS] | CVIS
5/13/2024 5:41:23 PM | [NSO Update] Luzon Grid-05/13/2024 17:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1738H from forward power direction. [WEBSMS] | CLUZ
5/13/2024 5:02:27 PM | Luzon Grid-05/13/2024 17:02: Diliman-Novaliches 115kV Line tripped/reclosed at 1643H, frequency reach, at 60.395hz, due to tripping of voltage sensitive load (Unplanned Outage) [WEBSMS] | CLUZ
5/13/2024 4:57:22 PM | [NSO Update] Visayas Grid-05/13/2024 16:57: Update on System Advisory: Visayas Grid Yellow Alert notice issued today has been lifted at 1656H. [WEBSMS] | CVIS
5/13/2024 4:49:03 PM | Luzon Grid-05/13/2024 16:49: Masinloc 1 online at 1647H (Unplanned Outage) [WEBSMS] | CLUZ
5/13/2024 4:26:46 PM | Luzon Grid-05/13/2024 16:26: Masinloc 1 tripped at 1625H with a load of 25MW (Unplanned Outage) [WEBSMS] | CLUZ
5/13/2024 4:23:04 PM | Visayas Grid-05/13/2024 16:23: MECO Gaisano Grand Mall ILP off-line at 1619H (Unplanned Outage) [WEBSMS] | CVIS
5/13/2024 3:55:57 PM | Luzon Grid-05/13/2024 15:56: Masinloc 1 online at 1554H (Unplanned Outage) [WEBSMS] | CLUZ
5/13/2024 3:02:16 PM | Visayas Grid-05/13/2024 15:02: MECO Gaisano Grand Mall implemented ILP at 1446H (Unplanned Outage) [WEBSMS] | CVIS
5/13/2024 2:59:54 PM | [NSO Update] Visayas Grid-05/13/2024 15:00: System Advisory: 13-May-2024, Visayas Grid is on YELLOW Alert for interval hour 1600H. Total capacity on forced outage is 308.3MW. Total of de-rated capacity is 216.3MW. [WEBSMS] | CVIS
5/13/2024 2:58:44 PM | Mindanao Grid-05/13/2024 15:03: Agus6 U4 online at 1455H. (Unplanned Outage) [WEBSMS] | CMIN
5/13/2024 2:48:10 PM | Mindanao Grid-05/13/2024 14:53: Agus6 U4 HEPP tripped with 15MW load at 1438H. (Unplanned Outage) [WEBSMS] | CMIN
5/13/2024 1:26:35 PM | Mindanao Grid-05/13/2024 13:31: Agus6 100MVA 138/69kV Power Transformer 3 tripped at 1239H. (Unplanned Outage) [WEBSMS] | CMIN
5/13/2024 1:22:20 PM | [NSO Update] Luzon Grid-05/13/2024 13:22: System Advisory: 13-May-2024, Luzon Grid is on YELLOW Alert for interval hours 1400H, 1500H, 1600H, 1700H and 1900H, 2000H. Total capacity on forced outage is 1762.9MW. Total of de-rated capacity is 339MW. [WEBSMS] | CLUZ
5/13/2024 1:18:06 PM | [NSO Update] Mindanao Grid-05/13/2024 13:23: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2996MW, PK=2562MW, RR=73MW, NetOpMargin: PM=361, EVE=456 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @36MW [WEBSMS] | CMIN
5/13/2024 1:16:29 PM | [NSO Update] Visayas Grid-05/13/2024 13:16: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2942MW, PK=2627MW, RR=91MW, NetOpMargin: PM=224, EVE=229 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @294MW [WEBSMS] | CVIS
5/13/2024 1:13:52 PM | [NSO Update] Luzon Grid-05/13/2024 13:14: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14573MW, PK=13760MW, RR=486MW, NetOpMargin: PM=326, EVE=511 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC2 @340MW, SLPGC 1 @90MW, SLTEC 1 @116MW, SLTEC 2 @118MW, ILIJAN A @400MW [WEBSMS] | CLUZ
5/13/2024 1:11:56 PM | Mindanao Grid-05/13/2024 13:17: Pulangi4 U2 shutdown at 1308H. Low Water Forebay Elevation. Outside Management Control (OMC). [WEBSMS] | CMIN
5/13/2024 12:11:25 PM | Luzon Grid-05/13/2024 12:11: Mexico - San Rafael 230kV Line 2 restored at 1211H (Unplanned Outage) [WEBSMS] | CLUZ
5/13/2024 10:19:52 AM | Mindanao Grid-05/13/2024 10:24: WMPC DG8 online at 1000H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/13/2024 10:01:16 AM | [NSO Update] Visayas Grid-05/13/2024 10:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0954H with power going to Visayas [WEBSMS] | CVIS
5/13/2024 10:00:43 AM | [NSO Update] Luzon Grid-05/13/2024 10:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0954H with power going to Visayas [WEBSMS] | CLUZ
5/13/2024 9:58:14 AM | [NSO Update] Luzon Grid-05/13/2024 09:58: Correction: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0944H from forward power direction [WEBSMS] | CLUZ
5/13/2024 9:57:15 AM | [NSO Update] Visayas Grid-05/13/2024 09:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0944H from forward power direction [WEBSMS] | CVIS
5/13/2024 9:55:45 AM | [NSO Update] Luzon Grid-05/13/2024 09:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0944H from reverse power direction [WEBSMS] | CLUZ
5/13/2024 9:51:05 AM | Luzon Grid-05/13/2024 09:51: Mexico - San Rafael 230kV Line 2 tripped at 0947H (Unplanned Outage) [WEBSMS] | CLUZ
5/13/2024 9:13:55 AM | Mindanao Grid-05/13/2024 09:19: WMPC DG03 online at 0849H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/13/2024 9:06:22 AM | Luzon Grid-05/13/2024 09:06: Concepcion-Clark 230kV Line 1 unlooped via Clark side at 0904H (Planned Outage) [WEBSMS] | CLUZ
5/13/2024 8:39:30 AM | Mindanao Grid-05/13/2024 08:44: WMPC DG10 online at 0823H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/13/2024 6:47:59 AM | Visayas Grid-05/13/2024 06:48: Compostela SS 230kV Bus 1 de-energized at 0632H (Planned Outage) [WEBSMS] | CVIS
5/13/2024 6:18:00 AM | [NSO Update] Luzon Grid-05/13/2024 06:18: System Advisory: 13-May-2024, Luzon Grid is on YELLOW Alert for interval hours 1500H and 1600H. Total capacity on forced outage is 1771.5MW. Total of de-rated capacity is 279MW. [WEBSMS] | CLUZ
5/13/2024 6:13:06 AM | [NSO Update] Luzon Grid-05/13/2024 06:13: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=14733MW, PK=12683MW, RR=512MW, NetOpMargin: AM=1538, PM=708, EVE=846 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC2 @340MW, SLTEC 1 @116MW, SLTEC 2 @118MW, ILIJAN A @400MW [WEBSMS] | CLUZ
5/13/2024 6:01:53 AM | [NSO Update] Mindanao Grid-05/13/2024 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3008MW, PK=2521MW, RR=73MW, NetOpMargin: AM=414, PM=341, EVE=440 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @36MW [WEBSMS] | CMIN
5/13/2024 6:00:34 AM | [NSO Update] Visayas Grid-05/13/2024 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2952MW, PK=2534MW, RR=91MW, NetOpMargin: AM=327, PM=203, EVE=230 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @307MW [WEBSMS] | CVIS
5/13/2024 4:35:00 AM | [NSO Update] Mindanao Grid-05/13/2024 04:40: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
5/13/2024 4:34:49 AM | [NSO Update] Visayas Grid-05/13/2024 04:34: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
5/13/2024 4:34:37 AM | [NSO Update] Luzon Grid-05/13/2024 04:34: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
5/13/2024 1:42:41 AM | Luzon Grid-05/13/2024 01:42: MPGC 3 tripped at 0125H with a load of 150MW, frequency reach at 59.5Hz (Unplanned Outage - ongoing boiler combustion tuning) [WEBSMS] | CLUZ
5/13/2024 1:11:20 AM | Luzon Grid-05/13/2024 01:11: SLPGC 1 online at 0105H (Unplanned Outage) [WEBSMS] | CLUZ
5/12/2024 11:03:55 PM | Mindanao Grid-05/12/2024 23:09: WMPC DG04 shutdown at 2301H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/12/2024 11:02:31 PM | Mindanao Grid-05/12/2024 23:07: Update: Mt Apo Unit 3 tripped at 2033H. Indication: Due to brine pressure Low Low. (Unplanned Outage) [WEBSMS] | CMIN
5/12/2024 9:41:46 PM | Mindanao Grid-05/12/2024 21:46: Maramag-Bunawan 230 kV L2 re-energized 2137H. Planned Outage. [WEBSMS] | CMIN
5/12/2024 8:37:05 PM | Mindanao Grid-05/12/2024 20:42: Mt Apo Unit 3 tripped at 2033H. Details to follow (Unplanned Outage) [WEBSMS] | CMIN
5/12/2024 7:43:37 PM | Mindanao Grid-05/12/2024 19:48: Correction: Kibawe -SKU 138 kV Line auto-tripped at 1726H and auto-reclosed at Kibawe SS only. SKU SS on power loss with total LD=62.40 MW (including LAMSAN with generation of 13.48 MW) [WEBSMS] | CMIN
5/12/2024 7:37:04 PM | Mindanao Grid-05/12/2024 19:42: Correction: Kibawe -SKU 138 kV Line auto-tripped at 1726H and auto-reclosed at Kibawe SS only. SKU SS on power loss with total LD=62.40 MW (including LAMSAN with generation of 13.48 MW) [WEBSMS] | CMIN
5/12/2024 6:35:47 PM | Mindanao Grid-05/12/2024 18:40: WMPC DG10 online at 1823H. SO dispatched. [WEBSMS] | CMIN
5/12/2024 6:09:59 PM | Mindanao Grid-05/12/2024 18:15: Lamsan Biomass (LSK) online at 1758H. (Unplanned Outage) [WEBSMS] | CMIN
5/12/2024 6:06:34 PM | Mindanao Grid-05/12/2024 18:11: Kibawe -SKU 138 kV Line restored at 1751H. [WEBSMS] | CMIN
5/12/2024 5:59:55 PM | Mindanao Grid-05/12/2024 18:05: Kibawe -SKU 138 kV Line auto-tripped at 1726H and auto-reclosed at Kibawe SS only. SKU SS on power loss with total LD=76.2 MW (including LAMSAN with generation of 13.48 MW) [WEBSMS] | CMIN
5/12/2024 5:54:42 PM | Mindanao Grid-05/12/2024 17:59: Lamsan Power Corp. with 13.48MW load isolated by the tripping of Kibawe - Sultan Kudarat 138kV Line. (Unplanned outage) [WEBSMS] | CMIN
5/12/2024 5:48:39 PM | Luzon Grid-05/12/2024 17:48: Ambuklao 230kV Bus 1 restored at 1748H (Planned Outage) [WEBSMS] | CLUZ
5/12/2024 5:46:41 PM | [NSO Update] Mindanao Grid-05/12/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2946MW, PK=2254MW, RR=73MW, NetOpMargin: EVE=620 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/12/2024 5:45:27 PM | [NSO Update] Visayas Grid-05/12/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2584MW, PK=2186MW, RR=90MW, NetOpMargin: EVE=308 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @300MW [WEBSMS] | CVIS
5/12/2024 5:44:13 PM | [NSO Update] Luzon Grid-05/12/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13546MW, PK=11630MW, RR=294MW, NetOpMargin: EVE=1622 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 1 @116MW, SLTEC 2 @118MW, ILIJAN A @400MW [WEBSMS] | CLUZ
5/12/2024 4:44:44 PM | Luzon Grid-05/12/2024 16:44: Mexico-San Rafael 230kV Line 2 restored at 1644H (Planned Outage) [WEBSMS] | CLUZ
5/12/2024 4:22:33 PM | Luzon Grid-05/12/2024 16:22: Taytay SS 300MVA T04 restored at 1622H (Planned Outage) [WEBSMS] | CLUZ
5/12/2024 3:32:30 PM | Luzon Grid-05/12/2024 15:32: Santiago-Gamu 230kV Line restored at 1532H (Planned Outage) [WEBSMS] | CLUZ
5/12/2024 3:10:06 PM | Mindanao Grid-05/12/2024 15:15: Manolo 1 Unit 3 online at 1455H from OMC. (Unplanned Outage) [WEBSMS] | CMIN
5/12/2024 3:09:03 PM | Mindanao Grid-05/12/2024 15:14: Manolo 1 unit 4 online at 1503H. (Planned Outage-GOMP) [WEBSMS] | CMIN
5/12/2024 3:07:51 PM | Luzon Grid-05/12/2024 15:08: SLPGC 1 with a load of 150MW tripped at 1456H. Lowest Frequency is 59.60Hz (Unplanned Outage) [WEBSMS] | CLUZ
5/12/2024 1:22:56 PM | Luzon Grid-05/12/2024 13:23: Labo-Gumaca 230kV Line 2 restored at 1322H. (Planned Outage) [WEBSMS] | CLUZ
5/12/2024 1:21:58 PM | Visayas Grid-05/12/2024 13:22: Malitbog U2 tripped at 1319H (Unplanned Outage) [WEBSMS] | CVIS
5/12/2024 12:52:39 PM | [NSO Update] Mindanao Grid-05/12/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2963MW, PK=2115MW, RR=73MW, NetOpMargin: PM=776, EVE=573 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/12/2024 12:51:26 PM | [NSO Update] Visayas Grid-05/12/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2840MW, PK=2080MW, RR=87MW, NetOpMargin: PM=674, EVE=317 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 272MW [WEBSMS] | CVIS
5/12/2024 12:48:10 PM | [NSO Update] Luzon Grid-05/12/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14764MW, PK=11215MW, RR=346MW, NetOpMargin: PM=3203, EVE=1662 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 500MW, SLTEC 1 @ 116MW, SLTEC 2 @ 118MW [WEBSMS] | CLUZ
5/12/2024 11:58:59 AM | Luzon Grid-05/12/2024 11:59: Gumaca - Labo 230kV Line 1 looped at Gumaca side at 1158H. (Unplanned Outage) [WEBSMS] | CLUZ
5/12/2024 11:53:49 AM | Luzon Grid-05/12/2024 11:53: Gumaca - Labo 230kV Line 1 tripped at 1149H (reclosed at Gumaca side only). (Unplanned Outage) [WEBSMS] | CLUZ
5/12/2024 9:28:17 AM | Luzon Grid-05/12/2024 09:28: Limay SS 230kV Bus 1 restored at 0928H. (Planned Outage) [WEBSMS] | CLUZ
5/12/2024 8:04:46 AM | Luzon Grid-05/12/2024 08:04: Currimao-Laoag 115kV Line restored at 0803H. (Unplanned Outage) [WEBSMS] | CLUZ
5/12/2024 7:02:45 AM | Mindanao Grid-05/12/2024 07:07: Maramag-Bunawan 230 kV L2 de-energized 0654H. Planned Outage. [WEBSMS] | CMIN
5/12/2024 6:45:24 AM | Luzon Grid-05/12/2024 06:45: Ambuklao SS 230kV Bus 1 de-energized at 0645H. (Planned Outage) [WEBSMS] | CLUZ
5/12/2024 6:40:52 AM | Luzon Grid-05/12/2024 06:41: Taytay SS 300MVA T04 de-energized at 0640H. (Planned Outage) [WEBSMS] | CLUZ
5/12/2024 6:05:49 AM | Luzon Grid-05/12/2024 06:05: Limay SS 230kV Bus 1 de-energized at 0605H. (Planned Outage) [WEBSMS] | CLUZ
5/12/2024 5:59:09 AM | [NSO Update] Mindanao Grid-05/12/2024 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2993MW, PK=2059MW, RR=73MW, NetOpMargin: AM=861, PM=752, EVE=562 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/12/2024 5:53:41 AM | [NSO Update] Visayas Grid-05/12/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2779MW, PK=2007MW, RR=85MW, NetOpMargin: AM=687, PM=441, EVE=187 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @307MW [WEBSMS] | CVIS
5/12/2024 5:52:58 AM | [NSO Update] Luzon Grid-05/12/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14995MW, PK=10430MW, RR=345MW, NetOpMargin: AM=4221, PM=2692, EVE=1742 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @ 400MW [WEBSMS] | CLUZ
5/12/2024 5:34:28 AM | Luzon Grid-05/12/2024 05:34: Labo-Gumaca 230kV Line 2 de-energized at 0534H (Planned Outage) [WEBSMS] | CLUZ
5/12/2024 4:27:25 AM | Luzon Grid-05/12/2024 04:27: Mexico-San Rafael 230kV Line 2 de-energized at 0427H (Planned Outage) [WEBSMS] | CLUZ
5/12/2024 4:17:14 AM | [NSO Update] Luzon Grid-05/12/2024 04:17: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CLUZ
5/12/2024 4:17:11 AM | [NSO Update] Visayas Grid-05/12/2024 04:17: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CVIS
5/12/2024 4:17:08 AM | [NSO Update] Mindanao Grid-05/12/2024 04:22: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CMIN
5/12/2024 4:14:17 AM | Luzon Grid-05/12/2024 04:14: Santiago-Gamu 230kV Line de-energized at 0403H (Planned Outage) [WEBSMS] | CLUZ
5/12/2024 3:31:29 AM | Luzon Grid-05/12/2024 03:31: Bantay-Currimao 115kV Line restored at 0329H (Unplanned Outage) [WEBSMS] | CLUZ
5/12/2024 3:24:30 AM | Luzon Grid-05/12/2024 03:24: Bantay-Currimao 115kV Line and Currimao-Laoag 115kV Line tripped again at 0320H (Unplanned Outage) [WEBSMS] | CLUZ
5/12/2024 3:22:52 AM | Luzon Grid-05/12/2024 03:23: Bantay-Currimao 115kV Line and Currimao 115kV Line tripped again at 0320H (Unplanned Outage) [WEBSMS] | CLUZ
5/12/2024 3:14:55 AM | Luzon Grid-05/12/2024 03:15: Bantay-Currimao 115kV Line and Currimao-Laoag 115kV Line restored at 0311H & 0314H, respectively (Unplanned Outage) [WEBSMS] | CLUZ
5/12/2024 2:55:30 AM | Luzon Grid-05/12/2024 02:55: Correction: Bantay-Currimao 115kV Line and Currimao-Laoag 115kV Line tripped at 0249H isolating Currimao Substation (Unplanned Outage) [WEBSMS] | CLUZ
5/12/2024 2:53:50 AM | Luzon Grid-05/12/2024 02:54: Bantay-Currimao 115kV Line and Currimao 115kV Line tripped at 0249H isolating Currimao Substation (Unplanned Outage) [WEBSMS] | CLUZ
5/12/2024 12:07:20 AM | Mindanao Grid-05/12/2024 00:12: Maramag - Bunawan 230kV Line 1 energized/restored at 2355H and completely looped at 2357H, at Maramag SS side. From Planned Outage (Non-GOMP). [WEBSMS] | CMIN
5/11/2024 11:44:50 PM | Visayas Grid-05/11/2024 23:44: Colon - Dumanjug 138 kV Line 2 energized at 2343H (Planned Outage) [WEBSMS] | CVIS
5/11/2024 10:20:33 PM | Mindanao Grid-05/11/2024 22:25: WMPC DG10 shutdown at 2216H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/11/2024 10:19:48 PM | Mindanao Grid-05/11/2024 22:24: WMPC DG4 shutdown at 2201H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/11/2024 9:57:22 PM | [NSO Update] Visayas Grid-05/11/2024 21:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2154H with power going to Luzon. [WEBSMS] | CVIS
5/11/2024 9:57:01 PM | [NSO Update] Luzon Grid-05/11/2024 21:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2154H with power going to Luzon. [WEBSMS] | CLUZ
5/11/2024 9:49:00 PM | [NSO Update] Visayas Grid-05/11/2024 21:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2144H from reverse power direction. [WEBSMS] | CVIS
5/11/2024 9:48:45 PM | [NSO Update] Luzon Grid-05/11/2024 21:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2144H from reverse power direction. [WEBSMS] | CLUZ
5/11/2024 8:46:54 PM | Visayas Grid-05/11/2024 20:47: Colon - Dumanjug 138 kV Line 2 de-energized at 2039H (Planned Outage) [WEBSMS] | CVIS
5/11/2024 8:45:40 PM | Visayas Grid-05/11/2024 20:45: Colon - Dumanjug 138 kV Line 1 energized at 1956H (Planned Outage) [WEBSMS] | CVIS
5/11/2024 7:49:50 PM | Mindanao Grid-05/11/2024 19:54: Manolo Fortich SS - HEDCOR 1 (MN1 HEPP) 138kV L1 energized/restored at 1944H and looped at HEDCOR Manolo 1 HEPP side, at 1945H. From PO(GOMP). (Note: HEDCOR/MN1 HEPP Management approved shutdown request). [WEBSMS] | CMIN
5/11/2024 6:16:31 PM | [NSO Update] Luzon Grid-05/11/2024 18:16: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13090MW, PK=11390MW, RR=474MW, NetOpMargin: EVE=1226 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 400MW, SLTEC 1 @ 116MW, SLTEC 2 @ 118MW [WEBSMS] | CLUZ
5/11/2024 6:12:02 PM | [NSO Update] Mindanao Grid-05/11/2024 18:17: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2920MW, PK=2383MW, RR=73MW, NetOpMargin: EVE=464 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/11/2024 6:10:01 PM | [NSO Update] Visayas Grid-05/11/2024 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2631MW, PK=2323MW, RR=92MW, NetOpMargin: EVE=217 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 302MW [WEBSMS] | CVIS
5/11/2024 6:06:25 PM | Mindanao Grid-05/11/2024 18:11: WMPC DG4 Online at 1803H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/11/2024 5:22:11 PM | Luzon Grid-05/11/2024 17:22: Masinloc 3 online at 1720H (Unplanned Outage) [WEBSMS] | CLUZ
5/11/2024 5:10:24 PM | Mindanao Grid-05/11/2024 17:15: WMPC DG4 shutdown at 1706H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/11/2024 2:59:33 PM | Luzon Grid-05/11/2024 14:59: Labo-Gumaca 230kV line 1 restored at 1459H (Planned Outage) [WEBSMS] | CLUZ
5/11/2024 2:25:19 PM | Luzon Grid-05/11/2024 14:25: Binga-La Trinidad 230kV L2 energized at 1421H (Planned Outage) [WEBSMS] | CLUZ
5/11/2024 2:08:28 PM | Mindanao Grid-05/11/2024 14:13: WMPC DG08 Online at 1329H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/11/2024 1:27:09 PM | [NSO Update] Luzon Grid-05/11/2024 13:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1326H with power going to Visayas. [WEBSMS] | CLUZ
5/11/2024 1:27:07 PM | [NSO Update] Visayas Grid-05/11/2024 13:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1326H with power going to Visayas. [WEBSMS] | CVIS
5/11/2024 1:16:55 PM | [NSO Update] Visayas Grid-05/11/2024 13:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1315H from forward power direction. [WEBSMS] | CVIS
5/11/2024 1:16:44 PM | [NSO Update] Luzon Grid-05/11/2024 13:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1315H from forward power direction. [WEBSMS] | CLUZ
5/11/2024 12:55:30 PM | [NSO Update] Luzon Grid-05/11/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14153MW, PK=12211MW, RR=486MW, NetOpMargin: PM=1456, EVE=762 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 400MW, SLTEC 1 @ 116MW, SLTEC 2 @ 118MW [WEBSMS] | CLUZ
5/11/2024 12:44:30 PM | [NSO Update] Mindanao Grid-05/11/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2975MW, PK=2499MW, RR=73MW, NetOpMargin: PM=403, EVE=412 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/11/2024 12:43:04 PM | [NSO Update] Visayas Grid-05/11/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2684MW, PK=2370MW, RR=97MW, NetOpMargin: PM=217, EVE=189 Highest Unit O/L: THVI 1 & 2 @ 169 Derated Plant: Leyte A @ 298MW [WEBSMS] | CVIS
5/11/2024 11:45:34 AM | Luzon Grid-05/11/2024 11:44: Limay-Limay BESS 69kV Line restored at 1140H, de-energized at 0603H. (Planned Outage) [WEBSMS] | CLUZ
5/11/2024 9:53:48 AM | Luzon Grid-05/11/2024 09:53: Binga-La Trinidad 230kV Line 2 de-energized at 0804H (Planned Outage) [WEBSMS] | CLUZ
5/11/2024 9:42:46 AM | Mindanao Grid-05/11/2024 09:47: undefined at 0821H Updated: FDC U1 (Filinvest Development Corp. U1) auto-tripped at 0821H with a gross generation of 119.56 MW, resulting in Automatic Load dropping (ALD) of NGCP feeders, CEPALCO, and DLPC system. The lowest system frequency recorded was 59.1505Hz. (Unplanned Outage) [WEBSMS] | CMIN
5/11/2024 9:16:32 AM | Mindanao Grid-05/11/2024 09:21: NagaMindanao - Zamboanga 138kV Line 2 successfully energized at 0850H and looped at 0851H at NagaMin SS side, from Planned Outage (Non-GOMP). [WEBSMS] | CMIN
5/11/2024 8:38:24 AM | Mindanao Grid-05/11/2024 08:43: FDC U1 (Filinvest Development Corp. U1) auto-tripped at 0821H with a gross generation of 119.56 MW, resulting in Automatic Load dropping (ALD) of NGCP feeders, CEPALCO, and DLPC system. Lowest system frequency recorded was 59.1505Hz. [WEBSMS] | CMIN
5/11/2024 8:15:25 AM | Mindanao Grid-05/11/2024 08:20: WMPC DG10 Online at 0813H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/11/2024 7:56:33 AM | Mindanao Grid-05/11/2024 08:01: Manolo Fortich SS - HEDCOR 1 (MN1 HEPP) 138kV L1 de-energized at 0751H. Planned Outage (GOMP). (Note: HEDCOR/MN1 HEPP Management approved shutdown request). [WEBSMS] | CMIN
5/11/2024 7:36:52 AM | Mindanao Grid-05/11/2024 07:41: Manolo Fortich 1 HEP Unit 2 shutdown at 0713H. PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
5/11/2024 7:35:22 AM | Mindanao Grid-05/11/2024 07:40: Manolo Fortich 1 HEP Unit 1 shutdown at 0712H. PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
5/11/2024 6:48:28 AM | Visayas Grid-05/11/2024 06:48: Colon - Dumanjug 138 kV Line 1 de-energized at 0647H (Planned Outage) [WEBSMS] | CVIS
5/11/2024 6:32:48 AM | Mindanao Grid-05/11/2024 06:37: Correction: Maramag - Bunawan 230kV Line 1 De-energized/shutdown at 0618H. (Planned Outage) [WEBSMS] | CMIN
5/11/2024 6:30:47 AM | Luzon Grid-05/11/2024 06:30: Balsik PCB 9-01CB08BIK energized at 0628H (Planned Outage) [WEBSMS] | CLUZ
5/11/2024 6:20:53 AM | Mindanao Grid-05/11/2024 06:25: Maramag - Bunawan 138kV Line 1 De-energized/shutdown at 0618H. (Planned Outage) [WEBSMS] | CMIN
5/11/2024 5:48:15 AM | [NSO Update] Luzon Grid-05/11/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14788MW, PK=11765MW, RR=456MW, NetOpMargin: AM=2567, PM=1465, EVE=701 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @400MW, SLTEC 1 @116MW [WEBSMS] | CLUZ
5/11/2024 5:29:48 AM | [NSO Update] Visayas Grid-05/11/2024 05:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2909MW, PK=2219MW, RR=95MW, NetOpMargin: AM=595, PM=239, EVE=268 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @118.5MW, LEYTE A @307MW [WEBSMS] | CVIS
5/11/2024 5:25:02 AM | [NSO Update] Mindanao Grid-05/11/2024 05:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3106MW, PK=2170MW, RR=73MW, NetOpMargin: AM=864, PM=613, EVE=616 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @36MW [WEBSMS] | CMIN
5/11/2024 5:21:06 AM | Luzon Grid-05/11/2024 05:21: Labo-Gumaca 230kV line 1 was de-energized at 0518H. (Planned Outage) [WEBSMS] | CLUZ
5/11/2024 5:15:17 AM | Luzon Grid-05/11/2024 05:15: Balsik PCB 9-01CB08BIK was de-energized at 0509H (Planned Outage) [WEBSMS] | CLUZ
5/11/2024 4:45:00 AM | Luzon Grid-05/11/2024 04:45: Taytay-Masinag 115kV line was restored at 0442H. (Planned Outage - Customer Owned and Maintained Line)) [WEBSMS] | CLUZ
5/11/2024 4:08:07 AM | [NSO Update] Visayas Grid-05/11/2024 04:08: Weather Update: Shear Line affecting the eastern sections of Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
5/11/2024 4:07:01 AM | [NSO Update] Mindanao Grid-05/11/2024 04:12: Weather Update: Shear Line affecting the eastern sections of Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
5/11/2024 4:06:14 AM | [NSO Update] Luzon Grid-05/11/2024 04:06: Weather Update: Shear Line affecting the eastern sections of Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
5/11/2024 3:49:24 AM | Mindanao Grid-05/11/2024 03:54: Naga Mindanao - Zamboanga 138kV Line 2 shutdown at 0347H. (Planned Outage) [WEBSMS] | CMIN
5/11/2024 3:14:30 AM | Mindanao Grid-05/11/2024 03:19: Naga Mindanao SS SVC energized at 0311H. (Planned Outage) [WEBSMS] | CMIN
5/11/2024 3:13:24 AM | Mindanao Grid-05/11/2024 03:18: Naga Mindanao SS Bus 2 energized at 0309H. (Planned Outage) [WEBSMS] | CMIN
5/11/2024 3:03:19 AM | Luzon Grid-05/11/2024 03:03: QPPL shutdown at 0300H (Planned Outage) [WEBSMS] | CLUZ
5/11/2024 12:56:05 AM | Mindanao Grid-05/11/2024 01:01: WMPC DG10 Online at 0054H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/11/2024 12:40:23 AM | Luzon Grid-05/11/2024 00:40: Taytay-Masinag 115kV line de-energized at 0036H (Planned Outage) [WEBSMS] | CLUZ
5/11/2024 12:13:59 AM | Visayas Grid-05/11/2024 00:14: PGPP2 Nasulo cut out at 0005H. (Unplanned Outage) [WEBSMS] | CVIS
5/11/2024 12:07:12 AM | Mindanao Grid-05/11/2024 00:12: Naga Mindanao SS 138kV Bus 2 De-energized/shutdown at 0004H. (Planned Outage) [WEBSMS] | CMIN
5/11/2024 12:05:53 AM | Mindanao Grid-05/11/2024 00:10: Naga Mindanao SS SVC De-energized/shutdown at 0003H. (Planned Outage) [WEBSMS] | CMIN
5/10/2024 10:47:14 PM | Mindanao Grid-05/10/2024 22:52: WMPC DG10 Shutdown at 2245H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/10/2024 10:44:18 PM | Mindanao Grid-05/10/2024 22:49: Pulangi 4 Unit 2 online at 2239H from OMC. (Unplanned Outage) [WEBSMS] | CMIN
5/10/2024 10:04:16 PM | Mindanao Grid-05/10/2024 22:09: WMPC DG4 Shutdown at 2202H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/10/2024 9:25:29 PM | [NSO Update] Visayas Grid-05/10/2024 21:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2107H with power going to Luzon [WEBSMS] | CVIS
5/10/2024 9:24:52 PM | [NSO Update] Luzon Grid-05/10/2024 21:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2107H with power going to Luzon [WEBSMS] | CLUZ
5/10/2024 8:53:49 PM | [NSO Update] Visayas Grid-05/10/2024 20:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2049H from reverse power direction [WEBSMS] | CVIS
5/10/2024 8:53:08 PM | [NSO Update] Luzon Grid-05/10/2024 20:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2049H from reverse power direction [WEBSMS] | CLUZ
5/10/2024 8:12:01 PM | Luzon Grid-05/10/2024 20:12: Masinloc Unit 3 tripped at 2006H from 271MW load. The lowest system frequency was 59.424Hz. (Unplanned Outage) [WEBSMS] | CLUZ
5/10/2024 7:11:03 PM | Mindanao Grid-05/10/2024 19:16: Correction: Manolo 1 Unit 2 online at 1857H, and Manolo 1 unit 1 online at 1905H. (Planned Outage-GOMP) [WEBSMS] | CMIN
5/10/2024 7:01:56 PM | Mindanao Grid-05/10/2024 19:06: Manolo 1 Unit 1 online at 1857H (Planned Outage-GOMP) [WEBSMS] | CMIN
5/10/2024 6:36:23 PM | Mindanao Grid-05/10/2024 18:41: Kibawe Solar (AGEC) shutdown at 1817H. Power Transformer re-gasketing activity. ETC: May 13, 2024 at 1800H. (Unplanned Outage) [WEBSMS] | CMIN
5/10/2024 6:20:54 PM | [NSO Update] Mindanao Grid-05/10/2024 18:25: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3090MW, PK=2387MW, RR=73MW, NetOpMargin: EVE=630 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/10/2024 6:20:06 PM | Mindanao Grid-05/10/2024 18:25: Manolo Fortich SS - Manolo Fortich Plant 1 Energized and looped at 1817H. (Planned Outage). [WEBSMS] | CMIN
5/10/2024 6:11:14 PM | [NSO Update] Luzon Grid-05/10/2024 18:11: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14001MW, PK=11816MW, RR=492MW, NetOpMargin: EVE=1693 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @400MW [WEBSMS] | CLUZ
5/10/2024 5:58:53 PM | [NSO Update] Visayas Grid-05/10/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2692MW, PK=2372MW, RR=98MW, NetOpMargin: EVE=222 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @118.5MW, LEYTE A @302MW, NASULO @30MW [WEBSMS] | CVIS
5/10/2024 5:21:05 PM | Visayas Grid-05/10/2024 17:21: MECO - ILP last feeder restored at 1653H (SOLEA) [WEBSMS] | CVIS
5/10/2024 4:59:57 PM | Mindanao Grid-05/10/2024 17:04: NEW BATAAN (EURO HYDRO) with 0.6MW isolated at 1633H due to NORDECO feeder outage. (Unplanned Outage) [WEBSMS] | CMIN
5/10/2024 4:11:14 PM | Mindanao Grid-05/10/2024 16:16: WMPC DG8 Shutdown at 1608H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/10/2024 3:42:41 PM | Mindanao Grid-05/10/2024 15:47: Agus 6 Unit 4 online at 1538H (Planned Outage-GOMP) [WEBSMS] | CMIN
5/10/2024 1:50:08 PM | Visayas Grid-05/10/2024 13:50: MECO (Sheraton) implemented 1.5 MW ILP at 1347H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/10/2024 1:20:38 PM | Visayas Grid-05/10/2024 13:20: MECO (Gaisano Island Mall) implemented 1.5 MW ILP at 1316H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/10/2024 1:01:41 PM | Mindanao Grid-05/10/2024 13:06: WMPC DG8 Online at 1258H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/10/2024 12:45:50 PM | [NSO Update] Mindanao Grid-05/10/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3123MW, PK=2621MW, RR=73MW, NetOpMargin: PM=430, EVE=543 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/10/2024 12:44:11 PM | [NSO Update] Visayas Grid-05/10/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2873MW, PK=2586MW, RR=100MW, NetOpMargin: PM=188, EVE=258 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @118.5MW, LEYTE A @302MW, NASULO @30MW [WEBSMS] | CVIS
5/10/2024 12:40:01 PM | [NSO Update] Luzon Grid-05/10/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15164MW, PK=13478MW, RR=486MW, NetOpMargin: PM=1200, EVE=1036 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MASINLOC 3 @250MW, ILIJAN A @500MW [WEBSMS] | CLUZ
5/10/2024 11:03:10 AM | Visayas Grid-05/10/2024 11:03: GMC implemented 2 MW ILP at 1100H to prevent overloading of Cebu - Mandaue Line 2 [WEBSMS] | CVIS
5/10/2024 8:53:26 AM | Mindanao Grid-05/10/2024 08:58: WMPC DG4 Online at 0849H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/10/2024 8:34:22 AM | Mindanao Grid-05/10/2024 08:39: WMPC DG10 Online at 0832H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/10/2024 8:21:53 AM | [NSO Update] Visayas Grid-05/10/2024 08:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0820H with power going to Visayas [WEBSMS] | CVIS
5/10/2024 8:21:34 AM | [NSO Update] Luzon Grid-05/10/2024 08:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0820H with power going to Visayas [WEBSMS] | CLUZ
5/10/2024 8:12:30 AM | [NSO Update] Luzon Grid-05/10/2024 08:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0810H from forward power direction [WEBSMS] | CLUZ
5/10/2024 8:12:12 AM | [NSO Update] Visayas Grid-05/10/2024 08:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0810H from forward power direction [WEBSMS] | CVIS
5/10/2024 6:16:28 AM | Visayas Grid-05/10/2024 06:16: Compostela SS 138 kV Bus 1 de-energized at 0615H (Planned Outage) [WEBSMS] | CVIS
5/10/2024 5:52:04 AM | [NSO Update] Mindanao Grid-05/10/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3153MW, PK=2480MW, RR=73MW, NetOpMargin: AM=601, PM=450, EVE=542 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/10/2024 5:50:38 AM | [NSO Update] Visayas Grid-05/10/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2847MW, PK=2544MW, RR=100MW, NetOpMargin: AM=203, PM=172, EVE=253 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 304MW, Nasulo @ 30MW [WEBSMS] | CVIS
5/10/2024 5:49:34 AM | [NSO Update] Luzon Grid-05/10/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15405MW, PK=12665MW, RR=516MW, NetOpMargin: AM=2225, PM=796, EVE=1121 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 500MW [WEBSMS] | CLUZ
5/10/2024 5:16:40 AM | Luzon Grid-05/10/2024 05:16: Taytay-Masinag 115kV line was restored at 0513H, (Planned Outage-Customer Owned and Maintained Line) [WEBSMS] | CLUZ
5/10/2024 4:23:29 AM | [NSO Update] Mindanao Grid-05/10/2024 04:28: Weather Advisory: Frontal System affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
5/10/2024 4:23:16 AM | [NSO Update] Visayas Grid-05/10/2024 04:23: Weather Advisory: Frontal System affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
5/10/2024 4:23:04 AM | [NSO Update] Luzon Grid-05/10/2024 04:23: Weather Advisory: Frontal System affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
5/10/2024 4:17:25 AM | Luzon Grid-05/10/2024 04:17: San Jose 300MVA T02 restored at 0416H (Planned Outage) [WEBSMS] | CLUZ
5/10/2024 12:38:37 AM | Luzon Grid-05/10/2024 00:38: Taytay-Masinag 115kV line was de-energized at 0037H (Planned Outage-Customer Owned and Maintained Line) [WEBSMS] | CLUZ
5/10/2024 12:20:43 AM | Luzon Grid-05/10/2024 00:20: San Jose 300MVA T02 was de-energized at 0019H. (Planned Outage) [WEBSMS] | CLUZ
5/9/2024 10:23:16 PM | [NSO Update] Visayas Grid-05/09/2024 22:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2221H with power going to Luzon. [WEBSMS] | CVIS
5/9/2024 10:23:13 PM | [NSO Update] Luzon Grid-05/09/2024 22:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2221H with power going to Luzon. [WEBSMS] | CLUZ
5/9/2024 10:21:38 PM | Mindanao Grid-05/09/2024 22:26: WMPC DG08 shutdown at 2216H ( MRU - System Voltage Requirement ) [WEBSMS] | CMIN
5/9/2024 10:12:40 PM | [NSO Update] Luzon Grid-05/09/2024 22:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2211H from reverse power direction. [WEBSMS] | CLUZ
5/9/2024 10:12:38 PM | [NSO Update] Visayas Grid-05/09/2024 22:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2211H from reverse power direction. [WEBSMS] | CVIS
5/9/2024 8:25:33 PM | Mindanao Grid-05/09/2024 20:30: WMPC DG05 shutdown at 2023H ( MRU - System Voltage Requirement ) [WEBSMS] | CMIN
5/9/2024 7:31:21 PM | Mindanao Grid-05/09/2024 19:36: WMPC DG01 shutdown at 1918H ( MRU - System Voltage Requirement ) [WEBSMS] | CMIN
5/9/2024 5:57:46 PM | [NSO Update] Luzon Grid-05/09/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13900MW, PK=12240MW, RR=474MW, NetOpMargin: EVE=1186 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 500MW [WEBSMS] | CLUZ
5/9/2024 5:56:46 PM | [NSO Update] Mindanao Grid-05/09/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3115MW, PK=2485MW, RR=73MW, NetOpMargin: EVE=558 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/9/2024 5:52:37 PM | [NSO Update] Visayas Grid-05/09/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2777MW, PK=2432MW, RR=96MW, NetOpMargin: EVE=249 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 110.5MW, Leyte A @ 304MW, Nasulo @ 30MW [WEBSMS] | CVIS
5/9/2024 5:39:45 PM | Visayas Grid-05/09/2024 17:39: Mabinay-Kabankalan 138KV Line 2 Open loop at 1734H at Kabankalan SS. [WEBSMS] | CVIS
5/9/2024 4:59:50 PM | Visayas Grid-05/09/2024 16:59: Meco ILP last feeder restored at 1612H (Knowles Electronics) [WEBSMS] | CVIS
5/9/2024 4:53:36 PM | Visayas Grid-05/09/2024 16:53: Magdugo-Calatrava Line 1 energized at 1650H(Unplanned Outage) [WEBSMS] | CVIS
5/9/2024 4:41:07 PM | Luzon Grid-05/09/2024 16:41: Correction: Tayabas-San Jose 500kV line 2 was energized on Tayabas side at 1636H. (Anti-pilferage ) [WEBSMS] | CLUZ
5/9/2024 4:37:47 PM | Luzon Grid-05/09/2024 16:37: Tayabas-San Jose 500kV line 2 restored at 1636H (Planned Outage) [WEBSMS] | CLUZ
5/9/2024 4:36:17 PM | Mindanao Grid-05/09/2024 16:41: WMPC DG07 cut-out at 1633H (MO dispatch) [WEBSMS] | CMIN
5/9/2024 4:35:31 PM | Luzon Grid-05/09/2024 16:35: Naga-Tiwi C 230kV Line 3 restored at 1634H (Planned Outage) [WEBSMS] | CLUZ
5/9/2024 4:10:51 PM | Mindanao Grid-05/09/2024 16:15: WMPC DG05 Online at 1606H.( MRU - System Voltage Requirement ) as replacement of DG 10 which tripped at 1549H. [WEBSMS] | CMIN
5/9/2024 3:56:38 PM | Mindanao Grid-05/09/2024 16:01: WMPC DG10 tripped at 1549H, indication: Oil mist concentration high stop. MRU -System Voltage requirement. (Unplanned Outage) [WEBSMS] | CMIN
5/9/2024 3:25:31 PM | Visayas Grid-05/09/2024 15:25: Mabinay-Kabakanlan 138KV Line 2 energized at 1511H for looping to Magdugo-Calatrava 230KV Line 2. [WEBSMS] | CVIS
5/9/2024 1:50:40 PM | Luzon Grid-05/09/2024 13:50: Santiago - Magat 230kV Line 2 restored at 1350H (Unplanned Outage) [WEBSMS] | CLUZ
5/9/2024 1:26:34 PM | Mindanao Grid-05/09/2024 13:31: WMPC DG07 Online at 1322H. MO Dispatched. [WEBSMS] | CMIN
5/9/2024 1:23:27 PM | Visayas Grid-05/09/2024 13:23: GMC/GMC 2nd unit implemented ILP at 1300H/1320H (Unplanned Outage) [WEBSMS] | CVIS
5/9/2024 1:14:43 PM | [NSO Update] Visayas Grid-05/09/2024 13:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1311H with power going to Visayas. [WEBSMS] | CVIS
5/9/2024 1:14:23 PM | [NSO Update] Luzon Grid-05/09/2024 13:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1311H with power going to Visayas. [WEBSMS] | CLUZ
5/9/2024 1:03:18 PM | [NSO Update] Visayas Grid-05/09/2024 13:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1301H from forward power direction. [WEBSMS] | CVIS
5/9/2024 1:02:42 PM | [NSO Update] Luzon Grid-05/09/2024 13:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1301H from forward power direction. [WEBSMS] | CLUZ
5/9/2024 12:48:35 PM | [NSO Update] Mindanao Grid-05/09/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3161MW, PK=2682MW, RR=73MW, NetOpMargin: PM=406, EVE=517 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/9/2024 12:44:59 PM | [NSO Update] Visayas Grid-05/09/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2915MW, PK=2613MW, RR=100MW, NetOpMargin: PM=202, EVE=250 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @110.5MW, LEYTE A @304MW, NASULO @30MW [WEBSMS] | CVIS
5/9/2024 12:41:41 PM | [NSO Update] Luzon Grid-05/09/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15418MW, PK=13718MW, RR=486MW, NetOpMargin: PM=1214, EVE=953 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW, MPGC U1 @100 [WEBSMS] | CLUZ
5/9/2024 11:43:04 AM | Mindanao Grid-05/09/2024 11:48: Agus6 HEP U2 online at 1138H from Unplanned outage. [WEBSMS] | CMIN
5/9/2024 10:59:46 AM | Mindanao Grid-05/09/2024 11:04: Agus6 HEP U2 tripped at 1052H with a gross generation of 15 MW . Unplanned Outage. [WEBSMS] | CMIN
5/9/2024 10:40:03 AM | Mindanao Grid-05/09/2024 10:45: WMPC DG01 Online at 1037H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/9/2024 10:00:03 AM | Mindanao Grid-05/09/2024 10:05: Toril-Matanao 138 kV Line 1 (7LI1TOR-MAT) energized at Matanao SS side at 0955H and looped at Toril SS 0956H from Planned Outage/Non-GOMP. [WEBSMS] | CMIN
5/9/2024 9:12:06 AM | Mindanao Grid-05/09/2024 09:17: WMPC DG08 Online at 0906H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/9/2024 9:09:43 AM | Mindanao Grid-05/09/2024 09:14: Toril-Matanao 138 kV Line 1 (7LI1TOR-MAT) shutdown at 0904H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
5/9/2024 9:08:17 AM | Mindanao Grid-05/09/2024 09:13: AGUS 6 HEP Unit 4 shutdown at 0903H. PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
5/9/2024 8:32:07 AM | Mindanao Grid-05/09/2024 08:37: WMPC DG10 Online at 0825H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/9/2024 7:36:31 AM | Mindanao Grid-05/09/2024 07:41: Manolo Fortich - HEDCOR 1 (MN1 HEPP) 138kV L1 de-energized at 0729H. Planned Outage (GOP). (Note: HEDCOR Management approved shutdown request) [WEBSMS] | CMIN
5/9/2024 7:19:05 AM | Mindanao Grid-05/09/2024 07:24: MANOLO 1 Unit 1 shutdown at 0708H. PMS (GOMP). (Planned Outage) [WEBSMS] | CMIN
5/9/2024 6:41:27 AM | Luzon Grid-05/09/2024 06:41: Naga-Tiwi C 230kV Line 3 de-energized at 0641H (Planned Outage) [WEBSMS] | CLUZ
5/9/2024 6:13:29 AM | Luzon Grid-05/09/2024 06:13: Tayabas-San Jose 500kV line 2 de-energized at 0603H (Planned Outage) [WEBSMS] | CLUZ
5/9/2024 5:51:00 AM | [NSO Update] Mindanao Grid-05/09/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3126MW, PK=2510MW, RR=73MW, NetOpMargin: AM=542, PM=439, EVE=533 Highest Unit O/L: GNPK 1, 2, 3 & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/9/2024 5:49:40 AM | Mindanao Grid-05/09/2024 05:54: Agus 1 Unit 1 online at 0539H from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
5/9/2024 5:47:51 AM | [NSO Update] Visayas Grid-05/09/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2865MW, PK=2544MW, RR=98MW, NetOpMargin: AM=222, PM=169, EVE=231 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @110.5MW, LEYTE A @304MW [WEBSMS] | CVIS
5/9/2024 5:44:21 AM | [NSO Update] Luzon Grid-05/09/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15385MW, PK=12878MW, RR=440MW, NetOpMargin: AM=2068, PM=857, EVE=1092 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/9/2024 5:38:21 AM | Luzon Grid-05/09/2024 05:38: Taytay-Masinag 115kV Line (CO) restored at 0538H. (Planned Outage) [WEBSMS] | CLUZ
5/9/2024 5:12:25 AM | Luzon Grid-05/09/2024 05:12: Calauan SS 150MVA T02 (Customer Owned) restored at 0400H. (Planned Outage) [WEBSMS] | CLUZ
5/9/2024 4:20:51 AM | [NSO Update] Mindanao Grid-05/09/2024 04:25: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
5/9/2024 4:19:51 AM | [NSO Update] Visayas Grid-05/09/2024 04:19: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
5/9/2024 4:18:08 AM | [NSO Update] Luzon Grid-05/09/2024 04:18: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
5/9/2024 4:04:29 AM | Mindanao Grid-05/09/2024 04:09: Update: Agus 1 Unit 1 with 33MW tripped at 0347H. Indication: For investigation: Lowest Frequency reached at 59.576Hz with no ALD activation. [WEBSMS] | CMIN
5/9/2024 3:56:38 AM | Mindanao Grid-05/09/2024 04:01: Agus 1 Unit 1 with 33MW tripped at 0347H. Details to follow. (Unplanned Outage) [WEBSMS] | CMIN
5/9/2024 1:28:38 AM | Luzon Grid-05/09/2024 01:29: Calauan SS 150MVA T02 de-energized at 0125H (Planned Outage) [WEBSMS] | CLUZ
5/9/2024 12:45:10 AM | Luzon Grid-05/09/2024 00:45: Taytay-Masinag 115kV Line (CO) de-energized at 0041H (Planned Outage) [WEBSMS] | CLUZ
5/8/2024 10:26:02 PM | Mindanao Grid-05/08/2024 22:31: WMPC DG10 Shutdown at 2221H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/8/2024 10:07:49 PM | [NSO Update] Visayas Grid-05/08/2024 22:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2203H with power going to Luzon [WEBSMS] | CVIS
5/8/2024 10:07:04 PM | [NSO Update] Luzon Grid-05/08/2024 22:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2203H with power going to Luzon [WEBSMS] | CLUZ
5/8/2024 10:01:53 PM | [NSO Update] Visayas Grid-05/08/2024 22:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2153H from reverse power direction [WEBSMS] | CVIS
5/8/2024 10:01:13 PM | [NSO Update] Luzon Grid-05/08/2024 22:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2153H from reverse power direction [WEBSMS] | CLUZ
5/8/2024 9:49:20 PM | Luzon Grid-05/08/2024 21:49: Update: Santiago - Magat Line 1 and Line 2 tripped at 2055H, while Line 1 successfully reclosed. (Unplanned Outage) [WEBSMS] | CLUZ
5/8/2024 9:23:40 PM | Luzon Grid-05/08/2024 21:24: For information: New Tuguegarao 50MVar Capacitor Bank 2 commissioning completed at 2117H. (End of Commissioning) [WEBSMS] | CLUZ
5/8/2024 9:18:19 PM | Mindanao Grid-05/08/2024 21:23: WMPC DG08 Shutdown at 2116H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/8/2024 8:58:00 PM | Luzon Grid-05/08/2024 20:58: Santiago - Magat 230kV Line 2 tripped at 2055H. (Unplanned Outage) [WEBSMS] | CLUZ
5/8/2024 7:25:19 PM | Mindanao Grid-05/08/2024 19:30: WMPC DG07 Shutdown at 1923H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/8/2024 7:18:40 PM | Mindanao Grid-05/08/2024 19:23: Manolo 1 Unit 1 online at 1916H from GOMP. (Planned Outage) [WEBSMS] | CMIN
5/8/2024 7:03:25 PM | Mindanao Grid-05/08/2024 19:08: Manolo Fortich SS - HEDCOR 1 (MN1 HEPP) 138kV L1 energized/restored at 1855H and completely looped at 1856H at HEDCOR HEPP 1 (MN1) side. From Planned Outage (GOP). (Note: HEDCOR Management approved shutdown request). [WEBSMS] | CMIN
5/8/2024 6:25:15 PM | Mindanao Grid-05/08/2024 18:30: WMPC DG04 Online at 1823H. MO dispatched. [WEBSMS] | CMIN
5/8/2024 6:01:10 PM | [NSO Update] Mindanao Grid-05/08/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3102MW, PK=2442MW, RR=73MW, NetOpMargin: EVE=587 Highest Unit O/L: GNPK 1, 2, 3 & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/8/2024 5:54:25 PM | [NSO Update] Visayas Grid-05/08/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2803MW, PK=2454MW, RR=96MW, NetOpMargin: EVE=252 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @110.5MW, LEYTE A @305MW [WEBSMS] | CVIS
5/8/2024 5:48:38 PM | [NSO Update] Luzon Grid-05/08/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14025MW, PK=12048MW, RR=424MW, NetOpMargin: EVE=1554 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/8/2024 5:34:23 PM | Mindanao Grid-05/08/2024 17:39: Nabunturan - Masara (7LI1NAB-MSR) de-energized at 0752H, and energized/restored at 1727H. Planned Outage (Non-GOMP). Note: Approved Customers (Masara Management) request shutdown. [WEBSMS] | CMIN
5/8/2024 5:10:17 PM | Visayas Grid-05/08/2024 17:10: PGPP 1 U2 cut in at 1703H. (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 4:58:54 PM | Luzon Grid-05/08/2024 16:59: Tayabas-San Jose 500kV line 2 was energized at Tayabas side at 1658H. (Anti-pilferage) [WEBSMS] | CLUZ
5/8/2024 4:44:06 PM | Visayas Grid-05/08/2024 16:44: MECO (Gaisano Grand Mall) implement ILP at 1320H, cut off ILP at 1636H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 4:31:24 PM | Visayas Grid-05/08/2024 16:31: MECO (JPark) cut off ILP at 1621H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 4:22:40 PM | Visayas Grid-05/08/2024 16:22: MECO (GaisanoIM) cut off ILP at 1616H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 4:13:33 PM | Visayas Grid-05/08/2024 16:13: MECO (GMC 2nd unit) cut off ILP at 1610H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 4:03:38 PM | Visayas Grid-05/08/2024 16:03: MECO (Solea) cut off ILP at 1532H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 3:35:29 PM | Luzon Grid-05/08/2024 15:35: Naga-Tiwi C 230kV Line 2 restored at 1535H. (Planned Outage) [WEBSMS] | CLUZ
5/8/2024 3:26:47 PM | Visayas Grid-05/08/2024 15:27: MECO (GMC 1st unit) cut off ILP at 1515H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 3:10:30 PM | Visayas Grid-05/08/2024 15:10: PGPP 1 U2 tripped at 1506H. (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 3:02:58 PM | Visayas Grid-05/08/2024 15:03: MECO (Sheraton) cut off ILP at 1444H [WEBSMS] | CVIS
5/8/2024 3:00:56 PM | Visayas Grid-05/08/2024 15:01: MECO (Movenpick) cut off ILP at 1436H [WEBSMS] | CVIS
5/8/2024 2:58:45 PM | Luzon Grid-05/08/2024 14:59: For information: Tiwi C - TGP Binary Plant 69kV line commissioning completed at 1417H. [WEBSMS] | CLUZ
5/8/2024 2:33:14 PM | Visayas Grid-05/08/2024 14:33: MECO (JPark) implement ILP at 1416H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 2:01:58 PM | Visayas Grid-05/08/2024 14:02: MECO (GMC2nd unit) implement ILP at 1355H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 1:38:15 PM | Visayas Grid-05/08/2024 13:38: MECO (GMC) implement ILP at 1316H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 1:30:16 PM | Mindanao Grid-05/08/2024 13:35: WMPC DG04 Online at 1328H. MO dispatched. [WEBSMS] | CMIN
5/8/2024 1:15:08 PM | Visayas Grid-05/08/2024 13:15: MECO (GaisanoIM) implement ILP at 1307H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 1:13:39 PM | Visayas Grid-05/08/2024 13:13: Sangi-Cebeco3 34.5 kV line energized at 1312H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 1:00:29 PM | Luzon Grid-05/08/2024 13:00: For info: The Luzon System Frequency reached 60.55Hz at 1229H during the auto-tripping of the Malabon-Malinta 115kV line(Customer Owned) affecting voltage sensitive loads. Manually closed/restored at 1230H. [WEBSMS] | CLUZ
5/8/2024 1:00:28 PM | Visayas Grid-05/08/2024 13:00: Sangi-Cebeco3 34.5 kV line tripped at 1253H (Unplanned Outage [WEBSMS] | CVIS
5/8/2024 12:59:44 PM | [NSO Update] Luzon Grid-05/08/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15385MW, PK=13705MW, RR=526MW, NetOpMargin: PM=1154, EVE=1118 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/8/2024 12:54:41 PM | [NSO Update] Mindanao Grid-05/08/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3014MW, PK=2595MW, RR=73MW, NetOpMargin: PM=346, EVE=463 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/8/2024 12:52:47 PM | [NSO Update] Visayas Grid-05/08/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2881MW, PK=2607MW, RR=100MW, NetOpMargin: PM=175, EVE=251 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @114.5MW, LEYTE A @310MW, PGPP1 @75MW [WEBSMS] | CVIS
5/8/2024 12:44:53 PM | Visayas Grid-05/08/2024 12:45: Sangi-Cebeco3 34.5 kV line energized at 1244H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 12:35:03 PM | Mindanao Grid-05/08/2024 12:40: Agus 6 138kV Switchyard - Agus 7 HEP (7LI2AG6-AP7) 138kV L2 energized / restored at 1212H. From Planned Outage (Non-GOMP) [WEBSMS] | CMIN
5/8/2024 12:27:56 PM | Visayas Grid-05/08/2024 12:28: Sangi-Cebeco3 34.5 kV line tripped at 1223H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 11:34:14 AM | Mindanao Grid-05/08/2024 11:39: GNPK Unit 1 online at 1132H from Forced outage. (Unplanned Outage) [WEBSMS] | CMIN
5/8/2024 11:20:21 AM | Visayas Grid-05/08/2024 11:20: MECO (Solea) implement ILP at 1115H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 10:53:10 AM | Visayas Grid-05/08/2024 10:53: MECO (Movenpick) implement ILP at 1048H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 10:45:46 AM | [NSO Update] Luzon Grid-05/08/2024 10:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1044H with power going to Visayas. [WEBSMS] | CLUZ
5/8/2024 10:45:21 AM | [NSO Update] Visayas Grid-05/08/2024 10:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1044H with power going to Visayas. [WEBSMS] | CVIS
5/8/2024 10:44:50 AM | Visayas Grid-05/08/2024 10:45: MECO (Sheraton) implement ILP at 1039H (Unplanned Outage) [WEBSMS] | CVIS
5/8/2024 10:44:05 AM | [NSO Update] Luzon Grid-05/08/2024 10:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1034H from forward power direction. [WEBSMS] | CLUZ
5/8/2024 10:41:57 AM | [NSO Update] Visayas Grid-05/08/2024 10:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1034H from forward power direction. [WEBSMS] | CVIS
5/8/2024 10:37:28 AM | Mindanao Grid-05/08/2024 10:42: Therma 1 Unit 2 online at 1021H. SO dispatched. [WEBSMS] | CMIN
5/8/2024 10:21:28 AM | Mindanao Grid-05/08/2024 10:26: Therma 2 Unit 1 online at 1017H. SO dispatched. [WEBSMS] | CMIN
5/8/2024 10:09:29 AM | Mindanao Grid-05/08/2024 10:14: WMPC DG07 online at 1005H. SO dispatched. [WEBSMS] | CMIN
5/8/2024 9:01:09 AM | Mindanao Grid-05/08/2024 09:06: WMPC DG08 Online at 0858H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/8/2024 9:00:30 AM | Mindanao Grid-05/08/2024 09:05: WMPC DG10 Online at 0820H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/8/2024 8:56:00 AM | Mindanao Grid-05/08/2024 09:01: IDPP (Mapalad) online as DR at 0809H. Time of call at 0758H. [WEBSMS] | CMIN
5/8/2024 8:54:36 AM | Mindanao Grid-05/08/2024 08:59: Kegi Jimenez Unit 1 online as DR at 0819H. Time if call at 0809H. [WEBSMS] | CMIN
5/8/2024 8:50:57 AM | Mindanao Grid-05/08/2024 08:56: Kegi Panaon Unit 2 online as DR at 0812H. Time if call at 0800H. [WEBSMS] | CMIN
5/8/2024 8:50:02 AM | Mindanao Grid-05/08/2024 08:55: Therma 2 Unit 2 online as DR at 0813H. Time if call at 0759H. [WEBSMS] | CMIN
5/8/2024 8:07:39 AM | Mindanao Grid-05/08/2024 08:12: Update: GNPK Unit 1 (GN Power Kauswagan Ltd. Co. ) auto-tripped at 0754H with a gross generation of 151.0 MW that led to Automatic Load dropping (ALD) of NGCP, CEPALCO and DLPC feeders Lowest system frequency recorded was 59.0875Hz. [WEBSMS] | CMIN
5/8/2024 8:03:29 AM | Mindanao Grid-05/08/2024 08:08: GNPK Unit 1 (GN Power Kauswagan Ltd. Co. ) auto-tripped at 0754H with a gross generation of 151.0 MW that led to Automatic Load dropping (ALD) of NGCP and DLPC feeders Lowest system frequency recorded was 59.0875Hz. [WEBSMS] | CMIN
5/8/2024 7:48:40 AM | Mindanao Grid-05/08/2024 07:53: Manolo Fortich - HEDCOR 1 (MN1 HEPP) 138kV L1 de-energized at 0736H. Planned Outage (GOP). (Note: HEDCOR Management approved shutdown request) [WEBSMS] | CMIN
5/8/2024 7:15:12 AM | Luzon Grid-05/08/2024 07:15: Tuguegarao 230kV Bus 1 restored at 0714H (Planned Outage) [WEBSMS] | CLUZ
5/8/2024 6:38:54 AM | Luzon Grid-05/08/2024 06:39: Naga-Tiwi C 230kV Line 2 de-energized at 0635H (Planned Outage) [WEBSMS] | CLUZ
5/8/2024 6:06:38 AM | Luzon Grid-05/08/2024 06:06: Tayabas-San Jose 500kV Line 2 de-energized at 0603H (Planned Outage) [WEBSMS] | CLUZ
5/8/2024 6:02:24 AM | [NSO Update] Mindanao Grid-05/08/2024 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3153MW, PK=2457MW, RR=73MW, NetOpMargin: AM=622, PM=484, EVE=589 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/8/2024 5:57:53 AM | [NSO Update] Visayas Grid-05/08/2024 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2861MW, PK=2533MW, RR=97MW, NetOpMargin: AM=231, PM=194, EVE=232 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 114.5MW, Leyte A @ 310MW, Nasulo @ 27MW [WEBSMS] | CVIS
5/8/2024 5:53:17 AM | [NSO Update] Luzon Grid-05/08/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15301MW, PK=12745MW, RR=440MW, NetOpMargin: AM=2117, PM=1254, EVE=1045 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 500MW [WEBSMS] | CLUZ
5/8/2024 4:13:46 AM | [NSO Update] Mindanao Grid-05/08/2024 04:19: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CMIN
5/8/2024 4:13:02 AM | [NSO Update] Visayas Grid-05/08/2024 04:13: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CVIS
5/8/2024 4:12:49 AM | [NSO Update] Luzon Grid-05/08/2024 04:13: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CLUZ
5/8/2024 1:34:55 AM | Luzon Grid-05/08/2024 01:35: Tuguegarao 230kV Bus 1 de-energized at 0133H (Planned Outage) [WEBSMS] | CLUZ
5/7/2024 10:06:55 PM | Mindanao Grid-05/07/2024 22:12: WMPC DG10 Shutdown at 2204H. From MRU - System Voltage Reqyuirement. [WEBSMS] | CMIN
5/7/2024 9:25:49 PM | Mindanao Grid-05/07/2024 21:31: WMPC DG07 shutdown at 2123H. MO Dispatched. Follow RTD [WEBSMS] | CMIN
5/7/2024 9:23:39 PM | [NSO Update] Visayas Grid-05/07/2024 21:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2121H with power going to Luzon. [WEBSMS] | CVIS
5/7/2024 9:23:24 PM | [NSO Update] Luzon Grid-05/07/2024 21:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2121H with power going to Luzon. [WEBSMS] | CLUZ
5/7/2024 9:12:38 PM | [NSO Update] Visayas Grid-05/07/2024 21:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2111H from reverse power direction. [WEBSMS] | CVIS
5/7/2024 9:12:24 PM | [NSO Update] Luzon Grid-05/07/2024 21:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2111H from reverse power direction. [WEBSMS] | CLUZ
5/7/2024 8:37:22 PM | Mindanao Grid-05/07/2024 20:42: WMPC DG3 manually shutdown due to Exhaust Gas Leak at 0834H. From MRU - System Voltage Requirement. Forced Outage. [WEBSMS] | CMIN
5/7/2024 8:31:57 PM | Mindanao Grid-05/07/2024 20:37: WMPC DG7 Online at 0824H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
5/7/2024 6:17:28 PM | Mindanao Grid-05/07/2024 18:22: Manolo Fortich - Manolo Fortich Hydro 1 Power Plant 138kV Line 1 energized at 1815H. (Planned Outage) [WEBSMS] | CMIN
5/7/2024 5:49:45 PM | [NSO Update] Mindanao Grid-05/07/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3074MW, PK=2467MW, RR=73MW, NetOpMargin: EVE=534 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW, TSI U2 @120MW [WEBSMS] | CMIN
5/7/2024 5:48:17 PM | [NSO Update] Visayas Grid-05/07/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2673MW, PK=2407MW, RR=94MW, NetOpMargin: EVE=171 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 114.5MW, Leyte A @ 310MW [WEBSMS] | CVIS
5/7/2024 5:46:17 PM | [NSO Update] Luzon Grid-05/07/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14257MW, PK=12339MW, RR=464MW, NetOpMargin: EVE=1454 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 500MW [WEBSMS] | CLUZ
5/7/2024 5:43:45 PM | Visayas Grid-05/07/2024 17:44: PGPP 2 Nasulo cut-in at 1732H. (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 5:32:50 PM | Visayas Grid-05/07/2024 17:33: MECO Mactan Newtown Fdr MLD of 1.5MW restored at 1559H. (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 5:29:09 PM | Visayas Grid-05/07/2024 17:29: MECO Basak fdr 1 MLD of 2.0MW restored at 1545H (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 4:59:31 PM | Mindanao Grid-05/07/2024 17:04: TM2 Unit 1 shutdown at 1654H from MO Dispatch. [WEBSMS] | CMIN
5/7/2024 4:29:20 PM | Mindanao Grid-05/07/2024 16:34: WMPC DG08 Shutdown at 1620H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/7/2024 4:23:58 PM | Mindanao Grid-05/07/2024 16:29: WMPC DG8 Shutdown at 1620H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/7/2024 3:50:15 PM | Visayas Grid-05/07/2024 15:50: MECO Basak fdr 1 MLD of 2.3MW restored at 1543H (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 3:24:35 PM | Visayas Grid-05/07/2024 15:24: MECO Pajo load end restored from ELD at 1515H (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 3:21:55 PM | [NSO Update] Visayas Grid-05/07/2024 15:22: SO initiated Market Intervention for Visayas has been lifted today at 1516H. Market operations will resume starting interval 1525H. [WEBSMS] | CVIS
5/7/2024 3:21:02 PM | Visayas Grid-05/07/2024 15:21: EAUC U4 confirmed on stable condition at 1508H (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 3:16:51 PM | Visayas Grid-05/07/2024 15:17: EAUC U4 cut-in at 1506H . ( Unplanned outage ) [WEBSMS] | CVIS
5/7/2024 3:14:44 PM | Visayas Grid-05/07/2024 15:15: MECO Mactan Newtown Fdr implemented MLD at 1452H, L=1.5MW (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 3:08:11 PM | Mindanao Grid-05/07/2024 15:13: WMPC DG01 Shutdown at 1503H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/7/2024 2:07:29 PM | Mindanao Grid-05/07/2024 14:12: TM2 Unit 1 online at 1401H. MO Dispatch. [WEBSMS] | CMIN
5/7/2024 1:42:58 PM | Mindanao Grid-05/07/2024 13:48: SEDI EEI online at 1322H. MO Dispatched. [WEBSMS] | CMIN
5/7/2024 1:42:02 PM | Mindanao Grid-05/07/2024 13:47: WMPC DG07 online at 1328H. MO Dispatched. [WEBSMS] | CMIN
5/7/2024 1:22:21 PM | [NSO Update] Luzon Grid-05/07/2024 13:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1317H with power going to Visayas. [WEBSMS] | CLUZ
5/7/2024 1:21:58 PM | [NSO Update] Visayas Grid-05/07/2024 13:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1317H with power going to Visayas. [WEBSMS] | CVIS
5/7/2024 1:17:55 PM | Visayas Grid-05/07/2024 13:18: MECO Basak fdr 1 implemented MLD at 1310H, L=2.3 (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 1:14:50 PM | Visayas Grid-05/07/2024 13:15: MECO Pajo load end ELD at 1250H, L=8.1 (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 1:09:07 PM | [NSO Update] Visayas Grid-05/07/2024 13:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1307H from forward power direction. [WEBSMS] | CVIS
5/7/2024 1:08:49 PM | [NSO Update] Luzon Grid-05/07/2024 13:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1307H from forward power direction. [WEBSMS] | CLUZ
5/7/2024 1:00:54 PM | Luzon Grid-05/07/2024 13:01: Tayabas-San Jose 500kV line 2 was energized at Tayabas side at 1258H. (Anti-pilferage) [WEBSMS] | CLUZ
5/7/2024 12:59:11 PM | Mindanao Grid-05/07/2024 13:04: WMPC DG1 Online at 1254H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/7/2024 12:54:12 PM | [NSO Update] Visayas Grid-05/07/2024 12:54: SO initiated Market Intervention for Visayas is issued today at starting interval 1255H due to MLD implementation to prevent overloading of Cebu-Mandaue 138kV Line 2. [WEBSMS] | CVIS
5/7/2024 12:45:59 PM | [NSO Update] Luzon Grid-05/07/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15390MW, PK=13669MW, RR=526MW, NetOpMargin: PM=1195, EVE=1135 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/7/2024 12:39:31 PM | Mindanao Grid-05/07/2024 12:44: WMPC DG8 Online at 1238H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/7/2024 12:36:04 PM | Visayas Grid-05/07/2024 12:36: EAUC U4 tripped at 1229H (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 12:34:02 PM | [NSO Update] Mindanao Grid-05/07/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3128MW, PK=2635MW, RR=73MW, NetOpMargin: PM=421, EVE=538 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @37MW, TSI U2 @120MW [WEBSMS] | CMIN
5/7/2024 12:32:28 PM | [NSO Update] Visayas Grid-05/07/2024 12:32: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2920MW, PK=2600MW, RR=99MW, NetOpMargin: PM=221, EVE=251 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @114.5MW, LEYTE A @315MW [WEBSMS] | CVIS
5/7/2024 12:18:28 PM | Mindanao Grid-05/07/2024 12:23: WMPC DG8 Shutdown at 1216H. End of MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/7/2024 10:52:31 AM | Mindanao Grid-05/07/2024 10:57: WMPC DG8 Online at 1045H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/7/2024 10:45:25 AM | Visayas Grid-05/07/2024 10:45: EAUC U3 recut in at 1042H (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 10:42:19 AM | Mindanao Grid-05/07/2024 10:47: Pulangi4 U2 Shutdown at 1039H. OMC - Low Forebay Elevation. [WEBSMS] | CMIN
5/7/2024 10:30:13 AM | Visayas Grid-05/07/2024 10:30: EAUC U3 tripped at 1024H (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 10:02:05 AM | Luzon Grid-05/07/2024 10:02: San Gabriel online at 0959H. (From Reserve Shutdown) [WEBSMS] | CLUZ
5/7/2024 9:43:20 AM | Mindanao Grid-05/07/2024 09:48: Agus 6 SS - Agus 7 Plant Line 2 shutdown at 0938H. (Planned Outage) [WEBSMS] | CMIN
5/7/2024 9:21:33 AM | [NSO Update] Visayas Grid-05/07/2024 09:21: SO initiated Market Intervention for Visayas has been lifted today at 0918H. Market operations will resume starting interval 0925H. [WEBSMS] | CVIS
5/7/2024 9:15:16 AM | Mindanao Grid-05/07/2024 09:20: Agus 7 U1 online at 0905H. (Planned Outage) [WEBSMS] | CMIN
5/7/2024 9:14:13 AM | Mindanao Grid-05/07/2024 09:19: Agus 7 U2 shutdown at 0905H. (Planned Outage) [WEBSMS] | CMIN
5/7/2024 9:12:25 AM | Visayas Grid-05/07/2024 09:12: EAUC U1 re cut in at 0910H (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 9:08:32 AM | Visayas Grid-05/07/2024 09:08: EAUC U4/U2 recut in at 0848H/0906H, under observation. (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 9:04:08 AM | Visayas Grid-05/07/2024 09:04: erratum. MECO implemented ELD at 0817H, unavailability of EAUC U1, U2 and U4 (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 8:53:58 AM | Visayas Grid-05/07/2024 08:54: VECO implemented load transfer from Mandaue GIS to VECO L1/Quiot SS at 0844H, L=10MW (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 8:51:59 AM | Visayas Grid-05/07/2024 08:52: MECO Basak feeder load drop at 0839H, L=1.5 MW (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 8:51:30 AM | Mindanao Grid-05/07/2024 08:56: WMPC DG3 Online at 0849H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/7/2024 8:31:59 AM | Mindanao Grid-05/07/2024 08:37: WMPC DG10 online at 0830H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/7/2024 8:31:39 AM | Mindanao Grid-05/07/2024 08:36: WMPC DG10 Online at 0836H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/7/2024 8:29:06 AM | Mindanao Grid-05/07/2024 08:34: AGUS 1 HEP Unit 2 with 16MW Load shutdown at 0813H. PMS-GOMP (Planned Outage) [WEBSMS] | CMIN
5/7/2024 8:22:46 AM | Visayas Grid-05/07/2024 08:23: MECO implemented ELD at 0817H, unavailability of EAUC U1, U2 and U3 (Unplanned Outage) [WEBSMS] | CVIS
5/7/2024 8:22:14 AM | [NSO Update] Visayas Grid-05/07/2024 08:22: SO initiated Market Intervention for Visayas is issued today at starting interval 0820H due to MLD implementation to prevent overloading of Cebu-Mandaue 138kV Line 2 [WEBSMS] | CVIS
5/7/2024 8:06:42 AM | Mindanao Grid-05/07/2024 08:11: Manolo Fortich SS - Manolo Fortich Plant 1 138kV Line 1 shutdown at 0800H. (Planned Outage) [WEBSMS] | CMIN
5/7/2024 7:52:58 AM | Mindanao Grid-05/07/2024 07:58: Manolo Fortich-1 HEP with 8.0MW load shutdown at 0739H. (Planned Outage-GOP) [WEBSMS] | CMIN
5/7/2024 7:52:33 AM | Luzon Grid-05/07/2024 07:52: San Gabriel shutdown at 0748H. (Reserve Shutdown) [WEBSMS] | CLUZ
5/7/2024 6:16:56 AM | [NSO Update] Mindanao Grid-05/07/2024 06:22: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
5/7/2024 6:16:34 AM | [NSO Update] Visayas Grid-05/07/2024 06:16: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
5/7/2024 6:16:09 AM | [NSO Update] Luzon Grid-05/07/2024 06:16: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
5/7/2024 6:08:28 AM | [NSO Update] Mindanao Grid-05/07/2024 06:13: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3170MW, PK=2456MW, RR=73MW, NetOpMargin: AM=641, PM=480, EVE=553 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @37MW, TSI U2 @120MW [WEBSMS] | CMIN
5/7/2024 6:07:09 AM | [NSO Update] Visayas Grid-05/07/2024 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2824MW, PK=2426MW, RR=96MW, NetOpMargin: AM=303, PM=174, EVE=260 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @114.5MW, LEYTE A @315MW [WEBSMS] | CVIS
5/7/2024 6:05:22 AM | [NSO Update] Luzon Grid-05/07/2024 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15459MW, PK=13224MW, RR=435MW, NetOpMargin: AM=1800, PM=1020, EVE=1249 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/7/2024 4:09:00 AM | Mindanao Grid-05/07/2024 04:14: Mt Apo Unit 3 online at 0353H from Forced outage. (Unplanned Outage) [WEBSMS] | CMIN
5/7/2024 4:08:02 AM | Luzon Grid-05/07/2024 04:08: Correction: San Lorenzo 60 online at 0306H. (Unplanned Outage) [WEBSMS] | CLUZ
5/7/2024 3:08:15 AM | Luzon Grid-05/07/2024 03:08: San Lorenzo 60 online at 0306H (Planned Outage) [WEBSMS] | CLUZ
5/6/2024 10:18:53 PM | Mindanao Grid-05/06/2024 22:24: WMPC DG10 shutdown at 2218H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/6/2024 9:19:32 PM | Mindanao Grid-05/06/2024 21:24: WMPC DG03 shutdown at 2115H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/6/2024 7:13:11 PM | [NSO Update] Luzon Grid-05/06/2024 19:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1912H with power going to Luzon. [WEBSMS] | CLUZ
5/6/2024 7:12:55 PM | [NSO Update] Visayas Grid-05/06/2024 19:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1912H with power going to Luzon. [WEBSMS] | CVIS
5/6/2024 7:03:43 PM | [NSO Update] Visayas Grid-05/06/2024 19:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1902H from reverse power direction. [WEBSMS] | CVIS
5/6/2024 7:03:31 PM | [NSO Update] Luzon Grid-05/06/2024 19:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1902H from reverse power direction. [WEBSMS] | CLUZ
5/6/2024 6:06:11 PM | [NSO Update] Visayas Grid-05/06/2024 18:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1758H with power going to Visayas. [WEBSMS] | CVIS
5/6/2024 6:05:53 PM | [NSO Update] Luzon Grid-05/06/2024 18:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1758H with power going to Visayas. [WEBSMS] | CLUZ
5/6/2024 5:49:30 PM | Mindanao Grid-05/06/2024 17:54: Aurora - NagaMin138kV L1 auto-tripped and auto-reclosed at 1718H. (at both Aurora and NagaMin SS successfully). Unplanned Outage. [WEBSMS] | CMIN
5/6/2024 5:48:14 PM | [NSO Update] Mindanao Grid-05/06/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3094MW, PK=2449MW, RR=73MW, NetOpMargin: EVE=572 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/6/2024 5:46:51 PM | [NSO Update] Visayas Grid-05/06/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2686MW, PK=2391MW, RR=94MW, NetOpMargin: EVE=201 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 116.5MW, Leyte A @ 305MW [WEBSMS] | CVIS
5/6/2024 5:45:43 PM | [NSO Update] Luzon Grid-05/06/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13882MW, PK=12477MW, RR=469MW, NetOpMargin: EVE=936 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 500MW [WEBSMS] | CLUZ
5/6/2024 5:44:12 PM | [NSO Update] Visayas Grid-05/06/2024 17:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1742H from forward power direction. [WEBSMS] | CVIS
5/6/2024 5:43:58 PM | [NSO Update] Luzon Grid-05/06/2024 17:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1742H from forward power direction. [WEBSMS] | CLUZ
5/6/2024 5:30:28 PM | Mindanao Grid-05/06/2024 17:35: Opol SS 75MVA Power Transformer No.1 (7XF01OPO) energized at 1707H. From Planned Outage (GOMP). [WEBSMS] | CMIN
5/6/2024 5:11:26 PM | [NSO Update] Luzon Grid-05/06/2024 17:11: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1710H with power going to Luzon. [WEBSMS] | CLUZ
5/6/2024 5:11:10 PM | [NSO Update] Visayas Grid-05/06/2024 17:11: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1710H with power going to Luzon. [WEBSMS] | CVIS
5/6/2024 5:03:01 PM | [NSO Update] Visayas Grid-05/06/2024 17:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1700H from reverse power direction. [WEBSMS] | CVIS
5/6/2024 5:02:47 PM | [NSO Update] Luzon Grid-05/06/2024 17:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1700H from reverse power direction. [WEBSMS] | CLUZ
5/6/2024 4:32:29 PM | [NSO Update] Luzon Grid-05/06/2024 16:32: System Advisory: Luzon Grid Yellow Alert notice issued today has been lifted at 1631H. [WEBSMS] | CLUZ
5/6/2024 4:26:48 PM | Visayas Grid-05/06/2024 16:27: MECO implemented 2.7 MW ILP to prevent overloading of Cebu - Mandaue 138 kV Line 2 lifted at 1625H [WEBSMS] | CVIS
5/6/2024 3:34:15 PM | Mindanao Grid-05/06/2024 15:39: Mt Apo Unit 3 with 2.8MW load tripped at 1508H. Indication: for further investigation. (Unplanned Outage) [WEBSMS] | CMIN
5/6/2024 2:41:42 PM | Mindanao Grid-05/06/2024 14:46: WMPC DG05 MO dispatch with 10MW emergency shutdown at 1433H due fuel leaked. (Unplanned Outage) [WEBSMS] | CMIN
5/6/2024 2:23:52 PM | Visayas Grid-05/06/2024 14:24: MECO implemented 2.7 MW ILP at 1413H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
5/6/2024 2:18:04 PM | Mindanao Grid-05/06/2024 14:23: Pulangi 4 Unit 2 online at 1415H from OMC. (Unplanned Outage) [WEBSMS] | CMIN
5/6/2024 1:04:08 PM | [NSO Update] Mindanao Grid-05/06/2024 13:09: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3140MW, PK=2603MW, RR=73MW, NetOpMargin: PM=465, EVE=581 Highest Unit O/L: GNPK 1, 2, 3. & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/6/2024 1:00:41 PM | [NSO Update] Visayas Grid-05/06/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2947MW, PK=2617MW, RR=100MW, NetOpMargin: PM=231, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @118.5MW, LEYTE A @315MW [WEBSMS] | CVIS
5/6/2024 12:53:43 PM | [NSO Update] Luzon Grid-05/06/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14905MW, PK=13634MW, RR=491MW, NetOpMargin: PM=780, EVE=839 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/6/2024 12:53:17 PM | Mindanao Grid-05/06/2024 12:58: WMPC DG01 online at 1238H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/6/2024 10:51:55 AM | [NSO Update] Visayas Grid-05/06/2024 10:52: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1045H with power going to Visayas [WEBSMS] | CVIS
5/6/2024 10:51:31 AM | [NSO Update] Luzon Grid-05/06/2024 10:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1045H with power going to Visayas [WEBSMS] | CLUZ
5/6/2024 10:45:55 AM | [NSO Update] Visayas Grid-05/06/2024 10:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1035H from forward power direction [WEBSMS] | CVIS
5/6/2024 10:45:18 AM | [NSO Update] Luzon Grid-05/06/2024 10:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1035H from forward power direction [WEBSMS] | CLUZ
5/6/2024 10:37:56 AM | Mindanao Grid-05/06/2024 10:43: WMPC DG08 online at 1014H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/6/2024 10:09:27 AM | Visayas Grid-05/06/2024 10:09: EAUC U1 re cut in at 1007H (Unplanned Outage) [WEBSMS] | CVIS
5/6/2024 9:58:02 AM | Visayas Grid-05/06/2024 09:58: EAUC U1 tripped at 0950H, overspeed (Unplanned Outage) [WEBSMS] | CVIS
5/6/2024 8:38:34 AM | Mindanao Grid-05/06/2024 08:43: WMPC DG03 online at 0836H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/6/2024 8:26:53 AM | Mindanao Grid-05/06/2024 08:32: WMPC DG10 online at 0824H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/6/2024 8:16:12 AM | Mindanao Grid-05/06/2024 08:21: Opol SS 75MVA Power Transformer No.1 (7XF01OPO) de-energized at 0811H. Planned Outage (GOMP) [WEBSMS] | CMIN
5/6/2024 7:06:27 AM | Luzon Grid-05/06/2024 07:06: Muntinlupa 300MVA T04 was energized at 0700H, while Muntinlupa-Gardner 115kV tie line 2 was restored at 0701H. (Planned Outage) [WEBSMS] | CLUZ
5/6/2024 6:39:11 AM | [NSO Update] Mindanao Grid-05/06/2024 06:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3154MW, PK=2506MW, RR=73MW, NetOpMargin: AM=575, PM=515, EVE=584 Highest Unit O/L: GNPK 1, 2, 3. & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/6/2024 6:37:23 AM | [NSO Update] Visayas Grid-05/06/2024 06:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3020MW, PK=2421MW, RR=96MW, NetOpMargin: AM=503, PM=230, EVE=236 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @118.5MW, LEYTE A @315MW [WEBSMS] | CVIS
5/6/2024 6:36:22 AM | [NSO Update] Luzon Grid-05/06/2024 06:36: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=14830MW, PK=12683MW, RR=440MW, NetOpMargin: AM=1707, PM=961, EVE=877 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/6/2024 6:32:23 AM | [NSO Update] Luzon Grid-05/06/2024 06:32: System Advisory: 06-May-2024, Luzon Grid is on YELLOW Alert for interval hour 1600H. Total capacity on forced outage is 1306.8MW. Total of de-rated capacity is 100MW. [WEBSMS] | CLUZ
5/6/2024 4:05:04 AM | [NSO Update] Mindanao Grid-05/06/2024 04:10: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
5/6/2024 4:04:47 AM | [NSO Update] Visayas Grid-05/06/2024 04:04: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
5/6/2024 4:04:31 AM | [NSO Update] Luzon Grid-05/06/2024 04:04: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
5/6/2024 2:06:52 AM | Luzon Grid-05/06/2024 02:07: Muntinlupa SS 300MVA T04 de-energized at 0205H (Planned Outage) [WEBSMS] | CLUZ
5/6/2024 2:04:52 AM | Luzon Grid-05/06/2024 02:04: Muntinlupa-Gardner 115kV Tie Line 2 de-energized at 0204H (Planned Outage) [WEBSMS] | CLUZ
5/5/2024 10:43:48 PM | Mindanao Grid-05/05/2024 22:48: Update: Mt. Apo Unit 3 (MA3) Online at 2208H from PMS (Non-GOMP). Unplanned Outage. [WEBSMS] | CMIN
5/5/2024 10:27:44 PM | Mindanao Grid-05/05/2024 22:32: Mt. Apo Unit 3 (MA3) Online from PMS (Non-GOMP). Unplanned Outage. [WEBSMS] | CMIN
5/5/2024 9:18:38 PM | Mindanao Grid-05/05/2024 21:23: WMPC DG05 shutdown at 2116H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/5/2024 7:51:22 PM | Mindanao Grid-05/05/2024 19:56: WMPC DG08 shutdown at 1948H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/5/2024 7:15:50 PM | Luzon Grid-05/05/2024 19:16: Lal-lo-Cagayan North Solar 69kV Line 1 & 2 restored at 1912H and 1915H, respectively (Planned Outage) [WEBSMS] | CLUZ
5/5/2024 5:47:07 PM | [NSO Update] Mindanao Grid-05/05/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3090MW, PK=2273MW, RR=73MW, NetOpMargin: EVE=745 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/5/2024 5:45:57 PM | [NSO Update] Visayas Grid-05/05/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2591MW, PK=2182MW, RR=93MW, NetOpMargin: EVE=316 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 303MW [WEBSMS] | CVIS
5/5/2024 5:44:36 PM | [NSO Update] Luzon Grid-05/05/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13438MW, PK=11519MW, RR=339MW, NetOpMargin: EVE=1580 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 500MW [WEBSMS] | CLUZ
5/5/2024 5:44:11 PM | Luzon Grid-05/05/2024 17:44: Lal-lo-Magapit BESS 69kV Line restored at 1744H (Planned Outage) [WEBSMS] | CLUZ
5/5/2024 5:38:37 PM | Luzon Grid-05/05/2024 17:38: Concepcion-San Manuel 230kV Line 1 restored at 1737H (Planned Outage) [WEBSMS] | CLUZ
5/5/2024 5:01:28 PM | Visayas Grid-05/05/2024 17:01: Calong-calong - Daanlungsod 138 kV Line 1 energized at 1701H (Planned Outage) [WEBSMS] | CVIS
5/5/2024 4:32:55 PM | Visayas Grid-05/05/2024 16:33: Daanlungsod SS 138 kV Bus 1 energized at 1631H (Planned Outage) [WEBSMS] | CVIS
5/5/2024 4:03:53 PM | Luzon Grid-05/05/2024 16:04: San Gabriel online at 1601H (Reserve Shutdown) [WEBSMS] | CLUZ
5/5/2024 3:08:23 PM | Mindanao Grid-05/05/2024 15:13: TM2 Unit 1 shutdown at 1501H. End of MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/5/2024 2:31:13 PM | Mindanao Grid-05/05/2024 14:36: Villanueva - Jasaan 138kV L1 energized at 1425H. (Planned Outage) [WEBSMS] | CMIN
5/5/2024 1:54:55 PM | Mindanao Grid-05/05/2024 14:00: Nagamin 100MVA Transformer #1 energized at 1210H (Unplanned Outage) [WEBSMS] | CMIN
5/5/2024 1:51:35 PM | Mindanao Grid-05/05/2024 13:56: Aurora - Nagamin 138KV Line 2 energized at 1210H (Unplanned Outage) [WEBSMS] | CMIN
5/5/2024 1:09:55 PM | [NSO Update] Mindanao Grid-05/05/2024 13:15: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3123MW, PK=2181MW, RR=73MW, NetOpMargin: PM=869, EVE=640 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/5/2024 1:06:14 PM | [NSO Update] Visayas Grid-05/05/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2899MW, PK=2049MW, RR=97MW, NetOpMargin: PM=753, EVE=238 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @305MW [WEBSMS] | CVIS
5/5/2024 1:03:03 PM | [NSO Update] Luzon Grid-05/05/2024 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15110MW, PK=11285MW, RR=3474MW, NetOpMargin: PM=3474, EVE=2059 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/5/2024 12:55:35 PM | Mindanao Grid-05/05/2024 13:00: WMPC DG08 online at 1234H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/5/2024 12:15:23 PM | Mindanao Grid-05/05/2024 12:20: Aurora - NagaMin 138kV L2 auto-tripped at 1153H. (Unplanned Outage) [WEBSMS] | CMIN
5/5/2024 11:36:11 AM | Mindanao Grid-05/05/2024 11:41: WMPC DG05 online at 1121H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/5/2024 11:18:31 AM | Mindanao Grid-05/05/2024 11:23: Maco - Therma Marine 1 138kV Line 1 energized at 1115H. (Planned Outage) [WEBSMS] | CMIN
5/5/2024 10:26:59 AM | Mindanao Grid-05/05/2024 10:32: Update: TM2 Unit 1 online at 0957H as MRU - Thermal Limits. (Unplanned Outage) [WEBSMS] | CMIN
5/5/2024 10:17:35 AM | Mindanao Grid-05/05/2024 10:22: San Francisco SS 138kV Transformer No. 2 energized at 1015H.(Planned Outage) [WEBSMS] | CMIN
5/5/2024 10:01:05 AM | Mindanao Grid-05/05/2024 10:06: TMI 2 Unit 2 online at 0957H as MRU - Thermal Limits. (Unplanned Outage) [WEBSMS] | CMIN
5/5/2024 8:26:57 AM | Mindanao Grid-05/05/2024 08:32: San Francisco SS 138kV Transformer No. 2 de-energized at 0809H. (Planned Outage) [WEBSMS] | CMIN
5/5/2024 8:08:58 AM | Mindanao Grid-05/05/2024 08:14: Maco - Therma Marine 1 138kV Line 1 de-energized at 0803H. (Planned Outage) [WEBSMS] | CMIN
5/5/2024 7:22:15 AM | Visayas Grid-05/05/2024 07:22: Daanglungsod SS 138KV Bus 1 de-energized at 0707H. (Planned Outage) [WEBSMS] | CVIS
5/5/2024 7:20:17 AM | Luzon Grid-05/05/2024 07:20: Muntinlupa SS 300MVA T03 restored at 0720H (Planned Outage) [WEBSMS] | CLUZ
5/5/2024 7:12:05 AM | Luzon Grid-05/05/2024 07:12: Muntinlupa 230kV Bus 2 restored at 0711H (Planned Outage) [WEBSMS] | CLUZ
5/5/2024 6:37:04 AM | Visayas Grid-05/05/2024 06:37: Calung-calung- Daanglungsod 138KV Line 1 de-energized at 0631H.(Planned Outage) [WEBSMS] | CVIS
5/5/2024 6:13:59 AM | Mindanao Grid-05/05/2024 06:19: Villanueva - Jasaan 138kV L1 de-energized at 0610H. (Planned Outage) [WEBSMS] | CMIN
5/5/2024 6:03:09 AM | Luzon Grid-05/05/2024 06:03: Concepcion-San Manuel 230kV Line 1 de-energized at 0603H (Planned Outage) [WEBSMS] | CLUZ
5/5/2024 5:55:10 AM | Luzon Grid-05/05/2024 05:55: Lal-lo-Magapit BESS 69kV Line de-energized at 0554H (Planned Outage) [WEBSMS] | CLUZ
5/5/2024 5:52:46 AM | [NSO Update] Mindanao Grid-05/05/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3146MW, PK=1982MW, RR=73MW, NetOpMargin: AM=1091, PM=879, EVE=689 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/5/2024 5:52:29 AM | Luzon Grid-05/05/2024 05:52: Lal-lo-Cagayan North Solar 69kV Line 1 & 2 de-energized at 0550H & 0551H, respectively (Planned Outage) [WEBSMS] | CLUZ
5/5/2024 5:51:00 AM | [NSO Update] Visayas Grid-05/05/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2819MW, PK=1982MW, RR=95MW, NetOpMargin: AM=742, PM=755, EVE=247 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @118.5MW, LEYTE A @315MW [WEBSMS] | CVIS
5/5/2024 5:47:50 AM | [NSO Update] Luzon Grid-05/05/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15341MW, PK=10378MW, RR=350MW, NetOpMargin: AM=4614, PM=3470, EVE=2203 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/5/2024 5:31:11 AM | Luzon Grid-05/05/2024 05:31: San Gabriel shutdown at 0529H (Reserve Shutdown) [WEBSMS] | CLUZ
5/5/2024 4:46:16 AM | [NSO Update] Mindanao Grid-05/05/2024 04:51: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
5/5/2024 4:45:51 AM | [NSO Update] Visayas Grid-05/05/2024 04:46: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
5/5/2024 4:45:37 AM | [NSO Update] Luzon Grid-05/05/2024 04:45: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
5/5/2024 3:44:32 AM | Luzon Grid-05/05/2024 03:44: Quezon-Mexico 230kV Line restored at 0339H (Planned Outage) [WEBSMS] | CLUZ
5/5/2024 2:23:45 AM | Luzon Grid-05/05/2024 02:23: Muntinlupa 230kV Bus 2 de-energized at 0223H (Planned Outage) [WEBSMS] | CLUZ
5/5/2024 2:21:30 AM | Luzon Grid-05/05/2024 02:21: Muntinlupa 300MVA T03 de-energized at 0221H (Planned Outage) [WEBSMS] | CLUZ
5/5/2024 12:51:53 AM | Mindanao Grid-05/05/2024 00:57: (Correction) SIBULAN (SIB A U1 & U2, SIB B U1 & U2, TU1 U1, TU2 U1) with total load of 43.5MW shutdown at 0008H affected by DLPC scheduled line shutdown. [WEBSMS] | CMIN
5/5/2024 12:48:46 AM | Mindanao Grid-05/05/2024 00:53: SIBULAN (SIB A U1 & U2, SIB B U1 & U2, TL1 U1, TU2 U1) with total load of 43.5MW shutdown at 0008H affected by DLPC scheduled line shutdown. [WEBSMS] | CMIN
5/4/2024 11:55:20 PM | Luzon Grid-05/04/2024 23:55: Bacnotan-CIP2 69kV Line tripped at 2257H and restored at 2348H (Unplanned Outage) [WEBSMS] | CLUZ
5/4/2024 11:35:07 PM | Luzon Grid-05/04/2024 23:35: Quezon-Mexico 230kV L de-energized at 2334H (Planned Outage) [WEBSMS] | CLUZ
5/4/2024 10:40:11 PM | Mindanao Grid-05/04/2024 22:45: Tagoloan SS 100MVA 138/69kV/13.8kV Power Transformer 1 successfully energized/restored at 2226H. From Planned Outage/ Non-GOMP. Note: Approved P&E requested shutdown. [WEBSMS] | CMIN
5/4/2024 8:24:29 PM | Mindanao Grid-05/04/2024 20:29: WMPC DG10 shutdown at 2016H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/4/2024 8:23:49 PM | Mindanao Grid-05/04/2024 20:28: WMPC DG01 shutdown at 1919H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/4/2024 7:42:02 PM | [NSO Update] Visayas Grid-05/04/2024 19:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1940H with power going to Luzon [WEBSMS] | CVIS
5/4/2024 7:41:44 PM | [NSO Update] Luzon Grid-05/04/2024 19:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1940H with power going to Luzon [WEBSMS] | CLUZ
5/4/2024 7:41:05 PM | [NSO Update] Visayas Grid-05/04/2024 19:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1930H from reverse power direction [WEBSMS] | CVIS
5/4/2024 7:40:48 PM | [NSO Update] Luzon Grid-05/04/2024 19:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1930H from reverse power direction [WEBSMS] | CLUZ
5/4/2024 7:12:40 PM | Mindanao Grid-05/04/2024 19:17: SBPI JASAAN BESS online at 1900H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 6:49:19 PM | Mindanao Grid-05/04/2024 18:54: SBPI JASAAN BESS shutdown at 1800H due to unbalance voltage (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 6:19:55 PM | [NSO Update] Mindanao Grid-05/04/2024 18:25: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2952MW, PK=2298MW, RR=73MW, NetOpMargin: EVE=581 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/4/2024 6:18:41 PM | [NSO Update] Visayas Grid-05/04/2024 18:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2576MW, PK=2258MW, RR=93MW, NetOpMargin: EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @308MW [WEBSMS] | CVIS
5/4/2024 6:17:43 PM | [NSO Update] Luzon Grid-05/04/2024 18:17: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13136MW, PK=11777MW, RR=429MW, NetOpMargin: EVE=930 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @220MW, MSLC3 @280MW, ILIJAN A @500MW [WEBSMS] | CLUZ
5/4/2024 5:51:20 PM | Mindanao Grid-05/04/2024 17:56: Tagoloan-Manolo 138kV L2 successfully energized/restored at 1743H and looped (@ Manolo SS) at 1744H. From Planned Outage (Non-GOMP) [WEBSMS] | CMIN
5/4/2024 5:45:16 PM | Mindanao Grid-05/04/2024 17:50: GNPK Unit 3 online at 1744H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 5:42:33 PM | Mindanao Grid-05/04/2024 17:47: Tagoloan - SME 138kVL (7LI1TAG-SME: CEPALCO owned & maintained 138kVL) energized/restored at 1732H. From Planned Outage (Non-GOMP) [WEBSMS] | CMIN
5/4/2024 5:40:43 PM | Luzon Grid-05/04/2024 17:40: Bauang 230kV Bus 2 restored at 1740H (Planned Outage) [WEBSMS] | CLUZ
5/4/2024 5:37:39 PM | Mindanao Grid-05/04/2024 17:42: Tagoloan SS 138kV Bus #1 successfully energized/restored at 1731H. From Planned Outage (Non-GOMP) [WEBSMS] | CMIN
5/4/2024 5:21:09 PM | Mindanao Grid-05/04/2024 17:26: LAKE MAINIT online at 1717H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 5:20:38 PM | Mindanao Grid-05/04/2024 17:25: ASIGA online at 1656H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 5:18:47 PM | Mindanao Grid-05/04/2024 17:23: WMPC DG08 shutdown at 1717H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/4/2024 4:51:36 PM | Mindanao Grid-05/04/2024 16:56: MANOLO FORTICH 2 online at 1635H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 4:48:02 PM | Mindanao Grid-05/04/2024 16:53: DCP (TSI) Unit 2 online at 1646H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 4:42:29 PM | Mindanao Grid-05/04/2024 16:47: ASIGA (load=2MW) and LAKE MAINIT (14.3MW) isolated at 1635H due to outage of Butuan-Santiago 69 kV feeder (Unplanned Outage). [WEBSMS] | CMIN
5/4/2024 4:33:13 PM | Mindanao Grid-05/04/2024 16:38: MANOLO FORTICH 1 online at 1631H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 4:10:34 PM | Mindanao Grid-05/04/2024 16:15: TM2 Unit 1 shutdown at 1608H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/4/2024 4:07:55 PM | Luzon Grid-05/04/2024 16:08: San Juan 230kV Bus 2 restored at 1607H (Planned Outage) [WEBSMS] | CLUZ
5/4/2024 4:06:35 PM | Mindanao Grid-05/04/2024 16:11: (Correction) MANOLO FORTICH 1 with 5.6MW load tripped at 1539H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 3:54:32 PM | Mindanao Grid-05/04/2024 15:59: MANOLO FORTICH 1 with 5.6MW load tripped at 1544H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 3:53:49 PM | Mindanao Grid-05/04/2024 15:58: MANOLO FORTICH 2 with 7.2MW load tripped at 1539H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 3:45:47 PM | Mindanao Grid-05/04/2024 15:50: MANOLO FORTICH 2 online at 1305H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 3:44:59 PM | Mindanao Grid-05/04/2024 15:50: MANOLO FORTICH 1 online at 1246H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 3:42:55 PM | Mindanao Grid-05/04/2024 15:48: Tagoloan-Manolo 138kV L1 energized/restored at 1517H & completely looped (@ Manolo SS) at 1539H. From Unplanned Outage. [WEBSMS] | CMIN
5/4/2024 3:26:15 PM | [NSO Update] Visayas Grid-05/04/2024 15:26: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1445H with power going to Visayas [WEBSMS] | CVIS
5/4/2024 3:25:37 PM | [NSO Update] Luzon Grid-05/04/2024 15:25: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1445H with power going to Visayas [WEBSMS] | CLUZ
5/4/2024 3:23:01 PM | [NSO Update] Visayas Grid-05/04/2024 15:23: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1435H from reverse power direction [WEBSMS] | CVIS
5/4/2024 3:22:39 PM | [NSO Update] Luzon Grid-05/04/2024 15:22: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1435H from reverse power direction [WEBSMS] | CLUZ
5/4/2024 2:50:26 PM | Visayas Grid-05/04/2024 14:50: Toledo SS 138 kV bus 2 energized 1449H (Planned Outage) [WEBSMS] | CVIS
5/4/2024 2:38:55 PM | Mindanao Grid-05/04/2024 14:44: TM2 Unit 1 online at 1348H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/4/2024 1:23:25 PM | Mindanao Grid-05/04/2024 13:28: WMPC DG01 online at 1318H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/4/2024 1:09:51 PM | [NSO Update] Luzon Grid-05/04/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14392MW, PK=12438MW, RR=519MW, NetOpMargin: PM=1435, EVE=783 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 190MW, Masinloc 3 @ 220MW [WEBSMS] | CLUZ
5/4/2024 1:07:54 PM | [NSO Update] Mindanao Grid-05/04/2024 13:13: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2856MW, PK=2476MW, RR=73MW, NetOpMargin: PM=307, EVE=337 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/4/2024 1:07:47 PM | Luzon Grid-05/04/2024 13:07: San Gabriel online at 1206H (Reserve Shutdown) [WEBSMS] | CLUZ
5/4/2024 1:06:36 PM | [NSO Update] Visayas Grid-05/04/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2533MW, PK=2262MW, RR=97MW, NetOpMargin: PM=174, EVE=213 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 295MW [WEBSMS] | CVIS
5/4/2024 12:20:23 PM | Visayas Grid-05/04/2024 12:20: Colon-Dumanjug 138KV line 2 energized @ 1149H(Planned Outage) [WEBSMS] | CVIS
5/4/2024 12:15:39 PM | Luzon Grid-05/04/2024 12:15: San Lorenzo Module 60 (263MW) tripped at 1211H. Lowest system frequency is 59.346Hz. [WEBSMS] | CLUZ
5/4/2024 11:40:34 AM | Mindanao Grid-05/04/2024 11:45: WMPC DG08 online at 1139H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/4/2024 11:40:23 AM | Visayas Grid-05/04/2024 11:40: 138KV Colon-Dumanjug line 1 energized @1133H.(Planned Outage) [WEBSMS] | CVIS
5/4/2024 11:18:26 AM | Mindanao Grid-05/04/2024 11:23: LAMSAN BIOMASS online at 0920H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 11:17:45 AM | Mindanao Grid-05/04/2024 11:22: LAMSAN BIOMASS with 13.5MW load (net) tripped at 0909H. Indication: 50N, non-directional earth fault. (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 11:11:07 AM | Mindanao Grid-05/04/2024 11:16: Tagoloan-Manolo 138kV L1 auto-tripped again at 1059H. Unplanned Outage [WEBSMS] | CMIN
5/4/2024 11:00:17 AM | Mindanao Grid-05/04/2024 11:05: MANOLO FORTICH 1 (Units 1,2,4 with total load=5.7MW) & MANOLO FORTICH 2 (Units 2,3 with total load=5.1MW) tripped at 1036H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 10:48:26 AM | Mindanao Grid-05/04/2024 10:53: Tagoloan-Manolo 138kV L1 auto-tripped at 1017H then energized/restored at 1030H. Unplanned Outage. [WEBSMS] | CMIN
5/4/2024 10:39:04 AM | Mindanao Grid-05/04/2024 10:44: GNPK Unit 3 with 107.5MW load tripped at 1024H. Cause: for verification. Lowest frequency recorder was 59.18Hz. No ALD. (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 10:37:29 AM | [NSO Update] Visayas Grid-05/04/2024 10:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1036H with power going to Mindanao. [WEBSMS] | CVIS
5/4/2024 10:37:16 AM | [NSO Update] Mindanao Grid-05/04/2024 10:42: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1036H with power going to Mindanao. [WEBSMS] | CMIN
5/4/2024 10:35:08 AM | Luzon Grid-05/04/2024 10:35: San Juan 230kV Bus 2 de-energized at 1034H (Planned Outage) [WEBSMS] | CLUZ
5/4/2024 10:27:42 AM | [NSO Update] Mindanao Grid-05/04/2024 10:32: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1026H from forward power direction. [WEBSMS] | CMIN
5/4/2024 10:27:22 AM | [NSO Update] Visayas Grid-05/04/2024 10:27: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1026H from forward power direction. [WEBSMS] | CVIS
5/4/2024 9:58:56 AM | Mindanao Grid-05/04/2024 10:04: WMPC DG10 online at 0955H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/4/2024 9:07:26 AM | Mindanao Grid-05/04/2024 09:12: WMPC DG04 declared forced outage at 0900H (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 8:27:19 AM | [NSO Update] Visayas Grid-05/04/2024 08:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0825H with power going to Visayas. [WEBSMS] | CVIS
5/4/2024 8:27:06 AM | [NSO Update] Luzon Grid-05/04/2024 08:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0825H with power going to Visayas. [WEBSMS] | CLUZ
5/4/2024 8:17:03 AM | [NSO Update] Luzon Grid-05/04/2024 08:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0814H from forward power direction. [WEBSMS] | CLUZ
5/4/2024 8:16:48 AM | [NSO Update] Visayas Grid-05/04/2024 08:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0814H from forward power direction. [WEBSMS] | CVIS
5/4/2024 8:07:04 AM | Luzon Grid-05/04/2024 08:07: Pantabangan HEPP SS 75MVA T02 de-energized at 0805H (Planned Outage) [WEBSMS] | CLUZ
5/4/2024 7:34:15 AM | Mindanao Grid-05/04/2024 07:39: Villanueva SS 138kV Bus #1 successfully energized & restored at 0729H. From Planned Outage (Non-GOMP) [WEBSMS] | CMIN
5/4/2024 7:33:35 AM | Luzon Grid-05/04/2024 07:33: Mariveles SS PCB 9-04CB24MAO restored at 0732H (Planned Outage) [WEBSMS] | CLUZ
5/4/2024 7:08:54 AM | Mindanao Grid-05/04/2024 07:14: PULANGI 4 Unit 2 shutdown at 0707H due to low forebay elevation (Unplanned Outage) [WEBSMS] | CMIN
5/4/2024 7:00:04 AM | Visayas Grid-05/04/2024 07:00: undefined at Invalid dateH Toledo SS 138KV Bus 2 de-energized 0652H (Planned Outage) [WEBSMS] | CVIS
5/4/2024 6:36:45 AM | Luzon Grid-05/04/2024 06:36: Bauang 230kV Bus 2 de-energized at 0636H (Planned Outage) [WEBSMS] | CLUZ
5/4/2024 6:25:39 AM | Mindanao Grid-05/04/2024 06:30: Tagoloan SS 138kV Bus 1 de-energized/shutdown at 0624H. (Planned Outage) [WEBSMS] | CMIN
5/4/2024 6:23:23 AM | Mindanao Grid-05/04/2024 06:28: Tagoloan - SME 138kV Line de-energized/shutdown at 0622H. (Planned Outage) [WEBSMS] | CMIN
5/4/2024 6:21:25 AM | Mindanao Grid-05/04/2024 06:26: Tagoloan - Manolo Fortich 138kV Line 2 de-energized/shutdown at 0619H. (Planned Outage) [WEBSMS] | CMIN
5/4/2024 6:18:33 AM | Mindanao Grid-05/04/2024 06:23: Tagoloan SS 100MVA 138/69kV Power Transformer 1 De-energized/shutdown at 0616H. (Planned Outage) [WEBSMS] | CMIN
5/4/2024 6:12:02 AM | Visayas Grid-05/04/2024 06:12: Colon-Dumanjug 138KV line 2 de-energized @0603H (Planned Outage) [WEBSMS] | CVIS
5/4/2024 5:44:05 AM | Luzon Grid-05/04/2024 05:44: San Gabriel shutdown at 0529H (Reserve Shutdown) [WEBSMS] | CLUZ
5/4/2024 5:39:54 AM | [NSO Update] Mindanao Grid-05/04/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3067MW, PK=2185MW, RR=73MW, NetOpMargin: AM=809, PM=620, EVE=596 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/4/2024 5:37:50 AM | [NSO Update] Visayas Grid-05/04/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2847MW, PK=2225MW, RR=95MW, NetOpMargin: AM=527, PM=169, EVE=169 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @315MW [WEBSMS] | CVIS
5/4/2024 5:35:33 AM | [NSO Update] Luzon Grid-05/04/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15435MW, PK=11642MW, RR=483MW, NetOpMargin: AM=3310, PM=1455, EVE=1075 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/4/2024 5:35:04 AM | Luzon Grid-05/04/2024 05:35: Taytay-Masinag 115kV Line (CO) restored at 0528H (Planned Outage) [WEBSMS] | CLUZ
5/4/2024 5:15:24 AM | Luzon Grid-05/04/2024 05:15: Bolo - Labrador 230kV Line 2 restored at 0514H (Planned Outage) [WEBSMS] | CLUZ
5/4/2024 5:14:19 AM | Visayas Grid-05/04/2024 05:14: 138KV Colon-Dumanjug line 1 de-energized @0514H. ( Planned Outage ) [WEBSMS] | CVIS
5/4/2024 4:10:39 AM | Mindanao Grid-05/04/2024 04:15: Villanueva SS 138kV Bus 1 de-energized at 0408H. (Planned Outage) [WEBSMS] | CMIN
5/4/2024 4:05:44 AM | [NSO Update] Mindanao Grid-05/04/2024 04:10: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
5/4/2024 4:05:28 AM | [NSO Update] Visayas Grid-05/04/2024 04:05: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
5/4/2024 4:04:47 AM | [NSO Update] Luzon Grid-05/04/2024 04:04: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
5/4/2024 3:40:47 AM | Luzon Grid-05/04/2024 03:40: Bolo - Labrador 230kV Line 2 de-energized at 0340H (Planned Outage) [WEBSMS] | CLUZ
5/4/2024 1:34:44 AM | Luzon Grid-05/04/2024 01:34: SBMA - Subic Solar Power 230kV Line (CO) restored at 0132H (Planned Outage) [WEBSMS] | CLUZ
5/4/2024 1:07:15 AM | Luzon Grid-05/04/2024 01:07: Mariveles SS PCB 9-04CB24MAO de-energized at 0106H (Planned Outage) [WEBSMS] | CLUZ
5/4/2024 12:40:59 AM | Luzon Grid-05/04/2024 00:41: Taytay-Masinag 115kV Line (CO) de-energized at 0038H (Planned Outage) [WEBSMS] | CLUZ
5/3/2024 10:50:32 PM | Mindanao Grid-05/03/2024 22:55: WMPC DG10 shutdown at 2246H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/3/2024 10:08:55 PM | Mindanao Grid-05/03/2024 22:14: WMPC DG1 shutdown at 2207H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/3/2024 9:46:57 PM | [NSO Update] Visayas Grid-05/03/2024 21:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2145H with power going to Luzon [WEBSMS] | CVIS
5/3/2024 9:46:42 PM | [NSO Update] Luzon Grid-05/03/2024 21:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2145H with power going to Luzon [WEBSMS] | CLUZ
5/3/2024 9:36:52 PM | [NSO Update] Visayas Grid-05/03/2024 21:36: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2135H from reverse power direction [WEBSMS] | CVIS
5/3/2024 9:36:25 PM | [NSO Update] Luzon Grid-05/03/2024 21:36: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2135H from reverse power direction [WEBSMS] | CLUZ
5/3/2024 8:58:37 PM | Luzon Grid-05/03/2024 20:58: SBMA-Subic Solar Power 230kV Line (CO) de-energized at 2053H (Planned Outage) [WEBSMS] | CLUZ
5/3/2024 6:06:00 PM | [NSO Update] Mindanao Grid-05/03/2024 18:11: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2947MW, PK=2495MW, RR=73MW, NetOpMargin: EVE=379 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/3/2024 6:04:47 PM | [NSO Update] Visayas Grid-05/03/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2729MW, PK=2376MW, RR=94MW, NetOpMargin: EVE=260 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @306MW [WEBSMS] | CVIS
5/3/2024 6:02:20 PM | [NSO Update] Luzon Grid-05/03/2024 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13602MW, PK=12132MW, RR=339MW, NetOpMargin: EVE=1131 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/3/2024 5:35:14 PM | Luzon Grid-05/03/2024 17:35: For info: The Luzon System Frequency reached 60.58Hz at 1723H during the auto-tripping/reclosing of the Malinta-Malabon 115kV Line (Customer Owned) which could have affected voltage sensitive loads. [WEBSMS] | CLUZ
5/3/2024 5:03:01 PM | Mindanao Grid-05/03/2024 17:08: WMPC DG7 shutdown at 1701H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/3/2024 4:23:54 PM | Mindanao Grid-05/03/2024 16:29: WMPC DG4 shutdown at 1620H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/3/2024 3:18:58 PM | Mindanao Grid-05/03/2024 15:24: GNPK Unit 1 online at 1515H. (Unplanned Outage) [WEBSMS] | CMIN
5/3/2024 3:18:00 PM | Mindanao Grid-05/03/2024 15:23: GNPK U1 online at 1515H. (Unplanned Outage) [WEBSMS] | CMIN
5/3/2024 12:52:46 PM | Mindanao Grid-05/03/2024 12:52: WMPV DG4 Online at 1245H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/3/2024 12:47:50 PM | [NSO Update] Mindanao Grid-05/03/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2930MW, PK=2540MW, RR=73MW, NetOpMargin: PM=317, EVE=396 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/3/2024 12:47:40 PM | Mindanao Grid-05/03/2024 12:52: WMPV DG4 Online at 1245H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/3/2024 12:43:24 PM | [NSO Update] Visayas Grid-05/03/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2887MW, PK=2535MW, RR=100MW, NetOpMargin: PM=252, EVE=252 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 300MW [WEBSMS] | CVIS
5/3/2024 12:43:18 PM | [NSO Update] Visayas Grid-05/03/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2887MW, PK=2535MW, RR=100MW, NetOpMargin: PM=252, EVE=252 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 300MW [WEBSMS] | CVIS
5/3/2024 12:42:44 PM | [NSO Update] Mindanao Grid-05/03/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2930MW, PK=2540MW, RR=73MW, NetOpMargin: PM=317, EVE=396 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/3/2024 12:40:29 PM | [NSO Update] Luzon Grid-05/03/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15331MW, PK=13394MW, RR=491MW, NetOpMargin: PM=1446, EVE=1071 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan B @ 500MW [WEBSMS] | CLUZ
5/3/2024 11:57:04 AM | Mindanao Grid-05/03/2024 12:02: Affected ALD feeders of CEPALCO, DLPC and NGCP restored at 1102H, 1109H, and 1111H respectively. [WEBSMS] | CMIN
5/3/2024 11:07:37 AM | Mindanao Grid-05/03/2024 11:12: ALD occurred at NGCP and DLPC system at 1052H due to the tripping of TSI U2 with 151.8MW. The lowest frequency is 59.1Hz. [WEBSMS] | CMIN
5/3/2024 10:37:54 AM | Mindanao Grid-05/03/2024 10:43: WMPC DG7 Online at 1034H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/3/2024 10:17:24 AM | Mindanao Grid-05/03/2024 10:22: Opol SS 75MVA 138/69kV Power Transformer 2 energized at 1014H. (Planned Outage) [WEBSMS] | CMIN
5/3/2024 8:54:44 AM | Mindanao Grid-05/03/2024 08:59: WMPC DG1 Online at 0853H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/3/2024 8:43:51 AM | [NSO Update] Visayas Grid-05/03/2024 08:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0841H with power going to Visayas. [WEBSMS] | CVIS
5/3/2024 8:43:46 AM | [NSO Update] Visayas Grid-05/03/2024 08:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0841H with power going to Visayas. [WEBSMS] | CVIS
5/3/2024 8:43:35 AM | [NSO Update] Luzon Grid-05/03/2024 08:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0841H with power going to Visayas. [WEBSMS] | CLUZ
5/3/2024 8:43:29 AM | [NSO Update] Luzon Grid-05/03/2024 08:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0841H with power going to Visayas. [WEBSMS] | CLUZ
5/3/2024 8:31:47 AM | Mindanao Grid-05/03/2024 08:36: WMPC DG10 Online at 0829H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/3/2024 8:29:27 AM | [NSO Update] Visayas Grid-05/03/2024 08:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0826H from forward power direction. [WEBSMS] | CVIS
5/3/2024 8:29:19 AM | [NSO Update] Luzon Grid-05/03/2024 08:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0826H from forward power direction. [WEBSMS] | CLUZ
5/3/2024 8:29:14 AM | [NSO Update] Luzon Grid-05/03/2024 08:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0826H from forward power direction. [WEBSMS] | CLUZ
5/3/2024 8:15:05 AM | Mindanao Grid-05/03/2024 08:20: Opol SS 75MVA 138/69kV Power Transformer 2 shutdown at 0808H. (Planned Outage) [WEBSMS] | CMIN
5/3/2024 8:13:36 AM | Mindanao Grid-05/03/2024 08:18: Villanueva SS 138kV Bus 2 energized at 0800H. (Planned Outage) [WEBSMS] | CMIN
5/3/2024 7:50:38 AM | Mindanao Grid-05/03/2024 07:55: Therma South Inc. (TSI) Unit 2 online at 0731H. (Unplanned Outage) [WEBSMS] | CMIN
5/3/2024 6:17:30 AM | [NSO Update] Mindanao Grid-05/03/2024 06:22: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2940MW, PK=2391MW, RR=73MW, NetOpMargin: AM=476, PM=270, EVE=335 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW [WEBSMS] | CMIN
5/3/2024 6:14:40 AM | [NSO Update] Visayas Grid-05/03/2024 06:14: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3078MW, PK=2398MW, RR=96MW, NetOpMargin: AM=585, PM=413, EVE=368 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @308MW [WEBSMS] | CVIS
5/3/2024 6:10:12 AM | [NSO Update] Luzon Grid-05/03/2024 06:10: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15251MW, PK=12485MW, RR=491MW, NetOpMargin: AM=2275, PM=1062, EVE=1093 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/3/2024 5:35:40 AM | Luzon Grid-05/03/2024 05:35: Taytay-Masinag 115kV line was restored at 0534H. (Planned Outage) [WEBSMS] | CLUZ
5/3/2024 4:41:50 AM | Mindanao Grid-05/03/2024 04:46: GNPK U1 with a gross gen of 143.80 MW tripped at 0432H with UFR activation [WEBSMS] | CMIN
5/3/2024 4:12:17 AM | [NSO Update] Mindanao Grid-05/03/2024 04:17: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
5/3/2024 4:11:49 AM | Mindanao Grid-05/03/2024 04:16: Villanueva SS 138 kV Bus 2 de-energized at 0411H. Planned Outage [WEBSMS] | CMIN
5/3/2024 4:11:48 AM | [NSO Update] Visayas Grid-05/03/2024 04:11: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
5/3/2024 4:11:02 AM | [NSO Update] Luzon Grid-05/03/2024 04:11: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
5/3/2024 12:47:10 AM | Luzon Grid-05/03/2024 00:47: Taytay-Masinag 115kV line was de-energized at 0039H (Planned Outage-Customer Owned and Maintained Line) [WEBSMS] | CLUZ
5/3/2024 12:28:18 AM | Visayas Grid-05/03/2024 00:28: Colon-Dumanjug 138KV Line 1 energized at 0008H.(Planned Outage) [WEBSMS] | CVIS
5/2/2024 10:19:45 PM | Mindanao Grid-05/02/2024 22:24: WMPC DG10 shutdown at 2217H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/2/2024 9:54:27 PM | Mindanao Grid-05/02/2024 21:59: WMPC DG07 shutdown at 2151H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/2/2024 9:25:41 PM | Mindanao Grid-05/02/2024 21:30: AGUS 6 Unit 1 online at 2118H (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 9:06:49 PM | Mindanao Grid-05/02/2024 21:11: WMPC DG02 end of MRU-System Voltage Requirement at 2100H. Converted to energy (MO dispatch). [WEBSMS] | CMIN
5/2/2024 8:03:46 PM | Luzon Grid-05/02/2024 20:03: Kalayaan Unit 3 tripped at 1956H from 184MW load. The lowest system frequency was 59.493 Hz. (Unplanned Outage-On-going Internal NCC Test) [WEBSMS] | CLUZ
5/2/2024 7:13:47 PM | Visayas Grid-05/02/2024 19:13: Leyte A UMPP Unit#4 cut-in @ 1857H. ( Unplanned Outage ) [WEBSMS] | CVIS
5/2/2024 6:17:43 PM | [NSO Update] Luzon Grid-05/02/2024 18:17: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13485MW, PK=12279MW, RR=389MW, NetOpMargin: EVE=817 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/2/2024 5:55:38 PM | [NSO Update] Mindanao Grid-05/02/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2996MW, PK=2462MW, RR=73MW, NetOpMargin: EVE=461 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @37MW [WEBSMS] | CMIN
5/2/2024 5:54:22 PM | [NSO Update] Visayas Grid-05/02/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2940MW, PK=2361MW, RR=94MW, NetOpMargin: EVE=486 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @295MW [WEBSMS] | CVIS
5/2/2024 5:01:20 PM | Mindanao Grid-05/02/2024 17:06: WMPC DG08 shutdown at 1648H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/2/2024 4:37:40 PM | [NSO Update] Luzon Grid-05/02/2024 16:37: System Advisory: Luzon Grid Yellow Alert Notice issued today has been lifted at 1620H. [WEBSMS] | CLUZ
5/2/2024 3:31:59 PM | Mindanao Grid-05/02/2024 15:37: TM2 Unit 2 shutdown as DR at 1133H. [WEBSMS] | CMIN
5/2/2024 3:07:35 PM | Mindanao Grid-05/02/2024 15:12: WMPC DG08 dispatched as MRU-System Voltage Requirement at 1440H. [WEBSMS] | CMIN
5/2/2024 3:05:34 PM | Mindanao Grid-05/02/2024 15:10: PULANGI 4 Unit 1 shutdown at 1504H due to low forebay elevation (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 2:56:36 PM | Luzon Grid-05/02/2024 14:56: Dasmarinas-TMC II (Ternate) 115kV Line was energized at 1451H. (Planned Outage) [WEBSMS] | CLUZ
5/2/2024 2:52:02 PM | Mindanao Grid-05/02/2024 14:57: WMPC DG01 declared available at 1435H (from Forced Outage). [WEBSMS] | CMIN
5/2/2024 2:39:17 PM | Luzon Grid-05/02/2024 14:39: For info: San Jose 300MVA T01 was paralleled with San Jose 300MVA T02 and T03 at 1431H. San Jose 300MVA T03 was unlooped from the 230kV side at 1433H. [WEBSMS] | CLUZ
5/2/2024 2:38:16 PM | Mindanao Grid-05/02/2024 14:43: TSI /DCP U1 synchronized back the grid at 1434H from unplanned outage. [WEBSMS] | CMIN
5/2/2024 1:01:08 PM | [NSO Update] Mindanao Grid-05/02/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2955MW, PK=2649MW, RR=73MW, NetOpMargin: PM=234, EVE=360 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @37MW [WEBSMS] | CMIN
5/2/2024 12:59:14 PM | [NSO Update] Visayas Grid-05/02/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3010MW, PK=2527MW, RR=100MW, NetOpMargin: PM=383, EVE=288 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @118.5MW, LEYTE A @300MW [WEBSMS] | CVIS
5/2/2024 12:57:46 PM | [NSO Update] Luzon Grid-05/02/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=15154MW, PK=13749MW, RR=491MW, NetOpMargin: PM=913, EVE=670 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/2/2024 12:54:52 PM | Mindanao Grid-05/02/2024 12:59: WMPC DG2 Online at 1247H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/2/2024 12:46:16 PM | Mindanao Grid-05/02/2024 12:51: NEW BATAAN (EURO HYDRO) online at 1145H (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 12:39:17 PM | Mindanao Grid-05/02/2024 12:44: WMPC DG01 declared forced outage at 1232H due to fuel leak (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 12:37:59 PM | Mindanao Grid-05/02/2024 12:43: NEW BATAAN (EURO HYDRO) tripped at 1052H (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 12:35:48 PM | Mindanao Grid-05/02/2024 12:40: MANOLO FORTICH 2 Unit 1 shutdown at 0921H due to insufficient water supply (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 12:01:23 PM | Mindanao Grid-05/02/2024 12:06: AGUS 6 Unit 2 online at 0856H (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 12:00:41 PM | Mindanao Grid-05/02/2024 12:05: SBPI JASAAN BESS online at 0844H (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 11:37:57 AM | Mindanao Grid-05/02/2024 11:43: WMPC DG05 shutdown as DR at 1132H (replacement power of IDPP). [WEBSMS] | CMIN
5/2/2024 11:36:37 AM | Mindanao Grid-05/02/2024 11:41: IDPP end of DR at 1055H (Note: with remaining DR dispatched WMPC DG05 as replacement power). Converted to energy as MO dispatch. [WEBSMS] | CMIN
5/2/2024 11:16:00 AM | Mindanao Grid-05/02/2024 11:21: WMPC DG4 Online at 1108H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/2/2024 11:03:41 AM | [NSO Update] Visayas Grid-05/02/2024 11:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1059H with power going to Visayas. [WEBSMS] | CVIS
5/2/2024 11:03:15 AM | [NSO Update] Luzon Grid-05/02/2024 11:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1059H with power going to Visayas. [WEBSMS] | CLUZ
5/2/2024 10:51:50 AM | [NSO Update] Visayas Grid-05/02/2024 10:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1049H from forward power direction. [WEBSMS] | CVIS
5/2/2024 10:51:27 AM | [NSO Update] Luzon Grid-05/02/2024 10:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1049H from forward power direction. [WEBSMS] | CLUZ
5/2/2024 10:16:18 AM | Mindanao Grid-05/02/2024 10:21: (Correction) DCP (TSI) Unit 2 with 149.8MW load tripped at 0830H. Lowest frequency recorded was 59.103Hz. ALD=51.74MW (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 10:15:08 AM | Mindanao Grid-05/02/2024 10:20: DCP (TSI) Unit 1 with 139MW load tripped at 0832H. Lowest frequency recorded was 58.893Hz. ALD=116.2MW (Unplanned Outage). Note: DCP (TSI) Unit 2 tripped 0830H with ALD=51.74MW, hence, total ALD of 167.94MW. [WEBSMS] | CMIN
5/2/2024 10:12:43 AM | Mindanao Grid-05/02/2024 10:17: DCP (TSI) Unit 2 with 149.8MW load tripped at 0830H. Lowest frequency recorded was 59.103Hz. ALD=51.74Hz (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 10:11:48 AM | Luzon Grid-05/02/2024 10:11: San Gabriel online at 1009H (Planned Outage) [WEBSMS] | CLUZ
5/2/2024 10:06:12 AM | Mindanao Grid-05/02/2024 10:11: Affected ALD feeders of CEPALCO, DLPC, and NGCP were restored at 0838H, 0924H, and 0925H respectively. (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 10:04:07 AM | Mindanao Grid-05/02/2024 10:09: Correction: ALD occurred at NGCP and DLPC and CEPALCO system at 0830H due to the tripping of TSI U2 with 149.8MW. The lowest frequency is 59.1Hz (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 9:45:12 AM | Mindanao Grid-05/02/2024 09:50: AGUS 6 Unit 2 online at 0856H (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 9:44:30 AM | Mindanao Grid-05/02/2024 09:49: AGUS 6 Unit 2 with 10MW load isolated at 0832H due to ALD of Agus --Kauswagan 69 kV feeder (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 9:34:39 AM | Mindanao Grid-05/02/2024 09:39: TM2 Unit 2 online as DR at 0917H. [WEBSMS] | CMIN
5/2/2024 9:34:05 AM | Visayas Grid-05/02/2024 09:34: Sangi-2nd Lift 34.5 kV Line restored at 0931H. (Unplanned Outage) [WEBSMS] | CVIS
5/2/2024 9:22:43 AM | Mindanao Grid-05/02/2024 09:27: MPC (IDPP) online as DR at 0914H. [WEBSMS] | CMIN
5/2/2024 9:22:02 AM | Mindanao Grid-05/02/2024 09:27: WMPC DG05 online as DR at 0907H (Note: DR replacement for IDPP DG02, 05). [WEBSMS] | CMIN
5/2/2024 9:14:26 AM | Mindanao Grid-05/02/2024 09:19: SBPI JASAAN BESS with 19.5MW load tripped at 0837H. Indication: low frequency (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 9:11:57 AM | Mindanao Grid-05/02/2024 09:17: Agus 6 U2 14.5MW load tripped(affected) at 0832H. (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 9:08:01 AM | Luzon Grid-05/02/2024 09:08: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0906H (Planned Outage) [WEBSMS] | CLUZ
5/2/2024 9:06:12 AM | Mindanao Grid-05/02/2024 09:11: ALD occurred at NGCP and DLPC and CEPALCO system at 0832H due to tripping of TSI U1 with 149.8MW. The lowest frequency recorded is 58.9Hz. (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 9:02:34 AM | Mindanao Grid-05/02/2024 09:07: ALD occurred at NGCP and DLPC and CEPALCO system at 0830H due to tripping of TSI U1 with 149.8MW. The lowest frequency is 59.1Hz [WEBSMS] | CMIN
5/2/2024 8:37:55 AM | Mindanao Grid-05/02/2024 08:42: WMPC DG10 Online at 0832H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/2/2024 8:37:44 AM | Visayas Grid-05/02/2024 08:37: Sangi-2nd Lift 34.5 kV Line tripped at 0759H. (Unplanned Outage) [WEBSMS] | CVIS
5/2/2024 8:26:14 AM | Mindanao Grid-05/02/2024 08:31: Marawi Switchyard 50MVA 138/69kV Power Transformer 1 tripped at 0809H. (Unplanned Outage) [WEBSMS] | CMIN
5/2/2024 6:01:36 AM | [NSO Update] Luzon Grid-05/02/2024 06:01: System Advisory: 02-May-2024, Luzon Grid is on YELLOW Alert for interval hour 1600H. Total capacity on forced outage is 1269.3MW. Total of de-rated capacity is 100MW. [WEBSMS] | CLUZ
5/2/2024 5:57:45 AM | [NSO Update] Luzon Grid-05/02/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=15516MW, PK=12888MW, RR=400MW, NetOpMargin: AM=2228, PM=807, EVE=679 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/2/2024 5:28:45 AM | [NSO Update] Mindanao Grid-05/02/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3219MW, PK=2465MW, RR=73MW, NetOpMargin: AM=681, PM=645, EVE=747 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @37MW [WEBSMS] | CMIN
5/2/2024 5:25:22 AM | [NSO Update] Visayas Grid-05/02/2024 05:25: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2842MW, PK=2381MW, RR=96MW, NetOpMargin: AM=365, PM=296, EVE=228 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @118MW, LEYTE A @290MW [WEBSMS] | CVIS
5/2/2024 4:31:36 AM | Luzon Grid-05/02/2024 04:31: San Gabriel shutdown at 0430H (Reserved Shutdown) [WEBSMS] | CLUZ
5/2/2024 4:15:13 AM | [NSO Update] Mindanao Grid-05/02/2024 04:20: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
5/2/2024 4:14:22 AM | [NSO Update] Visayas Grid-05/02/2024 04:14: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
5/2/2024 4:13:51 AM | [NSO Update] Luzon Grid-05/02/2024 04:13: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
5/2/2024 12:01:50 AM | Mindanao Grid-05/02/2024 00:06: Agus 6 SS 100MVA Power Transformer No. 3 energized for the first time at 2358H. [WEBSMS] | CMIN
5/1/2024 11:06:31 PM | Mindanao Grid-05/01/2024 23:11: Therma South Inc. (TSI) Unit 2 online at 2255H. (Unplanned Outage) [WEBSMS] | CMIN
5/1/2024 10:05:41 PM | Mindanao Grid-05/01/2024 22:10: WMPC DG10 shutdown at 2144H from MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/1/2024 9:26:56 PM | [NSO Update] Luzon Grid-05/01/2024 21:26: System Advisory: Luzon Grid Yellow Alert notice issued today has been lifted at 2120H. [WEBSMS] | CLUZ
5/1/2024 8:43:28 PM | Mindanao Grid-05/01/2024 20:48: Therma South Inc. (TSI) Unit 2 with gross generation of 150.24MW tripped at 2022H. System frequency dipped to a low of 59.098Hz. ALD of 47.09MW Unplanned Outage. [WEBSMS] | CMIN
5/1/2024 8:06:03 PM | Mindanao Grid-05/01/2024 20:11: WMPC DG4 shutdown at 1943H. from MRU - System Voltage Requirement. [WEBSMS] | CMIN
5/1/2024 6:19:34 PM | Mindanao Grid-05/01/2024 18:24: AGUS 1 Unit 1 HEP online at 1812 from PMS-GOMP (Planned Outage) [WEBSMS] | CMIN
5/1/2024 6:04:59 PM | [NSO Update] Mindanao Grid-05/01/2024 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3125MW, PK=2306MW, RR=73MW, NetOpMargin: EVE=746 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @37MW [WEBSMS] | CMIN
5/1/2024 6:04:20 PM | Luzon Grid-05/01/2024 18:04: San Gabriel online at 1801H (Unplanned Outage) [WEBSMS] | CLUZ
5/1/2024 6:03:32 PM | Mindanao Grid-05/01/2024 18:08: AGUS6 U2 online at 1746H. (Planned Outage) [WEBSMS] | CMIN
5/1/2024 6:03:06 PM | [NSO Update] Visayas Grid-05/01/2024 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2607MW, PK=2261MW, RR=94MW, NetOpMargin: EVE=252 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @305MW [WEBSMS] | CVIS
5/1/2024 6:02:00 PM | [NSO Update] Luzon Grid-05/01/2024 18:02: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=13056MW, PK=12067MW, RR=429MW, NetOpMargin: EVE=561 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/1/2024 5:31:01 PM | Mindanao Grid-05/01/2024 17:36: Agus 6 SY - Agus 6 HEP 69kV L2 energized at 1728H (Planned Outage) [WEBSMS] | CMIN
5/1/2024 4:41:16 PM | Luzon Grid-05/01/2024 16:41: Botolan-Labrador 230kV Line restored at 1641H (Planned Outage) [WEBSMS] | CLUZ
5/1/2024 4:36:27 PM | Mindanao Grid-05/01/2024 16:41: Agus 6 SS 138kV Bus No. 2 at 1632H (Planned Outage) [WEBSMS] | CMIN
5/1/2024 4:32:34 PM | Luzon Grid-05/01/2024 16:32: Binan-Muntinlupa 230kV Line 3 restored at 1631H (Planned Outage) [WEBSMS] | CLUZ
5/1/2024 4:08:47 PM | Luzon Grid-05/01/2024 16:08: San Jose-Angat 115kV line 4 restored at 1606H (Unplanned Outage) [WEBSMS] | CLUZ
5/1/2024 3:53:48 PM | Mindanao Grid-05/01/2024 15:58: AGUS6 U1 shutdown at 1428H due to low forebay elevation(OMC). [WEBSMS] | CMIN
5/1/2024 3:46:20 PM | Mindanao Grid-05/01/2024 15:51: Maramag - Kibawe 138kV L1 energized at 1543H. (Planned Outage) [WEBSMS] | CMIN
5/1/2024 3:16:17 PM | Luzon Grid-05/01/2024 15:16: San Jose-Angat 115kV line 4 tripped at 1512H (Unplanned Outage) [WEBSMS] | CLUZ
5/1/2024 2:16:40 PM | Luzon Grid-05/01/2024 14:16: Santiago 230kV Bus 2 restored at 1416H (Planned Outage) [WEBSMS] | CLUZ
5/1/2024 1:54:08 PM | Mindanao Grid-05/01/2024 13:59: WMPC DG04 online at 1338H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/1/2024 1:51:38 PM | Luzon Grid-05/01/2024 13:51: San Jose-Angat 115kV line 2 restored at 1349H (Planned Outage) [WEBSMS] | CLUZ
5/1/2024 1:50:20 PM | Luzon Grid-05/01/2024 13:50: San Jose 300MVA T01 energized 1346H (Planned Outage) [WEBSMS] | CLUZ
5/1/2024 1:49:22 PM | Mindanao Grid-05/01/2024 13:54: Agus 6 SS 138kV Bus No. 2 de-energized at 1339H. (Planned Outage) [WEBSMS] | CMIN
5/1/2024 1:08:41 PM | [NSO Update] Visayas Grid-05/01/2024 13:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1304H with power going to Luzon. [WEBSMS] | CVIS
5/1/2024 1:08:15 PM | [NSO Update] Luzon Grid-05/01/2024 13:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1304H with power going to Luzon. [WEBSMS] | CLUZ
5/1/2024 1:05:58 PM | [NSO Update] Visayas Grid-05/01/2024 13:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1254H from reverse power direction. [WEBSMS] | CVIS
5/1/2024 1:05:38 PM | [NSO Update] Luzon Grid-05/01/2024 13:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1254H from reverse power direction. [WEBSMS] | CLUZ
5/1/2024 1:04:45 PM | Mindanao Grid-05/01/2024 13:09: Maramag - Kibawe 138kV L1 de-energized at 1303H. (Planned Outage) [WEBSMS] | CMIN
5/1/2024 12:51:27 PM | [NSO Update] Mindanao Grid-05/01/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3196MW, PK=2173MW, RR=73MW, NetOpMargin: PM=950, EVE=844 Highest Unit O/L: GNPK 1,2,3&4 Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @37MW [WEBSMS] | CMIN
5/1/2024 12:49:39 PM | [NSO Update] Visayas Grid-05/01/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2822MW, PK=2252MW, RR=96MW, NetOpMargin: PM=475, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @118MW, LEYTE A @290MW [WEBSMS] | CVIS
5/1/2024 12:47:27 PM | [NSO Update] Luzon Grid-05/01/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14826MW, PK=11886MW, RR=351MW, NetOpMargin: PM=2589, EVE=479 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
5/1/2024 12:11:23 PM | Mindanao Grid-05/01/2024 12:16: PULANGI 4 Unit 1 online at 1202H. (Planned Outage) [WEBSMS] | CMIN
5/1/2024 10:59:16 AM | Luzon Grid-05/01/2024 10:59: Binga 230kV Bus 2 restored at 1059H (Planned Outage) [WEBSMS] | CLUZ
5/1/2024 10:58:14 AM | Visayas Grid-05/01/2024 10:58: TGPP U2 cut-in at 1055H (Unplanned Outage) [WEBSMS] | CVIS
5/1/2024 9:57:11 AM | Luzon Grid-05/01/2024 09:57: San Jose 230kV Bus 1 restored at 0951H (Planned Outage) [WEBSMS] | CLUZ
5/1/2024 9:47:28 AM | [NSO Update] Mindanao Grid-05/01/2024 09:52: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0939H with power going to Visayas. [WEBSMS] | CMIN
5/1/2024 9:47:08 AM | [NSO Update] Visayas Grid-05/01/2024 09:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0939H with power going to Visayas. [WEBSMS] | CVIS
5/1/2024 9:33:11 AM | Mindanao Grid-05/01/2024 09:38: WMPC DG10 online at 0929H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
5/1/2024 9:21:41 AM | [NSO Update] Mindanao Grid-05/01/2024 09:26: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0918H from forward power direction. [WEBSMS] | CMIN
5/1/2024 9:20:17 AM | [NSO Update] Visayas Grid-05/01/2024 09:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0918H from forward power direction. [WEBSMS] | CVIS
5/1/2024 9:14:28 AM | Visayas Grid-05/01/2024 09:14: TGPP U2 tripped at 0910H (Unplanned Outage) [WEBSMS] | CVIS
5/1/2024 8:39:02 AM | [NSO Update] Visayas Grid-05/01/2024 08:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0836H with power going to Visayas. [WEBSMS] | CVIS
5/1/2024 8:38:29 AM | [NSO Update] Luzon Grid-05/01/2024 08:38: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0836H with power going to Visayas. [WEBSMS] | CLUZ
5/1/2024 8:12:22 AM | Mindanao Grid-05/01/2024 08:17: PULANGI 4 Unit 1 shutdown at 0802H. (Planned Outage) [WEBSMS] | CMIN
5/1/2024 7:56:23 AM | [NSO Update] Luzon Grid-05/01/2024 07:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0746H from forward power direction. [WEBSMS] | CLUZ
5/1/2024 7:54:42 AM | [NSO Update] Visayas Grid-05/01/2024 07:54: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0746H from forward power direction. [WEBSMS] | CVIS
5/1/2024 7:53:20 AM | Mindanao Grid-05/01/2024 07:58: PULANGI 4 Unit 2 online at 0742H from OMC Outage. (Unplanned Outage) [WEBSMS] | CMIN
5/1/2024 7:52:51 AM | Mindanao Grid-05/01/2024 07:57: Agus 6 SY - Agus 6 HEP 69kV L2 de-energized at 0742H. (Planned Outage) [WEBSMS] | CMIN
5/1/2024 7:41:15 AM | Mindanao Grid-05/01/2024 07:46: AGUS 6 Unit 2 shutdown at 0715H. (Planned Outage) [WEBSMS] | CMIN
5/1/2024 6:50:47 AM | Luzon Grid-05/01/2024 06:50: Binga 230kV Bus 2 de-energized at 0647H (Planned Outage) [WEBSMS] | CLUZ
5/1/2024 6:36:02 AM | Luzon Grid-05/01/2024 06:36: Santiago 230kV Bus 2 de-energized at 0634H (Planned Outage) [WEBSMS] | CLUZ
5/1/2024 6:33:45 AM | Luzon Grid-05/01/2024 06:33: San Gabriel shutdown at 0631H (Unplanned Outage) [WEBSMS] | CLUZ
5/1/2024 6:30:27 AM | Luzon Grid-05/01/2024 06:30: Binan-Muntinlupa 230kV Line 3 de-energized at 0629H (Planned Outage) [WEBSMS] | CLUZ
5/1/2024 6:13:54 AM | Luzon Grid-05/01/2024 06:13: Botolan-Labrador 230kV Line de-energized at 0610H (Planned Outage) [WEBSMS] | CLUZ
5/1/2024 5:47:19 AM | [NSO Update] Luzon Grid-05/01/2024 05:47: System Advisory: Luzon Grid is on YELLOW Alert for interval hours 2100H-2200H. Total capacity on forced outage is 1269.3MW. Total of de-rated capacity is 140MW. [WEBSMS] | CLUZ
5/1/2024 5:45:43 AM | [NSO Update] Luzon Grid-05/01/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=15541MW, PK=11855MW, RR=423MW, NetOpMargin: AM=3263, PM=1686, EVE=267 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 500MW, Calaca 1 @ 200MW [WEBSMS] | CLUZ
5/1/2024 5:34:39 AM | [NSO Update] Mindanao Grid-05/01/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3149MW, PK=2060MW, RR=73MW, NetOpMargin: AM=1017, PM=876, EVE=849 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @37MW [WEBSMS] | CMIN
5/1/2024 5:33:08 AM | [NSO Update] Visayas Grid-05/01/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2987MW, PK=2284MW, RR=95MW, NetOpMargin: AM=608, PM=513, EVE=228 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @295MW, CEDC U3 @75MW, Panay Diesel 3-E @11MW, Panay Diesel 1-U2 @4.5MW, Nasulo Geo @41MW, Power Barge 104-U2 @5MW, Power Barge 104-U3 @5MW, Panay Diesel 1-U5 @4MW [WEBSMS] | CVIS
5/1/2024 4:25:09 AM | [NSO Update] Mindanao Grid-05/01/2024 04:30: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
5/1/2024 4:24:53 AM | [NSO Update] Visayas Grid-05/01/2024 04:24: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
5/1/2024 4:24:38 AM | [NSO Update] Luzon Grid-05/01/2024 04:24: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
5/1/2024 12:27:08 AM | Luzon Grid-05/01/2024 00:27: San Jose 300MVA T01 was de-energized at 0026H. (Planned Outage) [WEBSMS] | CLUZ
5/1/2024 12:23:02 AM | Luzon Grid-05/01/2024 00:23: San Jose-Angat 115kV line 2 was de-energized at 0021H. (Planned Outage) [WEBSMS] | CLUZ
4/30/2024 11:47:29 PM | Luzon Grid-04/30/2024 23:47: San Jose 230kV Bus 1 was de-energized at 2346H. (Planned Outage) [WEBSMS] | CLUZ
4/30/2024 11:19:26 PM | [NSO Update] Luzon Grid-04/30/2024 23:19: System Advisory: Luzon Grid Yellow Alert notice issued today has been lifted at 2318H. [WEBSMS] | CLUZ
4/30/2024 10:18:17 PM | Mindanao Grid-04/30/2024 22:23: WMPC DG10 shutdown at 2216H. From MRU-System Voltage Requirement. [WEBSMS] | CMIN
4/30/2024 9:15:23 PM | Mindanao Grid-04/30/2024 21:20: MANOLO FORTICH 2 Unit 1 online at 2114H (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 8:24:45 PM | [NSO Update] Visayas Grid-04/30/2024 20:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2019H with power going to Luzon [WEBSMS] | CVIS
4/30/2024 8:24:05 PM | [NSO Update] Luzon Grid-04/30/2024 20:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2019H with power going to Luzon [WEBSMS] | CLUZ
4/30/2024 8:20:39 PM | Mindanao Grid-04/30/2024 20:25: WMPC DG4 shutdown at 2017H. from MRU - System Voltage Requirement. [WEBSMS] | CMIN
4/30/2024 8:12:15 PM | [NSO Update] Visayas Grid-04/30/2024 20:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2009H from reverse power direction [WEBSMS] | CVIS
4/30/2024 8:11:27 PM | [NSO Update] Luzon Grid-04/30/2024 20:11: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2009H from reverse power direction [WEBSMS] | CLUZ
4/30/2024 6:17:58 PM | [NSO Update] Luzon Grid-04/30/2024 18:18: Update on System Advisory: 30-Apr-2024, Luzon Grid is on YELLOW Alert for interval hours 1900H-2300H. Total capacity on forced outage is 1269.3MW. Total of de-rated capacity is 100MW [WEBSMS] | CLUZ
4/30/2024 5:46:01 PM | [NSO Update] Mindanao Grid-04/30/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2939MW, PK=2216MW, RR=73MW, NetOpMargin: EVE=650 Highest Unit O/L: GNPK 1,2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @37MW [WEBSMS] | CMIN
4/30/2024 5:43:15 PM | [NSO Update] Visayas Grid-04/30/2024 17:43: GRID UPDATE AS OF Invalid date System Condition: NORMAL CAP=2729MW, PK=229MW, RR=95MW, Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @302MW, CEDC U3 @75MW, Tongonan Power Plant @117MW, Panay Diesel 3-E @11MW, Panay Diesel 1-U5 @4.5MW, Nasulo Geo @41MW, Power Barge 104-U2 @5MW, Power Barge 104-U3 @5MW, GTEC @5MW [WEBSMS] | CVIS
4/30/2024 5:40:31 PM | [NSO Update] Luzon Grid-04/30/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=13084MW, PK=12720MW, RR=335MW, NetOpMargin: EVE=29 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
4/30/2024 3:38:27 PM | Mindanao Grid-04/30/2024 15:43: NEW BATAAN (EURO HYDRO) online at 1520H (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 3:08:39 PM | Visayas Grid-04/30/2024 15:08: MLD of 3.6 MW total load for MECO, advise to restore at 1500H to prevent overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
4/30/2024 3:02:43 PM | Mindanao Grid-04/30/2024 15:07: WMPC DG7 Shutdown at 1500H. From MRU - System Voltage Requirement. [WEBSMS] | CMIN
4/30/2024 2:55:09 PM | Mindanao Grid-04/30/2024 15:00: GNPK Unit 3 online at 1452H (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 2:54:11 PM | Mindanao Grid-04/30/2024 14:59: NEW BATAAN (EURO HYDRO) with 1.02MW isolated at 1254H due to NORDECO feeder outage (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 2:03:50 PM | [NSO Update] Visayas Grid-04/30/2024 14:04: SO initiated Market Intervention for Visayas has been lifted today at 1401H. Market operations will resume starting interval 1410H. [WEBSMS] | CVIS
4/30/2024 1:54:31 PM | [NSO Update] Visayas Grid-04/30/2024 13:54: [ERRATUM] SO initiated Market Intervention for Visayas is issued today at starting interval 1340H due to MLD implementation to prevent overloading of Cebu-Mandaue 138kV Line [WEBSMS] | CVIS
4/30/2024 1:52:34 PM | [NSO Update] Visayas Grid-04/30/2024 13:52: SO initiated Market Intervention for Visayas is issued today at starting interval 1340H due to MLD implementation to prevent overloading of Cebu-Mandaue 230kV Line [WEBSMS] | CVIS
4/30/2024 1:46:53 PM | Visayas Grid-04/30/2024 13:47: Implemented Manual Load Dropping of 3.6 MW total load starting 1335H, affected customer - MECO, overloading of Cebu - Mandaue 138 kV Line 2 [WEBSMS] | CVIS
4/30/2024 1:34:29 PM | Mindanao Grid-04/30/2024 13:39: (Correction) SUPREME POWER MATI online at 1316H (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 1:16:01 PM | Mindanao Grid-04/30/2024 13:21: SUPREME POWER MATI online at 1255H (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 1:09:23 PM | [NSO Update] Visayas Grid-04/30/2024 13:09: Update on System Advisory: Visayas Grid Yellow Alert notice issued today has been lifted at 1300H. [WEBSMS] | CVIS
4/30/2024 1:06:34 PM | [NSO Update] Visayas Grid-04/30/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2899MW, PK=2629MW, RR=100MW, NetOpMargin: PM=170, EVE=203 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @302MW, CEDC U3 @75MW, Tongonan Power Plant @117MW, Panay Diesel 3-E @11MW, Panay Diesel 1-U5 @4.5MW, Nasulo Geo @41MW, Power Barge 104-U2 @5MW, Power Barge 104-U3 @5MW, GTEC @5MW [WEBSMS] | CVIS
4/30/2024 1:00:57 PM | [NSO Update] Mindanao Grid-04/30/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2974MW, PK=2401MW, RR=73MW, NetOpMargin: PM=500, EVE=506 Highest Unit O/L: GNPK 1,2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @37MW [WEBSMS] | CMIN
4/30/2024 12:58:29 PM | [NSO Update] Luzon Grid-04/30/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14960MW, PK=13903MW, RR=441MW, NetOpMargin: PM=616, EVE=742 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
4/30/2024 12:38:36 PM | Mindanao Grid-04/30/2024 12:43: SUPREME POWER MATI with 3.2MW load isolated at 1225H due to Maco-Banaybanay 69 kV line outage (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 12:29:36 PM | Mindanao Grid-04/30/2024 12:34: MANOLO FORTICH 1 Unit 3 online at 1209H. Cause: Nozzle #5 failure (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 11:54:26 AM | Mindanao Grid-04/30/2024 11:59: LIBERTAD POWER online at 1145H (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 10:35:11 AM | Luzon Grid-04/30/2024 10:35: For info: San Gabriel online at 1000H (Reserve Shutdown) [WEBSMS] | CLUZ
4/30/2024 10:33:58 AM | Luzon Grid-04/30/2024 10:34: For info: San Gabriel online at 1000H (Reserve Shutdown) [WEBSMS] | CLUZ
4/30/2024 10:33:28 AM | Mindanao Grid-04/30/2024 10:38: WMPC DG7 online at 1031H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
4/30/2024 10:20:10 AM | Mindanao Grid-04/30/2024 10:25: MANOLO FORTICH 1 Unit 3 with 4.5MW load tripped at 1008H (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 9:02:18 AM | Mindanao Grid-04/30/2024 09:07: WMPC DG4 Online at 0900H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
4/30/2024 8:31:47 AM | Mindanao Grid-04/30/2024 08:37: WMPC DG10 online at 0830H. MRU - System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 8:27:56 AM | Mindanao Grid-04/30/2024 08:33: TALOMO 1 Unit 2 online at 0815H (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 8:21:39 AM | [NSO Update] Luzon Grid-04/30/2024 08:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0816H with power going to Visayas. [WEBSMS] | CLUZ
4/30/2024 8:21:21 AM | [NSO Update] Visayas Grid-04/30/2024 08:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0816H with power going to Visayas. [WEBSMS] | CVIS
4/30/2024 8:15:13 AM | Mindanao Grid-04/30/2024 08:20: LAKE MAINIT online at 0741H. Note: Plant tripped at 0440H (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 8:11:41 AM | [NSO Update] Luzon Grid-04/30/2024 08:11: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0806H from forward power direction. [WEBSMS] | CLUZ
4/30/2024 8:10:35 AM | [NSO Update] Visayas Grid-04/30/2024 08:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0806H from forward power direction. [WEBSMS] | CVIS
4/30/2024 7:22:00 AM | Mindanao Grid-04/30/2024 07:27: ASIGA online at 0718H. Note: Plant tripped at 0440H (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 7:00:36 AM | Luzon Grid-04/30/2024 07:00: San Gabriel shutdown at 0658H (Reserve Shutdown) [WEBSMS] | CLUZ
4/30/2024 6:05:53 AM | [NSO Update] Visayas Grid-04/30/2024 06:06: System Advisory: Visayas Grid is on YELLOW Alert for interval 1400H-1600H, 1900H and 2100H. Total capacity on forced outage is 364.3MW. Total of de-rated capacity is 207.6MW. [WEBSMS] | CVIS
4/30/2024 6:04:21 AM | [NSO Update] Luzon Grid-04/30/2024 06:04: System Advisory: Luzon Grid is on YELLOW Alert for interval hours 1500H-1600H and 2100H-2200H. Total capacity on forced outage is 1269.3MW. Total of de-rated capacity is 100MW. [WEBSMS] | CLUZ
4/30/2024 5:56:36 AM | [NSO Update] Luzon Grid-04/30/2024 05:56: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=15339MW, PK=12608MW, RR=334MW, NetOpMargin: AM=2396, PM=607, EVE=120 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 500MW [WEBSMS] | CLUZ
4/30/2024 5:53:03 AM | [NSO Update] Visayas Grid-04/30/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=3038MW, PK=2496MW, RR=95MW, NetOpMargin: AM=447, PM=200, EVE=216 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, Tongonan Power Plant @117MW, Panay Diesel 3-E @11MW, Panay Diesel 1-U5 @4.5MW, Nasulo Geo @41MW, Power Barge 104-U2 @5MW, Power Barge 104-U3 @5MW [WEBSMS] | CVIS
4/30/2024 5:49:18 AM | [NSO Update] Mindanao Grid-04/30/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2821MW, PK=2510MW, RR=73MW, NetOpMargin: AM=237, PM=152, EVE=287 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.5MW, MA2 @37MW, GNPK 4 @61MW [WEBSMS] | CMIN
4/30/2024 4:39:53 AM | Mindanao Grid-04/30/2024 04:45: AGUS 6 HEP Unit 1 online at 2350H from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
4/30/2024 4:17:58 AM | [NSO Update] Mindanao Grid-04/30/2024 04:23: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
4/30/2024 4:17:23 AM | [NSO Update] Visayas Grid-04/30/2024 04:17: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
4/30/2024 4:17:02 AM | [NSO Update] Luzon Grid-04/30/2024 04:17: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
4/30/2024 4:08:28 AM | Mindanao Grid-04/30/2024 04:13: STEAG Unit 1 online at 0405H from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
4/29/2024 11:23:31 PM | [NSO Update] Luzon Grid-04/29/2024 23:23: System Advisory: Luzon Grid Yellow Alert notice issued today has been lifted at 2321H. [WEBSMS] | CLUZ
4/29/2024 9:20:27 PM | Mindanao Grid-04/29/2024 21:25: WMPC DG09 shutdown at 1846H - MO Dispatched. [WEBSMS] | CMIN
4/29/2024 9:19:38 PM | Mindanao Grid-04/29/2024 21:24: WMPC DG08 shutdown at 1847H - MO Dispatched. [WEBSMS] | CMIN
4/29/2024 9:18:52 PM | Mindanao Grid-04/29/2024 21:24: WMPC DG07 shutdown at 1847H - MO Dispatched. [WEBSMS] | CMIN
4/29/2024 9:18:08 PM | Mindanao Grid-04/29/2024 21:23: WMPC DG02 shutdown at 1850H - MO Dispatched. [WEBSMS] | CMIN
4/29/2024 9:07:42 PM | [NSO Update] Visayas Grid-04/29/2024 21:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2105H with power going to Luzon. [WEBSMS] | CVIS
4/29/2024 9:07:28 PM | [NSO Update] Luzon Grid-04/29/2024 21:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2105H with power going to Luzon. [WEBSMS] | CLUZ
4/29/2024 8:55:03 PM | [NSO Update] Visayas Grid-04/29/2024 20:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2053H from reverse power direction. [WEBSMS] | CVIS
4/29/2024 8:54:49 PM | [NSO Update] Luzon Grid-04/29/2024 20:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2053H from reverse power direction. [WEBSMS] | CLUZ
4/29/2024 7:58:05 PM | [NSO Update] Visayas Grid-04/29/2024 19:58: System Advisory: Visayas Grid Yellow Alert notice issued today has been lifted at 1956H. [WEBSMS] | CVIS
4/29/2024 7:03:26 PM | Mindanao Grid-04/29/2024 19:08: AGUS 6 HEP Unit 1 with load of 20MW tripped at 1843H. Indication: Generator upper guide bearing too high tempt trip. (Unplanned Outage) [WEBSMS] | CMIN
4/29/2024 6:36:09 PM | Mindanao Grid-04/29/2024 18:41: Peak Power Socsargen online at 1755H - MO Dispatched. [WEBSMS] | CMIN
4/29/2024 6:32:57 PM | Mindanao Grid-04/29/2024 18:38: WMPC DG02 online at 1825H - MO Dispatched. [WEBSMS] | CMIN
4/29/2024 6:32:19 PM | Mindanao Grid-04/29/2024 18:37: WMPC DG08 online at 1823H - MO Dispatched. [WEBSMS] | CMIN
4/29/2024 6:29:44 PM | Mindanao Grid-04/29/2024 18:34: WMPC DG07 online at 1822H - MO Dispatched. [WEBSMS] | CMIN
4/29/2024 6:29:00 PM | Mindanao Grid-04/29/2024 18:34: WMPC DG02 online at 1821H - MO Dispatched. [WEBSMS] | CMIN
4/29/2024 5:55:36 PM | [NSO Update] Luzon Grid-04/29/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=13684MW, PK=12632MW, RR=377MW, NetOpMargin: EVE=674 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 500MW [WEBSMS] | CLUZ
4/29/2024 5:52:42 PM | [NSO Update] Visayas Grid-04/29/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2614MW, PK=2367MW, RR=95MW, NetOpMargin: EVE=152 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @306MW, CEDC U3 @75MW, Tongonan Power Plant @110MW, Panay Diesel 3-E @9MW, Panay Diesel 1-U5 @4.5MW, Nasulo Geo @41MW, Power Barge 104-U2 @5MW, Power Barge 104-U3 @5MW [WEBSMS] | CVIS
4/29/2024 5:41:59 PM | [NSO Update] Mindanao Grid-04/29/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2765MW, PK=2395MW, RR=73MW, NetOpMargin: EVE=297 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @28.9MW, MA1 @48.5MW, MA2 @37MW, GNPK 4 @61MW [WEBSMS] | CMIN
4/29/2024 4:23:10 PM | Visayas Grid-04/29/2024 16:23: Mandaue GIS fdr 5 and fdr 2 energized at 1603H/1617H respectively (Unplanned Outage) [WEBSMS] | CVIS
4/29/2024 3:17:37 PM | Visayas Grid-04/29/2024 15:17: Magdugo-Cebu 230KV Line 2 energized at 1458H(Unplanned Outage) [WEBSMS] | CVIS
4/29/2024 2:33:22 PM | Visayas Grid-04/29/2024 14:33: Cebu-Magdugo 230 KV Line 2 and Cebu-Mandaue 138 KV Line 1 tripped at 1352H, affecting Mandaue fdr 5 with a load of 66.77 MW due to SIPS activation. [WEBSMS] | CVIS
4/29/2024 2:06:47 PM | Mindanao Grid-04/29/2024 14:12: AGUS 5 Unit 1 with 10MW load shutdown at 1402H due to low forebay elevation. (Unplanned Outage) [WEBSMS] | CMIN
4/29/2024 2:01:15 PM | Mindanao Grid-04/29/2024 14:06: TMI 1 Unit 2 online at 1340H. MO Dispatched. [WEBSMS] | CMIN
4/29/2024 1:57:05 PM | Mindanao Grid-04/29/2024 14:02: TMI 2 Unit 1 online at 1302H. MO Dispatched. [WEBSMS] | CMIN
4/29/2024 1:52:20 PM | Mindanao Grid-04/29/2024 13:57: NACSUR Online at 1200H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
4/29/2024 1:37:43 PM | Mindanao Grid-04/29/2024 13:42: WMPC DG10 with 10MW gross generation and run as MRU-System Voltage Requirement tripped at 1309H. Unplanned Outage. [WEBSMS] | CMIN
4/29/2024 1:27:28 PM | [NSO Update] Mindanao Grid-04/29/2024 13:32: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1320H with power going to Visayas. [WEBSMS] | CMIN
4/29/2024 1:27:20 PM | [NSO Update] Visayas Grid-04/29/2024 13:27: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1320H with power going to Visayas. [WEBSMS] | CVIS
4/29/2024 1:25:03 PM | [NSO Update] Visayas Grid-04/29/2024 13:25: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1310H from reverse power direction. [WEBSMS] | CVIS
4/29/2024 1:24:59 PM | [NSO Update] Mindanao Grid-04/29/2024 13:30: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1310H from reverse power direction. [WEBSMS] | CMIN
4/29/2024 1:08:22 PM | [NSO Update] Luzon Grid-04/29/2024 13:08: Update on System Advisory: 29-Apr-2024, Luzon Grid is on YELLOW Alert for interval hours 1500H-1700H and 1900H-2300H. Total capacity on forced outage is 1343.3MW. Total of de-rated capacity is 100MW. [WEBSMS] | CLUZ
4/29/2024 1:02:27 PM | [NSO Update] Visayas Grid-04/29/2024 13:02: System Advisory: 29-Apr-2024, Visayas Grid is on YELLOW Alert for interval hours 1400H, 1500H, 1600H, 1900H and 2000H. Total capacity on forced outage is 335.3MW. Total of de-rated capacity is 282.6MW. [WEBSMS] | CVIS
4/29/2024 12:57:15 PM | [NSO Update] Visayas Grid-04/29/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2835MW, PK=2596MW, RR=100MW, NetOpMargin: PM=139, EVE=175 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @240MW, CEDC U3 @75MW, Tongonan Power Plant @110MW, Panay Diesel 1-U2 @4.5MW, Panay Diesel 1-U5 @4MW, Nasulo Geo @41MW, Power Barge 104-U2 @5MW, Power Barge 104-U3 @5MW (Total deration: 279.6MW) [WEBSMS] | CVIS
4/29/2024 12:53:20 PM | [NSO Update] Luzon Grid-04/29/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14952MW, PK=13893MW, RR=401MW, NetOpMargin: PM=658, EVE=297 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
4/29/2024 12:50:56 PM | [NSO Update] Mindanao Grid-04/29/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2803MW, PK=2535MW, RR=73MW, NetOpMargin: PM=195, EVE=306 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @28.9MW, MA1 @48.5MW, MA2 @37MW, GNPK 4 @61MW [WEBSMS] | CMIN
4/29/2024 11:59:59 AM | Visayas Grid-04/29/2024 12:00: Carcon-Sangi 34.5 KV Line 1 energized at 1159H (Planned Outage) [WEBSMS] | CVIS
4/29/2024 11:57:31 AM | Mindanao Grid-04/29/2024 12:02: AGUS 5 HEP Unit 2 online at 1153H from OMC Outage. (Unplanned Outage) [WEBSMS] | CMIN
4/29/2024 11:49:18 AM | Luzon Grid-04/29/2024 11:49: Kalayaan Unit 1 (101MW) tripped as generator at 1145H. Lowest system frequency is 59.664Hz. [WEBSMS] | CLUZ
4/29/2024 10:35:32 AM | Mindanao Grid-04/29/2024 10:40: PULANGI 4 HEP Unit 1 online from OMC Outage. Unplanned Outage. [WEBSMS] | CMIN
4/29/2024 10:35:23 AM | Visayas Grid-04/29/2024 10:35: EDC-Leyte A Maha U1 tripped at 1023H (Unplanned Outage) [WEBSMS] | CVIS
4/29/2024 10:11:04 AM | Visayas Grid-04/29/2024 10:11: Carcon-Sangi 34.5 KV Line 1 de-energized at 1010H (Planned Outage) [WEBSMS] | CVIS
4/29/2024 9:09:24 AM | [NSO Update] Mindanao Grid-04/29/2024 09:14: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0902H with power going to Mindanao. [WEBSMS] | CMIN
4/29/2024 9:09:21 AM | [NSO Update] Visayas Grid-04/29/2024 09:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0902H with power going to Mindanao. [WEBSMS] | CVIS
4/29/2024 8:58:41 AM | [NSO Update] Mindanao Grid-04/29/2024 09:03: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0849H from forward power direction. [WEBSMS] | CMIN
4/29/2024 8:58:32 AM | [NSO Update] Visayas Grid-04/29/2024 08:58: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0849H from forward power direction. [WEBSMS] | CVIS
4/29/2024 8:57:01 AM | Mindanao Grid-04/29/2024 09:02: WMPC DG04 online at 0853H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
4/29/2024 8:43:12 AM | [NSO Update] Luzon Grid-04/29/2024 08:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0837H with power going to Visayas. [WEBSMS] | CLUZ
4/29/2024 8:42:41 AM | [NSO Update] Visayas Grid-04/29/2024 08:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0837H with power going to Visayas. [WEBSMS] | CVIS
4/29/2024 8:39:09 AM | Mindanao Grid-04/29/2024 08:44: WMPC DG10 online at 0831H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
4/29/2024 8:32:45 AM | [NSO Update] Luzon Grid-04/29/2024 08:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0827H from forward power direction. [WEBSMS] | CLUZ
4/29/2024 8:31:38 AM | [NSO Update] Visayas Grid-04/29/2024 08:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0827H from forward power direction. [WEBSMS] | CVIS
4/29/2024 6:25:28 AM | [NSO Update] Luzon Grid-04/29/2024 06:25: System Advisory: 29-Apr-2024, Luzon Grid is on YELLOW Alert for interval hours 1600H-1700H and 2100H-2300H. Total capacity on forced outage is 1343.3MW. Total of de-rated capacity is 100MW. [WEBSMS] | CLUZ
4/29/2024 6:24:57 AM | [NSO Update] Mindanao Grid-04/29/2024 06:30: System Advisory: 29-Apr-2024, Luzon Grid is on YELLOW Alert for interval hours 1600H-1700H and 2100H-2300H. Total capacity on forced outage is 1343.3MW. Total of de-rated capacity is 100MW. [WEBSMS] | CMIN
4/29/2024 6:20:00 AM | [NSO Update] Mindanao Grid-04/29/2024 06:25: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2872MW, PK=2468MW, RR=73MW, NetOpMargin: AM=331, PM=220, EVE=356 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @28.9MW, MA1 @48.5MW, MA2 @37MW, GNPK 4 @115MW [WEBSMS] | CMIN
4/29/2024 6:16:05 AM | [NSO Update] Visayas Grid-04/29/2024 06:16: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2911MW, PK=2494MW, RR=95MW, NetOpMargin: AM=322, PM=189, EVE=198 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, CEDC U3 @75MW, TGPP @110MW, PDPP 1-U2 @4.5MW, PDPP 1-U5 @4MW, Nasulo @41MW, PDPP 3-E @10MW, PDPP 104-U2 @5MW, PDPP 104-U3 @5MW [WEBSMS] | CVIS
4/29/2024 5:59:18 AM | [NSO Update] Luzon Grid-04/29/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=15170MW, PK=13176MW, RR=296MW, NetOpMargin: AM=1698, PM=678, EVE=410 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
4/29/2024 5:11:48 AM | Luzon Grid-04/29/2024 05:11: Tayabas SS 600MVA T03 restored at 0509H (Planned Outage) [WEBSMS] | CLUZ
4/29/2024 4:25:35 AM | [NSO Update] Mindanao Grid-04/29/2024 04:30: Weather Update: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
4/29/2024 4:25:04 AM | [NSO Update] Visayas Grid-04/29/2024 04:25: Weather Update: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
4/29/2024 4:24:31 AM | [NSO Update] Luzon Grid-04/29/2024 04:24: Weather Update: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
4/29/2024 4:20:59 AM | Luzon Grid-04/29/2024 04:21: La Trinidad - Bauang 230kV Line 2 restored at 0419H (Planned Outage) [WEBSMS] | CLUZ
4/29/2024 3:10:49 AM | Luzon Grid-04/29/2024 03:10: Binan - Southwoods 115kV Line restored at 0302H (Planned Outage) [WEBSMS] | CLUZ
4/29/2024 3:08:24 AM | Luzon Grid-04/29/2024 03:08: Binan SS 300MVA T03 restored at 0258H (Planned Outage) [WEBSMS] | CLUZ
4/29/2024 12:34:53 AM | Luzon Grid-04/29/2024 00:35: Tayabas 600MVA T03 was de-energized at 0034H. (Planned Outage) [WEBSMS] | CLUZ
4/29/2024 12:23:19 AM | Mindanao Grid-04/29/2024 00:28: Mt. Apo 3 shutdown at 0005H for maintenance (Unplanned Outage) [WEBSMS] | CMIN
4/28/2024 11:51:20 PM | Visayas Grid-04/28/2024 23:51: Colon - Dumanjug 138 kV Line 2 energized at 2350H (Planned Outage) [WEBSMS] | CVIS
4/28/2024 9:42:45 PM | Mindanao Grid-04/28/2024 21:47: AGUS 6 Unit 5 online at 2141H (Unplanned Outage) [WEBSMS] | CMIN
4/28/2024 8:22:34 PM | [NSO Update] Visayas Grid-04/28/2024 20:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2021H with power going to Luzon [WEBSMS] | CVIS
4/28/2024 8:22:08 PM | [NSO Update] Luzon Grid-04/28/2024 20:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2021H with power going to Luzon [WEBSMS] | CLUZ
4/28/2024 8:20:55 PM | [NSO Update] Visayas Grid-04/28/2024 20:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2011H from reverse power direction [WEBSMS] | CVIS
4/28/2024 8:20:21 PM | [NSO Update] Luzon Grid-04/28/2024 20:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2011H from reverse power direction [WEBSMS] | CLUZ
4/28/2024 8:17:57 PM | Mindanao Grid-04/28/2024 20:23: WMPC DG10 shutdown at 2017H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
4/28/2024 8:09:46 PM | Visayas Grid-04/28/2024 20:09: Dumanjug SS 138kV Bus 2 energized at 2004H. (Unplanned Outage) [WEBSMS] | CVIS
4/28/2024 6:38:36 PM | [NSO Update] Mindanao Grid-04/28/2024 18:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2803MW, PK=2312MW, RR=73MW, NetOpMargin: EVE=418 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @28.9MW, MA1 @48.5MW, MA2 @37MW, GNPK 4 @115MW [WEBSMS] | CMIN
4/28/2024 6:35:41 PM | [NSO Update] Visayas Grid-04/28/2024 18:35: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2596MW, PK=2333MW, RR=94MW, NetOpMargin: EVE=169 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @308MW, CEDC U3 @75MW, Tongonan Power Plant @107MW, Panay Diesel 1-U2 @4.5MW, Panay Diesel 1-U5 @4MW, Nasulo Geo @45.5MW, Panay Diesel 3-E @10MW, Power Barge 104-U2 @5MW, Power Barge 104-U3 @5MW, Panay Diesel 3-G @8MW [WEBSMS] | CVIS
4/28/2024 6:25:40 PM | Luzon Grid-04/28/2024 18:25: Binan 300MVA T03 was de-energized at 1821H. (Planned Outage) [WEBSMS] | CLUZ
4/28/2024 6:20:12 PM | [NSO Update] Luzon Grid-04/28/2024 18:20: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13087MW, PK=12017MW, RR=205MW, NetOpMargin: EVE=865 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
4/28/2024 6:18:22 PM | Luzon Grid-04/28/2024 18:18: Binan-Southwoods 115kV line was de-energized at 1816H. (Planned Outage) [WEBSMS] | CLUZ
4/28/2024 6:16:17 PM | [NSO Update] Visayas Grid-04/28/2024 18:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1751H with power going to Visayas [WEBSMS] | CVIS
4/28/2024 6:15:55 PM | [NSO Update] Luzon Grid-04/28/2024 18:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1751H with power going to Visayas [WEBSMS] | CLUZ
4/28/2024 5:46:11 PM | [NSO Update] Visayas Grid-04/28/2024 17:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1741H from forward power direction [WEBSMS] | CVIS
4/28/2024 5:44:44 PM | [NSO Update] Luzon Grid-04/28/2024 17:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1741H from forward power direction [WEBSMS] | CLUZ
4/28/2024 5:31:11 PM | Luzon Grid-04/28/2024 17:31: Santiago 230kV Bus 1 was energized at 1728H. (Planned Outage) [WEBSMS] | CLUZ
4/28/2024 4:58:14 PM | Mindanao Grid-04/28/2024 17:03: Aurora SS Power Transformer No.3 energized at 1657H from Planned Outage (GOMP) [WEBSMS] | CMIN
4/28/2024 3:17:42 PM | Mindanao Grid-04/28/2024 15:22: General Santos SS Power Transformer No.5 energized back at 1515H from Planned Outage. [WEBSMS] | CMIN
4/28/2024 2:41:17 PM | Mindanao Grid-04/28/2024 14:46: WMPC DG10 online at 1439H. MRU-System Voltage Requirement. [WEBSMS] | CMIN
4/28/2024 2:08:13 PM | Luzon Grid-04/28/2024 14:08: Lumban - Gumaca 230kV Line 1 restored at 1407H (Unplanned Outage) [WEBSMS] | CLUZ
4/28/2024 2:05:57 PM | Luzon Grid-04/28/2024 14:05: Lumban - Gumaca 230kV Line 1 tripped at 1402H (Unplanned Outage) [WEBSMS] | CLUZ
4/28/2024 2:03:31 PM | Luzon Grid-04/28/2024 14:03: BCCPP-Petron RSF 230kV Tie Line 1 restored at 1401H (Planned Outage) [WEBSMS] | CLUZ
4/28/2024 1:50:37 PM | Luzon Grid-04/28/2024 13:50: Kalayaan Unit 1 tripped as pump at 1347H. Highest system frequency is 60.400Hz. [WEBSMS] | CLUZ
4/28/2024 1:35:08 PM | Luzon Grid-04/28/2024 13:35: San Gabriel online at 1334H (Reserve Shutdown) [WEBSMS] | CLUZ
4/28/2024 12:54:49 PM | [NSO Update] Mindanao Grid-04/28/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2834MW, PK=2149MW, RR=73MW, NetOpMargin: PM=612, EVE=424 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @28.9MW, MA1 @48.5MW, MA2 @37MW, GNPK 4 @115MW [WEBSMS] | CMIN
4/28/2024 12:46:18 PM | Mindanao Grid-04/28/2024 12:51: AGUS 6 Unit 3 online at 1244H (Planned Outage) [WEBSMS] | CMIN
4/28/2024 12:45:08 PM | [NSO Update] Luzon Grid-04/28/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14396MW, PK=11582MW, RR=261MW, NetOpMargin: PM=2553, EVE=765 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: QPPL @ 410MW [WEBSMS] | CLUZ
4/28/2024 12:02:35 PM | Luzon Grid-04/28/2024 12:02: Lumban - Gumaca 230kV Line 1 restored at 1202H (Unplanned Outage) [WEBSMS] | CLUZ
4/28/2024 12:00:02 PM | Luzon Grid-04/28/2024 12:00: Lumban - Gumaca 230kV Line 1 tripped at 1154H (Unplanned Outage) [WEBSMS] | CLUZ
4/28/2024 11:11:10 AM | Luzon Grid-04/28/2024 11:11: San Rafael - Cabanatuan 230kV Line restored at 1110H (Unplanned Outage) [WEBSMS] | CLUZ
4/28/2024 10:04:55 AM | Mindanao Grid-04/28/2024 10:10: SIBULAN B Unit 1 online at 0900H (Planned Outage) [WEBSMS] | CMIN
4/28/2024 10:04:16 AM | Mindanao Grid-04/28/2024 10:09: SIBULAN B Unit 2 online at 0857H (Planned Outage) [WEBSMS] | CMIN
4/28/2024 10:03:23 AM | Mindanao Grid-04/28/2024 10:08: SIBULAN A Unit 2 online at 0852H (Planned Outage) [WEBSMS] | CMIN
4/28/2024 10:02:41 AM | Mindanao Grid-04/28/2024 10:07: TUDAYA 1 Unit 1 online at 0848H (Planned Outage) [WEBSMS] | CMIN
4/28/2024 10:02:00 AM | Mindanao Grid-04/28/2024 10:07: SIBULAN A Unit 1 online at 0848H (Planned Outage) [WEBSMS] | CMIN
4/28/2024 9:55:10 AM | [NSO Update] Luzon Grid-04/28/2024 09:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0952H with power going to Luzon. [WEBSMS] | CLUZ
4/28/2024 9:51:46 AM | [NSO Update] Luzon Grid-04/28/2024 09:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0940H from reverse power direction. [WEBSMS] | CLUZ
4/28/2024 9:10:45 AM | Luzon Grid-04/28/2024 09:10: BCCPP-Petron RSF 230kV Tie Line 1 de-energized at 0910H (Planned Outage) [WEBSMS] | CLUZ
4/28/2024 9:07:16 AM | Mindanao Grid-04/28/2024 09:12: Maramag SS Power Transformer #1 (7XF01MRM) energized back at 0905H from Planned Outage/ Non-GOMP. [WEBSMS] | CMIN
4/28/2024 8:51:36 AM | Luzon Grid-04/28/2024 08:51: San Rafael - Cabanatuan 230kV Line de-energized at 0850H (Unplanned Outage) [WEBSMS] | CLUZ
4/28/2024 7:21:35 AM | Visayas Grid-04/28/2024 07:21: Dumanjug SS 138 KV bus 2 de-energized at 0718H (Planned Outage) [WEBSMS] | CVIS
4/28/2024 7:20:12 AM | [NSO Update] Luzon Grid-04/28/2024 07:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0718H with power going to Visayas. [WEBSMS] | CLUZ
4/28/2024 7:19:57 AM | [NSO Update] Visayas Grid-04/28/2024 07:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0718H with power going to Visayas. [WEBSMS] | CVIS
4/28/2024 7:16:04 AM | Mindanao Grid-04/28/2024 07:21: Maramag SS Power Transformer #1 (7XF01MRM) de-energized at 0714H. Planned Outage/ Non-GOMP. [WEBSMS] | CMIN
4/28/2024 7:10:36 AM | [NSO Update] Visayas Grid-04/28/2024 07:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0708H from forward power direction. [WEBSMS] | CVIS
4/28/2024 7:10:22 AM | [NSO Update] Luzon Grid-04/28/2024 07:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0708H from forward power direction. [WEBSMS] | CLUZ
4/28/2024 6:49:23 AM | Luzon Grid-04/28/2024 06:49: Santiago SS 230kV Bus 1 de-energized at 0649H (Planned Outage) [WEBSMS] | CLUZ
4/28/2024 6:46:52 AM | Luzon Grid-04/28/2024 06:47: La Trinidad-Bauang 230kV Line 2 de-energized at 0643H (Planned Outage) [WEBSMS] | CLUZ
4/28/2024 6:45:30 AM | Luzon Grid-04/28/2024 06:45: San Gabriel shutdown at 0636H (Reserve Shutdown) [WEBSMS] | CLUZ
4/28/2024 6:38:33 AM | Mindanao Grid-04/28/2024 06:43: General Santos SS Power Transformer No.5 shutdown at 0635H (Planned Outage) [WEBSMS] | CMIN
4/28/2024 6:19:23 AM | Mindanao Grid-04/28/2024 06:24: Aurora SS Power Transformer No.3 shutdown at 0609H (Planned Outage/GOMP) [WEBSMS] | CMIN
4/28/2024 6:17:41 AM | [NSO Update] Mindanao Grid-04/28/2024 06:22: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2817MW, PK=2120MW, RR=73MW, NetOpMargin: AM=624, PM=544, EVE=333 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @28.9MW, MA1 @48.5MW, MA2 @37MW, GNPK 4 @115MW [WEBSMS] | CMIN
4/28/2024 6:13:04 AM | [NSO Update] Visayas Grid-04/28/2024 06:13: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2538MW, PK=2087MW, RR=89MW, NetOpMargin: AM=362, PM=397, EVE=208 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @315MW, CEDC U3 @75MW, Tongonan Power Plant @107MW, Panay Diesel 1-U2 @4.5MW, Panay Diesel 1-U5 @4MW, Nasulo Geo @45.5MW [WEBSMS] | CVIS
4/28/2024 6:08:02 AM | [NSO Update] Luzon Grid-04/28/2024 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14768MW, PK=11342MW, RR=244MW, NetOpMargin: AM=3181, PM=2051, EVE=895 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
4/28/2024 5:56:26 AM | Visayas Grid-04/28/2024 05:56: Colon - Dumanjug 138 kV Line 1 de-energized at 0555H (Planned Outage) [WEBSMS] | CVIS
4/28/2024 5:11:29 AM | Visayas Grid-04/28/2024 05:11: Colon - Dumanjug 138 kV Line 2 de-energized at 0510H (Planned Outage) [WEBSMS] | CVIS
4/28/2024 4:56:58 AM | [NSO Update] Mindanao Grid-04/28/2024 05:02: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
4/28/2024 4:56:42 AM | [NSO Update] Visayas Grid-04/28/2024 04:56: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
4/28/2024 4:56:24 AM | [NSO Update] Luzon Grid-04/28/2024 04:56: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/28/2024 4:26:57 AM | Luzon Grid-04/28/2024 04:27: Dona Imelda-Kamuning 115kV Line restored at 0426H (Planned Outage) [WEBSMS] | CLUZ
4/28/2024 1:26:04 AM | Luzon Grid-04/28/2024 01:26: Dona Imelda-Kamuning 115kV Line de-energized at 0122H (Planned Outage) [WEBSMS] | CLUZ
4/28/2024 12:52:52 AM | Mindanao Grid-04/28/2024 00:58: Pulangui4 U1 shutdown at 0047H due to low forebay elevation(OMC). [WEBSMS] | CMIN
4/27/2024 11:46:16 PM | Visayas Grid-04/27/2024 23:46: Dumanjug SS 138 kV Bus 1 energized at 2339H (Planned Outage) [WEBSMS] | CVIS
4/27/2024 10:47:28 PM | [NSO Update] Visayas Grid-04/27/2024 22:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2227H with power going to Luzon [WEBSMS] | CVIS
4/27/2024 10:47:04 PM | [NSO Update] Luzon Grid-04/27/2024 22:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2227H with power going to Luzon [WEBSMS] | CLUZ
4/27/2024 10:44:56 PM | [NSO Update] Visayas Grid-04/27/2024 22:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2214H from reverse power direction [WEBSMS] | CVIS
4/27/2024 10:44:47 PM | [NSO Update] Luzon Grid-04/27/2024 22:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2214H from reverse power direction [WEBSMS] | CLUZ
4/27/2024 9:59:50 PM | Mindanao Grid-04/27/2024 22:05: WMPC DG04 with 10.2MW load tripped at 2144H. Indication: HT Low Pressure Stop. (Unplanned Outage) [WEBSMS] | CMIN
4/27/2024 8:46:51 PM | Mindanao Grid-04/27/2024 20:52: Sultan Kudarat SS 138kV Bus #1 energized at 2041H. (Planned Outage) [WEBSMS] | CMIN
4/27/2024 6:58:42 PM | Luzon Grid-04/27/2024 18:58: Mexico-Concepcion 230kV line 1 restored at 1858H (Planned Outage) [WEBSMS] | CLUZ
4/27/2024 6:32:48 PM | Mindanao Grid-04/27/2024 18:37: WMPC DG02 with 10.2MW load tripped at 1816H. Indication: Lube Oil High Temperature Stop. (Unplanned Outage) [WEBSMS] | CMIN
4/27/2024 6:29:51 PM | Mindanao Grid-04/27/2024 18:35: WMPC DG02 online at 1801H. MO Dispatched. [WEBSMS] | CMIN
4/27/2024 6:27:42 PM | Luzon Grid-04/27/2024 18:27: Bauang 230kV Bus 1 restored at 1827H (Planned Outage) [WEBSMS] | CLUZ
4/27/2024 6:03:25 PM | [NSO Update] Luzon Grid-04/27/2024 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13611MW, PK=12144MW, RR=417MW, NetOpMargin: EVE=1050 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
4/27/2024 6:01:03 PM | [NSO Update] Visayas Grid-04/27/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2761MW, PK=2417MW, RR=94MW, NetOpMargin: EVE=250 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @100.5MW, LEYTE A @305MW [WEBSMS] | CVIS
4/27/2024 5:59:00 PM | [NSO Update] Mindanao Grid-04/27/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2792MW, PK=2301MW, RR=73MW, NetOpMargin: EVE=419 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @28.9MW, MA1 @48.5MW, MA2 @37MW, GNPK 4@115MW [WEBSMS] | CMIN
4/27/2024 5:07:10 PM | Mindanao Grid-04/27/2024 17:12: Kauswagan-GN Power 230kV Line 3 energized/restored at 1701H. (Unplanned Outage). [WEBSMS] | CMIN
4/27/2024 4:55:04 PM | Mindanao Grid-04/27/2024 17:00: Toril-Matanao 138kV Line 2 restored/energized at 1651H. (Planned Outage). [WEBSMS] | CMIN
4/27/2024 4:48:52 PM | Mindanao Grid-04/27/2024 16:54: WMPC DG04 shutdown at 1646H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
4/27/2024 4:42:58 PM | Luzon Grid-04/27/2024 16:42: BCCPP-Petron RSF 230kV Tie Line 2 restored at 1640H (Planned Outage) [WEBSMS] | CLUZ
4/27/2024 3:10:45 PM | Mindanao Grid-04/27/2024 15:15: Agus 6 SWY-Agus 6 Unit #5 HEPP 138kV Line manually de-energized at 1501H, as per request by AGUS 6 HEPP. (Unplanned Outage) [WEBSMS] | CMIN
4/27/2024 3:05:36 PM | Mindanao Grid-04/27/2024 15:10: AGUS 6 HEP Unit 5 on emergency shutdown at 1456H. For further investigation. (Unplanned Outage) [WEBSMS] | CMIN
4/27/2024 2:59:59 PM | Luzon Grid-04/27/2024 15:00: Nagsaag - Casecnan 230kV Line 2 restored at 1459H (Planned Outage) [WEBSMS] | CLUZ
4/27/2024 2:42:20 PM | [NSO Update] Mindanao Grid-04/27/2024 14:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1439H with power going to Visayas. [WEBSMS] | CMIN
4/27/2024 2:42:13 PM | [NSO Update] Visayas Grid-04/27/2024 14:42: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1439H with power going to Visayas. [WEBSMS] | CVIS
4/27/2024 2:32:35 PM | [NSO Update] Mindanao Grid-04/27/2024 14:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1429H from reverse power direction. [WEBSMS] | CMIN
4/27/2024 2:32:07 PM | [NSO Update] Visayas Grid-04/27/2024 14:32: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1429H from reverse power direction. [WEBSMS] | CVIS
4/27/2024 2:30:59 PM | [NSO Update] Visayas Grid-04/27/2024 14:31: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0912H with power going to Mindanao. [WEBSMS] | CVIS
4/27/2024 2:30:29 PM | [NSO Update] Mindanao Grid-04/27/2024 14:35: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0912H with power going to Mindanao. [WEBSMS] | CMIN
4/27/2024 1:46:57 PM | Mindanao Grid-04/27/2024 13:52: WMPC DG04 online at 1343H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
4/27/2024 1:06:57 PM | Mindanao Grid-04/27/2024 13:12: Toril-Matanao 138kV Line 2 de-energized at 1301H. (Planned Outage). [WEBSMS] | CMIN
4/27/2024 1:05:10 PM | [NSO Update] Mindanao Grid-04/27/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2854MW, PK=2403MW, RR=73MW, NetOpMargin: PM=378, EVE=342 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @28.9MW, MA1 @48.5MW, MA2 @37MW, GNPK 4@115MW [WEBSMS] | CMIN
4/27/2024 1:02:01 PM | [NSO Update] Visayas Grid-04/27/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2723MW, PK=2361MW, RR=90MW, NetOpMargin: PM=272, EVE=277 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @100.5MW, LEYTE A @305MW [WEBSMS] | CVIS
4/27/2024 12:59:37 PM | [NSO Update] Luzon Grid-04/27/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15047MW, PK=12581MW, RR=444MW, NetOpMargin: PM=2022, EVE=1137 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
4/27/2024 12:55:30 PM | Mindanao Grid-04/27/2024 13:00: WMPC DG10 online at 1252H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
4/27/2024 11:06:30 AM | Luzon Grid-04/27/2024 11:06: Balsik PCB 9-02CB08BIK was energized at 1104H. (Planned Outage) [WEBSMS] | CLUZ
4/27/2024 10:11:00 AM | Luzon Grid-04/27/2024 10:11: Balsik PCB 9-02CB08BIK was de-energized at 1008H. (Planned Outage) [WEBSMS] | CLUZ
4/27/2024 9:37:43 AM | Luzon Grid-04/27/2024 09:37: Balsik 9-01CB04BIK was energized at 0935H. (Planned Outage) [WEBSMS] | CLUZ
4/27/2024 9:36:21 AM | Luzon Grid-04/27/2024 09:36: BCCPP-Petron RSF 230kV Tie Line 2 de-energized at 0821H. (Planned Outage) [WEBSMS] | CLUZ
4/27/2024 9:16:08 AM | Mindanao Grid-04/27/2024 09:21: Kauswagan-GN Power Unit #3 de-energized at 0902H as per request by GN Power. (Unplanned Outage) [WEBSMS] | CMIN
4/27/2024 9:04:44 AM | [NSO Update] Visayas Grid-04/27/2024 09:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0902H from forward power direction. [WEBSMS] | CVIS
4/27/2024 9:04:22 AM | [NSO Update] Mindanao Grid-04/27/2024 09:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0902H from forward power direction. [WEBSMS] | CMIN
4/27/2024 8:04:30 AM | Luzon Grid-04/27/2024 08:04: Balsik PCB 9-01CB04BIK was de-energized at 0802H. (Planned Outage) [WEBSMS] | CLUZ
4/27/2024 7:48:05 AM | [NSO Update] Luzon Grid-04/27/2024 07:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0745H with power going to Visayas. [WEBSMS] | CLUZ
4/27/2024 7:47:56 AM | [NSO Update] Visayas Grid-04/27/2024 07:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0745H with power going to Visayas. [WEBSMS] | CVIS
4/27/2024 7:37:02 AM | [NSO Update] Luzon Grid-04/27/2024 07:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0735H from forward power direction. [WEBSMS] | CLUZ
4/27/2024 7:36:29 AM | [NSO Update] Visayas Grid-04/27/2024 07:36: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0735H from forward power direction. [WEBSMS] | CVIS
4/27/2024 7:07:33 AM | Luzon Grid-04/27/2024 07:07: Mexico-Concepcion 230kV line 1 was de-energized at 0705H. (Planned Outage) [WEBSMS] | CLUZ
4/27/2024 6:46:12 AM | Luzon Grid-04/27/2024 06:46: Bauang 230kV Bus 1 was de-energized at 0643H. (Planned Outage) [WEBSMS] | CLUZ
4/27/2024 6:43:22 AM | Visayas Grid-04/27/2024 06:43: 138KV Barotac-Concepcion line 1 de-energized @ 0640H. ( Planned Outage ). [WEBSMS] | CVIS
4/27/2024 6:36:42 AM | Visayas Grid-04/27/2024 06:36: 138KV Dumanjug Bus 1 de-energized @0618H. ( Planned Outage ). [WEBSMS] | CVIS
4/27/2024 6:34:34 AM | Visayas Grid-04/27/2024 06:34: 34.5KV Sangi-Toledo de-energized @ 0626H, customers request. ( Planned Outage ). [WEBSMS] | CVIS
4/27/2024 6:13:48 AM | Mindanao Grid-04/27/2024 06:18: Sultan Kudarat SS 138kV Bus #1 de-energized at 0606H. (Planned Outage). [WEBSMS] | CMIN
4/27/2024 5:47:57 AM | [NSO Update] Luzon Grid-04/27/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14929MW, PK=11600MW, RR=424MW, NetOpMargin: AM=2904, PM=1921, EVE=1055 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MASINLOC 2 @280MW, ILIJAN A @500MW [WEBSMS] | CLUZ
4/27/2024 5:45:30 AM | Mindanao Grid-04/27/2024 05:50: AGUS 5 Unit 2 with 10MW load shutdown at 0542H due to low forebay elevation (Unplanned Outage) [WEBSMS] | CMIN
4/27/2024 5:33:06 AM | [NSO Update] Mindanao Grid-04/27/2024 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3099MW, PK=2409MW, RR=73MW, NetOpMargin: AM=618, PM=371, EVE=311 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @28.9MW, MA1 @48.5MW, MA2 @37MW, GNPK 4@115MW [WEBSMS] | CMIN
4/27/2024 5:29:11 AM | [NSO Update] Visayas Grid-04/27/2024 05:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2763MW, PK=2224MW, RR=89MW, NetOpMargin: AM=450, PM=336, EVE=251 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @91MW, LEYTE A @315MW [WEBSMS] | CVIS
4/27/2024 4:06:50 AM | [NSO Update] Mindanao Grid-04/27/2024 04:11: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
4/27/2024 4:06:27 AM | [NSO Update] Visayas Grid-04/27/2024 04:06: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
4/27/2024 4:06:14 AM | [NSO Update] Luzon Grid-04/27/2024 04:06: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/27/2024 1:35:08 AM | Luzon Grid-04/27/2024 01:35: Hermosa-Malolos 230kV Line tripped at 0129H and but reclosed on Hermosa side only. Successfully loop at 0134H on Malolos side (Unplanned Outage) [WEBSMS] | CLUZ
4/26/2024 11:46:01 PM | Mindanao Grid-04/26/2024 23:51: WMPC DG04 declared available at 2245H (From Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 11:13:45 PM | [NSO Update] Visayas Grid-04/26/2024 23:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2312H with power going to Luzon. [WEBSMS] | CVIS
4/26/2024 11:13:21 PM | [NSO Update] Luzon Grid-04/26/2024 23:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2312H with power going to Luzon. [WEBSMS] | CLUZ
4/26/2024 11:05:15 PM | Luzon Grid-04/26/2024 23:05: Laoag Solar - Laoag Solar 2 230kV Line 1 looped at 2304H (On Commissioning Test) [WEBSMS] | CLUZ
4/26/2024 11:03:53 PM | [NSO Update] Visayas Grid-04/26/2024 23:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2302H from reverse power direction. [WEBSMS] | CVIS
4/26/2024 11:03:28 PM | [NSO Update] Luzon Grid-04/26/2024 23:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2302H from reverse power direction [WEBSMS] | CLUZ
4/26/2024 10:52:48 PM | [NSO Update] Luzon Grid-04/26/2024 22:52: Update on System Advisory: Luzon Grid Yellow Alert notice issued today has been lifted at 2250H. [WEBSMS] | CLUZ
4/26/2024 10:42:19 PM | Luzon Grid-04/26/2024 22:42: Laoag Solar - Laoag Solar 2 230kV Line 1 unlooped at 2239H (On Commissioning Test) [WEBSMS] | CLUZ
4/26/2024 10:16:14 PM | Mindanao Grid-04/26/2024 22:21: WMPC DG10 end of MRU-System Voltage at 2200H. Converted to Energy (MO dispatch). [WEBSMS] | CMIN
4/26/2024 9:40:16 PM | [NSO Update] Visayas Grid-04/26/2024 21:40: Update on System Advisory: Visayas Grid Yellow Alert notice issued today has been lifted at 2135H. [WEBSMS] | CVIS
4/26/2024 9:35:10 PM | Mindanao Grid-04/26/2024 21:40: WMPC DG07 end of MRU-System Voltage at 2130H. Converted to Energy (MO dispatch). [WEBSMS] | CMIN
4/26/2024 9:32:16 PM | Luzon Grid-04/26/2024 21:32: Laoag Solar - Laoag Solar 2 230kV Line 1 looped at 2131H (On Commissioning Test) [WEBSMS] | CLUZ
4/26/2024 8:37:49 PM | Visayas Grid-04/26/2024 20:37: PGPP2 Sogongon U1 cut-out at 2032H (Planned Outage) [WEBSMS] | CVIS
4/26/2024 7:08:35 PM | Mindanao Grid-04/26/2024 19:13: LIBERTAD POWER online at 1854H (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 6:50:39 PM | Mindanao Grid-04/26/2024 18:55: LIBERTAD POWER with 3.8MW load tripped at 1722H (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 6:35:08 PM | Luzon Grid-04/26/2024 18:35: For info: Luzon System Frequency reach 60.57Hz at 1806H. There was a initial reported tripping of Malinta-Malabon 115kV Line which could have affected the motor loads nearby. [WEBSMS] | CLUZ
4/26/2024 5:48:46 PM | Visayas Grid-04/26/2024 17:48: Calongcalong - Asturias 69 kV Line re-energized at 1748H (Unplanned Outage) [WEBSMS] | CVIS
4/26/2024 5:47:14 PM | [NSO Update] Mindanao Grid-04/26/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2806MW, PK=2455MW, RR=73MW, NetOpMargin: EVE=278 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, GNPK 4 @115MW [WEBSMS] | CMIN
4/26/2024 5:45:25 PM | [NSO Update] Visayas Grid-04/26/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2668MW, PK=2401MW, RR=94MW, NetOpMargin: EVE=172 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @310MW, CEDC U3 @75MW, Tongonan Power Plant @73MW, Power Barge 104-U3 @5MW, Power Barge 104-U2 @5MW, Panay Diesel 1-U5 @4MW, Panay Diesel 3-C @11MW, Panay Diesel 3-E @10MW, Panay Diesel 1-U2 @4MW [WEBSMS] | CVIS
4/26/2024 5:41:51 PM | [NSO Update] Luzon Grid-04/26/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=12882MW, PK=12313MW, RR=305MW, NetOpMargin: EVE=264 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @500MW, Masinloc 2 @280MW, Calaca 1 @210MW [WEBSMS] | CLUZ
4/26/2024 5:38:29 PM | Visayas Grid-04/26/2024 17:38: Calongcalong - Asturias 69 kV Line tripped at 1735H (Unplanned Outage) [WEBSMS] | CVIS
4/26/2024 5:34:40 PM | Mindanao Grid-04/26/2024 17:39: WMPC DG04 starting failure/ declared forced outage at 1542H. (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 5:22:01 PM | Mindanao Grid-04/26/2024 17:27: NEW BATAAN (EURO HYDRO) online at 1402H (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 4:41:14 PM | [NSO Update] Visayas Grid-04/26/2024 16:41: Update on System Advisory: Visayas Grid Red Alert notice issued today has been lifted at 1630H. Total capacity on forced outage is 351MW. Total of de-rated capacity is 238.6MW. [WEBSMS] | CVIS
4/26/2024 4:20:06 PM | Mindanao Grid-04/26/2024 16:25: WMPC DG01 end of MRU-System Voltage Requirement at 1615H. Converted to Energy (MO dispatch). [WEBSMS] | CMIN
4/26/2024 4:08:33 PM | Mindanao Grid-04/26/2024 16:13: PULANGI 4 Unit 1 online at 1607H (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 3:49:08 PM | [NSO Update] Mindanao Grid-04/26/2024 15:54: Update on System Advisory: Mindanao Grid Yellow Alert notice issued today has been lifted at 1506H. Total capacity of forced outage is 505.4MW. Total of de-rated capacity is 118.58MW. [WEBSMS] | CMIN
4/26/2024 3:23:09 PM | Mindanao Grid-04/26/2024 15:28: WMPC DG04 declared available at 1520H (from Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 3:22:19 PM | Mindanao Grid-04/26/2024 15:27: WMPC DG04 end of MRU-System Voltage Requirement at 1449H due to tripping of said unit at 1436H. [WEBSMS] | CMIN
4/26/2024 2:42:33 PM | Mindanao Grid-04/26/2024 14:47: WMPC DG4 tripped at 1436H. MRU - System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 1:38:28 PM | Mindanao Grid-04/26/2024 13:43: (Correction) NEW BATAAN (EURO HYDRO) with 0.6MW load tripped at 1038H due to unbalanced voltage (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 1:36:07 PM | [NSO Update] Mindanao Grid-04/26/2024 13:41: System Advisory: Mindanao Grid is on YELLOW Alert for interval hours 1400H-1500H. Total capacity on forced outage is 505.4MW. Total of de-rated capacity is 118.58MW. [WEBSMS] | CMIN
4/26/2024 1:35:20 PM | [NSO Update] Visayas Grid-04/26/2024 13:35: System Advisory: Visayas Grid is on RED Alert for interval hour 1600H and YELLOW Alert for interval 1400H-1500H, 1700H-1900H and 2100H. Total capacity on forced outage is 351MW. Total of de-rated capacity is 238.6MW. [WEBSMS] | CVIS
4/26/2024 1:34:33 PM | [NSO Update] Luzon Grid-04/26/2024 13:34: System Advisory Update: Luzon Grid is on YELLOW Alert for interval hours 1400H-1700H and 2000H-2200H. Total capacity on forced outage is 1348.7MW. Total of de-rated capacity is 194MW. [WEBSMS] | CLUZ
4/26/2024 1:31:09 PM | [NSO Update] Mindanao Grid-04/26/2024 13:36: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2861MW, PK=2680MW, RR=73MW, NetOpMargin: PM=109, EVE=217 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, GNPK 4 @115MW [WEBSMS] | CMIN
4/26/2024 1:29:42 PM | [NSO Update] Visayas Grid-04/26/2024 13:29: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=2829MW, PK=2615MW, RR=100MW, NetOpMargin: PM=114, EVE=129 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @315MW, CEDC U3 @75MW, TGPP @73MW, Power Barge 104-U3 @5MW, Power Barge 104-U2 @5MW, Panay Diesel 1-U5 @4MW, Panay Diesel 3-C @11MW, Panay Diesel 3-E @10MW, Panay Diesel 1-U2 @4MW [WEBSMS] | CVIS
4/26/2024 1:27:29 PM | Mindanao Grid-04/26/2024 13:32: NEW BATAAN (EURO HYDRO) with 0.6MW load tripped at 1028H due to unbalanced voltage (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 1:21:21 PM | [NSO Update] Luzon Grid-04/26/2024 13:21: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14493MW, PK=13803MW, RR=411MW, NetOpMargin: PM=278, EVE=692 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 210MW, Masinloc 2 @ 280MW, Ilijan A @ 500MW [WEBSMS] | CLUZ
4/26/2024 1:11:38 PM | Mindanao Grid-04/26/2024 13:16: WMPC DG9 online at 1308H. Follow RTD. (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 1:07:19 PM | [NSO Update] Visayas Grid-04/26/2024 13:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1305H with power going to Visayas. [WEBSMS] | CVIS
4/26/2024 1:07:06 PM | [NSO Update] Mindanao Grid-04/26/2024 13:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1305H with power going to Visayas. [WEBSMS] | CMIN
4/26/2024 1:04:26 PM | [NSO Update] Mindanao Grid-04/26/2024 13:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1255H from reverse power direction. [WEBSMS] | CMIN
4/26/2024 1:04:13 PM | [NSO Update] Visayas Grid-04/26/2024 13:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1255H from reverse power direction. [WEBSMS] | CVIS
4/26/2024 1:03:05 PM | Mindanao Grid-04/26/2024 13:08: WMPC DG8 online at 1300H. Follow RTD. (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 1:02:16 PM | Mindanao Grid-04/26/2024 13:07: WMPC DG3 online at 1259H. Follow RTD. (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 1:01:07 PM | Mindanao Grid-04/26/2024 13:06: ASIGA online at 1101H (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 12:58:11 PM | Mindanao Grid-04/26/2024 13:03: WMPC DG2 online at 1256H. Follow RTD. (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 12:23:10 PM | Visayas Grid-04/26/2024 12:23: 34.5KV Sangi-Carcon Line 1 energized @1220H. ( Unplanned Outage ) [WEBSMS] | CVIS
4/26/2024 11:35:24 AM | Mindanao Grid-04/26/2024 11:40: LAKE MAINIT online at 1115H (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 10:32:23 AM | Mindanao Grid-04/26/2024 10:37: WMPC DG1 online at 1028H. MRU - System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 10:27:34 AM | Visayas Grid-04/26/2024 10:27: 34.5KV Sangi-Carcon Line 1 Emergency out @1009H, customers request. ( Unplanned Outage ) [WEBSMS] | CVIS
4/26/2024 10:08:37 AM | Mindanao Grid-04/26/2024 10:13: WMPC DG7 online at 1000H. MRU - System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 9:40:03 AM | Mindanao Grid-04/26/2024 09:45: LAKE MAINIT (load=15.6MW) and ASIGA (load=2.2MW) isolated at 0911H due to tripping of Butuan-Santiago 69 kV feeder (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 9:01:50 AM | Mindanao Grid-04/26/2024 09:06: WMPC DG4 online at 0859H. MRU - System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
4/26/2024 8:39:53 AM | Mindanao Grid-04/26/2024 08:45: WMPC DG10 online at 0835H. MRU - System Voltage Requirement. [WEBSMS] | CMIN
4/26/2024 8:21:28 AM | [NSO Update] Mindanao Grid-04/26/2024 08:26: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0819H with power going to Mindanao. [WEBSMS] | CMIN
4/26/2024 8:21:10 AM | [NSO Update] Visayas Grid-04/26/2024 08:21: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0819H with power going to Mindanao. [WEBSMS] | CVIS
4/26/2024 8:08:05 AM | [NSO Update] Mindanao Grid-04/26/2024 08:13: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0805H from forward power direction. [WEBSMS] | CMIN
4/26/2024 8:07:51 AM | [NSO Update] Visayas Grid-04/26/2024 08:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0805H from forward power direction. [WEBSMS] | CVIS
4/26/2024 7:29:46 AM | [NSO Update] Visayas Grid-04/26/2024 07:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0726H with power going to Visayas. [WEBSMS] | CVIS
4/26/2024 7:29:30 AM | [NSO Update] Luzon Grid-04/26/2024 07:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0726H with power going to Visayas. [WEBSMS] | CLUZ
4/26/2024 7:18:09 AM | [NSO Update] Visayas Grid-04/26/2024 07:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0716H from forward power direction. [WEBSMS] | CVIS
4/26/2024 7:17:54 AM | [NSO Update] Luzon Grid-04/26/2024 07:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0716H from forward power direction. [WEBSMS] | CLUZ
4/26/2024 6:07:36 AM | [NSO Update] Visayas Grid-04/26/2024 06:07: System Advisory: 26-Apr-2024, Visayas Grid is on YELLOW Alert for interval hours 1400H, 1500H, 1600H and 1900H. Total capacity on forced outage is 366.5MW. Total of de-rated capacity is 237.6MW. [WEBSMS] | CVIS
4/26/2024 6:05:22 AM | [NSO Update] Luzon Grid-04/26/2024 06:05: System Advisory: 26-Apr-2024, Luzon Grid is on YELLOW Alert for interval hours 1500H,1600H, 2100H and 2200H. Total capacity on forced outage is 1348.7MW. Total of de-rated capacity is 164MW. [WEBSMS] | CLUZ
4/26/2024 6:01:36 AM | [NSO Update] Mindanao Grid-04/26/2024 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2868MW, PK=2544MW, RR=73MW, NetOpMargin: AM=251, PM=179, EVE=277 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @28.9MW, MA1 @48.5MW, MA2 @37MW, GNPK 4 @115MW [WEBSMS] | CMIN
4/26/2024 5:59:54 AM | [NSO Update] Visayas Grid-04/26/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2989MW, PK=2444MW, RR=96MW, NetOpMargin: AM=449, PM=161, EVE=242 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @315MW, CEDC U3 @75MW, TGPP @73MW, Power Barge 104-U3 @5MW, Power Barge 104-U2 @5MW, Panay Diesel 1-U5 @4MW, Panay Diesel 3-C @11MW, Panay Diesel 3-E @10MW (Total deration: 237.6MW) [WEBSMS] | CVIS
4/26/2024 5:55:44 AM | [NSO Update] Luzon Grid-04/26/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=14747MW, PK=12783MW, RR=436MW, NetOpMargin: AM=1528, PM=373, EVE=250 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW, MASINLOC 2 @280MW [WEBSMS] | CLUZ
4/26/2024 4:02:48 AM | [NSO Update] Mindanao Grid-04/26/2024 04:07: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
4/26/2024 4:02:34 AM | [NSO Update] Visayas Grid-04/26/2024 04:02: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
4/26/2024 4:02:21 AM | [NSO Update] Luzon Grid-04/26/2024 04:02: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/26/2024 1:19:57 AM | Visayas Grid-04/26/2024 01:19: Quiot SS 100 MVA TR2 energized at 0119H (Unplanned Outage) [WEBSMS] | CVIS
4/25/2024 11:23:16 PM | [NSO Update] Luzon Grid-04/25/2024 23:23: Update on System Advisory: Luzon Grid Yellow Alert notice issued today has been lifted at 2314H. [WEBSMS] | CLUZ
4/25/2024 11:16:06 PM | [NSO Update] Luzon Grid-04/25/2024 23:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2309H with power going to Luzon. [WEBSMS] | CLUZ
4/25/2024 11:16:04 PM | [NSO Update] Visayas Grid-04/25/2024 23:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2309H with power going to Luzon. [WEBSMS] | CVIS
4/25/2024 11:10:33 PM | [NSO Update] Visayas Grid-04/25/2024 23:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2259H from reverse power direction. [WEBSMS] | CVIS
4/25/2024 11:10:16 PM | [NSO Update] Luzon Grid-04/25/2024 23:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2259H from reverse power direction. [WEBSMS] | CLUZ
4/25/2024 10:30:08 PM | Visayas Grid-04/25/2024 22:30: Quiot SS 100 MVA TR2 de-energized at 2228H, emergency customers request (Unplanned Outage) [WEBSMS] | CVIS
4/25/2024 9:44:36 PM | [NSO Update] Visayas Grid-04/25/2024 21:44: Update on System Advisory: Visayas Grid Yellow Alert notice issued today has been lifted at 2130H. [WEBSMS] | CVIS
4/25/2024 9:38:49 PM | Visayas Grid-04/25/2024 21:38: PGPP2 Okoy 5 cut-out at 2131H (Planned Outage) [WEBSMS] | CVIS
4/25/2024 8:02:11 PM | Visayas Grid-04/25/2024 20:02: PGPP2 Sogongon U2 cut-in at 1959H (Unplanned Outage) [WEBSMS] | CVIS
4/25/2024 7:45:37 PM | Luzon Grid-04/25/2024 19:45: Lumban 100MVA T01 looped via low side at 1943H (On Commissioning) [WEBSMS] | CLUZ
4/25/2024 6:08:44 PM | [NSO Update] Luzon Grid-04/25/2024 18:08: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=13616MW, PK=12404MW, RR=337MW, NetOpMargin: EVE=875 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW, SUAL 1@600MW, SCPC 1@105MW [WEBSMS] | CLUZ
4/25/2024 6:08:42 PM | [NSO Update] Luzon Grid-04/25/2024 18:08: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=13616MW, PK=12404MW, RR=337MW, NetOpMargin: EVE=875 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW, SUAL 1@600MW, SCPC 1@105MW [WEBSMS] | CLUZ
4/25/2024 6:08:04 PM | [NSO Update] Mindanao Grid-04/25/2024 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2839MW, PK=2521MW, RR=73MW, NetOpMargin: EVE=245 Highest Unit O/L: GNPK 1&2@138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, GNPK 4 @115MW [WEBSMS] | CMIN
4/25/2024 6:06:42 PM | [NSO Update] Visayas Grid-04/25/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2595MW, PK=2445MW, RR=95MW, NetOpMargin: EVE=55 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, CEDC U3 @75MW, Tongonan Power Plant @73MW, Power Barge 104-U3 @5MW, Power Barge 104-U2 @5MW, Panay Diesel 1-U2 @4MW, Panay Diesel 1-U5 @4MW [WEBSMS] | CVIS
4/25/2024 6:06:41 PM | [NSO Update] Visayas Grid-04/25/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2595MW, PK=2445MW, RR=95MW, NetOpMargin: EVE=55 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, CEDC U3 @75MW, Tongonan Power Plant @73MW, Power Barge 104-U3 @5MW, Power Barge 104-U2 @5MW, Panay Diesel 1-U2 @4MW, Panay Diesel 1-U5 @4MW [WEBSMS] | CVIS
4/25/2024 6:02:58 PM | [NSO Update] Mindanao Grid-04/25/2024 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2839MW, PK=2521MW, RR=73MW, NetOpMargin: EVE=245 Highest Unit O/L: GNPK 1&2@138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, GNPK 4 @115MW [WEBSMS] | CMIN
4/25/2024 4:22:59 PM | Mindanao Grid-04/25/2024 16:22: WMPC DG03 shutdown at 1537H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/25/2024 4:17:53 PM | Mindanao Grid-04/25/2024 16:22: WMPC DG03 shutdown at 1537H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/25/2024 3:12:48 PM | Mindanao Grid-04/25/2024 15:12: STEAG (STE)U1 on emergency shutdown at 1500H due to boiler fouling. [WEBSMS] | CMIN
4/25/2024 3:07:42 PM | Mindanao Grid-04/25/2024 15:12: STEAG (STE)U1 on emergency shutdown at 1500H due to boiler fouling. [WEBSMS] | CMIN
4/25/2024 2:01:32 PM | Mindanao Grid-04/25/2024 14:01: WMPC DG05 online at 1341H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
4/25/2024 2:00:04 PM | [NSO Update] Mindanao Grid-04/25/2024 14:00: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1231H with power going to Visayas [WEBSMS] | CMIN
4/25/2024 1:59:01 PM | [NSO Update] Mindanao Grid-04/25/2024 13:59: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1221H from reverse power direction [WEBSMS] | CMIN
4/25/2024 1:56:26 PM | Mindanao Grid-04/25/2024 14:01: WMPC DG05 online at 1341H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
4/25/2024 1:54:58 PM | [NSO Update] Mindanao Grid-04/25/2024 14:00: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1231H with power going to Visayas [WEBSMS] | CMIN
4/25/2024 1:54:34 PM | [NSO Update] Visayas Grid-04/25/2024 13:54: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1231H with power going to Visayas [WEBSMS] | CVIS
4/25/2024 1:54:33 PM | [NSO Update] Visayas Grid-04/25/2024 13:54: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1231H with power going to Visayas [WEBSMS] | CVIS
4/25/2024 1:53:55 PM | [NSO Update] Mindanao Grid-04/25/2024 13:59: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1221H from reverse power direction [WEBSMS] | CMIN
4/25/2024 1:53:41 PM | [NSO Update] Visayas Grid-04/25/2024 13:53: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1221H from reverse power direction [WEBSMS] | CVIS
4/25/2024 1:53:40 PM | [NSO Update] Visayas Grid-04/25/2024 13:53: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1221H from reverse power direction [WEBSMS] | CVIS
4/25/2024 1:44:19 PM | Mindanao Grid-04/25/2024 13:49: Pulangui4 U1 shutdown at 1322H due to low forebay elevation(OMC). [WEBSMS] | CMIN
4/25/2024 1:14:50 PM | Mindanao Grid-04/25/2024 13:19: WMPC DG03 online at 1311H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
4/25/2024 1:08:58 PM | [NSO Update] Mindanao Grid-04/25/2024 13:14: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2996MW, PK=2603MW, RR=73MW, NetOpMargin: PM=320, EVE=433 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, GNPK 4 @115MW [WEBSMS] | CMIN
4/25/2024 1:07:07 PM | [NSO Update] Visayas Grid-04/25/2024 13:07: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2861MW, PK=2579MW, RR=100MW, NetOpMargin: PM=183, EVE=287 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @310MW, CEDC U3 @75MW, Tongonan Power Plant @70MW, Power Barge 104-U3 @5MW, Power Barge 104-U2 @5MW, Panay Diesel 1-U2 @4MW, Panay Diesel 1-U5 @4MW [WEBSMS] | CVIS
4/25/2024 1:00:59 PM | [NSO Update] Luzon Grid-04/25/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14795MW, PK=13825MW, RR=361MW, NetOpMargin: PM=609, EVE=810 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
4/25/2024 1:00:57 PM | [NSO Update] Luzon Grid-04/25/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14795MW, PK=13825MW, RR=361MW, NetOpMargin: PM=609, EVE=810 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @500MW [WEBSMS] | CLUZ
4/25/2024 12:29:22 PM | Mindanao Grid-04/25/2024 12:34: Minergy Coal Plant/ MCC Unit 3 ( Balingasag) synchronized at 1204H from unplanned outage. [WEBSMS] | CMIN
4/25/2024 11:18:57 AM | [NSO Update] Mindanao Grid-04/25/2024 11:24: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1115H with power going to Mindanao [WEBSMS] | CMIN
4/25/2024 11:18:35 AM | [NSO Update] Visayas Grid-04/25/2024 11:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1115H with power going to Mindanao [WEBSMS] | CVIS
4/25/2024 10:45:17 AM | Mindanao Grid-04/25/2024 10:50: Tagoloan- Manolo Fortich 138 kV Line 1 energized at 1038H from emergency shutdown . [WEBSMS] | CMIN
4/25/2024 10:24:58 AM | [NSO Update] Mindanao Grid-04/25/2024 10:30: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0954H from forward power direction [WEBSMS] | CMIN
4/25/2024 10:24:36 AM | [NSO Update] Visayas Grid-04/25/2024 10:24: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0954H from forward power direction [WEBSMS] | CVIS
4/25/2024 10:12:05 AM | [NSO Update] Visayas Grid-04/25/2024 10:12: THIS IS ONLY A DRILL: Luzon-Visayas and Mindanao-Visayas HVDC referencing activities are now transferred back to the Central Grid Operations (CGO) at 1003H. [WEBSMS] | CVIS
4/25/2024 10:09:02 AM | Mindanao Grid-04/25/2024 10:14: WMPC DG07 online at 0959H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
4/25/2024 9:04:12 AM | Mindanao Grid-04/25/2024 09:09: WMPC DG04 online at 0901H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
4/25/2024 8:42:09 AM | [NSO Update] Visayas Grid-04/25/2024 08:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0828H with power going to Visayas [WEBSMS] | CVIS
4/25/2024 8:41:48 AM | [NSO Update] Luzon Grid-04/25/2024 08:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0828H with power going to Visayas [WEBSMS] | CLUZ
4/25/2024 8:39:33 AM | [NSO Update] Visayas Grid-04/25/2024 08:39: THIS IS ONLY A DRILL: For information, the Central Grid Operations (CGO) evacuated at 0839H due to fire. Luzon-Visayas HVDC referencing was delegated to VRCC while the Mindanao-Visayas HVDC referencing was delegated to MRCC. [WEBSMS] | CVIS
4/25/2024 8:35:50 AM | Mindanao Grid-04/25/2024 08:40: WMPC DG10 online at 0827H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
4/25/2024 8:21:37 AM | [NSO Update] Visayas Grid-04/25/2024 08:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0818H from forward power direction. [WEBSMS] | CVIS
4/25/2024 8:21:10 AM | [NSO Update] Luzon Grid-04/25/2024 08:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0818H from forward power direction. [WEBSMS] | CLUZ
4/25/2024 8:21:09 AM | [NSO Update] Luzon Grid-04/25/2024 08:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0818H from forward power direction. [WEBSMS] | CLUZ
4/25/2024 7:43:01 AM | Mindanao Grid-04/25/2024 07:48: Tagoloan- Manolo Fortich 138 kV Line 1 de-energized at 0740H as emergency shutdown due to hotspot correction at drop wire between DS75TG123 (7Z-05DS123TAG) and DS 75TG05 (7Z-05DS05TAG) Phase B. [WEBSMS] | CMIN
4/25/2024 7:03:39 AM | Mindanao Grid-04/25/2024 07:08: Minergy Coal Plant/ MCC U3 ( Balingasag) tripped at 0652H with 33.92 MW gross generation.(Unplanned Outage) [WEBSMS] | CMIN
4/25/2024 6:53:43 AM | [NSO Update] Mindanao Grid-04/25/2024 06:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2861MW, PK=2540MW, RR=73MW, NetOpMargin: AM=249, PM=173, EVE=318 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, GNPK 4 @105MW [WEBSMS] | CMIN
4/25/2024 6:51:17 AM | [NSO Update] Luzon Grid-04/25/2024 06:51: System Advisory: 25-Apr-2024, Luzon Grid is on YELLOW Alert for interval hours 1400H-1700H and 2000H-2300H. Total capacity on forced outage is 1224.3MW. Total of de-rated capacity is 200MW. [WEBSMS] | CLUZ
4/25/2024 6:51:16 AM | [NSO Update] Luzon Grid-04/25/2024 06:51: System Advisory: 25-Apr-2024, Luzon Grid is on YELLOW Alert for interval hours 1400H-1700H and 2000H-2300H. Total capacity on forced outage is 1224.3MW. Total of de-rated capacity is 200MW. [WEBSMS] | CLUZ
4/25/2024 6:50:13 AM | [NSO Update] Visayas Grid-04/25/2024 06:50: System Advisory: 25-Apr-2024, Visayas Grid is on YELLOW Alert for interval hours 1400H-1600H, 1900H, and 2100H. Total capacity on forced outage is 424.7MW. Total of de-rated capacity is 246.1MW. [WEBSMS] | CVIS
4/25/2024 6:49:08 AM | [NSO Update] Visayas Grid-04/25/2024 06:49: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2699MW, PK=2405MW, RR=96MW, NetOpMargin: AM=197, PM=174, EVE=184 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @312MW, CEDC U3 @75MW, TGPP @70MW, PB 104-U3 @5MW, PB 104-U2 @5MW, Nasulo Geothermal @45MW, Panay Diesel 3-C @11MW, BBPP U1 @3.5MW, BDPP U2 @3.5MW, BDPP U3 @3.7MW, BDPP U4 @3.5MW, Panay Diesel 1-U5 @4MW [WEBSMS] | CVIS
4/25/2024 6:34:07 AM | [NSO Update] Luzon Grid-04/25/2024 06:34: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=15005MW, PK=13142MW, RR=384MW, NetOpMargin: AM=1479, PM=266, EVE=30 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @400MW [WEBSMS] | CLUZ
4/25/2024 6:34:06 AM | [NSO Update] Luzon Grid-04/25/2024 06:34: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=15005MW, PK=13142MW, RR=384MW, NetOpMargin: AM=1479, PM=266, EVE=30 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @400MW [WEBSMS] | CLUZ
4/25/2024 4:49:05 AM | [NSO Update] Mindanao Grid-04/25/2024 04:54: Weather Update: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
4/25/2024 4:48:26 AM | [NSO Update] Visayas Grid-04/25/2024 04:48: Weather Update: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
4/25/2024 4:48:09 AM | [NSO Update] Luzon Grid-04/25/2024 04:48: Weather Update: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
4/25/2024 3:01:32 AM | Mindanao Grid-04/25/2024 03:06: SMCPC U2 online at 0259H. (Unplanned Outage) [WEBSMS] | CMIN
4/25/2024 1:58:52 AM | Mindanao Grid-04/25/2024 02:04: TM2 U1 online at 0153H. MOT Raise. (Planned Outage) [WEBSMS] | CMIN
4/25/2024 1:15:36 AM | Mindanao Grid-04/25/2024 01:20: SMCPC U2 tripped with 51MW load at 0104H. (Unplanned Outage) [WEBSMS] | CMIN
4/25/2024 1:07:54 AM | Luzon Grid-04/25/2024 01:07: Laoag Solar - Laoag Solar 2 230kV Line 1 energized at 0104H (On Commissioning Test) [WEBSMS] | CLUZ
4/25/2024 1:07:35 AM | Luzon Grid-04/25/2024 01:07: Laoag Solar - Laoag Solar 2 230kV Line 1 energized at 0104H (On Commissioning Test) [WEBSMS] | CLUZ
4/25/2024 12:12:59 AM | Luzon Grid-04/25/2024 00:12: Laoag Solar-Laoag Solar 2 230kV Line 2 energized at 0011H (On Commissioning Test) [WEBSMS] | CLUZ
4/25/2024 12:12:40 AM | Luzon Grid-04/25/2024 00:12: Laoag Solar-Laoag Solar 2 230kV Line 2 energized at 0011H (On Commissioning Test) [WEBSMS] | CLUZ
4/24/2024 11:23:07 PM | [NSO Update] Luzon Grid-04/24/2024 23:23: Update on System Advisory: Luzon Grid Yellow Alert notice issued today has been lifted at 2320H. [WEBSMS] | CLUZ
4/24/2024 9:58:22 PM | [NSO Update] Visayas Grid-04/24/2024 21:58: Update on System Advisory: Visayas Grid Yellow Alert notice issued today has been lifted at 2156H. [WEBSMS] | CVIS
4/24/2024 8:57:31 PM | [NSO Update] Visayas Grid-04/24/2024 20:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2052H with power going to Luzon [WEBSMS] | CVIS
4/24/2024 8:57:08 PM | [NSO Update] Luzon Grid-04/24/2024 20:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2052H with power going to Luzon [WEBSMS] | CLUZ
4/24/2024 8:47:42 PM | [NSO Update] Visayas Grid-04/24/2024 20:48: Update on System Advisory: Visayas Grid Red Alert notice issued today is lifted at 2043H. Visayas Grid still on Yellow Alert for interval 2100H. [WEBSMS] | CVIS
4/24/2024 8:44:40 PM | [NSO Update] Visayas Grid-04/24/2024 20:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2042H from reverse power direction [WEBSMS] | CVIS
4/24/2024 8:44:05 PM | [NSO Update] Luzon Grid-04/24/2024 20:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2042H from reverse power direction [WEBSMS] | CLUZ
4/24/2024 7:48:43 PM | Mindanao Grid-04/24/2024 19:54: Balo-i - Luga-it 138kV Line restored/loop at 1947H. (Unplanned Outage) [WEBSMS] | CMIN
4/24/2024 7:47:26 PM | Mindanao Grid-04/24/2024 19:52: Balo-i - Agus2 138kV Line1 restored/re-energized at 1945H. (Unplanned Outage) [WEBSMS] | CMIN
4/24/2024 6:01:10 PM | [NSO Update] Visayas Grid-04/24/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=2349MW, PK=2413MW, RR=92MW, NetOpMargin: EVE=0 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @300MW, CEDC U3 @75MW, TGPP @65MW, PB104-U3 @5MW, PB104-U2 @5MW, Nasulo Geothermal @45MW, PDPP3-C @11MW, PDPP3-E @9MW, BDPP U1 @3.5MW, BDPP U2 @3.5MW, BDPP U3 @3.7MW, BDPP U4 @3.5MW, PDPP1-U5 @4MW [WEBSMS] | CVIS
4/24/2024 5:55:25 PM | [NSO Update] Luzon Grid-04/24/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=13598MW, PK=12538MW, RR=467MW, NetOpMargin: EVE=593 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @400MW [WEBSMS] | CLUZ
4/24/2024 5:48:36 PM | [NSO Update] Mindanao Grid-04/24/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2773MW, PK=2488MW, RR=73MW, NetOpMargin: EVE=212 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, AG1 @35MW, AG2 @50MW, AG4 @70MW, AG5 @20MW, AG6 @91MW, AG7 @17MW, PG4 @50MW [WEBSMS] | CMIN
4/24/2024 5:33:44 PM | Mindanao Grid-04/24/2024 17:39: Balo-i - Luga-it 138kV Line tripped/open at Balo-i side only at 1712H. Affected by the tripping of Balo-i - Agus2 138kV L1. (Unplanned Outage) [WEBSMS] | CMIN
4/24/2024 5:31:02 PM | Mindanao Grid-04/24/2024 17:36: Balo-i -Agus2 138kV Line1 tripped at 1712H. (Unplanned Outage) [WEBSMS] | CMIN
4/24/2024 5:11:01 PM | Mindanao Grid-04/24/2024 17:16: SMCPC U2 online at 1705H. (Unplanned Outage) [WEBSMS] | CMIN
4/24/2024 5:09:09 PM | Mindanao Grid-04/24/2024 17:14: Mt. Apo U2 online at 1702H. (Unplanned Outage) [WEBSMS] | CMIN
4/24/2024 5:03:49 PM | Mindanao Grid-04/24/2024 17:09: Bunawan - Maco 138kV Line restored/re-energized at 1701H. (Unplanned Outage) [WEBSMS] | CMIN
4/24/2024 4:16:30 PM | [NSO Update] Luzon Grid-04/24/2024 16:16: Update on System Advisory: Luzon Grid Red Alert notice issued today is lifted at 1605H. Luzon Grid still on Yellow Alert for intervals 1700H-2300H. [WEBSMS] | CLUZ
4/24/2024 3:44:05 PM | Luzon Grid-04/24/2024 15:44: System Advisory: The Highest Luzon Grid Peak Load for the year 2024 is 14,016MW occurred at 1454H today, April 24, 2024, Wednesday. The previous highest peak was 13,864MW which occurred yesterday April 23, 2024, Tuesday at 1447H. [WEBSMS] | CLUZ
4/24/2024 3:16:06 PM | [NSO Update] Mindanao Grid-04/24/2024 15:21: Update on System Advisory: Mindanao Grid Yellow Alert notice issued today has been lifted at 1509H. [WEBSMS] | CMIN
4/24/2024 3:05:27 PM | Luzon Grid-04/24/2024 15:05: April 24, 2024: Demand Control Imminent Warning (DCIW) is issued at 1501H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency [WEBSMS] | CLUZ
4/24/2024 2:36:43 PM | Mindanao Grid-04/24/2024 14:42: Bunawan - Maco 138kV Line tripped at 1423H. (Unplanned Outage) [WEBSMS] | CMIN
4/24/2024 2:22:29 PM | Visayas Grid-04/24/2024 14:22: Magdugo-Calatrava 230 KV Line 2 energized at 1404H. (Unplanned Outage) [WEBSMS] | CVIS
4/24/2024 2:17:12 PM | Mindanao Grid-04/24/2024 14:22: Mt. Apo Unit2 tripped with 37MW load at 1409H. (Unplanned Outage) [WEBSMS] | CMIN
4/24/2024 1:56:58 PM | [NSO Update] Visayas Grid-04/24/2024 13:57: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=2593MW, PK=2564MW, RR=100MW, NetOpMargin: PM=0, EVE=0 Highest Unit O/L: Leyte A @315MW, CEDC U3 @75MW, Tongonan Power Plant @60MW, Power Barge 104-U3 @5MW, Power Barge 104-U2 @5MW, Nasulo Geothermal @45MW, Panay Diesel 3-C @11MW, Panay Diesel 3-E @9MW Derated Plant: [WEBSMS] | CVIS
4/24/2024 1:30:04 PM | [NSO Update] Mindanao Grid-04/24/2024 13:35: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2862MW, PK=2672MW, RR=73MW, NetOpMargin: PM=118, EVE=230 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, GNPK 4 @115MW [WEBSMS] | CMIN
4/24/2024 1:28:17 PM | [NSO Update] Luzon Grid-04/24/2024 13:28: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=14801MW, PK=13903MW, RR=494MW, NetOpMargin: PM=404, EVE=465 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @400MW [WEBSMS] | CLUZ
4/24/2024 12:16:07 PM | Mindanao Grid-04/24/2024 12:21: WMPC DG3 online at 1213H. RPS - System Voltage Requirement. (Planned Outage) [WEBSMS] | CMIN
4/24/2024 10:37:55 AM | Mindanao Grid-04/24/2024 10:43: WMPC DG1 online at 1029H. MOT Raise. (Planned Outage) [WEBSMS] | CMIN
4/24/2024 10:36:37 AM | Mindanao Grid-04/24/2024 10:41: WMPC DG7 online at 1034H. RPS - System Voltage Requirement. (Planned Outage) [WEBSMS] | CMIN
4/24/2024 9:02:15 AM | Mindanao Grid-04/24/2024 09:07: WMPC DG4 online at 0900H. RPS - System Voltage Requirement. (Planned Outage) [WEBSMS] | CMIN
4/24/2024 8:40:02 AM | [NSO Update] Visayas Grid-04/24/2024 08:40: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0815H with power going to Visayas. [WEBSMS] | CVIS
4/24/2024 8:39:05 AM | [NSO Update] Luzon Grid-04/24/2024 08:39: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0815H with power going to Visayas. [WEBSMS] | CLUZ
4/24/2024 8:35:53 AM | [NSO Update] Visayas Grid-04/24/2024 08:36: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0805H from forward power direction. [WEBSMS] | CVIS
4/24/2024 8:34:54 AM | [NSO Update] Luzon Grid-04/24/2024 08:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0805H from forward power direction. [WEBSMS] | CLUZ
4/24/2024 8:31:49 AM | Visayas Grid-04/24/2024 08:32: Carcon-Sangi 34.5KV line 1 de-energized at 0815H (Planned Outage) [WEBSMS] | CVIS
4/24/2024 8:29:35 AM | Mindanao Grid-04/24/2024 08:34: WMPC DG10 online at 0827H. RPS - System Voltage Requirement. (Planned Outage) [WEBSMS] | CMIN
4/24/2024 8:26:42 AM | Mindanao Grid-04/24/2024 08:32: TM1 U1 online at 0801H. DENR Emission Testing. (Planned Outage) [WEBSMS] | CMIN
4/24/2024 8:23:25 AM | Luzon Grid-04/24/2024 08:23: GN Power 1 online at 0822H (Unplanned Outage) [WEBSMS] | CLUZ
4/24/2024 7:34:29 AM | [NSO Update] Mindanao Grid-04/24/2024 07:39: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2762MW, PK=2578MW, RR=73MW, NetOpMargin: AM=112, PM=75, EVE=148 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, GNPK 4 @105MW [WEBSMS] | CMIN
4/24/2024 7:31:28 AM | Visayas Grid-04/24/2024 07:31: Magdugo-Calatrava 230 KV Line 2 de-energized at 0709H. (Unplanned Outage) [WEBSMS] | CVIS
4/24/2024 7:28:33 AM | [NSO Update] Visayas Grid-04/24/2024 07:28: GRID UPDATE AS OF 6:00 AM System Condition: RED ALERT CAP=2617MW, PK=2444MW, RR=96MW, NetOpMargin: AM=77, PM=0, EVE=0 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @315MW, CEDC U3 @75MW, Tongonan Power Plant @60MW, Power Barge 104-U3 @5MW, Power Barge 104-U2 @5MW, Nasulo Geothermal @45MW, Panay Diesel 3-C @11MW, Panay Diesel 3-E @9MW [WEBSMS] | CVIS
4/24/2024 7:14:40 AM | [NSO Update] Mindanao Grid-04/24/2024 07:20: System Advisory: 24-Apr-2024, Mindanao Grid is on YELLOW Alert for interval hours 1100H-1600H. Total capacity on forced outage is 545.4MW. Total of de-rated capacity is 128.58MW. [WEBSMS] | CMIN
4/24/2024 7:03:02 AM | [NSO Update] Visayas Grid-04/24/2024 07:03: System Advisory: 24-Apr-2024, Visayas Grid is on RED Alert for interval hour 1300H-1700H, 1900H, and 2000H, while YELLOW Alert for interval hours 1100H, 1200H, 1800H, and 2100H. Total capacity on forced outage is 368.5MW. Total of de-rated capacity is 253.1MW. [WEBSMS] | CVIS
4/24/2024 7:02:24 AM | [NSO Update] Luzon Grid-04/24/2024 07:02: System Advisory: 24-Apr-2024, Luzon Grid is on RED Alert for interval hour 1600H, while YELLOW Alert for interval hours 1400H, 1500H, 1700H, 1800H, and 1900H-2200H. Total capacity on forced outage is 1540.3MW. Total of de-rated capacity is 300MW. [WEBSMS] | CLUZ
4/24/2024 6:39:15 AM | Mindanao Grid-04/24/2024 06:44: PULANGI 4 Unit 1 HEP online at 0555H from OMC outage. (Unplanned Outage) [WEBSMS] | CMIN
4/24/2024 5:44:29 AM | [NSO Update] Luzon Grid-04/24/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: RED ALERT CAP=14613MW, PK=13016MW, RR=476MW, NetOpMargin: AM=1121, PM=106, EVE=348 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @ 340MW, Ilijan B @ 560MW [WEBSMS] | CLUZ
4/24/2024 5:17:00 AM | Mindanao Grid-04/24/2024 05:22: GNPK Unit 3 tripped at 0503H. No ALD. (Unplanned Outage) [WEBSMS] | CMIN
4/24/2024 5:06:54 AM | Luzon Grid-04/24/2024 05:07: Taytay-Masinag 115kV Line (CO) restored at 0506H. (Planned Outage) [WEBSMS] | CLUZ
4/24/2024 4:26:45 AM | [NSO Update] Visayas Grid-04/24/2024 04:27: Weather Update: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
4/24/2024 4:26:28 AM | [NSO Update] Mindanao Grid-04/24/2024 04:31: Weather Update: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
4/24/2024 4:25:30 AM | [NSO Update] Luzon Grid-04/24/2024 04:25: Weather Update: Intertropical Convergence Zone (ITCZ) affecting southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
4/24/2024 3:45:50 AM | Luzon Grid-04/24/2024 03:46: San Jose - Camarin 115kV Line restored at 0343H (Planned Outage) [WEBSMS] | CLUZ
4/24/2024 2:07:42 AM | Mindanao Grid-04/24/2024 02:13: NagaMin SS SVC (7XF03NAA) energized at 0205H. (Unplanned outage) [WEBSMS] | CMIN
4/24/2024 1:02:22 AM | Luzon Grid-04/24/2024 01:02: Taytay-Masinag 115kV Line (CO) de-energized at 0100H. (Planned Outage) [WEBSMS] | CLUZ
4/24/2024 1:00:01 AM | Mindanao Grid-04/24/2024 01:05: NagaMin SS SVC (7XF03NAA) de-energized at 0052H. Unplanned Outage. [WEBSMS] | CMIN
4/24/2024 12:54:52 AM | Mindanao Grid-04/24/2024 01:00: Zamboanga-Pitogo 138kV Line 2 restored/energized at 0047H. (Planned Outage) [WEBSMS] | CMIN
4/24/2024 12:30:48 AM | [NSO Update] Luzon Grid-04/24/2024 00:31: Luzon Grid Yellow Alert notice issued on April 23, 2024 has been lifted at 0029H of April 24, 2024. [WEBSMS] | CLUZ
4/23/2024 11:46:12 PM | Luzon Grid-04/23/2024 23:46: San Jose-Camarin 115kV Line de-energized at 2343H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2024 11:01:52 PM | [NSO Update] Luzon Grid-04/23/2024 23:02: Luzon Grid Red Alert notice issued today is lifted at 2255H. Luzon Grid still on Yellow Alert for intervals 2300H and 2400H. [WEBSMS] | CLUZ
4/23/2024 9:34:13 PM | Mindanao Grid-04/23/2024 21:39: WMPC DG02 declared available at 2130H. (Unplanned Outage). [WEBSMS] | CMIN
4/23/2024 9:00:03 PM | [NSO Update] Visayas Grid-04/23/2024 21:00: Update on System Advisory: Visayas Grid YELLOW Alert notice issued today has been lifted at 2059H. [WEBSMS] | CVIS
4/23/2024 8:08:11 PM | Mindanao Grid-04/23/2024 20:13: WMPC DG02 tripped at 1940H. (Unplanned outage) [WEBSMS] | CMIN
4/23/2024 7:09:20 PM | Luzon Grid-04/23/2024 19:09: SCPC 3 online at 1857H. (Unplanned Outage) [WEBSMS] | CLUZ
4/23/2024 7:07:15 PM | Luzon Grid-04/23/2024 19:07: SCPC 1 online at 1543H. (Unplanned Outage) [WEBSMS] | CLUZ
4/23/2024 6:00:06 PM | [NSO Update] Luzon Grid-04/23/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=12707MW, PK=12654MW, RR=467MW, NetOpMargin: EVE=0 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SCPC @25MW, ILIJAN A @400MW [WEBSMS] | CLUZ
4/23/2024 5:52:11 PM | [NSO Update] Visayas Grid-04/23/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2610MW, PK=2424MW, RR=93MW, NetOpMargin: EVE=93 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @312MW, PGPP1 @110.5MW [WEBSMS] | CVIS
4/23/2024 5:51:23 PM | [NSO Update] Mindanao Grid-04/23/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2897MW, PK=2418MW, RR=73MW, NetOpMargin: EVE=406 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @98MW, AG7 @19MW, PG4 @20MW, GNPK 3 @83MW, GNPK 4 @105MW [WEBSMS] | CMIN
4/23/2024 5:45:17 PM | Luzon Grid-04/23/2024 17:45: (RESENDING) - For info: GMEC 1 @312MW, SCPC1 @150MW, SCPC3 @150MW and BCCPP Block B at 147MW simultaneously tripped at 1530H. (Unplanned Outage) [WEBSMS] | CLUZ
4/23/2024 5:43:14 PM | Luzon Grid-04/23/2024 17:43: (RESENDING) - For infor: ALD occured at Meralco and NGCP area at 1530H due to tripping of Balsik - San Jose 500kV Line and activation of SIPS. Lowest system frequency is 59.006Hz. [WEBSMS] | CLUZ
4/23/2024 5:12:32 PM | Mindanao Grid-04/23/2024 17:17: TM2 Unit 1 shutdown at 1706H. (Unplanned Outage) [WEBSMS] | CMIN
4/23/2024 5:00:26 PM | [NSO Update] Luzon Grid-04/23/2024 17:00: SO-initiated Market Intervention for the Luzon Grid has been lifted today, 23 April 2024, at 1649H. Market operations will resume starting interval 1655H. [WEBSMS] | CLUZ
4/23/2024 4:58:44 PM | Visayas Grid-04/23/2024 16:58: This is a drill, VRCC dispatching activities is now transferred back to the Visayas Regional Control Center at 1700H. [WEBSMS] | CVIS
4/23/2024 4:49:25 PM | Visayas Grid-04/23/2024 16:49: �This is a drill, VRCC dispatching activities is transferred to the Visayas Back-up Regional Control Center in Mandaue at 1638H. [WEBSMS] | CVIS
4/23/2024 4:21:14 PM | [NSO Update] Luzon Grid-04/23/2024 16:21: [ERRATUM] System Advisory Update: Luzon Grid is on RED Alert for interval hours 1600H, 1900H-2200H and YELLOW Alert for interval hours 1700H-1800H and 2300H-2400H. Total capacity on forced outage is 1684.9MW. Total of de-rated capacity is 425MW. [WEBSMS] | CLUZ
4/23/2024 4:13:20 PM | [NSO Update] Visayas Grid-04/23/2024 16:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1608H with power going to Luzon [WEBSMS] | CVIS
4/23/2024 4:12:50 PM | [NSO Update] Luzon Grid-04/23/2024 16:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1608H with power going to Luzon [WEBSMS] | CLUZ
4/23/2024 4:12:16 PM | [NSO Update] Visayas Grid-04/23/2024 16:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1557H from reverse power direction [WEBSMS] | CVIS
4/23/2024 4:04:32 PM | [NSO Update] Luzon Grid-04/23/2024 16:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1557H from reverse power direction [WEBSMS] | CLUZ
4/23/2024 4:01:59 PM | Luzon Grid-04/23/2024 16:02: For info: GMEC 1 @312MW, SCPC1 @150MW, SCPC3@150MW and BCCPP Block B at 147MW simultaneously tripped at 1530H. [WEBSMS] | CLUZ
4/23/2024 3:53:13 PM | Luzon Grid-04/23/2024 15:53: Affected ALD feeders of NGCP and MERALCO restored at 1546H AND 1550H, respectively. [WEBSMS] | CLUZ
4/23/2024 3:46:30 PM | [NSO Update] Luzon Grid-04/23/2024 15:46: SO-initiated Market Intervention is issued today for the Luzon grid starting interval 1540H after implementation of Manual Load Dropping (MLD) due to generation deficiency. [WEBSMS] | CLUZ
4/23/2024 3:46:19 PM | [NSO Update] Luzon Grid-04/23/2024 15:46: System Advisory Update: Luzon Grid is on RED Alert for interval hours 1600H, 1900H-2200H and YELLOW Alert for interval hours 1700H-1800H and 2300H-2400H. Total capacity on forced outage is 1834.9MW. Total of de-rated capacity is 300MW. [WEBSMS] | CLUZ
4/23/2024 3:41:21 PM | Luzon Grid-04/23/2024 15:41: Balsik - San Jose 500kV Line restored at 1537H. (Unplanned Outage) [WEBSMS] | CLUZ
4/23/2024 3:39:54 PM | Luzon Grid-04/23/2024 15:40: For infor: ALD occured at Meralco and NGCP at 1530H are due to tripping of Balsik - San Jose 500kV Line and activation of SIPS. Lowest system frequency is 59.006Hz. [WEBSMS] | CLUZ
4/23/2024 2:38:49 PM | Visayas Grid-04/23/2024 14:39: "THIS IS A DRILL " Cebu Sub-Grid PRH completed 0950H to 1257H."THIS IS A DRILL" [WEBSMS] | CVIS
4/23/2024 1:50:13 PM | Visayas Grid-04/23/2024 13:50: This is a drill, VRCC has received instructions to evacuate at 1340H. The VRCC temporary dispatching activities will continue at the Modular Dispatch Center and will be transferred to the Visayas Back-up Regional Control Center at the Mandaue GIS in approximately 30 minutes. [WEBSMS] | CVIS
4/23/2024 1:38:56 PM | Visayas Grid-04/23/2024 13:39: This is a drill, the Visayas Regional Control Center Shift personnel on duty have exited Building No. 1 due to the occurrence of an earthquake. VRCC dispatching activities is temporarily transferred to the Modular Dispatch Center at the back of the RCC building pending assessment and further instructions. [WEBSMS] | CVIS
4/23/2024 1:27:02 PM | Mindanao Grid-04/23/2024 13:32: AGUS 4 HEP Unit 3 shutdown at 1301H. (Unplanned Outage) [WEBSMS] | CMIN
4/23/2024 1:24:13 PM | Mindanao Grid-04/23/2024 13:29: WMPC DG04 online at 1317H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/23/2024 1:20:48 PM | [NSO Update] Visayas Grid-04/23/2024 13:21: System Advisory: Visayas Grid is on YELLOW Alert for interval hours 1400H-2000H. Total capacity on forced outage is 355.8MW. Total of de-rated capacity is 248.6MW. [WEBSMS] | CVIS
4/23/2024 1:19:21 PM | [NSO Update] Luzon Grid-04/23/2024 13:19: System Advisory: Luzon Grid is on YELLOW Alert for interval hours 1400H-1700H and 1900H-2200H. Total capacity on forced outage is 1218.9MW. Total of de-rated capacity is 300MW. [WEBSMS] | CLUZ
4/23/2024 1:15:03 PM | [NSO Update] Mindanao Grid-04/23/2024 13:20: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2948MW, PK=2603MW, RR=73MW, NetOpMargin: PM=272, EVE=365 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, GNPK 3 @83MW, GNPK 4 @105MW [WEBSMS] | CMIN
4/23/2024 1:15:00 PM | [NSO Update] Visayas Grid-04/23/2024 13:15: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2742MW, PK=2571MW, RR=99MW, NetOpMargin: PM=72, EVE=81 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @305MW, CEDC U3 @75MW, Tongonan Power Plant @79.5MW, Power Barge 104-U3 @5MW, Power Barge 104-U2 @5MW, Nasulo Geothermal @45MW, Panay Diesel 3-C @11MW, Panay Diesel 3-E @9MW, Panay Diesel 3-G @8MW [WEBSMS] | CVIS
4/23/2024 1:14:54 PM | [NSO Update] Luzon Grid-04/23/2024 13:15: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=14799MW, PK=13690MW, RR=494MW, NetOpMargin: PM=615, EVE=480 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @340MW, ILIJAN B @560MW [WEBSMS] | CLUZ
4/23/2024 10:56:36 AM | Mindanao Grid-04/23/2024 11:01: WMPC DG06 online at 1044H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/23/2024 10:43:34 AM | [NSO Update] Visayas Grid-04/23/2024 10:43: THIS IS ONLY A DRILL: SO-initiated market intervention has been issued today, starting interval 0955H, due to the total system blackout of the Visayas grid. [WEBSMS] | CVIS
4/23/2024 10:35:32 AM | Mindanao Grid-04/23/2024 10:40: AGUS 4 HEP Unit 3 online at 1015H. (Unplanned Outage) [WEBSMS] | CMIN
4/23/2024 10:25:54 AM | Visayas Grid-04/23/2024 10:26: "THIS IS A DRILL " Cebu Sub-grid Black-Start Plant CPPC cut-in at 1004H, TPVI CUT-IN at 0959H, TPC-CARMEN cut-in at 1006H, EAUC cut-in at 1005H."THIS IS A DRILL" [WEBSMS] | CVIS
4/23/2024 10:21:28 AM | Mindanao Grid-04/23/2024 10:26: WMPC DG07 online at 0958H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/23/2024 9:53:54 AM | Visayas Grid-04/23/2024 09:54: "THIS IS A DRILL " Visayas Total Power Blackout at 0950H due to tripping of Magdugo-Cebu 230KV TL Line 1 & 2. "THIS IS A DRILL". (Unplanned Outage) [WEBSMS] | CVIS
4/23/2024 9:08:05 AM | Mindanao Grid-04/23/2024 09:13: WMPC DG01 online at 0903H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/23/2024 9:06:40 AM | Mindanao Grid-04/23/2024 09:12: WMPC DG10 online at 0830H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/23/2024 8:01:49 AM | [NSO Update] Visayas Grid-04/23/2024 08:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0751H with power going to Visayas [WEBSMS] | CVIS
4/23/2024 8:01:34 AM | [NSO Update] Luzon Grid-04/23/2024 08:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0751H with power going to Visayas [WEBSMS] | CLUZ
4/23/2024 7:59:25 AM | [NSO Update] Luzon Grid-04/23/2024 07:59: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0741H from forward power direction [WEBSMS] | CLUZ
4/23/2024 7:59:01 AM | [NSO Update] Visayas Grid-04/23/2024 07:59: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0741H from forward power direction [WEBSMS] | CVIS
4/23/2024 7:18:02 AM | Mindanao Grid-04/23/2024 07:23: PULANGI 4 HEP Unit 1 shutdown at 0650H. (Unplanned Outage) [WEBSMS] | CMIN
4/23/2024 6:35:17 AM | Mindanao Grid-04/23/2024 06:40: Zamboanga-Pitogo 138kV Line 2 de-energized at 0629H. (Planned Outage) [WEBSMS] | CMIN
4/23/2024 6:02:23 AM | [NSO Update] Luzon Grid-04/23/2024 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14700MW, PK=12581MW, RR=476MW, NetOpMargin: AM=1643, PM=670, EVE=760 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 340MW, Ilijan B @ 560MW [WEBSMS] | CLUZ
4/23/2024 5:29:03 AM | [NSO Update] Visayas Grid-04/23/2024 05:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3006MW, PK=2484MW, RR=95MW, NetOpMargin: AM=428, PM=203, EVE=224 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 315MW [WEBSMS] | CVIS
4/23/2024 5:26:52 AM | [NSO Update] Mindanao Grid-04/23/2024 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3029MW, PK=2499MW, RR=73MW, NetOpMargin: AM=457, PM=345, EVE=434 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @98MW, AG7 @19MW, PG4 @40MW [WEBSMS] | CMIN
4/23/2024 4:03:39 AM | [NSO Update] Mindanao Grid-04/23/2024 04:08: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CMIN
4/23/2024 4:03:27 AM | [NSO Update] Visayas Grid-04/23/2024 04:03: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CVIS
4/23/2024 4:03:11 AM | [NSO Update] Luzon Grid-04/23/2024 04:03: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CLUZ
4/22/2024 10:15:11 PM | Mindanao Grid-04/22/2024 22:20: WMPC DG10 shutdown at 2215H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/22/2024 10:07:41 PM | Mindanao Grid-04/22/2024 22:13: WMPC DG01 shutdown at 2159H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/22/2024 10:06:59 PM | Mindanao Grid-04/22/2024 22:12: WMPC DG07 shutdown at 2144H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/22/2024 8:52:30 PM | Mindanao Grid-04/22/2024 20:57: Therma 1 Unit 2 with 31.6MW load tripped at 2046H. Frequency dip to 59.654Hz no ALD activation. Details of tripping to follow. (Unplanned Outage) [WEBSMS] | CMIN
4/22/2024 8:45:19 PM | [NSO Update] Visayas Grid-04/22/2024 20:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2041H with power going to Luzon [WEBSMS] | CVIS
4/22/2024 8:44:39 PM | [NSO Update] Luzon Grid-04/22/2024 20:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2041H with power going to Luzon [WEBSMS] | CLUZ
4/22/2024 8:43:14 PM | [NSO Update] Visayas Grid-04/22/2024 20:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2031H from reverse power direction [WEBSMS] | CVIS
4/22/2024 8:42:38 PM | [NSO Update] Luzon Grid-04/22/2024 20:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2031H from reverse power direction [WEBSMS] | CLUZ
4/22/2024 5:59:43 PM | [NSO Update] Mindanao Grid-04/22/2024 18:05: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3003MW, PK=2473MW, RR=72MW, NetOpMargin: EVE=458 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @98MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/22/2024 5:56:23 PM | [NSO Update] Visayas Grid-04/22/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2682MW, PK=2355MW, RR=92MW, NetOpMargin: EVE=236 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @78MW, LEYTE A @315MW [WEBSMS] | CVIS
4/22/2024 5:51:37 PM | [NSO Update] Luzon Grid-04/22/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13613MW, PK=12320MW, RR=287MW, NetOpMargin: EVE=1006 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: None [WEBSMS] | CLUZ
4/22/2024 5:42:09 PM | Visayas Grid-04/22/2024 17:42: PGPP I Unit#3 cut-in to the system @1727H. ( Unplanned Outage ) [WEBSMS] | CVIS
4/22/2024 5:13:31 PM | Mindanao Grid-04/22/2024 17:18: WMPC DG04 shutdown at 1712H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/22/2024 5:07:07 PM | Mindanao Grid-04/22/2024 17:12: Baloi - Agus 6 138kV Line energized at 1702H. Planned Outage [WEBSMS] | CMIN
4/22/2024 4:31:18 PM | Luzon Grid-04/22/2024 16:31: Ilijan GT1-1 online at 1629H (Unplanned Outage) [WEBSMS] | CLUZ
4/22/2024 4:13:51 PM | Visayas Grid-04/22/2024 16:14: TGPP Unit#3 cut-in to the system at 1607H. (Unplanned Outage) [WEBSMS] | CVIS
4/22/2024 2:22:09 PM | Mindanao Grid-04/22/2024 14:27: WMPC DG03 shutdown at 1420H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/22/2024 2:10:11 PM | Visayas Grid-04/22/2024 14:10: PGPP I Unit#3 tripped with 19.7MW load at 1400H. (Unplanned Outage) [WEBSMS] | CVIS
4/22/2024 12:42:59 PM | [NSO Update] Luzon Grid-04/22/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14696MW, PK=12980MW, RR=314MW, NetOpMargin: PM=1402, EVE=1125 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @300MW [WEBSMS] | CLUZ
4/22/2024 12:36:38 PM | [NSO Update] Mindanao Grid-04/22/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3060MW, PK=2599MW, RR=72MW, NetOpMargin: PM=388, EVE=475 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @98MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/22/2024 12:34:09 PM | [NSO Update] Visayas Grid-04/22/2024 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2789MW, PK=2482MW, RR=99MW, NetOpMargin: PM=209, EVE=204 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @39MW, LEYTE A @310MW [WEBSMS] | CVIS
4/22/2024 12:05:57 PM | Mindanao Grid-04/22/2024 12:11: Naga Mindanao - Zamboanga 138kV Line2 energized and looped at 1203H (Unplanned Outage) [WEBSMS] | CMIN
4/22/2024 11:34:29 AM | Mindanao Grid-04/22/2024 11:39: WMPC DG03 Online at 1132H, as replacement for WMPC DG10. System Voltage Requirement. [WEBSMS] | CMIN
4/22/2024 11:31:31 AM | Luzon Grid-04/22/2024 11:31: For info: The Luzon System Frequency reached 60.534Hz at 1115H during the auto-tripping/auto-reclosing of the Malabon-Malinta 115kV line(Customer Owned) affecting voltage sensitive loads. [WEBSMS] | CLUZ
4/22/2024 11:28:10 AM | Mindanao Grid-04/22/2024 11:33: WMPC DG10 running as RPS with 8.5MW load tripped at 1125H. Indication: OIL Mist concentration high stop. (Unplanned Outage) [WEBSMS] | CMIN
4/22/2024 11:02:53 AM | Luzon Grid-04/22/2024 11:02: Nagsaag - Casecnan 230kV Line 2 shutdown at 1059H (Planned Outage) [WEBSMS] | CLUZ
4/22/2024 11:01:07 AM | Luzon Grid-04/22/2024 11:01: San Jose - Tayabas 500kV Line 2 de-energized at 1058H (Planned Outage) [WEBSMS] | CLUZ
4/22/2024 10:38:02 AM | Mindanao Grid-04/22/2024 10:43: WMPC DG06 Online at 1036H. System Voltage Requirement. [WEBSMS] | CMIN
4/22/2024 9:06:00 AM | Mindanao Grid-04/22/2024 09:11: WMPC DG04 Online at 0901H. System Voltage Requirement. Corrected. [WEBSMS] | CMIN
4/22/2024 9:05:14 AM | Mindanao Grid-04/22/2024 09:10: WMPC DG04 Online at 0904H. System Voltage Requirement. [WEBSMS] | CMIN
4/22/2024 8:22:53 AM | Mindanao Grid-04/22/2024 08:28: WMPC DG07 online at 0819H. System Voltage Requirement. [WEBSMS] | CMIN
4/22/2024 8:17:25 AM | Mindanao Grid-04/22/2024 08:22: WMPC DG06 running as RPS with 4MW load tripped at 0812H. OIL Mist concentration high. (Unplanned Outage) [WEBSMS] | CMIN
4/22/2024 8:11:20 AM | Mindanao Grid-04/22/2024 08:16: WMPC DG06 Online at 0808H. System Voltage Requirement. [WEBSMS] | CMIN
4/22/2024 7:19:09 AM | Mindanao Grid-04/22/2024 07:24: Baloi - Agus 6 138kV Line 1 de-energized at 0706H. Planned Outage [WEBSMS] | CMIN
4/22/2024 7:09:42 AM | [NSO Update] Luzon Grid-04/22/2024 07:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0705H with power going to Visayas [WEBSMS] | CLUZ
4/22/2024 7:08:01 AM | [NSO Update] Visayas Grid-04/22/2024 07:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0705H with power going to Visayas [WEBSMS] | CVIS
4/22/2024 6:28:48 AM | [NSO Update] Visayas Grid-04/22/2024 06:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0626H from forward power direction. [WEBSMS] | CVIS
4/22/2024 6:28:36 AM | [NSO Update] Luzon Grid-04/22/2024 06:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0626H from forward power direction. [WEBSMS] | CLUZ
4/22/2024 6:17:15 AM | Mindanao Grid-04/22/2024 06:22: Sultan Kudarat SS 138kV Bus #2 shutdown/De-energized at 0615H. (Planned Outage) [WEBSMS] | CMIN
4/22/2024 5:53:03 AM | [NSO Update] Visayas Grid-04/22/2024 05:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0550H with power going to Luzon. [WEBSMS] | CVIS
4/22/2024 5:52:48 AM | [NSO Update] Luzon Grid-04/22/2024 05:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0550H with power going to Luzon. [WEBSMS] | CLUZ
4/22/2024 5:47:47 AM | [NSO Update] Luzon Grid-04/22/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14903MW, PK=12183MW, RR=294MW, NetOpMargin: AM=2426, PM=1357, EVE=1088 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 300MW [WEBSMS] | CLUZ
4/22/2024 5:46:24 AM | [NSO Update] Visayas Grid-04/22/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2740MW, PK=2407MW, RR=94MW, NetOpMargin: AM=239, PM=178, EVE=219 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 79MW, Leyte A @ 312MW [WEBSMS] | CVIS
4/22/2024 5:38:10 AM | [NSO Update] Mindanao Grid-04/22/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3065MW, PK=2473MW, RR=72MW, NetOpMargin: AM=5159, PM=420, EVE=562 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @30MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @98MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/22/2024 5:21:29 AM | Mindanao Grid-04/22/2024 05:26: WMPC DG1 Online as RPS at 0516H. System Voltage Requirement. [WEBSMS] | CMIN
4/22/2024 5:20:07 AM | Mindanao Grid-04/22/2024 05:25: WMPC DG10 Online as RPS at 0512H. System Voltage Requirement. [WEBSMS] | CMIN
4/22/2024 5:15:55 AM | [NSO Update] Visayas Grid-04/22/2024 05:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0513H from forward power direction. [WEBSMS] | CVIS
4/22/2024 5:14:32 AM | [NSO Update] Luzon Grid-04/22/2024 05:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0513H from forward power direction. [WEBSMS] | CLUZ
4/22/2024 4:48:51 AM | Luzon Grid-04/22/2024 04:49: Ilijan A ST 1 online at 0447H (Unplanned Outage) [WEBSMS] | CLUZ
4/22/2024 4:03:26 AM | [NSO Update] Mindanao Grid-04/22/2024 04:08: Weather Advisory: Trough of Low Pressure Area (LPA) affecting southern Mindanao. Ridge of High Pressure Area extending over the eastern section of Northern Luzon. [WEBSMS] | CMIN
4/22/2024 4:03:12 AM | [NSO Update] Visayas Grid-04/22/2024 04:03: Weather Advisory: Trough of Low Pressure Area (LPA) affecting southern Mindanao. Ridge of High Pressure Area extending over the eastern section of Northern Luzon. [WEBSMS] | CVIS
4/22/2024 4:03:00 AM | [NSO Update] Luzon Grid-04/22/2024 04:03: Weather Advisory: Trough of Low Pressure Area (LPA) affecting southern Mindanao. Ridge of High Pressure Area extending over the eastern section of Northern Luzon. [WEBSMS] | CLUZ
4/22/2024 3:30:07 AM | Luzon Grid-04/22/2024 03:30: Ilijan GT 1-2 online at 0326H (Unplanned Outage) [WEBSMS] | CLUZ
4/22/2024 2:30:08 AM | Mindanao Grid-04/22/2024 02:35: Naga Mindanao - Zamboanga 138kV Line2 manually closed but tripped at 0151H. (Unplanned Outage) [WEBSMS] | CMIN
4/22/2024 1:53:44 AM | Mindanao Grid-04/22/2024 01:59: Naga Mindanao - Zamboanga 138kV Line2 tripped at 0141H. (Unplanned Outage) [WEBSMS] | CMIN
4/22/2024 1:18:55 AM | Luzon Grid-04/22/2024 01:19: Hermosa-Calaguiman restored at 0110H (Unplanned Outage) correction [WEBSMS] | CLUZ
4/22/2024 1:14:15 AM | Luzon Grid-04/22/2024 01:14: Hermosa-Calaguiman 69kV line de-energized at 0110H (Unplanned Outage) [WEBSMS] | CLUZ
4/22/2024 12:29:29 AM | Visayas Grid-04/22/2024 00:29: THVI unit #2 cut-in at 0021H initial load 10MW. (Unplanned Outage) [WEBSMS] | CVIS
4/21/2024 11:43:55 PM | Luzon Grid-04/21/2024 23:44: Ilijan A 1-1 and ST-1 with a load of 289MW tripped at 2337H, frequency reach at 59.4hz (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2024 11:12:08 PM | Luzon Grid-04/21/2024 23:12: Hermosa-Calaguiman de-energized at 2307H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2024 11:11:19 PM | Visayas Grid-04/21/2024 23:11: Compostela SS-Compostela-Consolacion 69KV fdr tripped at 2302H, auto-reclose.(Unplanned Outage) [WEBSMS] | CVIS
4/21/2024 10:48:44 PM | Luzon Grid-04/21/2024 22:48: Ilijan ST1 online at 2245H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2024 10:45:28 PM | [NSO Update] Visayas Grid-04/21/2024 22:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2243H with power going to Luzon. [WEBSMS] | CVIS
4/21/2024 10:45:14 PM | [NSO Update] Luzon Grid-04/21/2024 22:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2243H with power going to Luzon. [WEBSMS] | CLUZ
4/21/2024 10:34:59 PM | [NSO Update] Visayas Grid-04/21/2024 22:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2229H from reverse power direction. [WEBSMS] | CVIS
4/21/2024 10:34:44 PM | [NSO Update] Luzon Grid-04/21/2024 22:34: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2229H from reverse power direction. [WEBSMS] | CLUZ
4/21/2024 10:32:20 PM | Mindanao Grid-04/21/2024 22:37: WMPC DG10 shutdown at 2229H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/21/2024 9:44:53 PM | Luzon Grid-04/21/2024 21:45: Ilijan 1-2 online at 2142H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2024 9:43:50 PM | Luzon Grid-04/21/2024 21:44: Pagbilao 2 online at 2142H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2024 9:29:36 PM | Mindanao Grid-04/21/2024 21:34: Davao - Toril 138kV Line2 restored/energized at 2127H. (Planned Outage) [WEBSMS] | CMIN
4/21/2024 8:32:12 PM | Visayas Grid-04/21/2024 20:32: PGPP 1 Unit#2 cut-in to the system @2020H. ( Unplanned Outage ) [WEBSMS] | CVIS
4/21/2024 6:37:58 PM | Mindanao Grid-04/21/2024 18:43: PULANGI 4 HEP Unit 3 online at 1728H. (Unplanned Outage) [WEBSMS] | CMIN
4/21/2024 6:26:24 PM | [NSO Update] Mindanao Grid-04/21/2024 18:31: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2920MW, PK=2188MW, RR=72MW, NetOpMargin: EVE=660 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: Derated Plant: MCC @150MW, MA1 @48.9MW, MA2 @37MW [WEBSMS] | CMIN
4/21/2024 6:21:38 PM | [NSO Update] Visayas Grid-04/21/2024 18:21: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2463MW, PK=2135MW, RR=238MW, NetOpMargin: EVE=238 Highest Unit O/L: THVI 1 @169MW Derated Plant: TGPP @39.3MW, LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
4/21/2024 6:15:16 PM | [NSO Update] Luzon Grid-04/21/2024 18:15: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12552MW, PK=11047MW, RR=255MW, NetOpMargin: EVE=1250 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: None [WEBSMS] | CLUZ
4/21/2024 5:50:51 PM | Mindanao Grid-04/21/2024 17:56: WMPC DG10 online at 1737H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/21/2024 5:49:40 PM | [NSO Update] Visayas Grid-04/21/2024 17:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1747H with power going to Visayas [WEBSMS] | CVIS
4/21/2024 5:49:27 PM | [NSO Update] Luzon Grid-04/21/2024 17:49: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1747H with power going to Visayas [WEBSMS] | CLUZ
4/21/2024 5:47:54 PM | [NSO Update] Visayas Grid-04/21/2024 17:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1737H from forward power direction [WEBSMS] | CVIS
4/21/2024 5:47:08 PM | [NSO Update] Luzon Grid-04/21/2024 17:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1737H from forward power direction [WEBSMS] | CLUZ
4/21/2024 5:35:50 PM | Luzon Grid-04/21/2024 17:36: San Rafael-Cabanatuan 230kV Line restored at 1735H (Planned Outage) [WEBSMS] | CLUZ
4/21/2024 5:34:11 PM | Luzon Grid-04/21/2024 17:34: San Jose-Tayabas 500kV Line 1 restored at 1734H (Planned Outage) [WEBSMS] | CLUZ
4/21/2024 5:32:32 PM | Luzon Grid-04/21/2024 17:32: Pagbilao 2 tripped with a load of 19MW at 1729H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2024 5:25:22 PM | Luzon Grid-04/21/2024 17:25: Pagbilao 2 online at 1723H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2024 5:23:58 PM | Mindanao Grid-04/21/2024 17:29: General Santos SS 138/69kV 100MVA Power Transformer #1 restored/energized at 1720H. (Planned Outage) [WEBSMS] | CMIN
4/21/2024 5:17:29 PM | Mindanao Grid-04/21/2024 17:22: WMPC DG10 shutdown at 1714H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/21/2024 5:02:33 PM | Mindanao Grid-04/21/2024 17:07: PULANGI 4 HEP Unit 1 online at 1657H. (Unplanned Outage) [WEBSMS] | CMIN
4/21/2024 4:42:51 PM | Mindanao Grid-04/21/2024 16:48: WMPC DG06 shutdown at 1633H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/21/2024 4:32:44 PM | Mindanao Grid-04/21/2024 16:38: WMPC DG01 shutdown at 1628H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/21/2024 4:06:33 PM | Luzon Grid-04/21/2024 16:06: Ilijan 2-1 online at 1603H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2024 3:52:37 PM | Mindanao Grid-04/21/2024 15:57: Correction: Aurora - Naga Mindanao 138kV Line 1 restored/energized at 1546H. (Planned Outage) [WEBSMS] | CMIN
4/21/2024 3:47:52 PM | Mindanao Grid-04/21/2024 15:53: Correction: Aurora - Naga Mindanao 138kV Line 2 restored/energized at 1546H. (Planned Outage) [WEBSMS] | CMIN
4/21/2024 3:44:54 PM | Mindanao Grid-04/21/2024 15:50: Luga-it - Opol 138kV Line restored/energized at 1540H. (Planned Outage) [WEBSMS] | CMIN
4/21/2024 3:43:30 PM | Mindanao Grid-04/21/2024 15:48: Aurora - Naga Mindanao 138kV Line 2 restored/energized at 1540H. (Planned Outage) [WEBSMS] | CMIN
4/21/2024 3:12:48 PM | Mindanao Grid-04/21/2024 15:18: PULANGI 4 HEP Unit 3 tripped at 1458H. (Unplanned Outage) [WEBSMS] | CMIN
4/21/2024 3:01:02 PM | Visayas Grid-04/21/2024 15:01: Colon - Dumanjug 138 kV Line 1 energized at 1500H (Planned Outage) [WEBSMS] | CVIS
4/21/2024 2:20:22 PM | Luzon Grid-04/21/2024 14:20: San Juan-Calauan 230kV Line 2 restored at 1416H (Planned Outage) [WEBSMS] | CLUZ
4/21/2024 1:54:40 PM | Luzon Grid-04/21/2024 13:54: Ilijan ST2 online at 1354H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2024 1:19:11 PM | Mindanao Grid-04/21/2024 13:24: WMPC DG06 online at 1308H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/21/2024 1:18:21 PM | Mindanao Grid-04/21/2024 13:23: WMPC DG01 online at 1306H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/21/2024 1:11:22 PM | Mindanao Grid-04/21/2024 13:16: WMPC DG10 tripped at 1251H. (Unplanned outage) [WEBSMS] | CMIN
4/21/2024 1:05:21 PM | [NSO Update] Visayas Grid-04/21/2024 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2553MW, PK=2007MW, RR=90MW, NetOpMargin: PM=456, EVE=229 Highest Unit O/L: THVI 1 @169MW Derated Plant: TGPP @39.3MW, LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
4/21/2024 1:03:10 PM | [NSO Update] Luzon Grid-04/21/2024 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13256MW, PK=10711MW, RR=311MW, NetOpMargin: PM=2234, EVE=752 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: None [WEBSMS] | CLUZ
4/21/2024 1:01:40 PM | Luzon Grid-04/21/2024 13:01: San Jose-Tayabas 500kV Line 2 restored (to floating status) at 1259H (Planned Outage) [WEBSMS] | CLUZ
4/21/2024 12:57:11 PM | [NSO Update] Luzon Grid-04/21/2024 12:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1253H with power going to Luzon. [WEBSMS] | CLUZ
4/21/2024 12:56:45 PM | [NSO Update] Visayas Grid-04/21/2024 12:56: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1253H with power going to Luzon. [WEBSMS] | CVIS
4/21/2024 12:55:09 PM | [NSO Update] Mindanao Grid-04/21/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2950MW, PK=1946MW, RR=72MW, NetOpMargin: PM=932, EVE=685 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MA1 @48.9MW, MA2 @37MW [WEBSMS] | CMIN
4/21/2024 12:41:15 PM | Luzon Grid-04/21/2024 12:41: Ilijan GT2-2 online at 1237H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2024 12:40:43 PM | Mindanao Grid-04/21/2024 12:45: NAA, ZAM and PIT SS re-energized at 1156H. (Unplanned Outage) [WEBSMS] | CMIN
4/21/2024 12:35:28 PM | Mindanao Grid-04/21/2024 12:40: Aurora 138kV Bus2 energized at 1223H (Planned Outage) [WEBSMS] | CMIN
4/21/2024 12:33:48 PM | Mindanao Grid-04/21/2024 12:39: Aurora - Naga Mindanao 138kV Line 2 Re-energized at 1156H. (Unplanned Outage) [WEBSMS] | CMIN
4/21/2024 12:21:25 PM | [NSO Update] Luzon Grid-04/21/2024 12:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1153H from forward power direction. [WEBSMS] | CLUZ
4/21/2024 12:21:03 PM | [NSO Update] Visayas Grid-04/21/2024 12:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1153H from forward power direction. [WEBSMS] | CVIS
4/21/2024 12:14:11 PM | Mindanao Grid-04/21/2024 12:19: WMPC DG10 online at 1211H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/21/2024 11:43:45 AM | Mindanao Grid-04/21/2024 11:49: PULANGI 4 HEP Unit 3 tripped at 1043H. (Unplanned Outage) [WEBSMS] | CMIN
4/21/2024 10:50:01 AM | Mindanao Grid-04/21/2024 10:55: Aurora - Naga Mindanao 138kV Line2 tripped at 1041H. (Unplanned Outage) [WEBSMS] | CMIN
4/21/2024 10:40:05 AM | Mindanao Grid-04/21/2024 10:45: Naga Mindanao SS SVC energized at 1017H. (Unplanned Outage) [WEBSMS] | CMIN
4/21/2024 10:19:57 AM | Mindanao Grid-04/21/2024 10:25: Naga Mindanao SS SVC tripped at 1003H. (Unplanned Outage) [WEBSMS] | CMIN
4/21/2024 9:39:45 AM | Visayas Grid-04/21/2024 09:39: Amlan - Mabinay 138 kV Line 1 de-energized at 0938H (Planned Outage) [WEBSMS] | CVIS
4/21/2024 9:35:19 AM | Visayas Grid-04/21/2024 09:35: Mabinay - Kabankalan 138 kV Lines 1 and 2 energized at 0924H and 0925H from Mabinay SS side only (Planned Outage) [WEBSMS] | CVIS
4/21/2024 8:53:02 AM | Mindanao Grid-04/21/2024 08:58: Luga-it - Opol 138kV Line de-energized at 0844H. (Planned Outage) [WEBSMS] | CMIN
4/21/2024 8:37:52 AM | Mindanao Grid-04/21/2024 08:43: Aurora SS 138kV Bus2 de-energized at 0836H. (Planned Outage) [WEBSMS] | CMIN
4/21/2024 8:35:14 AM | Mindanao Grid-04/21/2024 08:40: Lamsan Baggase-Fired Power Plant online at 0828H. (Unplanned Outage) [WEBSMS] | CMIN
4/21/2024 8:19:56 AM | Mindanao Grid-04/21/2024 08:25: Aurora - Naga Mindanao 138kV Line1 de-energized at 0817H. (Planned Outage) [WEBSMS] | CMIN
4/21/2024 8:10:20 AM | Luzon Grid-04/21/2024 08:10: Muntinlupa 300MVA T01 and Muntinlupa - Gardner 115kV Tie Line 3 restored at 0807H (Planned Outage) [WEBSMS] | CLUZ
4/21/2024 7:57:24 AM | Mindanao Grid-04/21/2024 08:02: Lamsan Baggase-Fired Power Plant tripped with 15MW Load at 0657H. (Unplanned Outage) [WEBSMS] | CMIN
4/21/2024 7:49:05 AM | Luzon Grid-04/21/2024 07:49: Muntinlupa 230kV Bus 1 restored at 0746H (Planned Outage) [WEBSMS] | CLUZ
4/21/2024 7:10:25 AM | Luzon Grid-04/21/2024 07:10: System Advisory: Affected ALD feeders of NGCP and MERALCO restored at 0706H. [WEBSMS] | CLUZ
4/21/2024 7:06:45 AM | Luzon Grid-04/21/2024 07:06: System Advisory: ALD occurred NGCP and MERALCO feeders at 0658H due to tripping of Ilijan Blocks A & B at 750MW total load. Lowest Frequency=58.921Hz. [WEBSMS] | CLUZ
4/21/2024 6:47:50 AM | Visayas Grid-04/21/2024 06:47: Mabinay - Kabankalan 138 kV Lines 1 and 2 de-energized at 0646H and 0641H (Planned Outage) [WEBSMS] | CVIS
4/21/2024 6:44:58 AM | Mindanao Grid-04/21/2024 06:50: General Santos SS 138/69kV 100MVA Power Transformer #1 de-energized at 0641H. (Planned Outage) [WEBSMS] | CMIN
4/21/2024 6:26:08 AM | Visayas Grid-04/21/2024 06:26: Colon - Dumanjug 138 kV Line 1 de-energized at 0625H (Planned Outage) [WEBSMS] | CVIS
4/21/2024 6:09:48 AM | Mindanao Grid-04/21/2024 06:15: Davao - Toril 138kV Line2 de-energized at 0607H. (Planned Outage) [WEBSMS] | CMIN
4/21/2024 5:53:14 AM | Luzon Grid-04/21/2024 05:53: San Juan-Calauan 230kV Line 2 de-energized at 0551H. (Planned Outage) [WEBSMS] | CLUZ
4/21/2024 5:43:33 AM | [NSO Update] Mindanao Grid-04/21/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2974MW, PK=2064MW, RR=72MW, NetOpMargin: AM=838, PM=761, EVE=606 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MA1 @48.9MW, MA2 @37MW [WEBSMS] | CMIN
4/21/2024 5:41:51 AM | [NSO Update] Visayas Grid-04/21/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2391MW, PK=1927MW, RR=89MW, NetOpMargin: AM=375, PM=555, EVE=194 Highest Unit O/L: THVI 1 @169MW Derated Plant: TGPP @39.3MW, LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
4/21/2024 5:37:59 AM | [NSO Update] Luzon Grid-04/21/2024 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14534MW, PK=10475MW, RR=294MW, NetOpMargin: AM=3765, PM=3201, EVE=1363 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @300MW [WEBSMS] | CLUZ
4/21/2024 5:34:41 AM | Visayas Grid-04/21/2024 05:34: Cebu SS 100MVA TR 4 de-energized at 0533H (Planned Outage) [WEBSMS] | CVIS
4/21/2024 5:21:12 AM | Luzon Grid-04/21/2024 05:21: San Jose-Tayabas 500kV Line 1 de-energized at 0519H. (Planned Outage) [WEBSMS] | CLUZ
4/21/2024 5:18:09 AM | Luzon Grid-04/21/2024 05:18: San Jose-Tayabas 500kV Line 2 de-energized at 0457H. (Planned Outage) [WEBSMS] | CLUZ
4/21/2024 4:43:58 AM | [NSO Update] Mindanao Grid-04/21/2024 04:49: Weather Update: Trough of a Low Pressure Area (LPA) affecting southern Mindanao. Ridge of High Pressure Area extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CMIN
4/21/2024 4:43:44 AM | [NSO Update] Visayas Grid-04/21/2024 04:43: Weather Update: Trough of a Low Pressure Area (LPA) affecting southern Mindanao. Ridge of High Pressure Area extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CVIS
4/21/2024 4:43:26 AM | [NSO Update] Luzon Grid-04/21/2024 04:43: Weather Update: Trough of a Low Pressure Area (LPA) affecting southern Mindanao. Ridge of High Pressure Area extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CLUZ
4/21/2024 4:28:53 AM | Mindanao Grid-04/21/2024 04:34: PULANGI 4 HEP Unit 1 shutdown at 0423H due to insufficient water supply/ low forebay elevation (Unplanned Outage) [WEBSMS] | CMIN
4/21/2024 4:09:11 AM | Luzon Grid-04/21/2024 04:09: San Rafael-Cabanatuan 230kV Line de-energized at 0408H. (Planned Outage) [WEBSMS] | CLUZ
4/21/2024 3:29:59 AM | Visayas Grid-04/21/2024 03:30: Magdugo-Calatrava Line2 looped at Calatrava SS at 0323H (Planned Outage) [WEBSMS] | CVIS
4/21/2024 3:09:54 AM | Luzon Grid-04/21/2024 03:10: Pagbilao U1online at 0303H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2024 3:00:31 AM | Mindanao Grid-04/21/2024 03:05: Zamboanga SS 138/69kV 50MVA Power Transformer No. 2 (7XF02ZAM) energized back at 0259H. Planned Outage. [WEBSMS] | CMIN
4/21/2024 2:24:20 AM | Visayas Grid-04/21/2024 02:24: Magdugo-Calatrava 230kV Line 2 energized from Magdugo SS at 0219H (Unplanned Outage) [WEBSMS] | CVIS
4/21/2024 1:42:05 AM | Mindanao Grid-04/21/2024 01:47: Baloi SS 138kV Bus 1 (7BS01BLO) energized back at 0139H (Planned Outage). [WEBSMS] | CMIN
4/21/2024 1:35:23 AM | Luzon Grid-04/21/2024 01:35: Muntinlupa - Gardner 115kV Tie Line 3, Muntinlupa 300MVA T01 & Muntinlupa 230kV Bus 1 de-energized at 0111H, 0111H & 0125H, respectively (Planned Outage) [WEBSMS] | CLUZ
4/21/2024 1:20:30 AM | Mindanao Grid-04/21/2024 01:25: Zamboanga SS 138/69kV 50MVA Power Transformer No. 2 (7XF02ZAM) de-energized at 0117H. Planned Outage. [WEBSMS] | CMIN
4/21/2024 12:54:47 AM | Visayas Grid-04/21/2024 00:54: TGPP U3 tripped at 0038H (Unplanned Outage) [WEBSMS] | CVIS
4/20/2024 11:05:48 PM | Mindanao Grid-04/20/2024 23:11: Davao -Toril 138 kV Line 1 energized/looped at 2301H. Planned Outage. [WEBSMS] | CMIN
4/20/2024 11:01:33 PM | [NSO Update] Luzon Grid-04/20/2024 23:01: Update on System Advisory: Luzon Grid Yellow Alert notice issued today has been lifted at 2259H. [WEBSMS] | CLUZ
4/20/2024 10:58:13 PM | Mindanao Grid-04/20/2024 23:03: SEDI (EEI) Unit 1 declared available at 2250H (Unplanned Outage) [WEBSMS] | CMIN
4/20/2024 9:51:45 PM | Mindanao Grid-04/20/2024 21:57: Baloi SS 138kV Bus 1 (7BS01BLO) de-energized at 2149H (Planned Outage). [WEBSMS] | CMIN
4/20/2024 9:30:03 PM | [NSO Update] Visayas Grid-04/20/2024 21:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2127H with power going to Luzon [WEBSMS] | CVIS
4/20/2024 9:29:39 PM | [NSO Update] Luzon Grid-04/20/2024 21:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2127H with power going to Luzon [WEBSMS] | CLUZ
4/20/2024 9:27:32 PM | [NSO Update] Visayas Grid-04/20/2024 21:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2117H from reverse power direction [WEBSMS] | CVIS
4/20/2024 9:27:10 PM | [NSO Update] Luzon Grid-04/20/2024 21:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2117H from reverse power direction [WEBSMS] | CLUZ
4/20/2024 9:13:29 PM | Mindanao Grid-04/20/2024 21:18: WMPC DG10 end of RPS at 2000H. Converted to EN (MO dispatch). [WEBSMS] | CMIN
4/20/2024 9:02:50 PM | Mindanao Grid-04/20/2024 21:08: LIBERTAD POWER online at 2041H (Unplanned Outage) [WEBSMS] | CMIN
4/20/2024 7:16:16 PM | Luzon Grid-04/20/2024 19:16: Bauang-Bakun 230kV Line restored at 1916H. (Planned Outage) [WEBSMS] | CLUZ
4/20/2024 7:07:21 PM | Mindanao Grid-04/20/2024 19:12: IDPP declared available at 1900H (from Unplanned Outage) [WEBSMS] | CMIN
4/20/2024 7:04:36 PM | Luzon Grid-04/20/2024 19:04: Bakun-San Esteban 230kV Line restored at 1903H. (Planned Outage) [WEBSMS] | CLUZ
4/20/2024 6:37:32 PM | Mindanao Grid-04/20/2024 18:42: LIBERTAD POWER with 6MW load tripped at 1823H. Indicate: Earth Fault (Unplanned Outage) [WEBSMS] | CMIN
4/20/2024 6:31:48 PM | [NSO Update] Luzon Grid-04/20/2024 18:31: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=12386MW, PK=11488MW, RR=247MW, NetOpMargin: EVE=651 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @300MW [WEBSMS] | CLUZ
4/20/2024 6:31:03 PM | Mindanao Grid-04/20/2024 18:36: SEDI (EEI) Unit 1 on forced outage at 1811H due to failure to synchronized to the grid (Unplanned Outage) [WEBSMS] | CMIN
4/20/2024 5:53:56 PM | [NSO Update] Mindanao Grid-04/20/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2949MW, PK=2421MW, RR=72MW, NetOpMargin: EVE=456 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @98MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/20/2024 5:53:04 PM | [NSO Update] Visayas Grid-04/20/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2578MW, PK=2260MW, RR=94MW, NetOpMargin: EVE=225 Highest Unit O/L: THVI 1 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @308MW, PGPP1 @76MW [WEBSMS] | CVIS
4/20/2024 5:16:20 PM | Mindanao Grid-04/20/2024 17:21: WMPC DG01 shutdown at 1713H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/20/2024 3:38:30 PM | Luzon Grid-04/20/2024 15:38: San Rafael SS 230kV Bus 2 restored at 1537H. (Planned Outage) [WEBSMS] | CLUZ
4/20/2024 3:31:11 PM | Luzon Grid-04/20/2024 15:31: Daraga-Tiwi C 230kV Line restored at 1531H. (Planned Outage) [WEBSMS] | CLUZ
4/20/2024 3:29:30 PM | Visayas Grid-04/20/2024 15:29: Pajo LESS 10 MVA TR energized at 1522H (Planned Outage) [WEBSMS] | CVIS
4/20/2024 2:45:05 PM | Luzon Grid-04/20/2024 14:45: La Trinidad SS 230kV Bus 2 restored at 1444H. (Planned Outage) [WEBSMS] | CLUZ
4/20/2024 1:12:31 PM | [NSO Update] Luzon Grid-04/20/2024 13:12: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=13781MW, PK=11690MW, RR=404MW, NetOpMargin: PM=1688, EVE=278 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 300MW [WEBSMS] | CLUZ
4/20/2024 1:07:55 PM | [NSO Update] Visayas Grid-04/20/2024 13:08: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2518MW, PK=2243MW, RR=90MW, NetOpMargin: PM=185, EVE=226 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 308MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/20/2024 1:04:52 PM | [NSO Update] Mindanao Grid-04/20/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3009MW, PK=2419MW, RR=72MW, NetOpMargin: PM=518, EVE=435 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @98MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/20/2024 12:47:15 PM | Mindanao Grid-04/20/2024 12:52: WMPC DG01 online at 1245H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/20/2024 10:26:41 AM | Mindanao Grid-04/20/2024 10:31: WMPC DG10 online at 0946H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/20/2024 9:37:40 AM | [NSO Update] Mindanao Grid-04/20/2024 09:42: MO Initiated Market Intervention has been lifted today 20 April 2024 at 0923H for Luzon, Visayas and Mindanao. Market operation will resume starting interval 0925H. [WEBSMS] | CMIN
4/20/2024 9:36:23 AM | Mindanao Grid-04/20/2024 09:41: TUDAYA 2 Unit 2 online at 0751H (Unplanned Outage) [WEBSMS] | CMIN
4/20/2024 9:35:50 AM | [NSO Update] Visayas Grid-04/20/2024 09:35: MO Initiated Market Intervention has been lifted today 20 April 2024 at 0923H for Luzon, Visayas and Mindanao. Market operation will resume starting interval 0925H. [WEBSMS] | CVIS
4/20/2024 9:35:39 AM | Mindanao Grid-04/20/2024 09:40: TUDAYA 2 Unit 1 online at 0730H (Unplanned Outage) [WEBSMS] | CMIN
4/20/2024 9:33:02 AM | [NSO Update] Luzon Grid-04/20/2024 09:33: MO Initiated Market Intervention has been lifted today 20 April 2024 at 0923H for Luzon, Visayas and Mindanao. Market operation will resume starting interval 0925H. [WEBSMS] | CLUZ
4/20/2024 9:07:16 AM | [NSO Update] Mindanao Grid-04/20/2024 09:12: MO-initiated Market Intervention is issued today, 20 April 2024, for Luzon, Visayas, & Mindanao Grid for interval 0905H due to RTD generation failure. [WEBSMS] | CMIN
4/20/2024 9:06:25 AM | [NSO Update] Visayas Grid-04/20/2024 09:06: MO-initiated Market Intervention is issued today, 20 April 2024, for Luzon, Visayas, & Mindanao Grid for interval 0905H due to RTD generation failure. [WEBSMS] | CVIS
4/20/2024 9:05:32 AM | [NSO Update] Luzon Grid-04/20/2024 09:05: MO-initiated Market Intervention is issued today, 20 April 2024, for Luzon, Visayas, & Mindanao Grid for interval 0905H due to RTD generation failure. [WEBSMS] | CLUZ
4/20/2024 8:20:45 AM | [NSO Update] Visayas Grid-04/20/2024 08:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0817H with power going to Visayas. [WEBSMS] | CVIS
4/20/2024 8:20:13 AM | [NSO Update] Luzon Grid-04/20/2024 08:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0817H with power going to Visayas. [WEBSMS] | CLUZ
4/20/2024 8:13:20 AM | Luzon Grid-04/20/2024 08:13: San Rafael SS 230kV Bus 2 de-energized at 0812H (Planned Outage) [WEBSMS] | CLUZ
4/20/2024 8:10:02 AM | [NSO Update] Visayas Grid-04/20/2024 08:10: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0807H from forward power direction. [WEBSMS] | CVIS
4/20/2024 8:09:24 AM | [NSO Update] Luzon Grid-04/20/2024 08:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0807H from forward power direction. [WEBSMS] | CLUZ
4/20/2024 8:02:59 AM | Luzon Grid-04/20/2024 08:03: La Trinidad SS 230kV Bus 2 de-energized at 0802H (Planned Outage) [WEBSMS] | CLUZ
4/20/2024 7:21:08 AM | Luzon Grid-04/20/2024 07:21: Daraga-Tiwi C 230kV Line de-energized at 0647H (Planned Outage) [WEBSMS] | CLUZ
4/20/2024 7:18:12 AM | Mindanao Grid-04/20/2024 07:23: TUDAYA 2 Unit 1 (0.99MW) and Unit 2 (1.64MW) tripped at 0638H. Cause: Loss of signal for water level of Desander (Unplanned Outage) [WEBSMS] | CMIN
4/20/2024 6:30:14 AM | Luzon Grid-04/20/2024 06:30: Bakun-San Esteban 230kV Line de-energized at 0620H (Planned Outage) [WEBSMS] | CLUZ
4/20/2024 6:29:07 AM | Luzon Grid-04/20/2024 06:29: Bauang-Bakun 230kV Line de-energized at 0618H (Planned Outage) [WEBSMS] | CLUZ
4/20/2024 6:27:21 AM | Visayas Grid-04/20/2024 06:27: Pajo LESS 10 MVA TR de-energized at 0604H (Planned Outage) [WEBSMS] | CVIS
4/20/2024 6:25:01 AM | Mindanao Grid-04/20/2024 06:30: Davao -Toril 138 kV Line 1 de-energized at 0614H. Planned Outage. [WEBSMS] | CMIN
4/20/2024 5:50:56 AM | [NSO Update] Luzon Grid-04/20/2024 05:51: System Advisory: Luzon Grid is on YELLOW Alert for interval hours 1900H-2200H. Total capacity on forced outage is 2025.8MW. Total of de-rated capacity is 300MW. [WEBSMS] | CLUZ
4/20/2024 5:49:07 AM | [NSO Update] Luzon Grid-04/20/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=13672MW, PK=11238MW, RR=386MW, NetOpMargin: AM=2048, PM=1337, EVE=375 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 300MW [WEBSMS] | CLUZ
4/20/2024 5:34:17 AM | [NSO Update] Visayas Grid-04/20/2024 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2538MW, PK=2199MW, RR=89MW, NetOpMargin: AM=250, PM=263, EVE=225 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 312MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/20/2024 5:30:56 AM | [NSO Update] Mindanao Grid-04/20/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3019MW, PK=2251MW, RR=72MW, NetOpMargin: AM=696, PM=627, EVE=641 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @98MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/20/2024 5:10:40 AM | [NSO Update] Mindanao Grid-04/20/2024 05:15: Shutdown at 0323H (Unplanned Outage) - Emergency shutdown of Magdugo - Calatrava 230Kv L2 at 0323H due to the needed correction of hotspot at the Cable Sealing End (CSE) phase C at Calatrava CTS. [WEBSMS] | CMIN
4/20/2024 5:10:18 AM | [NSO Update] Visayas Grid-04/20/2024 05:10: Shutdown at 0323H (Unplanned Outage) - Emergency shutdown of Magdugo - Calatrava 230Kv L2 at 0323H due to the needed correction of hotspot at the Cable Sealing End (CSE) phase C at Calatrava CTS. [WEBSMS] | CVIS
4/20/2024 5:09:57 AM | [NSO Update] Luzon Grid-04/20/2024 05:09: Shutdown at 0323H (Unplanned Outage) - Emergency shutdown of Magdugo - Calatrava 230Kv L2 at 0323H due to the needed correction of hotspot at the Cable Sealing End (CSE) phase C at Calatrava CTS. [WEBSMS] | CLUZ
4/20/2024 4:28:58 AM | Luzon Grid-04/20/2024 04:29: Quezon-Duhat 230kV Lineenergized at 0428H (Planned Outage) [WEBSMS] | CLUZ
4/20/2024 4:27:30 AM | Luzon Grid-04/20/2024 04:27: Duhat SS 230kV Bus No. 2 & 300MVA T02 energized at 0426H (Planned Outage) [WEBSMS] | CLUZ
4/20/2024 4:05:39 AM | [NSO Update] Mindanao Grid-04/20/2024 04:10: Weather Advisory: Ridge of a High Pressure Area (HPA) extending over the eastern section of Luzon. [WEBSMS] | CMIN
4/20/2024 4:05:02 AM | [NSO Update] Visayas Grid-04/20/2024 04:05: Weather Advisory: Ridge of a High Pressure Area (HPA) extending over the eastern section of Luzon. [WEBSMS] | CVIS
4/20/2024 4:04:32 AM | [NSO Update] Luzon Grid-04/20/2024 04:04: Weather Advisory: Ridge of a High Pressure Area (HPA) extending over the eastern section of Luzon. [WEBSMS] | CLUZ
4/20/2024 3:29:28 AM | Visayas Grid-04/20/2024 03:29: Magdugo-Calatrava 230kV Line 2 de-energized at 0323H (Unplanned Outage) [WEBSMS] | CVIS
4/20/2024 1:25:43 AM | Luzon Grid-04/20/2024 01:25: Duhat SS 230kV Bus No. 2 & 300MVA T02 de-energized at 0125H (Planned Outage) [WEBSMS] | CLUZ
4/20/2024 1:23:53 AM | Luzon Grid-04/20/2024 01:24: Quezon-Duhat 230kV Line de-energized at 0123H (Planned Outage) [WEBSMS] | CLUZ
4/19/2024 11:59:43 PM | [NSO Update] Luzon Grid-04/19/2024 23:59: Update on System Advisory: Luzon Grid Yellow Alert notice issued today has been lifted at 2357H. [WEBSMS] | CLUZ
4/19/2024 10:54:47 PM | [NSO Update] Luzon Grid-04/19/2024 22:54: Luzon Grid Red Alert notice issued today is lifted at 2253H. Luzon Grid still on Yellow Alert for interval 2300H. [WEBSMS] | CLUZ
4/19/2024 10:17:45 PM | [NSO Update] Visayas Grid-04/19/2024 22:17: Visayas Grid Yellow Alert notice issued today has been lifted at 2214H. [WEBSMS] | CVIS
4/19/2024 10:05:48 PM | Mindanao Grid-04/19/2024 22:11: Agus 6 Unit 5 online at 2201H. (Unplanned Outage) [WEBSMS] | CMIN
4/19/2024 8:34:40 PM | [NSO Update] Visayas Grid-04/19/2024 20:34: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2033H with power going to Luzon. [WEBSMS] | CVIS
4/19/2024 8:34:21 PM | [NSO Update] Luzon Grid-04/19/2024 20:34: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2033H with power going to Luzon. [WEBSMS] | CLUZ
4/19/2024 8:27:52 PM | [NSO Update] Visayas Grid-04/19/2024 20:27: Visayas Grid Red Alert notice issued today is lifted at 2024H. Visayas Grid still on Yellow Alert for intervals 2100H-2200H. [WEBSMS] | CVIS
4/19/2024 8:26:23 PM | [NSO Update] Visayas Grid-04/19/2024 20:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2023H from reverse power direction. [WEBSMS] | CVIS
4/19/2024 8:26:07 PM | [NSO Update] Luzon Grid-04/19/2024 20:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2023H from reverse power direction. [WEBSMS] | CLUZ
4/19/2024 8:01:28 PM | Mindanao Grid-04/19/2024 20:06: IDPP Mapalad declared Forced outage at 1954H. Unable to process fuel. (Unplanned outage) [WEBSMS] | CMIN
4/19/2024 7:31:54 PM | Mindanao Grid-04/19/2024 19:37: GNPK Unit 2 online at 1929H from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
4/19/2024 7:05:24 PM | Mindanao Grid-04/19/2024 19:10: Update: Libertad Power with 6MW load tripped at 1706H. Indication: Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
4/19/2024 7:03:45 PM | Mindanao Grid-04/19/2024 19:08: Update: Pulangi 4 Unit 3 with 20MW tripped at 1805H. Indication: 64GB (Unplanned Outage) [WEBSMS] | CMIN
4/19/2024 6:59:11 PM | Mindanao Grid-04/19/2024 19:04: Pulangi 4 Unit 3 online at 1855H (Unplanned Outage) [WEBSMS] | CMIN
4/19/2024 6:42:08 PM | Mindanao Grid-04/19/2024 18:47: Pulangi 4 Unit 3 with 20MW tripped at 1805H. Details to follow (Unplanned Outage) [WEBSMS] | CMIN
4/19/2024 6:10:31 PM | [NSO Update] Visayas Grid-04/19/2024 18:10: Update on System Advisory: Visayas Grid is on RED Alert for interval hours 1900H-2100H and YELLOW Alert for interval 2200H. Total capacity on forced outage is 485.1MW. Total of de-rated capacity is 272.6MW. [WEBSMS] | CVIS
4/19/2024 6:09:44 PM | [NSO Update] Luzon Grid-04/19/2024 18:09: Update on System Advisory: Luzon Grid is on RED Alert for interval hours 2100H-2200H and YELLOW Alert for interval hours 1900H-2000H, and 2300H. Total capacity on forced outage is 1794.3MW. Total of de-rated capacity is 490MW. [WEBSMS] | CLUZ
4/19/2024 6:01:40 PM | [NSO Update] Visayas Grid-04/19/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=2248MW, PK=2322MW, RR=97MW, NetOpMargin: EVE=0 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 315MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/19/2024 5:59:19 PM | [NSO Update] Luzon Grid-04/19/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=12375MW, PK=11882MW, RR=377MW, NetOpMargin: EVE=116 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 300MW, Magat 1 @ 2MW, Magat 4 @ 2MW Remarks: Red Alert on intervals 2100H to 2200H [WEBSMS] | CLUZ
4/19/2024 5:53:25 PM | Mindanao Grid-04/19/2024 17:58: WMPC DG04 declared available at 0750H. (Unplanned Outage). [WEBSMS] | CMIN
4/19/2024 5:44:12 PM | [NSO Update] Mindanao Grid-04/19/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2777MW, PK=2472MW, RR=75MW, NetOpMargin: EVE=230 Highest Unit O/L: GNPK 1, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @50MW, AG7 @10MW, PG4 @40MW [WEBSMS] | CMIN
4/19/2024 5:23:38 PM | Mindanao Grid-04/19/2024 17:28: Libertad Power with 6MW load tripped at 1706H (Unplanned Outage) [WEBSMS] | CMIN
4/19/2024 5:18:26 PM | Mindanao Grid-04/19/2024 17:23: Baloi-Tagoloan 138kV Line restored/energized at 1716H. (Planned Outage). [WEBSMS] | CMIN
4/19/2024 5:11:21 PM | Mindanao Grid-04/19/2024 17:16: Agus 6 Unit 2 online at 1652H. (Unplanned outage) [WEBSMS] | CMIN
4/19/2024 4:58:43 PM | Mindanao Grid-04/19/2024 17:03: WMPC DG04 with 10MW tripped at 1644H. Indication: HT low pressure stop. (Unplanned Outage) [WEBSMS] | CMIN
4/19/2024 2:26:05 PM | [NSO Update] Luzon Grid-04/19/2024 14:26: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=13521MW, PK=12901MW, RR=401MW, NetOpMargin: PM=218, EVE=154 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 300MW [WEBSMS] | CLUZ
4/19/2024 1:28:36 PM | [NSO Update] Visayas Grid-04/19/2024 13:28: System Advisory: Visayas Grid is on RED Alert for interval hours 1400H-2000H and YELLOW Alert for interval hours 2100H. Total capacity on forced outage is 485.1MW. Total of de-rated capacity is 272.6MW. [WEBSMS] | CVIS
4/19/2024 1:08:04 PM | [NSO Update] Mindanao Grid-04/19/2024 13:13: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2824MW, PK=2588MW, RR=78MW, NetOpMargin: PM=158, EVE=228 Highest Unit O/L: GNPK 1, 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @50MW, AG7 @19MW, PG4 @20MW [WEBSMS] | CMIN
4/19/2024 1:06:19 PM | [NSO Update] Visayas Grid-04/19/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=2484MW, PK=2504MW, RR=98MW, NetOpMargin: PM=-117, EVE=-178 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 315MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/19/2024 12:55:59 PM | Mindanao Grid-04/19/2024 13:01: WMPC DG06 start RPS operation at 1245H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/19/2024 10:14:27 AM | Mindanao Grid-04/19/2024 10:19: Pulangi 4 Unit 1 online at 1012H from OMC low water inflow. (Unplanned Outage) [WEBSMS] | CMIN
4/19/2024 9:32:36 AM | Mindanao Grid-04/19/2024 09:37: WMPC DG1 online at 0929H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/19/2024 9:11:06 AM | Mindanao Grid-04/19/2024 09:16: Baloi-Tagoloan 138kV Line de-energized at 0906H. (Planned Outage) [WEBSMS] | CMIN
4/19/2024 8:45:19 AM | [NSO Update] Visayas Grid-04/19/2024 08:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0811H with power going to Visayas. [WEBSMS] | CVIS
4/19/2024 8:44:46 AM | [NSO Update] Luzon Grid-04/19/2024 08:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0811H with power going to Visayas. [WEBSMS] | CLUZ
4/19/2024 8:41:54 AM | [NSO Update] Visayas Grid-04/19/2024 08:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0801H from forward power direction [WEBSMS] | CVIS
4/19/2024 8:41:07 AM | [NSO Update] Luzon Grid-04/19/2024 08:41: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0801H from forward power direction. [WEBSMS] | CLUZ
4/19/2024 8:35:42 AM | Mindanao Grid-04/19/2024 08:40: WMPC DG10 online at 0831H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/19/2024 6:31:18 AM | Visayas Grid-04/19/2024 06:31: Mandaue GIS-Guizo 69 KV line energized at 0627H (Planned Outage) [WEBSMS] | CVIS
4/19/2024 5:45:09 AM | [NSO Update] Mindanao Grid-04/19/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2856MW, PK=2490MW, RR=77MW, NetOpMargin: AM=289, PM=228, EVE=358 Highest Unit O/L: GNPK 1, 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @73MW, AG7 @19MW, PG4 @20MW [WEBSMS] | CMIN
4/19/2024 5:43:31 AM | [NSO Update] Visayas Grid-04/19/2024 05:43: System Advisory: Visayas Grid is on YELLOW Alert for interval hours 1300H-1600H and 1800H-2000H. Total capacity on forced outage is 464.1MW. Total of de-rated capacity is 272.6MW. [WEBSMS] | CVIS
4/19/2024 5:42:00 AM | [NSO Update] Visayas Grid-04/19/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2861MW, PK=2399MW, RR=368MW, NetOpMargin: AM=368, PM=71, EVE=43 Highest Unit O/L: THVI U1 @169MW Derated Plant: Leyte A @315MW, PGPP1 @76MW, CEDC U3 @75MW, Tongonan Power Plant @79.5MW, Panay Diesel 3-E @9MW, Panay Diesel 3-G @8MW, Power Barge 104-U1 @5MW, Power Barge 104-U2 @5MW, Power Barge 104-U3 @5MW, Panay Diesel 1 -U5 @4MW [WEBSMS] | CVIS
4/19/2024 5:37:44 AM | [NSO Update] Luzon Grid-04/19/2024 05:37: System Advisory: Luzon Grid is on RED Alert for interval hours 1600H, 1900H-2200H and YELLOW Alert for interval hours 1300H-1500H, 1700H-1800H and 2300H. Total capacity on forced outage is 1794.3MW. Total of de-rated capacity is 490MW. [WEBSMS] | CLUZ
4/19/2024 5:35:22 AM | [NSO Update] Luzon Grid-04/19/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: RED ALERT CAP=13827MW, PK=12649MW, RR=386MW, NetOpMargin: AM=792, PM=66, EVE=0 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Ilijan A @300MW, Magat 4 @2MW, Magat 1 @2MW [WEBSMS] | CLUZ
4/19/2024 5:20:35 AM | Luzon Grid-04/19/2024 05:20: Taytay-Masinag 115kV Line (CO) restored at 0519H (Planned Outage) [WEBSMS] | CLUZ
4/19/2024 4:05:12 AM | Luzon Grid-04/19/2024 04:05: Correction: Taytay-Malaya 230kV Line 1 restored at 0338H (Unplanned Outage) [WEBSMS] | CLUZ
4/19/2024 4:02:48 AM | [NSO Update] Mindanao Grid-04/19/2024 04:08: Weather Advisory: Ridge of a High Pressure Area (HPA) extending over the eastern section of Luzon. [WEBSMS] | CMIN
4/19/2024 4:02:32 AM | [NSO Update] Visayas Grid-04/19/2024 04:02: Weather Advisory: Ridge of a High Pressure Area (HPA) extending over the eastern section of Luzon. [WEBSMS] | CVIS
4/19/2024 4:02:17 AM | [NSO Update] Luzon Grid-04/19/2024 04:02: Weather Advisory: Ridge of a High Pressure Area (HPA) extending over the eastern section of Luzon. [WEBSMS] | CLUZ
4/19/2024 3:40:22 AM | Luzon Grid-04/19/2024 03:40: Taytay-Malaya 230kV Line 1 at 0338H (Unplanned Outage) [WEBSMS] | CLUZ
4/19/2024 3:32:23 AM | Visayas Grid-04/19/2024 03:32: Mandaue GIS - Guizo 69 kV Line de-energized at 0331H (Planned Outage) [WEBSMS] | CVIS
4/19/2024 3:15:48 AM | Visayas Grid-04/19/2024 03:15: Magdugo - Calatrava 230 kV Line 2 energized from Magdugo SS at 0314H, for 24 hrs soaking [WEBSMS] | CVIS
4/19/2024 12:58:17 AM | Luzon Grid-04/19/2024 00:58: Taytay-Masinag 115kV Line (CO) de-energized at 0055H (Planned Outage) [WEBSMS] | CLUZ
4/19/2024 12:29:08 AM | [NSO Update] Luzon Grid-04/19/2024 00:29: Luzon Grid Yellow Alert notice issued on April 18, 2024 has been lifted at 0023H of April 19, 2024. [WEBSMS] | CLUZ
4/18/2024 10:43:29 PM | [NSO Update] Luzon Grid-04/18/2024 22:43: Luzon Grid Red Alert notice issued today is lifted at 2240H. Luzon Grid still on Yellow Alert for intervals 2300H-2400H. [WEBSMS] | CLUZ
4/18/2024 9:43:47 PM | [NSO Update] Luzon Grid-04/18/2024 21:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2105H with power going to Luzon. [WEBSMS] | CLUZ
4/18/2024 9:43:24 PM | [NSO Update] Visayas Grid-04/18/2024 21:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2105H with power going to Luzon. [WEBSMS] | CVIS
4/18/2024 9:12:35 PM | [NSO Update] Visayas Grid-04/18/2024 21:12: Update on System Advisory: Visayas Grid Yellow Alert notice issued today is lifted at 2107H. [WEBSMS] | CVIS
4/18/2024 9:00:02 PM | Luzon Grid-04/18/2024 21:00: April 18, 2024: Demand Control Imminent Warning (DCIW) is re-issued at 2100H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency [WEBSMS] | CLUZ
4/18/2024 8:58:29 PM | [NSO Update] Luzon Grid-04/18/2024 20:58: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2055H from reverse power direction. [WEBSMS] | CLUZ
4/18/2024 8:57:51 PM | [NSO Update] Visayas Grid-04/18/2024 20:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2055H from reverse power direction. [WEBSMS] | CVIS
4/18/2024 8:05:37 PM | Luzon Grid-04/18/2024 20:05: Malaya 2 shutdown at 2000H (Unplanned Outage) [WEBSMS] | CLUZ
4/18/2024 8:03:41 PM | Luzon Grid-04/18/2024 20:03: April 18, 2024: Demand Control Imminent Warning (DCIW) is re-issued at 2000H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
4/18/2024 8:02:40 PM | Mindanao Grid-04/18/2024 20:07: WMPC DG07 end of RPS at 2000H. Converted to EN. [WEBSMS] | CMIN
4/18/2024 7:33:50 PM | Luzon Grid-04/18/2024 19:33: Taytay-Malaya 230kV Line 1 de-energized at 1932H (Unplanned Outage) [WEBSMS] | CLUZ
4/18/2024 7:31:27 PM | [NSO Update] Visayas Grid-04/18/2024 19:31: Update on System Advisory: Visayas Grid Red Alert notice issued today is lifted at 1913H. Visayas Grid still on Yellow Alert for intervals 2000H-2100H. [WEBSMS] | CVIS
4/18/2024 6:43:18 PM | Mindanao Grid-04/18/2024 18:48: AGUS 6 Unit 2 with 10MW load emergency shutdown at 1800H. Reason: Main inlet valve (butterfly valve) low pressure (Unplanned Outage) [WEBSMS] | CMIN
4/18/2024 6:33:26 PM | Luzon Grid-04/18/2024 18:33: April 18, 2024: Demand Control Imminent Warning (DCIW) is issued at 1830H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
4/18/2024 5:59:03 PM | [NSO Update] Luzon Grid-04/18/2024 17:59: Update on System Advisory: Luzon Grid is on RED Alert for interval hours 2000H-2200H and YELLOW Alert for interval hours 1800H-1900H, and 2300H-2400H. Total capacity on forced outage is 2261.3MW. Total of de-rated capacity is 395MW. [WEBSMS] | CLUZ
4/18/2024 5:55:02 PM | [NSO Update] Mindanao Grid-04/18/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2865MW, PK=2407MW, RR=75MW, NetOpMargin: EVE=382 Highest Unit O/L: GNPK 1, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @30MW, AG6 @98MW, AG7 @19MW, PG4 @28MW [WEBSMS] | CMIN
4/18/2024 5:53:20 PM | [NSO Update] Visayas Grid-04/18/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=2416MW, PK=2374MW, RR=93MW, NetOpMargin: EVE=0 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 310MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/18/2024 5:51:32 PM | [NSO Update] Luzon Grid-04/18/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=12335MW, PK=11884MW, RR=337MW, NetOpMargin: EVE=114 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 300MW, Magat 4 @2MW [WEBSMS] | CLUZ
4/18/2024 5:14:55 PM | Mindanao Grid-04/18/2024 17:20: Manolo Fortich-HEDCOR Manolo 2 138kV Line 1 energized at 1714H. (Planned Outage) [WEBSMS] | CMIN
4/18/2024 4:54:02 PM | Mindanao Grid-04/18/2024 16:59: Zamboanga SS 138kV Bus #2 energized/restored at 1652H. (Planned Outage) [WEBSMS] | CMIN
4/18/2024 4:47:24 PM | Mindanao Grid-04/18/2024 16:52: WMPC DG01 end of RPS at 1630H. Converted to EN. [WEBSMS] | CMIN
4/18/2024 4:03:43 PM | Mindanao Grid-04/18/2024 16:08: WMPC DG08 online at 1548H (Unplanned Outage) [WEBSMS] | CMIN
4/18/2024 3:51:34 PM | Mindanao Grid-04/18/2024 15:56: WMPC DG08 with 10.1MW load tripped at 1531H. Cause: Main bearing 4 high temp. (Unplanned Outage) [WEBSMS] | CMIN
4/18/2024 3:26:35 PM | Luzon Grid-04/18/2024 15:26: Calaca-BCF(Batangas Cola Fired Power Plant) 230kV line 3 restored at 1524H (Planned Outage) [WEBSMS] | CLUZ
4/18/2024 3:04:33 PM | Luzon Grid-04/18/2024 15:04: System Advisory: April 18, 2024: Demand Control Imminent Warning (DCIW) is issued at 1500H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
4/18/2024 2:35:11 PM | Mindanao Grid-04/18/2024 14:40: WMPC DG09 shutdown at 1429H. From MOT Raise. [WEBSMS] | CMIN
4/18/2024 1:56:35 PM | Mindanao Grid-04/18/2024 14:01: TM2 Unit 1 online at 1327H as MOT Raise. [WEBSMS] | CMIN
4/18/2024 1:55:46 PM | Mindanao Grid-04/18/2024 14:00: (Correction) TM1 Unit 2 online at 1317H as MOT Raise. [WEBSMS] | CMIN
4/18/2024 1:54:46 PM | Mindanao Grid-04/18/2024 13:59: TM1 Unit 2 online at 1305H as MOT Raise. [WEBSMS] | CMIN
4/18/2024 1:53:42 PM | Mindanao Grid-04/18/2024 13:58: IDPP online at 1307H as MOT Raise. [WEBSMS] | CMIN
4/18/2024 1:49:06 PM | Mindanao Grid-04/18/2024 13:54: KEGI TANDAG online at 1250H as MOT Raise. [WEBSMS] | CMIN
4/18/2024 1:48:18 PM | Mindanao Grid-04/18/2024 13:53: KEGI MARAMAG online at 1249H as MOT Raise. [WEBSMS] | CMIN
4/18/2024 1:47:11 PM | Mindanao Grid-04/18/2024 13:52: KEGI PANAON Unit 1 online at 1249H as MOT Raise. [WEBSMS] | CMIN
4/18/2024 1:38:23 PM | [NSO Update] Visayas Grid-04/18/2024 13:38: Update on System Advisory: Visayas Grid is on RED Alert for interval 1900H and YELLOW Alert for interval hours 1400H-1800H and 2000H-2100H. Total capacity on forced outage is 428.1MW. Total of de-rated capacity is 268.6MW. [WEBSMS] | CVIS
4/18/2024 1:37:09 PM | [NSO Update] Luzon Grid-04/18/2024 13:37: undefined at 1300H Update on System Advisory: Luzon Grid is on RED Alert for interval hours 1600H, and 2100H-2200H and YELLOW Alert for interval hours 1400H-1500H, 1700H-2000H, and 2300H-2400H. Total capacity on forced outage is 1591.3MW. Total of de-rated capacity is 300MW. [WEBSMS] | CLUZ
4/18/2024 1:18:13 PM | [NSO Update] Visayas Grid-04/18/2024 13:18: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=2677MW, PK=2536MW, RR=99MW, NetOpMargin: PM=43, EVE=0 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 315MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/18/2024 1:13:29 PM | [NSO Update] Luzon Grid-04/18/2024 13:13: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=13580MW, PK=13089MW, RR=361MW, NetOpMargin: PM=129, EVE=182 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 300MW [WEBSMS] | CLUZ
4/18/2024 12:50:35 PM | [NSO Update] Mindanao Grid-04/18/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2924MW, PK=2520MW, RR=78MW, NetOpMargin: PM=325, EVE=365 Highest Unit O/L: GNPK 1, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @97MW, AG7 @19MW, PG4 @36MW [WEBSMS] | CMIN
4/18/2024 11:18:50 AM | Mindanao Grid-04/18/2024 11:24: PULANGI 4 Unit 1 shutdown at 1110H. Reason: Insufficient water supply (Unplanned Outage) [WEBSMS] | CMIN
4/18/2024 10:34:38 AM | Mindanao Grid-04/18/2024 10:39: WMPC DG01 online at 1031H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/18/2024 9:46:11 AM | Mindanao Grid-04/18/2024 09:51: WMPC DG07 online at 0931H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/18/2024 9:38:30 AM | Mindanao Grid-04/18/2024 09:43: AGUS 7 Unit 1 with 10MW load shutdown at 0921H. Reason: OMC due to low water inflow. Unplanned Outage. [WEBSMS] | CMIN
4/18/2024 9:11:53 AM | Mindanao Grid-04/18/2024 09:17: 9Correction) AGUS 7 Unit 2 online at 0846H (Unplanned Outage) [WEBSMS] | CMIN
4/18/2024 9:10:28 AM | Luzon Grid-04/18/2024 09:10: MPGC 2 online at 0907H (on commissioning) [WEBSMS] | CLUZ
4/18/2024 9:03:06 AM | Mindanao Grid-04/18/2024 09:08: AGUS 7 Unit 2 online at 0846H (Planned Outage) [WEBSMS] | CMIN
4/18/2024 8:39:16 AM | Mindanao Grid-04/18/2024 08:44: WMPC DG10 online at 0830H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/18/2024 8:09:32 AM | Mindanao Grid-04/18/2024 08:14: Zamboanga SS 138kV Bus #2 De-energized at 0804H. (Planned Outage) [WEBSMS] | CMIN
4/18/2024 8:01:07 AM | Mindanao Grid-04/18/2024 08:06: Manolo Fortich-HEDCOR Manolo 2 138kV Line 1 de-energized at 0757H. (Planned Outage) [WEBSMS] | CMIN
4/18/2024 7:32:06 AM | [NSO Update] Visayas Grid-04/18/2024 07:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0722H with power going to Visayas [WEBSMS] | CVIS
4/18/2024 7:31:43 AM | [NSO Update] Luzon Grid-04/18/2024 07:31: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0722H with power going to Visayas [WEBSMS] | CLUZ
4/18/2024 7:23:16 AM | Mindanao Grid-04/18/2024 07:28: MANOLO FORTICH 2 Unit 4 shutdown at 0703H (Planned Outage) [WEBSMS] | CMIN
4/18/2024 6:48:06 AM | [NSO Update] Luzon Grid-04/18/2024 06:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0644H from forward power direction. [WEBSMS] | CLUZ
4/18/2024 6:47:27 AM | [NSO Update] Visayas Grid-04/18/2024 06:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0644H from forward power direction. [WEBSMS] | CVIS
4/18/2024 6:06:54 AM | [NSO Update] Luzon Grid-04/18/2024 06:06: System Advisory: Luzon Grid is on RED Alert for interval hours 1600H, and 2100H-2200H and YELLOW Alert for interval hours 1400H-1500H, 1700H-2000H, and 2300H. Total capacity on forced outage is 1591.3MW. Total of de-rated capacity is 300MW. [WEBSMS] | CLUZ
4/18/2024 6:04:16 AM | [NSO Update] Luzon Grid-04/18/2024 06:04: GRID UPDATE AS OF 6:00 AM System Condition: RED ALERT CAP=13864MW, PK=12257MW, RR=386MW, NetOpMargin: AM=1221, PM=144, EVE=62 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @300MW [WEBSMS] | CLUZ
4/18/2024 5:46:29 AM | [NSO Update] Visayas Grid-04/18/2024 05:46: System Advisory: Visayas Grid is on YELLOW Alert for interval hours 1400H-2100H. Total capacity on forced outage is 428.1MW. Total of de-rated capacity is 268.6MW. [WEBSMS] | CVIS
4/18/2024 5:44:44 AM | [NSO Update] Visayas Grid-04/18/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2776MW, PK=2406MW, RR=94MW, NetOpMargin: AM=276, PM=99, EVE=41 Highest Unit O/L: THVI 1 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
4/18/2024 5:26:21 AM | [NSO Update] Mindanao Grid-04/18/2024 05:31: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2926MW, PK=2402MW, RR=77MW, NetOpMargin: AM=447, PM=334, EVE=408 Highest Unit O/L: GNPK 1,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @75MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/18/2024 4:04:25 AM | [NSO Update] Mindanao Grid-04/18/2024 04:09: Weather Update: Ridge of a High Pressure Area (HPA) extending over the eastern section of Luzon. [WEBSMS] | CMIN
4/18/2024 4:04:10 AM | [NSO Update] Visayas Grid-04/18/2024 04:04: Weather Update: Ridge of a High Pressure Area (HPA) extending over the eastern section of Luzon. [WEBSMS] | CVIS
4/18/2024 4:03:29 AM | [NSO Update] Luzon Grid-04/18/2024 04:03: Weather Update: Ridge of a High Pressure Area (HPA) extending over the eastern section of Luzon. [WEBSMS] | CLUZ
4/18/2024 3:37:45 AM | Mindanao Grid-04/18/2024 03:42: STEAG Unit 2 online at 0335H (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 11:38:49 PM | [NSO Update] Luzon Grid-04/17/2024 23:38: Update on System Advisory: Luzon Grid Yellow Alert notice issued today is lifted at 2301H. [WEBSMS] | CLUZ
4/17/2024 10:28:36 PM | [NSO Update] Visayas Grid-04/17/2024 22:28: Update on System Advisory: Visayas Grid Yellow Alert notice issued today is lifted at 2201H. [WEBSMS] | CVIS
4/17/2024 9:23:07 PM | [NSO Update] Visayas Grid-04/17/2024 21:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2114H with power going to Luzon [WEBSMS] | CVIS
4/17/2024 9:22:34 PM | [NSO Update] Luzon Grid-04/17/2024 21:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2114H with power going to Luzon [WEBSMS] | CLUZ
4/17/2024 9:21:33 PM | [NSO Update] Visayas Grid-04/17/2024 21:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2102H from reverse power direction [WEBSMS] | CVIS
4/17/2024 9:21:08 PM | [NSO Update] Luzon Grid-04/17/2024 21:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2102H from reverse power direction [WEBSMS] | CLUZ
4/17/2024 9:05:16 PM | [NSO Update] Visayas Grid-04/17/2024 21:05: Update on System Advisory: Visayas Grid Red Alert notice issued today is lifted at 2101H. Visayas Grid still on Yellow Alert for interval hour 2200H. [WEBSMS] | CVIS
4/17/2024 8:47:01 PM | Mindanao Grid-04/17/2024 20:52: WMPC DG02 WITH 10MW load tripped at 2041H. indication: Generator driving and bearing Temperature shutdown. (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 8:18:41 PM | Mindanao Grid-04/17/2024 20:23: Manolo Fortich 2 HEP online at 2015H (Planned Outage) [WEBSMS] | CMIN
4/17/2024 6:32:12 PM | [NSO Update] Visayas Grid-04/17/2024 18:32: Update on System Advisory: 17-Apr-2024, Visayas Grid is on RED Alert for interval hours 1800H-2100H and YELLOW Alert for interval hour 2200H. Total capacity on forced outage is 438.1MW. Total of de-rated capacity is 273.6MW. [WEBSMS] | CVIS
4/17/2024 6:26:54 PM | [NSO Update] Visayas Grid-04/17/2024 18:26: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=2394MW, PK=2339MW, RR=94MW, NetOpMargin: EVE=0 Highest Unit O/L: THVI 1 @169MW Derated Plant: Leyte A @305MW, PGPP1 @76MW, CEDC U3 @75MW, Tongonan Power Plant @79.5MW, Panay Diesel 3-E @8MW, BDPP 1 @3.5MW, BDPP 2 @3.5MW, BDPP 3 @3.7MW, BDPP 4 @3.5MW [WEBSMS] | CVIS
4/17/2024 6:25:38 PM | Mindanao Grid-04/17/2024 18:30: SMC Unit 2 with 130MW emergency shutdown at 1820H due to tube leak on cyclone inlet. (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 6:12:02 PM | [NSO Update] Mindanao Grid-04/17/2024 18:17: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2874MW, PK=2423MW, RR=75MW, NetOpMargin: EVE=376 Highest Unit O/L: GNPK 1, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @30MW, AG2 @54MW, AG4 @62MW, AG5 @20MW, AG6 @72MW, AG7 @19MW, PG4 @40MW [WEBSMS] | CMIN
4/17/2024 6:10:27 PM | [NSO Update] Luzon Grid-04/17/2024 18:10: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=12531MW, PK=12006MW, RR=337MW, NetOpMargin: EVE=188 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @300MW [WEBSMS] | CLUZ
4/17/2024 5:55:59 PM | Mindanao Grid-04/17/2024 18:01: GNPK Unit 2 with 22MW tripped again at 1754H. Indication: High differential pressure. (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 5:53:49 PM | [NSO Update] Visayas Grid-04/17/2024 17:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1714H with power going to Visayas [WEBSMS] | CVIS
4/17/2024 5:53:22 PM | [NSO Update] Luzon Grid-04/17/2024 17:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1714H with power going to Visayas [WEBSMS] | CLUZ
4/17/2024 5:53:04 PM | Mindanao Grid-04/17/2024 17:58: GNPK Unit 2 online at 1750H (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 5:52:47 PM | [NSO Update] Visayas Grid-04/17/2024 17:52: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1534H from reverse power direction [WEBSMS] | CVIS
4/17/2024 5:52:15 PM | Mindanao Grid-04/17/2024 17:57: Agus 6 Unit 4 online at 1748H (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 5:51:49 PM | [NSO Update] Luzon Grid-04/17/2024 17:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1534H from reverse power direction [WEBSMS] | CLUZ
4/17/2024 5:37:30 PM | Mindanao Grid-04/17/2024 17:42: Correction 2: Agus 5 Unit 2 online at 1719H from PMS-GOMP. (Planned outage). [WEBSMS] | CMIN
4/17/2024 5:30:28 PM | Mindanao Grid-04/17/2024 17:35: Corrected: Agus 5 Unit 2 online at 1719H from Forced Outage. (Unplanned outage). [WEBSMS] | CMIN
4/17/2024 5:27:51 PM | Mindanao Grid-04/17/2024 17:33: Agus 6 Unit 2 online at 1719H from PMS(GOMP). Planned outage. [WEBSMS] | CMIN
4/17/2024 4:53:05 PM | Mindanao Grid-04/17/2024 16:58: MEGC with 12.3MW load tripped at 1625H. Details to follow. (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 4:27:50 PM | Mindanao Grid-04/17/2024 16:32: Agus 6 Unit 4 with 25MW load tripped at 1547H. Indication Transformer Lock out relay. GET 60trip. (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 4:26:08 PM | Mindanao Grid-04/17/2024 16:31: ALD occurred at NGCP and DLPC system at 1552H due to tripping of GNPK U2 with 150MW. The lowest frequency is 59.142Hz. (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 4:16:02 PM | Mindanao Grid-04/17/2024 16:21: GNPK Unit 2 with 151MW tripped at 1552H. Frequency dip to 59.143Hz with ALD activation. Indication: Main Temp trip. (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 4:04:53 PM | Mindanao Grid-04/17/2024 16:10: GNPK U2 tripped with 150MW load at 1552H. (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 4:03:04 PM | Mindanao Grid-04/17/2024 16:08: Agus6 U4 tripped with 25MW load at 1547H. (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 3:43:53 PM | Luzon Grid-04/17/2024 15:43: Kalayaan Unit 1 online at 1542H (Unplanned Outage) [WEBSMS] | CLUZ
4/17/2024 3:26:33 PM | Luzon Grid-04/17/2024 15:26: Kalayaan Unit 1 (182MW) tripped at 1523H. Lowest system frequency is 59.562Hz. [WEBSMS] | CLUZ
4/17/2024 1:01:40 PM | [NSO Update] Mindanao Grid-04/17/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3060MW, PK=2562MW, RR=78MW, NetOpMargin: PM=419, EVE=506 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @30MW, AG2 @54MW, AG4 @62MW, AG5 @20MW, AG6 @75MW, AG7 @19MW, PG4 @40MW [WEBSMS] | CMIN
4/17/2024 1:00:48 PM | [NSO Update] Visayas Grid-04/17/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2747MW, PK=2490MW, RR=100MW, NetOpMargin: PM=157, EVE=34 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 315MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/17/2024 12:53:16 PM | [NSO Update] Luzon Grid-04/17/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=13639MW, PK=12974MW, RR=401MW, NetOpMargin: PM=264, EVE=239 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 3 @ 300MW, Ilijan A @ 300MW [WEBSMS] | CLUZ
4/17/2024 12:50:33 PM | Mindanao Grid-04/17/2024 12:55: WMPC DG01 online at 1244H. RPS System voltage requirement. [WEBSMS] | CMIN
4/17/2024 11:54:04 AM | Mindanao Grid-04/17/2024 11:59: Butuan - San Francisco 138kV Line Phase C tripped and Auto-reclosed at 1133H. Single Pole Tripping and Auto-reclosing successful. (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 10:24:44 AM | Mindanao Grid-04/17/2024 10:29: MACO BESS with 4.7MW load tripped at 1014H. Indication Over voltage.(Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 9:31:42 AM | Mindanao Grid-04/17/2024 09:36: WMPC DG07 online at 0929H. RPS System voltage requirement. [WEBSMS] | CMIN
4/17/2024 8:32:41 AM | Mindanao Grid-04/17/2024 08:37: WMPC DG10 online at 0828H. RPS System voltage requirement. [WEBSMS] | CMIN
4/17/2024 7:22:09 AM | [NSO Update] Visayas Grid-04/17/2024 07:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0719H with power going to Visayas. [WEBSMS] | CVIS
4/17/2024 7:21:51 AM | [NSO Update] Luzon Grid-04/17/2024 07:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0719H with power going to Visayas. [WEBSMS] | CLUZ
4/17/2024 7:08:42 AM | [NSO Update] Luzon Grid-04/17/2024 07:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0707H from forward power direction. [WEBSMS] | CLUZ
4/17/2024 7:08:25 AM | [NSO Update] Visayas Grid-04/17/2024 07:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0707H from forward power direction. [WEBSMS] | CVIS
4/17/2024 7:07:31 AM | Mindanao Grid-04/17/2024 07:12: Manolo Fortich 2 HEP with 6.6MW shutdown at 0704H (Planned Outage) [WEBSMS] | CMIN
4/17/2024 6:50:47 AM | [NSO Update] Visayas Grid-04/17/2024 06:50: 17-Apr-2024, Visayas Grid is on YELLOW Alert for interval hours 1400H-2200H. Total capacity on forced outage is 435.4MW. Total of de-rated capacity is 262.6MW. [WEBSMS] | CVIS
4/17/2024 6:44:27 AM | [NSO Update] Luzon Grid-04/17/2024 06:44: 17-Apr-2024, Luzon Grid is on YELLOW Alert for interval hours 1400H-2300H. Total capacity on forced outage is 1494.3MW. Total of de-rated capacity is 475MW. [WEBSMS] | CLUZ
4/17/2024 6:39:56 AM | [NSO Update] Visayas Grid-04/17/2024 06:39: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2686MW, PK=2385MW, RR=96MW, NetOpMargin: AM=205, PM=90, EVE=52 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 315MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/17/2024 6:38:05 AM | [NSO Update] Luzon Grid-04/17/2024 06:38: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=13859MW, PK=12138MW, RR=386MW, NetOpMargin: AM=1335, PM=332, EVE=207 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 3 @ 255MW, Ilijan A @ 300MW [WEBSMS] | CLUZ
4/17/2024 5:37:14 AM | [NSO Update] Mindanao Grid-04/17/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3194MW, PK=2438MW, RR=77MW, NetOpMargin: AM=679, PM=547, EVE=653 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @54MW, AG4 @67MW, AG5 @20MW, AG6 @75MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/17/2024 4:52:55 AM | Visayas Grid-04/17/2024 04:52: 230 KV Magdugo SS-Talavera CTS/ CalatravaSS-Calatrava CTS de-energized at 0345H/0357H (Planned Outage) [WEBSMS] | CVIS
4/17/2024 4:01:45 AM | [NSO Update] Mindanao Grid-04/17/2024 04:07: Weather Update: Trough of a Low Pressure Area (LPA) affecting the southeastern section of Mindanao. Ridge of a High Pressure Area (HPA) extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CMIN
4/17/2024 4:01:19 AM | [NSO Update] Visayas Grid-04/17/2024 04:01: Weather Update: Trough of a Low Pressure Area (LPA) affecting the southeastern section of Mindanao. Ridge of a High Pressure Area (HPA) extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CVIS
4/17/2024 4:00:52 AM | [NSO Update] Luzon Grid-04/17/2024 04:01: Weather Update: Trough of a Low Pressure Area (LPA) affecting the southeastern section of Mindanao. Ridge of a High Pressure Area (HPA) extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CLUZ
4/17/2024 3:06:26 AM | Luzon Grid-04/17/2024 03:06: Sta. Rita 40 online at 0303H (Unplanned Outage) [WEBSMS] | CLUZ
4/17/2024 1:54:18 AM | Visayas Grid-04/17/2024 01:54: KSPC U1 cut in at 0149H (Unplanned Outage) [WEBSMS] | CVIS
4/17/2024 1:16:17 AM | Mindanao Grid-04/17/2024 01:21: Agus 6 Switchyard-Agus 6 Unit #5 HEP 138kV Line shutdown at 0059H. (Unplanned Outage) [WEBSMS] | CMIN
4/17/2024 12:14:12 AM | [NSO Update] Luzon Grid-04/17/2024 00:14: Luzon Grid YELLOW ALERT NOTICE issued on April 16, 2024, has been lifted effective 0001H. [WEBSMS] | CLUZ
4/16/2024 11:41:31 PM | [NSO Update] Luzon Grid-04/16/2024 23:41: The Red Alert notice issued today has been lifted at 2301H. Luzon Grid still on Yellow Alert for interval hour 2400H. [WEBSMS] | CLUZ
4/16/2024 11:25:33 PM | [NSO Update] Visayas Grid-04/16/2024 23:25: Visayas Grid Yellow Alert notice issued today is lifted at 2301H [WEBSMS] | CVIS
4/16/2024 10:02:22 PM | Luzon Grid-04/16/2024 22:02: System Advisory: April 16, 2024: Demand Control Imminent Warning (DCIW) is re-issued at 2201H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
4/16/2024 9:36:30 PM | [NSO Update] Visayas Grid-04/16/2024 21:36: Visayas Grid Red Alert notice issued today is lifted at 2101H. Visayas Grid still on Yellow Alert for interval hours 2200H to 2300H. [WEBSMS] | CVIS
4/16/2024 9:30:08 PM | [NSO Update] Visayas Grid-04/16/2024 21:30: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2116H with power going to Luzon [WEBSMS] | CVIS
4/16/2024 9:29:42 PM | [NSO Update] Luzon Grid-04/16/2024 21:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2116H with power going to Luzon [WEBSMS] | CLUZ
4/16/2024 9:13:24 PM | [NSO Update] Visayas Grid-04/16/2024 21:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2106H from reverse power direction [WEBSMS] | CVIS
4/16/2024 9:12:56 PM | [NSO Update] Luzon Grid-04/16/2024 21:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2106H from reverse power direction [WEBSMS] | CLUZ
4/16/2024 8:55:50 PM | Luzon Grid-04/16/2024 20:56: System Advisory: April 16, 2024: Demand Control Imminent Warning (DCIW) is re-issued at 2055H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
4/16/2024 8:43:45 PM | Mindanao Grid-04/16/2024 20:49: AGUS 6 HEP Unit 5 with 20MW load tripped at 2027H. Indication: Frequency Trip, GE T60. (Unplanned Outage). [WEBSMS] | CMIN
4/16/2024 7:52:48 PM | [NSO Update] Luzon Grid-04/16/2024 19:53: Update on System Advisory: 16-Apr-2024, Luzon Grid is on RED Alert for interval hours 2000H-2300H and YELLOW Alert for interval hour 2400H. Total capacity on forced outage is 2021.3MW. Total of de-rated capacity is 391MW. [WEBSMS] | CLUZ
4/16/2024 6:29:32 PM | [NSO Update] Luzon Grid-04/16/2024 18:29: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=12031MW, PK=11995MW, RR=337MW, NetOpMargin: EVE=0 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC3 @250MW, SLTEC 1 @120MW, SLTEC 2 @120MW, ILIJAN A @300MW [WEBSMS] | CLUZ
4/16/2024 6:28:19 PM | Mindanao Grid-04/16/2024 18:33: Manolo Fortich-HEDCOR Manolo 2 138kV Line 1 energized at 1827H. (Planned Outage) [WEBSMS] | CMIN
4/16/2024 6:27:32 PM | [NSO Update] Visayas Grid-04/16/2024 18:27: GRID UPDATE AS OF 6:00 PM System Condition: RED ALERT CAP=2253MW, PK=2242MW, RR=95MW, NetOpMargin: EVE=0 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TGPP @79.5MW, LEYTE A @227MW, PGPP1 @76MW, PEDC U3 @90MW [WEBSMS] | CVIS
4/16/2024 6:21:30 PM | [NSO Update] Mindanao Grid-04/16/2024 18:26: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3066MW, PK=2388MW, RR=75MW, NetOpMargin: EVE=603 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @55MW, AG4 @68MW, AG5 @21MW, AG6 @97MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/16/2024 5:54:47 PM | [NSO Update] Luzon Grid-04/16/2024 17:54: SO-initiated Market Intervention for the Luzon Grid has been lifted today, 16 April 2024, at 1730H. Market operations will resume starting interval 1740H. [WEBSMS] | CLUZ
4/16/2024 5:48:04 PM | [NSO Update] Visayas Grid-04/16/2024 17:48: Update on System Advisory: 16-Apr-2024, Visayas Grid is on RED Alert for interval hours 1800H, 1900H, 2000H, and 2100H, and YELLOW Alert for interval hours 2200H and 2300H. Total capacity on forced outage 520.6MW. Total of de-rated capacity is 414.6MW. [WEBSMS] | CVIS
4/16/2024 5:43:25 PM | Luzon Grid-04/16/2024 17:43: System Advisory: April 16, 2024: Manual Load Dropping (MLD) of MERALCO & NGCP Feeders restored at 1720H & 1730H, respectively. [WEBSMS] | CLUZ
4/16/2024 5:29:39 PM | Luzon Grid-04/16/2024 17:29: Malaya 2 online at 1726H (Planned Outage) [WEBSMS] | CLUZ
4/16/2024 5:14:47 PM | Visayas Grid-04/16/2024 17:15: KSPC U1 tripped at 1712H. (Unplanned Outage) [WEBSMS] | CVIS
4/16/2024 4:51:42 PM | Luzon Grid-04/16/2024 16:51: Kalayaan 2 online at 1651H (Unplanned Outage) [WEBSMS] | CLUZ
4/16/2024 4:48:01 PM | Luzon Grid-04/16/2024 16:48: Kalayaan 1 online at 1647H (Unplanned Outage) [WEBSMS] | CLUZ
4/16/2024 4:34:07 PM | [NSO Update] Luzon Grid-04/16/2024 16:34: SO initiated Market Intervention is issued today for Luzon grid starting interval 1620H after the implementation of MLD due to generation deficiency. [WEBSMS] | CLUZ
4/16/2024 4:31:17 PM | Luzon Grid-04/16/2024 16:31: System Advisory: Affected ALD feeders of MERALCO restored at 1625H. [WEBSMS] | CLUZ
4/16/2024 4:29:37 PM | Luzon Grid-04/16/2024 16:29: System Advisory: April 16, 2024 : Manual Load Dropping (MLD) for MERALCO & NGCP feeders implemented at 1615H & 1616H respectively due to tripping of Kalayaan 1 & 2 and generation deficiency. [WEBSMS] | CLUZ
4/16/2024 4:21:01 PM | Luzon Grid-04/16/2024 16:21: System Advisory: ALD occurred at MERALCO feeders at 1611H due to tripping of Kalayaan 1 & 2 at 360MW total. Lowest Frequency=59.15Hz. [WEBSMS] | CLUZ
4/16/2024 4:17:02 PM | [NSO Update] Luzon Grid-04/16/2024 16:17: Update on System Advisory: 16-Apr-2024, Luzon Grid is on RED Alert for interval hours 1700H-2300H. Total capacity on forced outage is 2021.3MW. Total of de-rated capacity is 391MW. [WEBSMS] | CLUZ
4/16/2024 3:42:20 PM | Luzon Grid-04/16/2024 15:42: Tayabas PCB 9-05CB08TAY restored at 1540H (Planned Outage) [WEBSMS] | CLUZ
4/16/2024 2:59:51 PM | Luzon Grid-04/16/2024 15:00: System Advisory: April 16, 2024: Demand Control Imminent Warning (DCIW) is re-issued at 1500H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
4/16/2024 1:31:01 PM | Luzon Grid-04/16/2024 13:31: System Advisory: April 16, 2024: Demand Control Imminent Warning (DCIW) is issued at 1331H in preparation for the implementation of MLD of MERALCO and NGCP feeders due to generation deficiency. [WEBSMS] | CLUZ
4/16/2024 1:29:23 PM | [NSO Update] Mindanao Grid-04/16/2024 13:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3099MW, PK=2570MW, RR=78MW, NetOpMargin: PM=450, EVE=555 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @55MW, AG4 @68MW, AG5 @21MW, AG6 @97MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/16/2024 1:27:57 PM | [NSO Update] Visayas Grid-04/16/2024 13:28: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2712MW, PK=2494MW, RR=95MW, NetOpMargin: PM=123, EVE=117 Highest Unit O/L: THVI 1 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @240MW, PGPP1 @76MW, CEDC 3 @75MW, PDPP3-E @8MW, PDPP3-G @8MW [WEBSMS] | CVIS
4/16/2024 1:27:36 PM | Luzon Grid-04/16/2024 13:27: La Trinidad 230kV Bus 2 was energized at 1326H. (Planned Outage) [WEBSMS] | CLUZ
4/16/2024 1:22:12 PM | [NSO Update] Visayas Grid-04/16/2024 13:22: Update on System Advisory: 16-Apr-2024, Visayas Grid is on YELLOW Alert for interval hours 1400H-2100H. Total capacity on forced outage is 406.4MW. Total of de-rated capacity is 346.6MW. [WEBSMS] | CVIS
4/16/2024 1:17:36 PM | [NSO Update] Luzon Grid-04/16/2024 13:17: GRID UPDATE AS OF 1:00 PM System Condition: RED ALERT CAP=13126MW, PK=12914MW, RR=361MW, NetOpMargin: PM=0, EVE=0 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 1 @120MW, SLTEC 2 @120MW, ILIJAN A @300MW [WEBSMS] | CLUZ
4/16/2024 9:59:10 AM | Visayas Grid-04/16/2024 09:59: EDC-Malitbog Unit#3 cut-out @ 0945H with load of 70MW. ( Unplanned Outage ) [WEBSMS] | CVIS
4/16/2024 9:37:22 AM | Mindanao Grid-04/16/2024 09:42: Agus 6 Switchyard-Agus 6 HEP Unit #3 69kV Line de-energized at 0931H. (Planned Outage) [WEBSMS] | CMIN
4/16/2024 9:26:57 AM | Mindanao Grid-04/16/2024 09:32: WMPC DG07 online at 0921H. RPS System voltage requirement. [WEBSMS] | CMIN
4/16/2024 9:23:04 AM | [NSO Update] Luzon Grid-04/16/2024 09:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0913H with power going to Visayas. [WEBSMS] | CLUZ
4/16/2024 9:21:57 AM | [NSO Update] Visayas Grid-04/16/2024 09:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0913H with power going to Visayas. [WEBSMS] | CVIS
4/16/2024 9:20:38 AM | [NSO Update] Luzon Grid-04/16/2024 09:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0901H from forward power direction. [WEBSMS] | CLUZ
4/16/2024 9:18:38 AM | [NSO Update] Visayas Grid-04/16/2024 09:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0901H from forward power direction. [WEBSMS] | CVIS
4/16/2024 9:09:18 AM | Mindanao Grid-04/16/2024 09:14: Agus 6 Unit shutdown at 0902H. (Planned Outage) [WEBSMS] | CMIN
4/16/2024 8:29:29 AM | Mindanao Grid-04/16/2024 08:34: WMPC DG10 online at 0827H. RPS System voltage requirement. [WEBSMS] | CMIN
4/16/2024 8:27:34 AM | Luzon Grid-04/16/2024 08:27: Tayabas PCB 9-05CB08TAY was de-energized at 0822H. (Planned Outage) [WEBSMS] | CLUZ
4/16/2024 8:21:55 AM | Luzon Grid-04/16/2024 08:22: La Trinidad 230kV Bus 2 was de-energized at 0810H. (Planned Outage) [WEBSMS] | CLUZ
4/16/2024 7:45:14 AM | Mindanao Grid-04/16/2024 07:50: Manolo Fortich-HEDCOR Manolo 2 138kV Line 1 de-energized at 0738H.(Planned Outage) [WEBSMS] | CMIN
4/16/2024 7:31:03 AM | [NSO Update] Luzon Grid-04/16/2024 07:31: GRID UPDATE AS OF 6:00 AM System Condition: RED ALERT CAP=13474MW, PK=11986MW, RR=386MW, NetOpMargin: AM=1103, PM=149, EVE=0 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: SLTEC 1 @120MW, SLTEC 2 @120MW, ILIJAN A @300MW [WEBSMS] | CLUZ
4/16/2024 7:26:27 AM | [NSO Update] Visayas Grid-04/16/2024 07:26: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2864MW, PK=2408MW, RR=92MW, NetOpMargin: AM=365, PM=260, EVE=213 Highest Unit O/L: THVI 1 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @315MW, PGPP1 @76MW, CEDC 3 @75MW, PDPP3-E @8MW [WEBSMS] | CVIS
4/16/2024 7:21:44 AM | [NSO Update] Visayas Grid-04/16/2024 07:21: System Advisory: 16-Apr-2024, Visayas Grid is on YELLOW Alert for interval hours 1500H, 1600H, and 1900H. Total capacity on forced outage is 414.9MW. Total of de-rated capacity is 261.6MW. [WEBSMS] | CVIS
4/16/2024 7:14:27 AM | [NSO Update] Luzon Grid-04/16/2024 07:14: System Advisory: 16-Apr-2024, Luzon Grid is on YELLOW Alert for interval hours 1400H, 1700H, 1800H, 2200H, and 2300H, and RED Alert for interval hours 1500H, 1600H, 1900H, 2000H, and 2100H. Total capacity on forced outage is 1811.3MW. Total of de-rated capacity is 306MW. [WEBSMS] | CLUZ
4/16/2024 7:03:26 AM | Mindanao Grid-04/16/2024 07:08: Libertad Power energized at 0657H. (Unplanned Outage) [WEBSMS] | CMIN
4/16/2024 6:46:44 AM | Luzon Grid-04/16/2024 06:46: SLPGC Unit 2 online at 0644H. (From an unplanned outage) [WEBSMS] | CLUZ
4/16/2024 6:31:08 AM | Luzon Grid-04/16/2024 06:31: Pagbilao Unit 1 shutdown at 0627H. (Unplanned Outage) [WEBSMS] | CLUZ
4/16/2024 5:30:00 AM | Mindanao Grid-04/16/2024 05:35: Libertad Power with 5MW load tripped/isolated at 0450H. Details to follow. (Unplanned Outage) [WEBSMS] | CMIN
4/16/2024 5:29:54 AM | [NSO Update] Mindanao Grid-04/16/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3119MW, PK=2531MW, RR=77MW, NetOpMargin: AM=509, PM=431, EVE=537 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @55MW, AG4 @68MW, AG5 @21MW, AG6 @97MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/16/2024 4:15:22 AM | [NSO Update] Mindanao Grid-04/16/2024 04:20: Weather Update: Ridge of a High Pressure Area (HPA) extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CMIN
4/16/2024 4:13:46 AM | [NSO Update] Visayas Grid-04/16/2024 04:13: Weather Update: Ridge of a High Pressure Area (HPA) extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CVIS
4/16/2024 4:13:29 AM | [NSO Update] Luzon Grid-04/16/2024 04:13: Weather Update: Ridge of a High Pressure Area (HPA) extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CLUZ
4/15/2024 11:03:51 PM | Mindanao Grid-04/15/2024 23:09: Manolo Fortich 2 HEP online at 2027H (Planned Outage) [WEBSMS] | CMIN
4/15/2024 9:34:26 PM | Mindanao Grid-04/15/2024 21:39: Bunawan-DRA 138kV L1 (7LI1BUN-DRA) energized/ restored at 2121H. From Planned Outage/Non-GOMP. Note: PO00AC. MSRP Stage I; Schedule I. [WEBSMS] | CMIN
4/15/2024 9:23:48 PM | Luzon Grid-04/15/2024 21:23: Pagbilao Unit 2 emergency shutdown at 2123H (Unplanned Outage) [WEBSMS] | CLUZ
4/15/2024 8:51:27 PM | [NSO Update] Luzon Grid-04/15/2024 20:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2048H with power going to Luzon [WEBSMS] | CLUZ
4/15/2024 8:51:00 PM | [NSO Update] Visayas Grid-04/15/2024 20:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2048H with power going to Luzon [WEBSMS] | CVIS
4/15/2024 8:02:43 PM | [NSO Update] Visayas Grid-04/15/2024 20:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2001H from reverse power direction [WEBSMS] | CVIS
4/15/2024 8:02:14 PM | [NSO Update] Luzon Grid-04/15/2024 20:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2001H from reverse power direction [WEBSMS] | CLUZ
4/15/2024 6:44:42 PM | Mindanao Grid-04/15/2024 18:50: WMPC DG02 declared unavailable at 1835H. Indication: Unable to Synchronize. (Unplanned Outage) [WEBSMS] | CMIN
4/15/2024 6:03:55 PM | [NSO Update] Luzon Grid-04/15/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13199MW, PK=12087MW, RR=377MW, NetOpMargin: EVE=735 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: ILIJAN A @ 300MW [WEBSMS] | CLUZ
4/15/2024 5:39:30 PM | [NSO Update] Mindanao Grid-04/15/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3061MW, PK=2376MW, RR=88MW, NetOpMargin: EVE=596 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @55MW, AG4 @68MW, AG5 @21MW, AG6 @99MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/15/2024 5:38:21 PM | [NSO Update] Visayas Grid-04/15/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2630MW, PK=2316MW, RR=90MW, NetOpMargin: EVE=225 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TGPP @79.5MW, LEYTE A @232MW, PGPP1 @76MW [WEBSMS] | CVIS
4/15/2024 4:46:15 PM | Mindanao Grid-04/15/2024 16:51: Agus 2 Unit 1 online at 1549H (Unplanned Outage) [WEBSMS] | CMIN
4/15/2024 4:44:52 PM | Mindanao Grid-04/15/2024 16:50: Bunawan SS 138kV Bus #1 energized/restored at 1634H. From Planned Outage (Non-GOMP). Note: Approved P&E request. [WEBSMS] | CMIN
4/15/2024 4:44:25 PM | Visayas Grid-04/15/2024 16:44: EDC - Malitbog U3 emergency shutdown at 1632H (Unplanned Outage) [WEBSMS] | CVIS
4/15/2024 4:42:27 PM | Mindanao Grid-04/15/2024 16:47: Bunawan SS 138kV Bus #1 de-energized at 1311H. Planned Outage (Non-GOMP). Note: Approved P&E request. [WEBSMS] | CMIN
4/15/2024 4:37:34 PM | Visayas Grid-04/15/2024 16:37: EDC - Mahanagdong U3 synchronized at 1526H (Unplanned Outage) [WEBSMS] | CVIS
4/15/2024 12:44:14 PM | [NSO Update] Mindanao Grid-04/15/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3106MW, PK=2562MW, RR=91MW, NetOpMargin: PM=453, EVE=555 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @55MW, AG4 @68MW, AG5 @21MW, AG6 @99MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/15/2024 12:42:52 PM | [NSO Update] Visayas Grid-04/15/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2844MW, PK=2498MW, RR=96MW, NetOpMargin: PM=250, EVE=224 Highest Unit O/L: THVI 1 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @285MW, PGPP1 @76MW [WEBSMS] | CVIS
4/15/2024 12:41:36 PM | [NSO Update] Luzon Grid-04/15/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14293MW, PK=12715MW, RR=401MW, NetOpMargin: PM=1177, EVE=1120 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @300MW [WEBSMS] | CLUZ
4/15/2024 10:23:44 AM | Mindanao Grid-04/15/2024 10:29: WMPC DG01 online at 0926H. RPS System voltage requirement. [WEBSMS] | CMIN
4/15/2024 10:21:48 AM | Mindanao Grid-04/15/2024 10:27: WMPC DG06 online at 1018H. RPS System voltage requirement. [WEBSMS] | CMIN
4/15/2024 8:34:57 AM | [NSO Update] Visayas Grid-04/15/2024 08:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0832H with power going to Visayas [WEBSMS] | CVIS
4/15/2024 8:34:37 AM | [NSO Update] Luzon Grid-04/15/2024 08:34: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0832H with power going to Visayas [WEBSMS] | CLUZ
4/15/2024 8:32:50 AM | Mindanao Grid-04/15/2024 08:38: WMPC DG10 online at 0830H. RPS System voltage requirement. (Planned Outage) [WEBSMS] | CMIN
4/15/2024 8:24:20 AM | [NSO Update] Visayas Grid-04/15/2024 08:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0822H from forward power direction [WEBSMS] | CVIS
4/15/2024 8:23:59 AM | [NSO Update] Luzon Grid-04/15/2024 08:24: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0822H from forward power direction [WEBSMS] | CLUZ
4/15/2024 7:24:41 AM | Mindanao Grid-04/15/2024 07:30: Manolo Fortich 2 HEP Unit 2, 3, & 4 shutdown at 0710H. Semi-Annual PMS. (Planned Outage) [WEBSMS] | CMIN
4/15/2024 7:23:00 AM | Mindanao Grid-04/15/2024 07:28: Manolo Fortich 2 HEP Unit 1 shutdown at 0709H. Semi-Annual PMS. (Planned Outage) [WEBSMS] | CMIN
4/15/2024 6:54:48 AM | Luzon Grid-04/15/2024 06:54: Calamba SS 300MVA T02 (CO) and NGCP-MERALCO Calamba 230kV Tie L2 restored at 0653H (Planned Outage) [WEBSMS] | CLUZ
4/15/2024 6:17:46 AM | Mindanao Grid-04/15/2024 06:23: Villanueva-Jasaan 138kV Line 1 restored/energized at 0616H. (Planned Outage). [WEBSMS] | CMIN
4/15/2024 5:48:43 AM | [NSO Update] Mindanao Grid-04/15/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3130MW, PK=2333MW, RR=82MW, NetOpMargin: AM=715, PM=569, EVE=673 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @55MW, AG4 @68MW, AG5 @21MW, AG6 @99MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/15/2024 5:44:32 AM | [NSO Update] Visayas Grid-04/15/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2783MW, PK=2362MW, RR=92MW, NetOpMargin: AM=329, PM=314, EVE=237 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TGPP @79.5MW, LEYTE A @343MW, PGPP1 @76MW [WEBSMS] | CVIS
4/15/2024 5:41:05 AM | [NSO Update] Luzon Grid-04/15/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14464MW, PK=11632MW, RR=386MW, NetOpMargin: AM=2447, PM=1642, EVE=1815 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: N/A [WEBSMS] | CLUZ
4/15/2024 4:18:01 AM | Mindanao Grid-04/15/2024 04:23: Villanueva-Jasaan 138kV Line 1 de-energized at 0412H. (Planned Outage) [WEBSMS] | CMIN
4/15/2024 4:14:58 AM | [NSO Update] Visayas Grid-04/15/2024 04:15: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
4/15/2024 4:11:51 AM | [NSO Update] Mindanao Grid-04/15/2024 04:17: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
4/15/2024 4:11:08 AM | [NSO Update] Luzon Grid-04/15/2024 04:11: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/15/2024 3:16:27 AM | Luzon Grid-04/15/2024 03:16: Tayabas SS 600MVA T02 energized at 0314H (Planned Outage) [WEBSMS] | CLUZ
4/15/2024 12:58:46 AM | Luzon Grid-04/15/2024 00:58: Tayabas SS 600MVA T02 de-energized at 0058H. (Planned Outage) [WEBSMS] | CLUZ
4/15/2024 12:47:27 AM | Visayas Grid-04/15/2024 00:47: TVI U2 emergency cut out at 0047H (Unplanned Outage) [WEBSMS] | CVIS
4/15/2024 12:05:03 AM | Mindanao Grid-04/15/2024 00:10: Butuan-San Francisco 138kV Line restored/energized at 0001H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 11:46:29 PM | Luzon Grid-04/14/2024 23:46: San Jose-Balsik 500kV Line restored at 2346H. (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 9:44:30 PM | Luzon Grid-04/14/2024 21:44: NGCP-MERALCO Calamba 230kV Tie L2 de-energized at 2143H. (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 9:44:01 PM | Mindanao Grid-04/14/2024 21:49: Aurora-Polanco 138kV Line 2 restored/energized at 2142H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 9:43:26 PM | Luzon Grid-04/14/2024 21:43: Calamba SS 300MVA T02 (CO) de-energized at 2142H. (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 7:14:44 PM | Mindanao Grid-04/14/2024 19:20: Agus 6 SWY-Agus 7 HEP Unit No.2 138kV Line energized at 1910H. (Planned Outage) [WEBSMS] | CMIN
4/14/2024 6:19:17 PM | Mindanao Grid-04/14/2024 18:24: WMPC DG04 online at 1815H. RPS System voltage requirement. [WEBSMS] | CMIN
4/14/2024 6:12:45 PM | Mindanao Grid-04/14/2024 18:18: PULANGI 4 HEP Unit 1 online at 1807H. (Unplanned Outage) [WEBSMS] | CMIN
4/14/2024 5:49:26 PM | [NSO Update] Mindanao Grid-04/14/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3032MW, PK=2253MW, RR=80MW, NetOpMargin: EVE=0 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @55MW, AG4 @68MW, AG5 @21MW, AG6 @99MW, AG7 @19MW, PG4 @28MW [WEBSMS] | CMIN
4/14/2024 5:46:54 PM | [NSO Update] Visayas Grid-04/14/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2650MW, PK=2128MW, RR=94MW, NetOpMargin: EVE=428 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @79.5MW, LEYTE A @306MW, PGPP1 @76MW [WEBSMS] | CVIS
4/14/2024 5:42:32 PM | [NSO Update] Luzon Grid-04/14/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13575MW, PK=10980MW, RR=295MW, NetOpMargin: EVE=2299 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: N/A [WEBSMS] | CLUZ
4/14/2024 5:40:21 PM | Mindanao Grid-04/14/2024 17:45: Tagoloan SS 138/69kV 100MVA Power Transformer No. 1 energized at 1739H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 5:38:07 PM | Mindanao Grid-04/14/2024 17:43: Tagoloan-Manolo 138kV Line 2 restored/energized at 1737H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 5:36:47 PM | Mindanao Grid-04/14/2024 17:42: Tagoloan SS 138/69kV 100MVA Power Transformer No. 2 energized at 1735H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 5:34:33 PM | Mindanao Grid-04/14/2024 17:39: Tagoloan SS 138kV Bus 2 energized at 1731H. (Planned Outage) [WEBSMS] | CMIN
4/14/2024 5:32:13 PM | Mindanao Grid-04/14/2024 17:37: Tagoloan-Villanueva 138kV Line 2 restored/energized at 1730H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 4:59:32 PM | Mindanao Grid-04/14/2024 17:04: Tagoloan-Villanueva 138kV Line 2 de-energized at 1658H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 4:57:58 PM | Mindanao Grid-04/14/2024 17:03: Tagoloan-Villanueva 138kV Line 1 restored/energized at 1622H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 4:46:10 PM | [NSO Update] Luzon Grid-04/14/2024 16:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1643H with power going to Luzon [WEBSMS] | CLUZ
4/14/2024 4:44:46 PM | [NSO Update] Visayas Grid-04/14/2024 16:44: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1643H with power going to Luzon [WEBSMS] | CVIS
4/14/2024 4:27:32 PM | Luzon Grid-04/14/2024 16:27: San Jose SS 750MVA T05 restored at 1627H. (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 4:11:23 PM | Luzon Grid-04/14/2024 16:11: Naga SS 230kV Bus 2 restored at 1610H. (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 4:07:14 PM | Visayas Grid-04/14/2024 16:07: Compostela SS - Consolacion 69 KV line energized at 1604H(Planned Outage) [WEBSMS] | CVIS
4/14/2024 12:57:14 PM | [NSO Update] Visayas Grid-04/14/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2573MW, PK=2003MW, RR=90MW, NetOpMargin: PM=480, EVE=199 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @72.1MW, LEYTE A @298MW, PGPP1 @76MW [WEBSMS] | CVIS
4/14/2024 12:39:43 PM | [NSO Update] Mindanao Grid-04/14/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3083MW, PK=2046MW, RR=78MW, NetOpMargin: PM=959, EVE=697 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @55MW, AG4 @68MW, AG5 @21MW, AG6 @99MW, AG7 @19MW, PG4 @28MW [WEBSMS] | CMIN
4/14/2024 12:38:18 PM | [NSO Update] Luzon Grid-04/14/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14220MW, PK=10404MW, RR=311MW, NetOpMargin: PM=3505, EVE=2393 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @300MW [WEBSMS] | CLUZ
4/14/2024 12:13:11 PM | Luzon Grid-04/14/2024 12:13: Bolo SS 230kV Bus 1 restored at 1209H (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 11:01:46 AM | Luzon Grid-04/14/2024 11:01: Binga-Ambuklao 230kV Line 1 restored at 1101H (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 10:57:30 AM | Luzon Grid-04/14/2024 10:57: Sta. Rita Module 40 (264MW) tripped at 1055H. Lowest system frequency is 59.266Hz. [WEBSMS] | CLUZ
4/14/2024 10:03:37 AM | Luzon Grid-04/14/2024 10:03: Duhat 300MVA T02 restored at 1000H (Unplanned Outage) [WEBSMS] | CLUZ
4/14/2024 9:53:13 AM | Luzon Grid-04/14/2024 09:53: Duhat 300MVA T02 de-energized at 0947H (Unplanned Outage) [WEBSMS] | CLUZ
4/14/2024 8:32:04 AM | Luzon Grid-04/14/2024 08:32: Correction: Bolo SS 230kV Bus 1 de-energized at 0725H (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 8:24:21 AM | Mindanao Grid-04/14/2024 08:29: Tagoloan-Villanueva 138kV Line 1 de-energized at 0823H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 8:18:31 AM | Mindanao Grid-04/14/2024 08:23: Tagoloan-Villanueva 138kV Line 2 restored/energized at 0817H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 7:56:27 AM | Luzon Grid-04/14/2024 07:56: Dasmarinas - Rosario 115kV Line restored at 0755H (Unplanned Outage) [WEBSMS] | CLUZ
4/14/2024 7:31:02 AM | Mindanao Grid-04/14/2024 07:36: Tagoloan SS 138kV Bus 2 de-energized at 0726H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 7:29:31 AM | Mindanao Grid-04/14/2024 07:34: Tagoloan SS 138/69kV 100MVA Power Transformer No. 2 de-energized at 0724H. (Planned Outage) [WEBSMS] | CMIN
4/14/2024 7:26:40 AM | Mindanao Grid-04/14/2024 07:31: Tagoloan-Manolo 138kV Line 2 de-energized at 0722H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 7:25:47 AM | Luzon Grid-04/14/2024 07:25: Naga SS 230kV Bus 2 de-energized at 0725H (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 7:25:29 AM | Mindanao Grid-04/14/2024 07:30: Tagoloan-Villanueva 138kV Line 2 de-energized at 0718H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 7:23:24 AM | Mindanao Grid-04/14/2024 07:28: Tagoloan SS 138/69kV 100MVA Power Transformer No. 1 de-energized at 0714H. (Planned Outage) [WEBSMS] | CMIN
4/14/2024 7:03:45 AM | Luzon Grid-04/14/2024 07:03: Naga 230kV Bus 2 de-energized at 0702H (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 6:51:11 AM | Mindanao Grid-04/14/2024 06:56: Baloi SS 138kV Bus 1 energized at 0642H. (Planned Outage) [WEBSMS] | CMIN
4/14/2024 6:46:21 AM | Mindanao Grid-04/14/2024 06:51: Aurora-Polanco 138kV Line 2 de-energized at 0636H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 6:44:25 AM | Mindanao Grid-04/14/2024 06:49: Butuan-San Francisco 138kV Line de-energized at 0615H. (Planned Outage). [WEBSMS] | CMIN
4/14/2024 6:21:53 AM | Visayas Grid-04/14/2024 06:22: Compostela SS - 69KV Consolacion fdr. de-energized at 0608H(Planned Outage) [WEBSMS] | CVIS
4/14/2024 6:21:42 AM | Luzon Grid-04/14/2024 06:21: Dasmarinas - Rosario 115kV Line de-energized at 0613H (Unplanned Outage) [WEBSMS] | CLUZ
4/14/2024 6:13:29 AM | [NSO Update] Visayas Grid-04/14/2024 06:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0608H from forward power direction [WEBSMS] | CVIS
4/14/2024 6:13:09 AM | [NSO Update] Luzon Grid-04/14/2024 06:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0608H from forward power direction [WEBSMS] | CLUZ
4/14/2024 5:54:17 AM | [NSO Update] Luzon Grid-04/14/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14737MW, PK=10136MW, RR=294MW, NetOpMargin: AM=4307, PM=3613, EVE=2703 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 300MW [WEBSMS] | CLUZ
4/14/2024 5:53:17 AM | [NSO Update] Mindanao Grid-04/14/2024 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3090MW, PK=1980MW, RR=77MW, NetOpMargin: AM=1033, PM=906, EVE=704 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @55MW, AG4 @68MW, AG5 @21MW, AG6 @99MW, AG7 @19MW, PG4 @28MW [WEBSMS] | CMIN
4/14/2024 5:52:10 AM | [NSO Update] Visayas Grid-04/14/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2581MW, PK=1932MW, RR=89MW, NetOpMargin: AM=560, PM=414, EVE=336 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 72.1MW, Leyte A @ 275MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/14/2024 5:34:01 AM | Luzon Grid-04/14/2024 05:34: Binga-Ambuklao 230kV Line 1 de-energized at 0532H (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 5:07:27 AM | Luzon Grid-04/14/2024 05:07: San Jose SS 750MVA T05 de-energized at 0506H (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 5:05:16 AM | Luzon Grid-04/14/2024 05:05: San Jose-Balsik 500kV Line de-energized at 0504H (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 4:33:56 AM | [NSO Update] Luzon Grid-04/14/2024 04:34: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/14/2024 4:33:37 AM | [NSO Update] Mindanao Grid-04/14/2024 04:38: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
4/14/2024 4:33:18 AM | [NSO Update] Visayas Grid-04/14/2024 04:33: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
4/14/2024 3:40:15 AM | Luzon Grid-04/14/2024 03:40: Calamba 300MVA T01 restored at 0338H (Planned Outage) [WEBSMS] | CLUZ
4/14/2024 1:08:35 AM | Mindanao Grid-04/14/2024 01:13: Bunawan - Don Ramon 138kV L1 (DLPCs owned & maintained 138kVL) de-energized at 0100H. Planned Outage (Non-GOMP) [WEBSMS] | CMIN
4/13/2024 11:29:48 PM | Mindanao Grid-04/13/2024 23:35: Aurora - Polanco 138kV Line1 restored/energized at 2325H. (Planned Outage) [WEBSMS] | CMIN
4/13/2024 10:47:24 PM | Mindanao Grid-04/13/2024 22:52: WMPC DG04 shutdown at 2244H. RPS System voltage requirement. [WEBSMS] | CMIN
4/13/2024 10:35:20 PM | Mindanao Grid-04/13/2024 22:40: Pulangi4 Unit1 shutdown at 2208H due to Low Water Elevation. Outside Management Control. [WEBSMS] | CMIN
4/13/2024 10:12:23 PM | [NSO Update] Visayas Grid-04/13/2024 22:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2210H with power going to Luzon. [WEBSMS] | CVIS
4/13/2024 10:12:10 PM | [NSO Update] Luzon Grid-04/13/2024 22:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2210H with power going to Luzon. [WEBSMS] | CLUZ
4/13/2024 10:01:06 PM | [NSO Update] Visayas Grid-04/13/2024 22:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2159H from reverse power direction. [WEBSMS] | CVIS
4/13/2024 10:00:51 PM | [NSO Update] Luzon Grid-04/13/2024 22:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2159H from reverse power direction. [WEBSMS] | CLUZ
4/13/2024 9:49:24 PM | Mindanao Grid-04/13/2024 21:54: Balo-i SS 138kV Bus1 de-energized at 2148H. (Planned Outage) [WEBSMS] | CMIN
4/13/2024 9:47:29 PM | Luzon Grid-04/13/2024 21:47: Calamba-Calamba DP Tie Line 1 and 300MVA T01 de-energized at 2139H and 2138H respectively (Planned Outage) [WEBSMS] | CLUZ
4/13/2024 9:39:25 PM | Mindanao Grid-04/13/2024 21:44: MCC U2 online at 2135H. from Reserve Shutdown [WEBSMS] | CMIN
4/13/2024 8:17:07 PM | Mindanao Grid-04/13/2024 20:22: WMPC DG01 shutdown at 2014H. RPS System voltage requirement. [WEBSMS] | CMIN
4/13/2024 6:51:07 PM | Mindanao Grid-04/13/2024 18:56: WMPC DG01 online at 1758H. RPS System voltage requirement. [WEBSMS] | CMIN
4/13/2024 6:43:42 PM | Mindanao Grid-04/13/2024 18:48: WMPC DG01 shutdown at 1714H. RPS System voltage requirement. [WEBSMS] | CMIN
4/13/2024 6:32:45 PM | Mindanao Grid-04/13/2024 18:38: San Francisco SS 138/69kV 50MVA Power Transformer #2 energized at 1827H. (Planned Outage) [WEBSMS] | CMIN
4/13/2024 6:09:27 PM | Mindanao Grid-04/13/2024 18:14: Balo-i - Agus6 69kV Tie Line energized/loop at 1807H. (Unplanned Outage) [WEBSMS] | CMIN
4/13/2024 6:02:58 PM | [NSO Update] Visayas Grid-04/13/2024 18:03: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1759H with power going to Visayas. [WEBSMS] | CVIS
4/13/2024 6:02:45 PM | [NSO Update] Luzon Grid-04/13/2024 18:02: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1759H with power going to Visayas. [WEBSMS] | CLUZ
4/13/2024 5:57:32 PM | Mindanao Grid-04/13/2024 18:02: Balo-i - Agus6 69kV Tie Line tripped at 1712H. (Unplanned Outage) [WEBSMS] | CMIN
4/13/2024 5:50:33 PM | [NSO Update] Visayas Grid-04/13/2024 17:50: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1749H from forward power direction. [WEBSMS] | CVIS
4/13/2024 5:50:19 PM | [NSO Update] Luzon Grid-04/13/2024 17:50: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1749H from forward power direction. [WEBSMS] | CLUZ
4/13/2024 5:47:33 PM | [NSO Update] Mindanao Grid-04/13/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3069MW, PK=2373MW, RR=88MW, NetOpMargin: EVE=608 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @55MW, AG4 @68MW, AG5 @21MW, AG6 @99MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/13/2024 5:46:27 PM | [NSO Update] Visayas Grid-04/13/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2605MW, PK=2233MW, RR=94MW, NetOpMargin: EVE=278 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 73.1MW, Leyte A @ 290MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/13/2024 5:44:35 PM | [NSO Update] Luzon Grid-04/13/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13494MW, PK=11466MW, RR=377MW, NetOpMargin: EVE=1651 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Ilijan A @ 300MW [WEBSMS] | CLUZ
4/13/2024 4:21:36 PM | Mindanao Grid-04/13/2024 16:26: Jasaan SS 138kV Bus1 energized at 1619H. (Planned Outage) [WEBSMS] | CMIN
4/13/2024 3:21:38 PM | Luzon Grid-04/13/2024 15:21: San Gabriel online at 1519H (Planned Outage) [WEBSMS] | CLUZ
4/13/2024 2:42:29 PM | Luzon Grid-04/13/2024 14:42: Santiago-Magat HEPP 230kV Line 1 loop at 1439H (Planned Outage) [WEBSMS] | CLUZ
4/13/2024 1:40:01 PM | Luzon Grid-04/13/2024 13:40: Balsik SS PCB 9Z-01CB08BIK de-energized at 1332H (Planned Outage) [WEBSMS] | CLUZ
4/13/2024 1:22:20 PM | Luzon Grid-04/13/2024 13:22: Bolo SS 230kV Bus 2 restored at 1321H (Planned Outage) [WEBSMS] | CLUZ
4/13/2024 1:19:48 PM | Mindanao Grid-04/13/2024 13:25: Balo-i - Agus5 138kV Line restored/energized at 1316H. (Planned Outage) [WEBSMS] | CMIN
4/13/2024 1:13:12 PM | Mindanao Grid-04/13/2024 13:18: WMPC DG01 online at 1308H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/13/2024 12:38:02 PM | [NSO Update] Mindanao Grid-04/13/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3130MW, PK=2375MW, RR=91MW, NetOpMargin: PM=664, EVE=582 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @55MW, AG4 @68MW, AG5 @21MW, AG6 @99MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/13/2024 12:36:26 PM | [NSO Update] Visayas Grid-04/13/2024 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2735MW, PK=2214MW, RR=92MW, NetOpMargin: PM=429, EVE=172 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @74MW, LEYTE A @340MW, PGPP1 @76MW [WEBSMS] | CVIS
4/13/2024 12:35:00 PM | [NSO Update] Luzon Grid-04/13/2024 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14840MW, PK=11427MW, RR=404MW, NetOpMargin: PM=3009, EVE=2117 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @300MW [WEBSMS] | CLUZ
4/13/2024 12:32:02 PM | Mindanao Grid-04/13/2024 12:37: Aurora SS 138kV Bus1 energized at 1229H. (Planned Outage) [WEBSMS] | CMIN
4/13/2024 12:02:15 PM | Luzon Grid-04/13/2024 12:02: Balsik SS PCB 9Z-01CB24BIK restored at 1201H (Planned Outage) [WEBSMS] | CLUZ
4/13/2024 10:34:56 AM | Mindanao Grid-04/13/2024 10:40: WMPC DG04 online at 1030H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/13/2024 10:02:21 AM | Mindanao Grid-04/13/2024 10:07: Agus5 SY � Agus5 HEP Line 2 de-energized at 0930H. (Planned Outage) [WEBSMS] | CMIN
4/13/2024 9:06:47 AM | Luzon Grid-04/13/2024 09:06: Balsik SS PCB 9Z-01CB24BIK de-energized at 0905H (Planned Outage) [WEBSMS] | CLUZ
4/13/2024 8:12:55 AM | Mindanao Grid-04/13/2024 08:18: Aurora SS 138kV Bus1 de-energized at 0810H. (Planned Outage) [WEBSMS] | CMIN
4/13/2024 8:04:17 AM | Mindanao Grid-04/13/2024 08:09: Agus5 U2 shutdown at 0802H. (Planned Outage) [WEBSMS] | CMIN
4/13/2024 7:16:37 AM | Luzon Grid-04/13/2024 07:16: Bolo SS 230kV Bus 2 de-energized at 0716H (Planned Outage) [WEBSMS] | CLUZ
4/13/2024 7:16:28 AM | Mindanao Grid-04/13/2024 07:21: Balo-i - Agus5 138kV Line de-energized at 0714H. (Planned Outage) [WEBSMS] | CMIN
4/13/2024 7:01:00 AM | Mindanao Grid-04/13/2024 07:06: San Francisco SS 138/69kV 50MVA Power Transformer No. 2 de-energized at 0657H. (Planned Outage) [WEBSMS] | CMIN
4/13/2024 6:10:46 AM | Mindanao Grid-04/13/2024 06:16: Aurora - Polanco 138kV Line 1 de-energized at 0603H (Planned Outage). [WEBSMS] | CMIN
4/13/2024 5:49:07 AM | [NSO Update] Mindanao Grid-04/13/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3139MW, PK=2210MW, RR=82MW, NetOpMargin: AM=847, PM=771, EVE=695 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @55MW, AG4 @68MW, AG5 @21MW, AG6 @99MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/13/2024 5:47:40 AM | [NSO Update] Visayas Grid-04/13/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2589MW, PK=2181MW, RR=89MW, NetOpMargin: AM=319, PM=489, EVE=188 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @74MW, LEYTE A @340MW, PGPP1 @76MW [WEBSMS] | CVIS
4/13/2024 5:46:26 AM | [NSO Update] Luzon Grid-04/13/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14813MW, PK=10766MW, RR=386MW, NetOpMargin: AM=3661, PM=3417, EVE=2607 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @300MW [WEBSMS] | CLUZ
4/13/2024 5:37:59 AM | Mindanao Grid-04/13/2024 05:43: Jasaan SS 138kV Bus #1 shutdown at 0535H. (Planned Outage) [WEBSMS] | CMIN
4/13/2024 4:34:55 AM | Luzon Grid-04/13/2024 04:35: San Gabriel shutdown at 0431H. (Reserve shutdown) [WEBSMS] | CLUZ
4/13/2024 4:14:51 AM | [NSO Update] Mindanao Grid-04/13/2024 04:20: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
4/13/2024 4:14:28 AM | [NSO Update] Visayas Grid-04/13/2024 04:14: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
4/13/2024 4:14:11 AM | [NSO Update] Luzon Grid-04/13/2024 04:14: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/12/2024 9:15:32 PM | Mindanao Grid-04/12/2024 21:20: WMPC DG04 shutdown at 2114H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/12/2024 8:06:59 PM | [NSO Update] Luzon Grid-04/12/2024 20:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2004H with power going to Luzon [WEBSMS] | CLUZ
4/12/2024 8:06:41 PM | [NSO Update] Visayas Grid-04/12/2024 20:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2004H with power going to Luzon [WEBSMS] | CVIS
4/12/2024 8:01:13 PM | [NSO Update] Visayas Grid-04/12/2024 20:01: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1954H from reverse power direction [WEBSMS] | CVIS
4/12/2024 8:00:55 PM | [NSO Update] Luzon Grid-04/12/2024 20:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1954H from reverse power direction [WEBSMS] | CLUZ
4/12/2024 7:57:23 PM | Mindanao Grid-04/12/2024 20:02: WMPC DG10 shutdown at 1954H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/12/2024 7:43:54 PM | Mindanao Grid-04/12/2024 19:49: Baloi-Agus 5 138kV Line energized/looped at 1941H. Planned Outage. [WEBSMS] | CMIN
4/12/2024 6:20:45 PM | Mindanao Grid-04/12/2024 18:25: Bislig 138kV 50MVA TR#2 energized at 1815H. Planned Outage/GOMP. [WEBSMS] | CMIN
4/12/2024 6:16:06 PM | [NSO Update] Mindanao Grid-04/12/2024 18:21: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3044MW, PK=2427MW, RR=96MW, NetOpMargin: EVE=522 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @30MW, AG4 @68MW, AG5 @21MW, AG6 @99MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/12/2024 6:13:41 PM | [NSO Update] Visayas Grid-04/12/2024 18:13: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2562MW, PK=2303MW, RR=90MW, NetOpMargin: EVE=169 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @74MW, LEYTE A @340MW, PGPP1 @76MW [WEBSMS] | CVIS
4/12/2024 6:12:03 PM | [NSO Update] Luzon Grid-04/12/2024 18:12: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13401MW, PK=11649MW, RR=458MW, NetOpMargin: EVE=1293 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: N/A [WEBSMS] | CLUZ
4/12/2024 5:24:52 PM | Mindanao Grid-04/12/2024 17:30: WMPC DG01 shutdown at 1719H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/12/2024 2:25:20 PM | Mindanao Grid-04/12/2024 14:30: PULANGI 4 HEP Unit 2 online at 1358H. (Unplanned Outage) [WEBSMS] | CMIN
4/12/2024 2:19:39 PM | Luzon Grid-04/12/2024 14:19: SCPC 4 online at 1418H. (Unplanned Outage) [WEBSMS] | CLUZ
4/12/2024 1:01:46 PM | Mindanao Grid-04/12/2024 13:06: WMPC DG01 online at 1258H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/12/2024 12:57:10 PM | [NSO Update] Luzon Grid-04/12/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14355MW, PK=12424MW, RR=485MW, NetOpMargin: PM=1446, EVE=1267 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: N/A [WEBSMS] | CLUZ
4/12/2024 12:55:19 PM | [NSO Update] Visayas Grid-04/12/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2743MW, PK=2426MW, RR=97MW, NetOpMargin: PM=220, EVE=170 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @73MW, LEYTE A @337MW, PGPP1 @76MW [WEBSMS] | CVIS
4/12/2024 12:55:13 PM | [NSO Update] Mindanao Grid-04/12/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3106MW, PK=2521MW, RR=99MW, NetOpMargin: PM=486, EVE=547 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @30MW, AG4 @68MW, AG5 @21MW, AG6 @99MW, AG7 @19MW, PG4 @56MW [WEBSMS] | CMIN
4/12/2024 9:34:53 AM | Mindanao Grid-04/12/2024 09:40: WMPC DG10 online at 0931H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/12/2024 9:11:26 AM | Luzon Grid-04/12/2024 09:11: Hermosa-Malolos 230kV Line loop via Malolos side at 0909H (Unplanned Outage) [WEBSMS] | CLUZ
4/12/2024 9:08:09 AM | Luzon Grid-04/12/2024 09:08: Hermosa-Malolos 230kV Line tripped at 0900H and reclosed at Hermosa side. (Unplanned Outage) [WEBSMS] | CLUZ
4/12/2024 9:01:42 AM | Mindanao Grid-04/12/2024 09:06: WMPC DG04 online at 0858H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/12/2024 8:19:41 AM | [NSO Update] Visayas Grid-04/12/2024 08:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0818H with power going to Visayas. [WEBSMS] | CVIS
4/12/2024 8:19:34 AM | [NSO Update] Luzon Grid-04/12/2024 08:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0818H with power going to Visayas. [WEBSMS] | CLUZ
4/12/2024 8:07:33 AM | [NSO Update] Luzon Grid-04/12/2024 08:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0805H from forward power direction. [WEBSMS] | CLUZ
4/12/2024 8:07:02 AM | [NSO Update] Visayas Grid-04/12/2024 08:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0805H from forward power direction. [WEBSMS] | CVIS
4/12/2024 8:05:44 AM | Visayas Grid-04/12/2024 08:05: Cebu SS 138KV Bus 2 energized at 0758H.(Planned Outage) [WEBSMS] | CVIS
4/12/2024 6:45:44 AM | Mindanao Grid-04/12/2024 06:50: Bislig SS 138kV 50MVA TR#2 shutdown at 0639H. (Planned Outage) [WEBSMS] | CMIN
4/12/2024 6:43:24 AM | Mindanao Grid-04/12/2024 06:48: Baloi-Agus 5 138kV Line shutdown at 0632H. (Planned Outage) [WEBSMS] | CMIN
4/12/2024 5:52:12 AM | [NSO Update] Luzon Grid-04/12/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14563MW, PK=11613MW, RR=455MW, NetOpMargin: AM=2496, PM=1429, EVE=1474 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: N/A [WEBSMS] | CLUZ
4/12/2024 5:49:32 AM | [NSO Update] Mindanao Grid-04/12/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3170MW, PK=2295MW, RR=95MW, NetOpMargin: AM=780, PM=557, EVE=591 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @35MW, AG2 @55MW, AG4 @68MW, AG5 @21MW, AG6 @99MW, AG7 @19MW, PG4 @84MW [WEBSMS] | CMIN
4/12/2024 5:47:22 AM | [NSO Update] Visayas Grid-04/12/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2761MW, PK=2325MW, RR=94MW, NetOpMargin: AM=343, PM=204, EVE=170 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @73MW, LEYTE A @340MW, PGPP1 @76MW [WEBSMS] | CVIS
4/12/2024 5:13:31 AM | [NSO Update] Luzon Grid-04/12/2024 05:13: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/12/2024 5:11:57 AM | [NSO Update] Mindanao Grid-04/12/2024 05:17: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
4/12/2024 5:11:20 AM | [NSO Update] Visayas Grid-04/12/2024 05:11: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
4/12/2024 12:12:43 AM | Luzon Grid-04/12/2024 00:12: Bantay 7.5MVar Shunt Capacitor No. 1 restored at 0008H (Planned Outage) [WEBSMS] | CLUZ
4/11/2024 9:32:29 PM | Mindanao Grid-04/11/2024 21:37: WMPC DG04 cut-out at 2059H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/11/2024 9:01:07 PM | Mindanao Grid-04/11/2024 21:06: WMPC DG04 shutdown at 2059H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/11/2024 8:29:37 PM | Luzon Grid-04/11/2024 20:29: Bantay SS 7.5MVar Shunt Capacitor No. 1 de-energized at 2024H (Planned Outage) [WEBSMS] | CLUZ
4/11/2024 7:59:57 PM | [NSO Update] Visayas Grid-04/11/2024 19:59: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1957H with power going to Luzon [WEBSMS] | CVIS
4/11/2024 7:58:59 PM | [NSO Update] Luzon Grid-04/11/2024 19:59: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1957H with power going to Luzon [WEBSMS] | CLUZ
4/11/2024 7:51:41 PM | [NSO Update] Visayas Grid-04/11/2024 19:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1947H from reverse power direction [WEBSMS] | CVIS
4/11/2024 7:51:08 PM | [NSO Update] Luzon Grid-04/11/2024 19:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1947H from reverse power direction [WEBSMS] | CLUZ
4/11/2024 7:45:33 PM | Mindanao Grid-04/11/2024 19:50: WMPC DG10 shutdown at 1943H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/11/2024 5:58:05 PM | [NSO Update] Mindanao Grid-04/11/2024 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3044MW, PK=2368MW, RR=88MW, NetOpMargin: EVE=588 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @27MW, AG2 @31MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
4/11/2024 5:55:18 PM | [NSO Update] Visayas Grid-04/11/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2510MW, PK=2247MW, RR=92MW, NetOpMargin: EVE=171 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @74MW, LEYTE A @335MW, PGPP1 @76MW [WEBSMS] | CVIS
4/11/2024 5:51:17 PM | [NSO Update] Luzon Grid-04/11/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13471MW, PK=11531MW, RR=464MW, NetOpMargin: EVE=1476 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: N/A [WEBSMS] | CLUZ
4/11/2024 5:32:22 PM | Mindanao Grid-04/11/2024 17:37: WMPC DG01 cut-out at 1714H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/11/2024 3:20:13 PM | Mindanao Grid-04/11/2024 15:25: AGUS 1 HEP Unit 1 with 18.0MW load shutdown at 1512H. Semi-Annual PMS. (Planned Outage) [WEBSMS] | CMIN
4/11/2024 3:09:32 PM | Mindanao Grid-04/11/2024 15:14: AGUS4 HEP Unit 3 shutdown at 1501H due to OMC-low forebay elevation. Unplanned Outage. [WEBSMS] | CMIN
4/11/2024 2:21:21 PM | Mindanao Grid-04/11/2024 14:26: WMPC DG10 online at 1302H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/11/2024 12:53:21 PM | [NSO Update] Mindanao Grid-04/11/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3111MW, PK=2549MW, RR=91MW, NetOpMargin: PM=471, EVE=548 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @31MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
4/11/2024 12:49:57 PM | [NSO Update] Visayas Grid-04/11/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2738MW, PK=2443MW, RR=98MW, NetOpMargin: PM=197, EVE=170 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @74MW, LEYTE A @335MW, PGPP1 @76MW [WEBSMS] | CVIS
4/11/2024 12:48:02 PM | [NSO Update] Luzon Grid-04/11/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14387MW, PK=12432MW, RR=491MW, NetOpMargin: PM=1464, EVE=1533 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: N/A [WEBSMS] | CLUZ
4/11/2024 12:05:13 PM | Mindanao Grid-04/11/2024 12:10: STEAG Unit 2 on emergency shutdown at 1100H due to re-heater tube leak problem. Note: STEAG management initiated gradual unloading from 100MW to 0MW. (Unplanned Outage) [WEBSMS] | CMIN
4/11/2024 9:33:18 AM | Mindanao Grid-04/11/2024 09:38: WMPC DG01 online at 0931H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/11/2024 9:10:36 AM | Mindanao Grid-04/11/2024 09:15: WMPC DG04 online at 0858H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/11/2024 7:55:18 AM | [NSO Update] Visayas Grid-04/11/2024 07:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0754H with power going to Visayas. [WEBSMS] | CVIS
4/11/2024 7:55:12 AM | [NSO Update] Luzon Grid-04/11/2024 07:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0754H with power going to Visayas. [WEBSMS] | CLUZ
4/11/2024 7:47:24 AM | [NSO Update] Visayas Grid-04/11/2024 07:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0744H from forward power direction. [WEBSMS] | CVIS
4/11/2024 7:47:19 AM | [NSO Update] Luzon Grid-04/11/2024 07:47: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0744H from forward power direction. [WEBSMS] | CLUZ
4/11/2024 7:41:11 AM | Mindanao Grid-04/11/2024 07:46: AGUS 4 HEP Unit 3 online at 0733H from OMC outage. (Unplanned Outage) [WEBSMS] | CMIN
4/11/2024 5:45:49 AM | [NSO Update] Mindanao Grid-04/11/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3234MW, PK=2411MW, RR=88MW, NetOpMargin: AM=734, PM=657, EVE=757 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @31MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
4/11/2024 5:44:44 AM | [NSO Update] Visayas Grid-04/11/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2642MW, PK=2358MW, RR=94MW, NetOpMargin: AM=190, PM=263, EVE=216 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @72MW, LEYTE A @342MW, PGPP1 @76MW [WEBSMS] | CVIS
4/11/2024 5:42:44 AM | [NSO Update] Luzon Grid-04/11/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14627MW, PK=11635MW, RR=467MW, NetOpMargin: AM=2526, PM=1600, EVE=1578 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @190MW, ILIJAN A @300MW [WEBSMS] | CLUZ
4/11/2024 5:38:36 AM | Mindanao Grid-04/11/2024 05:43: Jasaan-Nasipit 138kV Line Energized/Looped at 0535H. (Planned Outage) [WEBSMS] | CMIN
4/11/2024 4:36:57 AM | Mindanao Grid-04/11/2024 04:42: Jasaan SS 138kV BUS #2 energized at 0433H. (Unplanned Outage) [WEBSMS] | CMIN
4/11/2024 4:28:04 AM | Mindanao Grid-04/11/2024 04:33: Jasaan SS 138kV BUS #2 tripped at 0411H. (Unplanned Outage) [WEBSMS] | CMIN
4/11/2024 4:19:03 AM | [NSO Update] Luzon Grid-04/11/2024 04:19: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/11/2024 4:17:56 AM | [NSO Update] Mindanao Grid-04/11/2024 04:23: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
4/11/2024 4:17:45 AM | [NSO Update] Visayas Grid-04/11/2024 04:17: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
4/11/2024 4:03:38 AM | Mindanao Grid-04/11/2024 04:08: Jasaan-Nasipit 138kV Line de-energized at 0401H. (Planned Outage) [WEBSMS] | CMIN
4/11/2024 2:54:40 AM | Luzon Grid-04/11/2024 02:54: Binan - Southwoods 115kV Line restored at 0253H (Planned Outage) [WEBSMS] | CLUZ
4/11/2024 2:51:54 AM | Luzon Grid-04/11/2024 02:51: Binan 300MVA T03 restored at 0251H (Planned Outage). [WEBSMS] | CLUZ
4/11/2024 12:14:19 AM | Luzon Grid-04/11/2024 00:14: Binan 300MVA T03 de-energized at 0013H (Planned Outage) [WEBSMS] | CLUZ
4/11/2024 12:11:17 AM | Luzon Grid-04/11/2024 00:11: Binan- Southwoods 115kV L de-energized at 0010H (Planned Outage) [WEBSMS] | CLUZ
4/10/2024 11:47:58 PM | Luzon Grid-04/10/2024 23:48: Binan 300MVA T02 energized at 2347H (Planned Outage) [WEBSMS] | CLUZ
4/10/2024 11:43:28 PM | Luzon Grid-04/10/2024 23:43: Binan 230kV Bus 2 energized at 2343H (Planned Outage) [WEBSMS] | CLUZ
4/10/2024 11:25:21 PM | Visayas Grid-04/10/2024 23:25: Compostela SS 150 MVA 230/138 kV TR1 energized at 2324H (Planned Outage) [WEBSMS] | CVIS
4/10/2024 8:27:41 PM | Luzon Grid-04/10/2024 20:27: Binan 230kV Bus 2 de-energized at 2026H (Planned Outage) [WEBSMS] | CLUZ
4/10/2024 8:24:16 PM | Luzon Grid-04/10/2024 20:24: Binan 300MVA T02 de-energized at 2023H (Planned Outage) [WEBSMS] | CLUZ
4/10/2024 8:10:28 PM | Luzon Grid-04/10/2024 20:10: Binan 300MVA T01 restored at 2009H (Unplanned Outage) [WEBSMS] | CLUZ
4/10/2024 7:40:29 PM | Mindanao Grid-04/10/2024 19:45: WMPC DG04 shutdown at 1938H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/10/2024 6:55:41 PM | [NSO Update] Visayas Grid-04/10/2024 18:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1854H with power going to Luzon [WEBSMS] | CVIS
4/10/2024 6:55:22 PM | [NSO Update] Luzon Grid-04/10/2024 18:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1854H with power going to Luzon [WEBSMS] | CLUZ
4/10/2024 6:48:06 PM | [NSO Update] Luzon Grid-04/10/2024 18:48: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1844H from reverse power direction [WEBSMS] | CLUZ
4/10/2024 6:46:35 PM | [NSO Update] Visayas Grid-04/10/2024 18:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1844H from reverse power direction [WEBSMS] | CVIS
4/10/2024 6:09:31 PM | [NSO Update] Luzon Grid-04/10/2024 18:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1807H with power going to Visayas [WEBSMS] | CLUZ
4/10/2024 6:09:05 PM | [NSO Update] Visayas Grid-04/10/2024 18:09: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1807H with power going to Visayas [WEBSMS] | CVIS
4/10/2024 6:00:15 PM | [NSO Update] Visayas Grid-04/10/2024 18:00: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1757H from forward power direction [WEBSMS] | CVIS
4/10/2024 5:59:30 PM | [NSO Update] Luzon Grid-04/10/2024 17:59: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1757H from forward power direction [WEBSMS] | CLUZ
4/10/2024 5:42:04 PM | [NSO Update] Mindanao Grid-04/10/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3180MW, PK=2328MW, RR=86MW, NetOpMargin: EVE=765 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @31MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @84MW [WEBSMS] | CMIN
4/10/2024 5:41:05 PM | [NSO Update] Visayas Grid-04/10/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2556MW, PK=2156MW, RR=91MW, NetOpMargin: EVE=309 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80MW, LEYTE A @316MW, PGPP1 @76MW [WEBSMS] | CVIS
4/10/2024 5:40:02 PM | [NSO Update] Luzon Grid-04/10/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13447MW, PK=10728MW, RR=427MW, NetOpMargin: EVE=2292 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC1 @190MW, ILIJAN A @300MW [WEBSMS] | CLUZ
4/10/2024 5:16:30 PM | Mindanao Grid-04/10/2024 17:21: WMPC DG01 shutdown at 1713H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/10/2024 3:15:42 PM | Mindanao Grid-04/10/2024 15:20: Lugait SS 75MVA TR#2 energized at 1513H. (Planned Outage) [WEBSMS] | CMIN
4/10/2024 2:39:05 PM | Visayas Grid-04/10/2024 14:39: Daanbantayan SS to Leyte subgrid and Bohol subgrid no monitoring on Scada data non-updating at 1359H, due to loss of 48Volts DC supply to Telecom equipment at Daan-bantayan SS restored at 1436H. [WEBSMS] | CVIS
4/10/2024 1:42:30 PM | Mindanao Grid-04/10/2024 13:47: WMPC DG01 online at 1339H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/10/2024 12:38:35 PM | [NSO Update] Mindanao Grid-04/10/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3179MW, PK=2243MW, RR=83MW, NetOpMargin: PM=852, EVE=708 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @31MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @84MW [WEBSMS] | CMIN
4/10/2024 12:37:46 PM | [NSO Update] Visayas Grid-04/10/2024 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2887MW, PK=2170MW, RR=92MW, NetOpMargin: PM=626, EVE=191 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 320MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/10/2024 12:36:43 PM | [NSO Update] Luzon Grid-04/10/2024 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14625MW, PK=11020MW, RR=448MW, NetOpMargin: PM=3157, EVE=2516 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 190MW, Ilijan A @ 300MW [WEBSMS] | CLUZ
4/10/2024 11:02:12 AM | Mindanao Grid-04/10/2024 11:07: WMPC DG04 online at 1059H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/10/2024 9:54:30 AM | Mindanao Grid-04/10/2024 09:59: AGUS2 HEP Unit 1 emergency shutdown at 0945H due to generator oil leak. (Unplanned Outage) [WEBSMS] | CMIN
4/10/2024 9:18:22 AM | Luzon Grid-04/10/2024 09:18: Ilijan A ST-1 online at 0917H. (Unplanned Outage) [WEBSMS] | CLUZ
4/10/2024 9:18:07 AM | Mindanao Grid-04/10/2024 09:23: TSI unit 2 online at 0910H. (Unplanned Outage) [WEBSMS] | CMIN
4/10/2024 8:36:50 AM | Luzon Grid-04/10/2024 08:36: Binan 300MVA T01 de-energized at 0836H. (Unplanned Outage) [WEBSMS] | CLUZ
4/10/2024 7:53:10 AM | Luzon Grid-04/10/2024 07:53: Ilijan A GT1-2 online at 0752H. (Unplanned Outage) [WEBSMS] | CLUZ
4/10/2024 6:19:40 AM | Mindanao Grid-04/10/2024 06:24: Lugait SS 75MVA TR#2 shutdown at 0610H. (Planned Outage) [WEBSMS] | CMIN
4/10/2024 6:18:33 AM | Visayas Grid-04/10/2024 06:18: Compostela SS 150 MVA 230/138 kV TR1 de-energized at 0614H (Planned Outage) [WEBSMS] | CVIS
4/10/2024 5:46:46 AM | [NSO Update] Mindanao Grid-04/10/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3263MW, PK=2092MW, RR=82MW, NetOpMargin: AM=1089, PM=926, EVE=827 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @84MW [WEBSMS] | CMIN
4/10/2024 5:45:49 AM | [NSO Update] Visayas Grid-04/10/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2541MW, PK=1994MW, RR=90MW, NetOpMargin: AM=458, PM=536, EVE=170 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @270MW, PGPP1 @76MW [WEBSMS] | CVIS
4/10/2024 5:44:37 AM | [NSO Update] Luzon Grid-04/10/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14348MW, PK=10081MW, RR=423MW, NetOpMargin: AM=3845, PM=2901, EVE=1790 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @190MW [WEBSMS] | CLUZ
4/10/2024 5:44:34 AM | Visayas Grid-04/10/2024 05:44: Cebu-Mandaue 138kV Line 2 energized at 0542H (Unplanned Outage) [WEBSMS] | CVIS
4/10/2024 5:17:55 AM | Luzon Grid-04/10/2024 05:18: For info: Ilijan GT2-2 online at 0259H from Unplanned Outage. [WEBSMS] | CLUZ
4/10/2024 5:00:28 AM | [NSO Update] Mindanao Grid-04/10/2024 05:05: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
4/10/2024 5:00:14 AM | [NSO Update] Visayas Grid-04/10/2024 05:00: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
4/10/2024 5:00:00 AM | [NSO Update] Luzon Grid-04/10/2024 05:00: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/10/2024 1:00:05 AM | Luzon Grid-04/10/2024 01:00: Ilijan ST2 online at 0058H (Unplanned Outage) [WEBSMS] | CLUZ
4/9/2024 11:44:51 PM | Luzon Grid-04/09/2024 23:45: Ilijan GT2-1 online at 2344H (Unplanned Outage) [WEBSMS] | CLUZ
4/9/2024 11:25:23 PM | Visayas Grid-04/09/2024 23:25: Cebu SS 300 MVA TR3 energized at 2323H (Planned Outage) [WEBSMS] | CVIS
4/9/2024 11:24:55 PM | Mindanao Grid-04/09/2024 23:30: ASIGA (ASG) HEP online at 2251H from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
4/9/2024 10:49:03 PM | Mindanao Grid-04/09/2024 22:54: WMPC DG05 shutdown at 2244H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/9/2024 10:45:28 PM | Mindanao Grid-04/09/2024 22:50: ASIGA (ASG) HEP with 2.79MW load tripped at 2244H. Indication: Restricted Earth Fault (Unplanned Outage) [WEBSMS] | CMIN
4/9/2024 10:39:52 PM | Mindanao Grid-04/09/2024 22:45: Jasaan - Butuan 138kV Line tripped and auto-reclosed at 2228H. (Unplanned Outage) [WEBSMS] | CMIN
4/9/2024 10:25:57 PM | Visayas Grid-04/09/2024 22:26: Cebu-Mandaue 138kV Line 2 de-energized at 2223H (Unplanned Outage) [WEBSMS] | CVIS
4/9/2024 8:07:12 PM | Mindanao Grid-04/09/2024 20:12: STEAG Unit 2 online at 1959H from F.O (Unplanned Outage). [WEBSMS] | CMIN
4/9/2024 8:05:00 PM | [NSO Update] Visayas Grid-04/09/2024 20:05: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2000H with power going to Luzon [WEBSMS] | CVIS
4/9/2024 8:04:43 PM | [NSO Update] Luzon Grid-04/09/2024 20:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2000H with power going to Luzon [WEBSMS] | CLUZ
4/9/2024 7:52:46 PM | [NSO Update] Luzon Grid-04/09/2024 19:53: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1929H from reverse power direction [WEBSMS] | CLUZ
4/9/2024 7:52:26 PM | [NSO Update] Visayas Grid-04/09/2024 19:52: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1929H from reverse power direction [WEBSMS] | CVIS
4/9/2024 7:47:55 PM | Mindanao Grid-04/09/2024 19:53: WMPC DG08 shutdown at 1944H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/9/2024 7:01:09 PM | Mindanao Grid-04/09/2024 19:06: WMPC DG08 online at 1805H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/9/2024 6:59:14 PM | Mindanao Grid-04/09/2024 19:04: WMPC DG08 shutdown at 1714H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/9/2024 6:34:18 PM | [NSO Update] Luzon Grid-04/09/2024 18:34: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1828H with power going to Visayas [WEBSMS] | CLUZ
4/9/2024 6:33:38 PM | [NSO Update] Visayas Grid-04/09/2024 18:33: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1828H with power going to Visayas [WEBSMS] | CVIS
4/9/2024 6:32:50 PM | [NSO Update] Luzon Grid-04/09/2024 18:33: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1817H from forward power direction [WEBSMS] | CLUZ
4/9/2024 6:32:22 PM | [NSO Update] Visayas Grid-04/09/2024 18:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1817H from forward power direction [WEBSMS] | CVIS
4/9/2024 6:03:48 PM | Luzon Grid-04/09/2024 18:04: La Trinidad-Bauang 230kV Line 1 restored at 1803H (Planned Outage) [WEBSMS] | CLUZ
4/9/2024 5:45:05 PM | [NSO Update] Mindanao Grid-04/09/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2975MW, PK=2381MW, RR=87MW, NetOpMargin: EVE=507 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @84MW [WEBSMS] | CMIN
4/9/2024 5:43:55 PM | [NSO Update] Visayas Grid-04/09/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2333MW, PK=2074MW, RR=89MW, NetOpMargin: EVE=169 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80MW, LEYTE A @264MW, PGPP1 @76MW [WEBSMS] | CVIS
4/9/2024 5:42:58 PM | [NSO Update] Luzon Grid-04/09/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12566MW, PK=10764MW, RR=407MW, NetOpMargin: EVE=1395 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @210MW [WEBSMS] | CLUZ
4/9/2024 5:07:54 PM | Luzon Grid-04/09/2024 17:08: San Gabriel online at 1704H (Unplanned Outage) [WEBSMS] | CLUZ
4/9/2024 5:07:04 PM | Luzon Grid-04/09/2024 17:07: San Gabriel online at 1704H (Unplanned Outage) [WEBSMS] | CLUZ
4/9/2024 4:15:56 PM | Visayas Grid-04/09/2024 16:16: Compostela 138 KV bus 1 energized at 1600H (Planned Outage) [WEBSMS] | CVIS
4/9/2024 3:59:55 PM | Luzon Grid-04/09/2024 16:00: Mexico 230kV Bus 1 restored at 1559H (Planned Outage) [WEBSMS] | CLUZ
4/9/2024 1:41:20 PM | Visayas Grid-04/09/2024 13:41: NNBP re-online at 1335H (Unplanned Outage) [WEBSMS] | CVIS
4/9/2024 1:22:11 PM | Mindanao Grid-04/09/2024 13:27: WMPC DG08 online . RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/9/2024 12:55:05 PM | [NSO Update] Mindanao Grid-04/09/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3139MW, PK=2240MW, RR=83MW, NetOpMargin: PM=816, EVE=647 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @84MW [WEBSMS] | CMIN
4/9/2024 12:48:07 PM | [NSO Update] Visayas Grid-04/09/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2639MW, PK=2058MW, RR=93MW, NetOpMargin: PM=488, EVE=171 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @79.5MW, LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
4/9/2024 12:37:56 PM | [NSO Update] Luzon Grid-04/09/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13417MW, PK=10573MW, RR=393MW, NetOpMargin: PM=2451, EVE=1466 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 1 @200MW [WEBSMS] | CLUZ
4/9/2024 12:08:01 PM | Visayas Grid-04/09/2024 12:08: NNBP tripped at 1155H (Unplanned Outage) [WEBSMS] | CVIS
4/9/2024 10:50:08 AM | Mindanao Grid-04/09/2024 10:55: WMPC DG05 online at 1045H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/9/2024 10:44:19 AM | Luzon Grid-04/09/2024 10:44: San Jose-Camarin 115kV Line restored at 1044H (Planned Outage) [WEBSMS] | CLUZ
4/9/2024 10:33:54 AM | Visayas Grid-04/09/2024 10:34: Nasulo re-online at 1019H (Unplanned Outage) [WEBSMS] | CVIS
4/9/2024 8:22:57 AM | Visayas Grid-04/09/2024 08:23: Compostela 138 KV bus 1 de-energized at 0818H (Planned Outage) [WEBSMS] | CVIS
4/9/2024 7:26:25 AM | Visayas Grid-04/09/2024 07:26: Cebu SS 300 MVA TR3 de-energized at 0713H (Planned Outage) [WEBSMS] | CVIS
4/9/2024 7:17:56 AM | Luzon Grid-04/09/2024 07:18: San Jose-Camarin 115kV Line de-energized at 0717H (Planned Outage) [WEBSMS] | CLUZ
4/9/2024 7:06:18 AM | Luzon Grid-04/09/2024 07:06: San Jose 83MVA T01 (CO) restored at 0704H (Planned Outage) [WEBSMS] | CLUZ
4/9/2024 6:34:03 AM | Luzon Grid-04/09/2024 06:34: La Trinidad-Bauang 230kV Line 1 de-energized at 0632H (Planned Outage) [WEBSMS] | CLUZ
4/9/2024 6:32:01 AM | Luzon Grid-04/09/2024 06:32: San Gabriel shutdown at 0630H (Unplanned Outage) [WEBSMS] | CLUZ
4/9/2024 6:02:57 AM | Luzon Grid-04/09/2024 06:03: Mexico 230kV Bus 1 de-energized at 0602H (Planned Outage) [WEBSMS] | CLUZ
4/9/2024 5:37:47 AM | [NSO Update] Mindanao Grid-04/09/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3150MW, PK=2036MW, RR=77MW, NetOpMargin: AM=1037, PM=932, EVE=871 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @84MW [WEBSMS] | CMIN
4/9/2024 5:36:19 AM | [NSO Update] Visayas Grid-04/09/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2558MW, PK=2083MW, RR=89MW, NetOpMargin: AM=386, PM=554, EVE=214 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @79.5MW, LEYTE A @323MW, PGPP1 @76MW [WEBSMS] | CVIS
4/9/2024 5:34:10 AM | [NSO Update] Luzon Grid-04/09/2024 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13870MW, PK=10136MW, RR=373MW, NetOpMargin: AM=3361, PM=3058, EVE=2033 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC1 @190MW [WEBSMS] | CLUZ
4/9/2024 5:07:35 AM | Mindanao Grid-04/09/2024 05:13: Minergy Coal Unit 2 on reserve shutdown at 0000H due to low load demand. [WEBSMS] | CMIN
4/9/2024 4:02:32 AM | [NSO Update] Luzon Grid-04/09/2024 04:02: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/9/2024 4:01:39 AM | [NSO Update] Mindanao Grid-04/09/2024 04:07: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
4/9/2024 4:01:28 AM | [NSO Update] Visayas Grid-04/09/2024 04:01: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
4/9/2024 3:44:13 AM | Mindanao Grid-04/09/2024 03:49: LIBERTAD POWER online at 0305H (Unplanned Outage) [WEBSMS] | CMIN
4/9/2024 3:43:34 AM | Mindanao Grid-04/09/2024 03:49: LIBERTAD POWER with 6MW load isolated at 0258H due to line-to-ground fault of ZAMSURECO 1 feeder. (Unplanned Outage) [WEBSMS] | CMIN
4/9/2024 2:17:29 AM | Luzon Grid-04/09/2024 02:17: Las Pinas 300MVA T01 loop at 0214H (Planned Outage) [WEBSMS] | CLUZ
4/9/2024 1:20:41 AM | Luzon Grid-04/09/2024 01:20: San Jose 83MVA T01 (CO) de-energized at 0119H (Planned Outage) [WEBSMS] | CLUZ
4/8/2024 11:39:45 PM | Luzon Grid-04/08/2024 23:39: Las Pinas 300MVA TO1 unloop at 2332H (Planned Outage) [WEBSMS] | CLUZ
4/8/2024 9:24:43 PM | Mindanao Grid-04/08/2024 21:30: WMPC DG05 shutdown at 2123H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/8/2024 7:42:11 PM | Luzon Grid-04/08/2024 19:42: Ilijan Block B with 377MW load tripped at 1934H. Lowest frequency is 59.126Hz. No ALD (Unplanned Outage) [WEBSMS] | CLUZ
4/8/2024 6:06:43 PM | Mindanao Grid-04/08/2024 18:12: TALOMO 2 Unit 2 online at 1158H (Planned Outage) [WEBSMS] | CMIN
4/8/2024 6:04:27 PM | Mindanao Grid-04/08/2024 18:09: TALOMO 2 Unit 1 & Unit 3 online at 1205H (Planned Outage) [WEBSMS] | CMIN
4/8/2024 5:48:39 PM | Luzon Grid-04/08/2024 17:48: For info: Commissioning of Lumban-Lumban BESS 69kV Line completed at 1747H [WEBSMS] | CLUZ
4/8/2024 5:45:40 PM | [NSO Update] Mindanao Grid-04/08/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2947MW, PK=2335MW, RR=88MW, NetOpMargin: EVE=524 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @37MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @31MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
4/8/2024 5:44:29 PM | [NSO Update] Visayas Grid-04/08/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2428MW, PK=2145MW, RR=54MW, NetOpMargin: EVE=229 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @72MW, LEYTE A @342MW, PGPP1 @76MW [WEBSMS] | CVIS
4/8/2024 5:43:33 PM | Luzon Grid-04/08/2024 17:43: Lumban-Lumban BESS 69kV Line energized at 1741H. On going commissioning test [WEBSMS] | CLUZ
4/8/2024 5:42:32 PM | [NSO Update] Luzon Grid-04/08/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12898MW, PK=11163MW, RR=456MW, NetOpMargin: EVE=1279 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC1 @190MW, ILIJAN B @ 300MW [WEBSMS] | CLUZ
4/8/2024 5:38:06 PM | Luzon Grid-04/08/2024 17:38: Ilijan GT2-1 online at 1736H (Unplanned Outage) [WEBSMS] | CLUZ
4/8/2024 5:18:31 PM | Mindanao Grid-04/08/2024 17:23: WMPC DG01 shutdown at 1714H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/8/2024 5:17:44 PM | Mindanao Grid-04/08/2024 17:23: WMPC DG01 online at 1600H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/8/2024 5:16:44 PM | Mindanao Grid-04/08/2024 17:22: WMPC DG01 end of RPS at 1435H (converted to EN=1.9MW from RPS) [WEBSMS] | CMIN
4/8/2024 4:37:07 PM | Luzon Grid-04/08/2024 16:37: Correction: Ilijan ST2 online at 1625H (Unplanned Outage) [WEBSMS] | CLUZ
4/8/2024 4:28:03 PM | Luzon Grid-04/08/2024 16:28: Ilijan ST2 online at 1625H (Planned Outage) [WEBSMS] | CLUZ
4/8/2024 3:34:46 PM | Mindanao Grid-04/08/2024 15:40: LIBERTAD POWER online at 1521H (Unplanned Outage) [WEBSMS] | CMIN
4/8/2024 3:30:55 PM | Mindanao Grid-04/08/2024 15:36: LIBERTAD POWER with 6MW load tripped at 1515H. Cause: Isolated due to tripping of customer-owned 13.2kV feeder (line-to-ground fault) (Unplanned Outage) [WEBSMS] | CMIN
4/8/2024 3:30:19 PM | Luzon Grid-04/08/2024 15:30: Ilijan GT2-2 online at 1526H (Unplanned Outage) [WEBSMS] | CLUZ
4/8/2024 1:49:41 PM | Luzon Grid-04/08/2024 13:49: San Gabriel online at 1338H (Unplanned Outage) [WEBSMS] | CLUZ
4/8/2024 1:03:14 PM | [NSO Update] Mindanao Grid-04/08/2024 13:08: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2998MW, PK=2465MW, RR=91MW, NetOpMargin: PM=442, EVE=515 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @37MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @31MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
4/8/2024 1:00:46 PM | [NSO Update] Visayas Grid-04/08/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2870MW, PK=2322MW, RR=57MW, NetOpMargin: PM=491, EVE=391 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @70MW, LEYTE A @342MW, PGPP1 @76MW [WEBSMS] | CVIS
4/8/2024 12:59:21 PM | [NSO Update] Luzon Grid-04/08/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13962MW, PK=12123MW, RR=486MW, NetOpMargin: PM=1352, EVE=1017 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @210MW [WEBSMS] | CLUZ
4/8/2024 12:58:54 PM | Mindanao Grid-04/08/2024 13:04: MANOLO FORTICH 1 Unit 1 online at 1255H (Unplanned Outage) [WEBSMS] | CMIN
4/8/2024 12:31:29 PM | Mindanao Grid-04/08/2024 12:36: WMPC DG01 online at 1229H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/8/2024 11:21:29 AM | Mindanao Grid-04/08/2024 11:26: MANOLO FORTICH 1 Unit 1 with 0.95MW load tripped at 1051H. Indication: DECS 250 communication fail (Unplanned Outage) [WEBSMS] | CMIN
4/8/2024 10:09:17 AM | Mindanao Grid-04/08/2024 10:14: PULANGI 4 HEP Unit 1 online at 0953H (as replacement for Pulangi 4 Unit 2) (Unplanned Outage) [WEBSMS] | CMIN
4/8/2024 10:06:23 AM | Luzon Grid-04/08/2024 10:06: Affected ALD feeders of MERALCO and NGCP were restored at 0959H & 1000H. [WEBSMS] | CLUZ
4/8/2024 10:06:18 AM | Mindanao Grid-04/08/2024 10:11: PULANGI 4 HEP Unit 2 shutdown at 1001H due to low forebay elevation (FBE) / insufficient water supply. (Unplanned Outage) [WEBSMS] | CMIN
4/8/2024 10:03:04 AM | Luzon Grid-04/08/2024 10:03: ALD occurred at MERALCO at NGCP feeders due to the tripping of Ilijan Block A (158MW) & B (464MW) at 0953H. Lowest system frequency is 58.955Hz. [WEBSMS] | CLUZ
4/8/2024 9:33:25 AM | Mindanao Grid-04/08/2024 09:38: WMPC DG08 online at 0930H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/8/2024 8:52:22 AM | Mindanao Grid-04/08/2024 08:57: WMPC DG05 at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/8/2024 7:57:17 AM | Mindanao Grid-04/08/2024 08:02: WMPC DG10 declared not available at 0710H. Reason: Charger A-bank heavy air leak (Unplanned Outage). [WEBSMS] | CMIN
4/8/2024 5:44:45 AM | [NSO Update] Mindanao Grid-04/08/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3037MW, PK=2338MW, RR=88MW, NetOpMargin: AM=611, PM=488, EVE=590 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @37MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @84MW [WEBSMS] | CMIN
4/8/2024 5:42:44 AM | [NSO Update] Visayas Grid-04/08/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2662MW, PK=2178MW, RR=54MW, NetOpMargin: AM=431, PM=261, EVE=170 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @63MW, LEYTE A @348MW, PGPP1 @76MW [WEBSMS] | CVIS
4/8/2024 5:40:18 AM | [NSO Update] Luzon Grid-04/08/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14335MW, PK=11392MW, RR=458MW, NetOpMargin: AM=2485, PM=1569, EVE=1572 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @190MW, ILIJAN A @300MW [WEBSMS] | CLUZ
4/8/2024 4:29:47 AM | [NSO Update] Mindanao Grid-04/08/2024 04:35: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
4/8/2024 4:28:14 AM | [NSO Update] Visayas Grid-04/08/2024 04:28: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
4/8/2024 4:27:50 AM | [NSO Update] Luzon Grid-04/08/2024 04:28: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/7/2024 9:26:29 PM | Luzon Grid-04/07/2024 21:26: System Advisory: ALD occurred at MERALCO feeders at 2119H due to tripping of San Gabriel at 409MW. Lowest Frequency=59.032Hz. Affected ALD feeders of MERALCO restored at 2123H. [WEBSMS] | CLUZ
4/7/2024 7:44:50 PM | Mindanao Grid-04/07/2024 19:50: WMPC DG10 shutdown at 1943H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/7/2024 7:31:01 PM | Luzon Grid-04/07/2024 19:31: Santiago-Magat HEPP 230kV Line 1 energized at 1929H @Santiago side (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 7:28:58 PM | Mindanao Grid-04/07/2024 19:34: TSI unit 2 emergency shutdown at 1921H due to boiler nozzle problem. (Unplanned Outage) [WEBSMS] | CMIN
4/7/2024 5:53:08 PM | [NSO Update] Mindanao Grid-04/07/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3157MW, PK=2235MW, RR=80MW, NetOpMargin: EVE=842 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @50MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @114MW [WEBSMS] | CMIN
4/7/2024 5:47:26 PM | [NSO Update] Visayas Grid-04/07/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2550MW, PK=2132MW, RR=60MW, NetOpMargin: EVE=358 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @65MW, LEYTE A @346MW, PGPP1 @76MW [WEBSMS] | CVIS
4/7/2024 5:39:09 PM | [NSO Update] Luzon Grid-04/07/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13616MW, PK=10566MW, RR=287MW, NetOpMargin: EVE=2763 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @170MW, ILIJAN A @300MW [WEBSMS] | CLUZ
4/7/2024 5:12:09 PM | Luzon Grid-04/07/2024 17:12: Dasmarinas 300MVA T03 restored at 1712H (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 4:56:37 PM | Luzon Grid-04/07/2024 16:56: Mexico-Concepcion 230kV Line 2 restored at 1656H (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 4:39:24 PM | Luzon Grid-04/07/2024 16:39: Bay-Ormat 69kV Line restored at 1637H (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 4:21:38 PM | Luzon Grid-04/07/2024 16:21: Correction: Calaca-Sta Rosa 230kV Line restored at 1559H (Unplanned Outage) [WEBSMS] | CLUZ
4/7/2024 3:59:59 PM | Luzon Grid-04/07/2024 16:00: Calaca-Sta Rosa 230kV Line tripped restored at 1559H (Unplanned Outage) [WEBSMS] | CLUZ
4/7/2024 3:58:37 PM | Luzon Grid-04/07/2024 15:58: Calaca-Sta Rosa 230kV Line tripped at 1555H. Reclosed at Sta Rosa side (Unplanned Outage) [WEBSMS] | CLUZ
4/7/2024 3:45:33 PM | Luzon Grid-04/07/2024 15:45: Duhat-Hermosa 230kV Line restored at 1545H (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 3:25:25 PM | Luzon Grid-04/07/2024 15:25: Lal-lo-Magapit BESS 69kV Line restored at 1525H (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 3:24:11 PM | Luzon Grid-04/07/2024 15:24: San Gabriel online at 1520H (Unplanned Outage) [WEBSMS] | CLUZ
4/7/2024 3:21:09 PM | Luzon Grid-04/07/2024 15:21: Lal-lo-Cagayan North Solar 69kV Line 1 & 2 restored at 1520H (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 2:52:10 PM | Luzon Grid-04/07/2024 14:52: Nagsaag SS PCB 9Z-01CB24NGS restored at 1448H (Planned Outage). [WEBSMS] | CLUZ
4/7/2024 1:18:46 PM | Mindanao Grid-04/07/2024 13:24: WMPC DG10 online at 1316H . RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/7/2024 12:47:28 PM | [NSO Update] Mindanao Grid-04/07/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3207MW, PK=2043MW, RR=78MW, NetOpMargin: PM=1086, EVE=840 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @50MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @114MW [WEBSMS] | CMIN
4/7/2024 12:45:51 PM | [NSO Update] Visayas Grid-04/07/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2922MW, PK=1971MW, RR=60MW, NetOpMargin: PM=891, EVE=349 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @65MW, LEYTE A @346MW, PGPP1 @76MW [WEBSMS] | CVIS
4/7/2024 12:44:20 PM | [NSO Update] Luzon Grid-04/07/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14774MW, PK=9972MW, RR=311MW, NetOpMargin: PM=4491, EVE=2826 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @200MW, ILIJAN A @300MW [WEBSMS] | CLUZ
4/7/2024 8:12:51 AM | Luzon Grid-04/07/2024 08:13: Dasmarinas SS PCB 9Z-03CB08DAS closed at 0812H (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 7:08:54 AM | Luzon Grid-04/07/2024 07:09: Santiago-Magat HEPP 230kV Line 1 de-energized at 0707H (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 7:05:04 AM | Luzon Grid-04/07/2024 07:05: Nagsaag SS PCB 9Z-01CB24NGS opened at 0702H (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 6:46:53 AM | Luzon Grid-04/07/2024 06:47: Lal-lo-Magapit BESS 69kV Line de-energized at 0644H (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 6:43:03 AM | Luzon Grid-04/07/2024 06:43: Bay-Ormat 69kV de-energized at 0638H (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 6:36:03 AM | Luzon Grid-04/07/2024 06:36: Mexico-Concepcion 230kV Line 2 de-energized at 0635H (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 6:22:14 AM | Luzon Grid-04/07/2024 06:22: Lal-lo-Cagayan North Solar 69kV Line 1 & 2 de-energized at 0616H and 0617H, respectively. (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 5:56:02 AM | [NSO Update] Mindanao Grid-04/07/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3228MW, PK=1927MW, RR=77MW, NetOpMargin: AM=1224, PM=1132, EVE=887 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @50MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @114MW [WEBSMS] | CMIN
4/7/2024 5:54:55 AM | [NSO Update] Visayas Grid-04/07/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2989MW, PK=1961MW, RR=60MW, NetOpMargin: AM=968, PM=785, EVE=359 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 65MW, Leyte A @ 346MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/7/2024 5:53:05 AM | [NSO Update] Luzon Grid-04/07/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14939MW, PK=9503MW, RR=296MW, NetOpMargin: AM=5140, PM=4288, EVE=3087 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 175MW, Ilijan A @ 300MW [WEBSMS] | CLUZ
4/7/2024 5:49:25 AM | Mindanao Grid-04/07/2024 05:54: (Correction) TALOMO 3 Unit 1 online at 0541H (Unplanned Outage) [WEBSMS] | CMIN
4/7/2024 5:48:44 AM | Mindanao Grid-04/07/2024 05:54: (Correction) TALOMO 3 Unit 2 online at 0537H (Unplanned Outage) [WEBSMS] | CMIN
4/7/2024 5:46:59 AM | Mindanao Grid-04/07/2024 05:52: TALOMO 3 Unit 1 online at 0537H (Unplanned Outage) [WEBSMS] | CMIN
4/7/2024 5:45:44 AM | Luzon Grid-04/07/2024 05:45: Dasmarinas SS 300MVA T03 de-energized at 0545H. (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 5:37:05 AM | Visayas Grid-04/07/2024 05:37: Cebu-Mandaue 138 KV Line 2 energized at 0537H (Planned Outage) [WEBSMS] | CVIS
4/7/2024 5:08:18 AM | Luzon Grid-04/07/2024 05:08: Duhat-Hermosa 230kV Line de-energized at 0508H. (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 5:03:16 AM | Visayas Grid-04/07/2024 05:03: Cebu-Mandaue 138 KV Line 2 de-energized at 0231H (Planned Outage) [WEBSMS] | CVIS
4/7/2024 4:37:02 AM | [NSO Update] Luzon Grid-04/07/2024 04:37: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CLUZ
4/7/2024 4:36:43 AM | [NSO Update] Mindanao Grid-04/07/2024 04:42: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CMIN
4/7/2024 4:36:16 AM | [NSO Update] Visayas Grid-04/07/2024 04:36: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CVIS
4/7/2024 4:33:26 AM | Mindanao Grid-04/07/2024 04:38: TALOMO 3 Unit 1 (0.68MW) and Unit 2 (0.6MW) isolated at 0416H due to loss of feedback power brought by tripping of DLPCs 13.8kV Tugbok Feeder (Unplanned Outage) [WEBSMS] | CMIN
4/7/2024 1:16:07 AM | Visayas Grid-04/07/2024 01:16: Cebu-Mandaue 138 KV Line 1 energized at 0116H (Planned Outage) [WEBSMS] | CVIS
4/7/2024 12:28:37 AM | Luzon Grid-04/07/2024 00:28: Nagsaag - San Manuel 230kV Tie Line 2 restored at 0020H (Planned Outage) [WEBSMS] | CLUZ
4/7/2024 12:26:23 AM | Luzon Grid-04/07/2024 00:26: San Manuel 230kV Bus 1 energized at 0017H (Planned Outage) [WEBSMS] | CLUZ
4/6/2024 10:30:18 PM | Visayas Grid-04/06/2024 22:30: EAUC first unit cut in at 2202H in preparation of de-energization of Cebu-Mandaue Line 1. [WEBSMS] | CVIS
4/6/2024 10:26:42 PM | Visayas Grid-04/06/2024 22:26: Cebu-Mandaue 138 KV Line 1 de-energized at 2226H (Planned Outage) [WEBSMS] | CVIS
4/6/2024 9:34:29 PM | Mindanao Grid-04/06/2024 21:39: Bislig - Nabunturan 13kV Line energized at 2127H. (Planned Outage) [WEBSMS] | CMIN
4/6/2024 7:58:07 PM | Mindanao Grid-04/06/2024 20:03: WMPC DG10 shutdown at 1944H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/6/2024 6:54:21 PM | Luzon Grid-04/06/2024 18:54: San Manuel-UPSI San Manuel BESS 69kV Line (CO) restored at 1853H. (Planned Outage) [WEBSMS] | CLUZ
4/6/2024 5:52:47 PM | [NSO Update] Mindanao Grid-04/06/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3071MW, PK=2239MW, RR=85MW, NetOpMargin: EVE=746 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
4/6/2024 5:51:14 PM | [NSO Update] Visayas Grid-04/06/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2587MW, PK=2275MW, RR=92MW, NetOpMargin: EVE=220 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 39.2MW, Leyte A @ 342MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/6/2024 5:50:00 PM | [NSO Update] Luzon Grid-04/06/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13039MW, PK=10678MW, RR=380MW, NetOpMargin: EVE=1981 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 150MW, Ilijan A @ 300MW [WEBSMS] | CLUZ
4/6/2024 4:16:34 PM | Luzon Grid-04/06/2024 16:16: La Trinidad 230kV Bus 2 restored at 1616H. (Planned Outage) [WEBSMS] | CLUZ
4/6/2024 4:03:11 PM | Mindanao Grid-04/06/2024 16:08: Naga Mindanao SS 50MVA 138/69kV Power Transformer #2 energized at 1600H (Planned Outage) [WEBSMS] | CMIN
4/6/2024 3:46:45 PM | Mindanao Grid-04/06/2024 15:52: Manolo Fortich - Maramag 138kV Line 2 energized at 1544H. (Planned Outage) [WEBSMS] | CMIN
4/6/2024 3:08:21 PM | Mindanao Grid-04/06/2024 15:13: Villanueva SS 300MVA 230/138kV Power Transformer #2 energized at 1505H. (Planned Outage) [WEBSMS] | CMIN
4/6/2024 2:55:55 PM | Mindanao Grid-04/06/2024 15:01: SPC Mati with 3MW load isolated at 1400H due to loss of feedback power brought by tripping of Pintatagan-Mati 69 kV feeder (Unplanned Outage). Note: SPC Mati was advised by DORECO not to reconnect to the grid. [WEBSMS] | CMIN
4/6/2024 2:26:13 PM | Mindanao Grid-04/06/2024 14:31: LAMSAN Biomass online at 1411H (Unplanned Outage) [WEBSMS] | CMIN
4/6/2024 2:23:26 PM | Mindanao Grid-04/06/2024 14:28: LAMSAN Biomass with 15.3MW load (gross) tripped at 1403H. Indication: 50N - non-directional earth fault (Unplanned Outage). [WEBSMS] | CMIN
4/6/2024 1:49:11 PM | Visayas Grid-04/06/2024 13:49: Daanbantayan 230kV BUS 2 energized at 1338H (Planned Outage) [WEBSMS] | CVIS
4/6/2024 1:48:02 PM | Mindanao Grid-04/06/2024 13:53: AGUS 5 HEP Unit 1 online at 1342H (Planned Outage) [WEBSMS] | CMIN
4/6/2024 1:45:41 PM | Mindanao Grid-04/06/2024 13:51: Manolo Fortich - Maramag 138kV Line 2 de-energized at 1334H. (Planned Outage) [WEBSMS] | CMIN
4/6/2024 1:32:28 PM | Mindanao Grid-04/06/2024 13:37: WMPC DG10 online at 1328H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/6/2024 1:09:51 PM | Luzon Grid-04/06/2024 13:09: Nagsaag PCB 9-01CB04NGS restored at 1309H (Planned Outage) [WEBSMS] | CLUZ
4/6/2024 12:53:37 PM | Mindanao Grid-04/06/2024 12:58: Continuation of shutdown of Pulangi 4 HEP Unit 1 at 1202H due to low forebay elevation (FBE) / insufficient water supply (outside management control). Note: Said unit was affected by planned outage of 7BS02MRM. 7BS02MRM was restored at 1202H but Pulangi 4 HEP Unit 1 to remain shutdown due to low FBE (Unplanned Outage). [WEBSMS] | CMIN
4/6/2024 12:42:03 PM | [NSO Update] Mindanao Grid-04/06/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3124MW, PK=2299MW, RR=88MW, NetOpMargin: PM=736, EVE=653 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
4/6/2024 12:41:02 PM | [NSO Update] Visayas Grid-04/06/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2733MW, PK=2257MW, RR=60MW, NetOpMargin: PM=416, EVE=170 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @39.2MW, LEYTE A @332MW, PGPP1 @76MW [WEBSMS] | CVIS
4/6/2024 12:37:56 PM | [NSO Update] Luzon Grid-04/06/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14770MW, PK=11022MW, RR=400MW, NetOpMargin: PM=3348, EVE=2204 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC1 @170MW, ILIJAN A @300MW [WEBSMS] | CLUZ
4/6/2024 12:13:17 PM | Visayas Grid-04/06/2024 12:13: LGPP unit 3 tripped at 1141H (Unplanned Outage) [WEBSMS] | CVIS
4/6/2024 12:07:03 PM | Mindanao Grid-04/06/2024 12:12: Maramag - Kibawe 13kV Line1 energized at 1205H. (Planned Outage) [WEBSMS] | CMIN
4/6/2024 12:04:09 PM | Mindanao Grid-04/06/2024 12:09: Maramag SS 138kV Bus2 energized at 1202H. (Planned Outage) [WEBSMS] | CMIN
4/6/2024 11:11:05 AM | Mindanao Grid-04/06/2024 11:16: Naga Mindanao SS 150MVA 138/69kV Power Transformer No.2 de-energized at 1106H. (Planned Outage) [WEBSMS] | CMIN
4/6/2024 10:45:40 AM | Luzon Grid-04/06/2024 10:45: Balsik 9-02CB24BIK restored at 1041H (Planned Outage) [WEBSMS] | CLUZ
4/6/2024 9:56:37 AM | Mindanao Grid-04/06/2024 10:01: AGUS 2 HEP Unit 1 online at 0953H (Unplanned Outage) [WEBSMS] | CMIN
4/6/2024 9:38:28 AM | Mindanao Grid-04/06/2024 09:43: (Update) AGUS 2 HEP Unit 1 with 25MW load tripped at 0927H. Frequency dipped at 59.64Hz. Cause: governor problem (Unplanned Outage). [WEBSMS] | CMIN
4/6/2024 9:33:27 AM | Mindanao Grid-04/06/2024 09:38: AGUS 2 HEP Unit 1 with 25MW load tripped at 0927H. Frequency dipped at 59.64Hz. Cause: for verification (Unplanned Outage). [WEBSMS] | CMIN
4/6/2024 9:02:27 AM | Luzon Grid-04/06/2024 09:02: Balsik 9-02CB24BIK de-energized at 0901H (Planned Outage) [WEBSMS] | CLUZ
4/6/2024 8:57:18 AM | Mindanao Grid-04/06/2024 09:02: Maramag SS 138kV Bus2 de-energized at 0855H. (Planned Outage) [WEBSMS] | CMIN
4/6/2024 8:50:15 AM | Visayas Grid-04/06/2024 08:50: Daanbantayan 230kV BUS 2 isolated at 0843H (Planned Outage) [WEBSMS] | CVIS
4/6/2024 8:38:37 AM | Luzon Grid-04/06/2024 08:38: Nagsaag-San Manuel 230kV Tie Line 2 de-energized at 0837H (Planned Outage) [WEBSMS] | CLUZ
4/6/2024 8:36:23 AM | Mindanao Grid-04/06/2024 08:41: Maramag - Kibawe 138kV Line 1 de-energized at 0834H (Planned Outage) [WEBSMS] | CMIN
4/6/2024 8:36:04 AM | Luzon Grid-04/06/2024 08:36: San Manuel 230kV Bus 1 de-energized at 0835H (Planned Outage) [WEBSMS] | CLUZ
4/6/2024 8:06:04 AM | Luzon Grid-04/06/2024 08:06: La Trinidad 230kV Bus 2 de-energized at 0805H (Planned Outage) [WEBSMS] | CLUZ
4/6/2024 8:03:50 AM | Mindanao Grid-04/06/2024 08:09: Bislig - Nabunturan 138KV lLine shutdown at 0754H (Planned Outage) [WEBSMS] | CMIN
4/6/2024 7:48:59 AM | Luzon Grid-04/06/2024 07:49: Nagsaag PCB 9-01CB04NGS de-energized at 0746H (Planned Outage) [WEBSMS] | CLUZ
4/6/2024 7:42:26 AM | Mindanao Grid-04/06/2024 07:47: (Correction) PULANGI 4 Unit 2 online at 0712H (Unplanned Outage) [WEBSMS] | CMIN
4/6/2024 7:30:50 AM | Mindanao Grid-04/06/2024 07:36: Pulangi4 U2 online at 0712H. (Planned Outage) [WEBSMS] | CMIN
4/6/2024 7:06:33 AM | Mindanao Grid-04/06/2024 07:11: PULANGI 4 HEP Unit 1 shutdown at 0701H. Affected by planned outage of 7BS02MRM under P&E request, outside management control (Unplanned Outage) [WEBSMS] | CMIN
4/6/2024 6:49:55 AM | Mindanao Grid-04/06/2024 06:55: Villanueva SS 300MVA 230/138kV Power Transformer #2 shutdown at 0644H.(Planned Outage) [WEBSMS] | CMIN
4/6/2024 6:36:11 AM | Luzon Grid-04/06/2024 06:36: San Gabriel shutdown at 0634H (Unplanned Outage) [WEBSMS] | CLUZ
4/6/2024 5:50:34 AM | [NSO Update] Mindanao Grid-04/06/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3137MW, PK=2325MW, RR=82MW, NetOpMargin: AM=729, PM=709, EVE=739 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
4/6/2024 5:46:43 AM | Visayas Grid-04/06/2024 05:46: Cebu-VECO 69 KV L2 energized at 0312H, customers request. [WEBSMS] | CVIS
4/6/2024 5:45:35 AM | [NSO Update] Visayas Grid-04/06/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2773MW, PK=2136MW, RR=89MW, NetOpMargin: AM=548, PM=518, EVE=318 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @79.5MW, LEYTE A @333MW, PGPP1 @76MW [WEBSMS] | CVIS
4/6/2024 5:40:38 AM | [NSO Update] Luzon Grid-04/06/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14930MW, PK=10948MW, RR=380MW, NetOpMargin: AM=3603, PM=3744, EVE=3277 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: N/A [WEBSMS] | CLUZ
4/6/2024 5:38:43 AM | Luzon Grid-04/06/2024 05:38: San Manuel-UPSI San Manuel BESS 69kV Line (CO de-energized at 0537H (Planned Outage) [WEBSMS] | CLUZ
4/6/2024 4:30:06 AM | [NSO Update] Luzon Grid-04/06/2024 04:30: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/6/2024 4:28:43 AM | [NSO Update] Mindanao Grid-04/06/2024 04:34: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
4/6/2024 4:28:01 AM | [NSO Update] Visayas Grid-04/06/2024 04:28: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
4/6/2024 3:46:56 AM | Mindanao Grid-04/06/2024 03:52: Agus 6 Unit 2 online at 0332H (Unplanned Outage) [WEBSMS] | CMIN
4/6/2024 1:13:55 AM | Mindanao Grid-04/06/2024 01:19: NagaMin SS SVC (7XF03NAA / SVC) energized/restored at 0109H from Planned Outage/Non-GOMP. [WEBSMS] | CMIN
4/6/2024 12:11:45 AM | Mindanao Grid-04/06/2024 00:17: NagaMin SS SVC (7XF03NAA / SVC) de-energized at 0007H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
4/5/2024 11:39:21 PM | Luzon Grid-04/05/2024 23:39: MPGC 2 with 150MW load tripped at 2337H (Unplanned Outage). [WEBSMS] | CLUZ
4/5/2024 9:46:26 PM | Mindanao Grid-04/05/2024 21:51: WMPC DG10 shutdown at 2145H. RPS-System Voltage Requirement [WEBSMS] | CMIN
4/5/2024 9:07:27 PM | Mindanao Grid-04/05/2024 21:12: WMPC DG08 shutdown at 2104H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/5/2024 8:19:59 PM | Mindanao Grid-04/05/2024 20:25: WMPC DG06 shutdown at 2018H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/5/2024 6:31:11 PM | Mindanao Grid-04/05/2024 18:36: WMPC DG06 online at 1827H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/5/2024 6:10:40 PM | Mindanao Grid-04/05/2024 18:15: Update: Agus 5 SY- Agus5 HEP 138 kV L1 energized at 1753H from Unplanned Outage/Non-GOMP. [WEBSMS] | CMIN
4/5/2024 6:02:28 PM | Mindanao Grid-04/05/2024 18:07: Agus 5 SY- Agus5 HEP 138 kV L1 energized at 1753H from Planned Outage/GOP. [WEBSMS] | CMIN
4/5/2024 5:51:25 PM | [NSO Update] Mindanao Grid-04/05/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3133MW, PK=2433MW, RR=95MW, NetOpMargin: EVE=584 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @84MW [WEBSMS] | CMIN
4/5/2024 5:47:47 PM | [NSO Update] Visayas Grid-04/05/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2430MW, PK=2193MW, RR=60MW, NetOpMargin: EVE=177 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @72MW, LEYTE A @333MW, PGPP1 @76MW [WEBSMS] | CVIS
4/5/2024 5:43:52 PM | [NSO Update] Luzon Grid-04/05/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13121MW, PK=11216MW, RR=427MW, NetOpMargin: EVE=1478 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: N/A [WEBSMS] | CLUZ
4/5/2024 5:24:03 PM | Luzon Grid-04/05/2024 17:24: Angat 115kV Bus 1 tripped at 1713H and restored at 1721H (Unplanned Outage) [WEBSMS] | CLUZ
4/5/2024 5:20:03 PM | Luzon Grid-04/05/2024 17:20: San Gabriel online at 1718H (LNG Commisioning) [WEBSMS] | CLUZ
4/5/2024 5:16:10 PM | Mindanao Grid-04/05/2024 17:21: WMPC DG06 shutdown at 1714H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/5/2024 5:00:40 PM | Mindanao Grid-04/05/2024 17:05: Agus6 SY- Agus6 HEP 69 kV L2 energized at 1655H. (Unplanned Outage) [WEBSMS] | CMIN
4/5/2024 3:41:01 PM | Luzon Grid-04/05/2024 15:41: Calaca 8-04CB24CLC closed at 1540H (Unplanned Outage) [WEBSMS] | CLUZ
4/5/2024 3:34:33 PM | Mindanao Grid-04/05/2024 15:39: WMPC DG01 shutdown at 1534H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/5/2024 2:27:17 PM | Mindanao Grid-04/05/2024 14:32: WMPC DG01 online at 1425H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/5/2024 1:39:32 PM | Luzon Grid-04/05/2024 13:39: Pagbilao Unit 1 online at 1332H (Unplanned Outage) [WEBSMS] | CLUZ
4/5/2024 1:32:54 PM | Luzon Grid-04/05/2024 13:33: Pagbilao Unit 1 restored at 1332H (Unplanned Outage) [WEBSMS] | CLUZ
4/5/2024 12:54:01 PM | [NSO Update] Mindanao Grid-04/05/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3156MW, PK=2485MW, RR=97MW, NetOpMargin: PM=574, EVE=612 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @84MW [WEBSMS] | CMIN
4/5/2024 12:52:32 PM | [NSO Update] Luzon Grid-04/05/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13845MW, PK=12068MW, RR=454MW, NetOpMargin: PM=1323, EVE=1198 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: N/A [WEBSMS] | CLUZ
4/5/2024 12:52:25 PM | [NSO Update] Visayas Grid-04/05/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2736MW, PK=2462MW, RR=60MW, NetOpMargin: PM=214, EVE=186 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @76MW, LEYTE A @328MW, PGPP1 @76MW [WEBSMS] | CVIS
4/5/2024 12:46:26 PM | Mindanao Grid-04/05/2024 12:51: WMPC DG06 online at 1240H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/5/2024 12:04:05 PM | Luzon Grid-04/05/2024 12:04: Correction: ALD occurred at MERALCO feeders at 1146H due to tripping of Pagbilao Unit 1 and was restored at 1150H. Lowest system frequency is at 59.019Hz. [WEBSMS] | CLUZ
4/5/2024 12:00:49 PM | Luzon Grid-04/05/2024 12:00: ALD occurred at MERALCO feeders at 1146H due to tripping of Pagbilao Unit 1 and was restored at 1150H. Lowest system frequency is at 59.010Hz. [WEBSMS] | CLUZ
4/5/2024 11:51:01 AM | Luzon Grid-04/05/2024 11:51: Pagbilao Unit 1 tripped at 1146H. Lowest system frequency is 59.019Hz. [WEBSMS] | CLUZ
4/5/2024 11:23:43 AM | Mindanao Grid-04/05/2024 11:29: Zamboanga SS 138 kV Bus 2 energized / restored at 1118H. P.O/Non-GOMP. [WEBSMS] | CMIN
4/5/2024 9:28:23 AM | Mindanao Grid-04/05/2024 09:33: WMPC DG08 online at 0924H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/5/2024 9:21:37 AM | Luzon Grid-04/05/2024 09:21: Ilijan ST1 online at 0920H (Unplanned Outage) [WEBSMS] | CLUZ
4/5/2024 8:50:40 AM | Luzon Grid-04/05/2024 08:50: Santiago - Magat 230kV Line 1 unlooped on Magat side at 0848H (Planned Outage) [WEBSMS] | CLUZ
4/5/2024 8:42:00 AM | Mindanao Grid-04/05/2024 08:47: WMPC DG10 online at 0840H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/5/2024 8:30:43 AM | Visayas Grid-04/05/2024 08:30: Cebu SS 138KV Bus 2 de-energized at 0827H.(Planned Outage) [WEBSMS] | CVIS
4/5/2024 8:13:56 AM | Mindanao Grid-04/05/2024 08:19: Zamboanga SS 138 kV Bus 2 de-energized at 0809H. P.O/Non-GOMP. [WEBSMS] | CMIN
4/5/2024 8:05:59 AM | Luzon Grid-04/05/2024 08:06: Ilijan GT1-1 online at 0805H (Unplanned Outage) [WEBSMS] | CLUZ
4/5/2024 7:44:13 AM | Mindanao Grid-04/05/2024 07:49: Villanueva SS 138 kV Bus 2 energized /restored at 0737H. P.O/Non-GOMP. [WEBSMS] | CMIN
4/5/2024 6:13:26 AM | Mindanao Grid-04/05/2024 06:18: Villanueva SS 138 kV Bus 2 de-energized at 0546H. P.O/Non-GOMP. [WEBSMS] | CMIN
4/5/2024 5:38:59 AM | [NSO Update] Mindanao Grid-04/05/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3134MW, PK=2491MW, RR=94MW, NetOpMargin: AM=549, PM=511, EVE=600 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48.9MW, MA2 @37MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @83MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
4/5/2024 5:37:42 AM | [NSO Update] Visayas Grid-04/05/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2784MW, PK=2364MW, RR=90MW, NetOpMargin: AM=330, PM=256, EVE=369 Highest Unit O/L: THVI @169MW Derated Plant: TGPP @79.5MW, LEYTE A @333MW, PGPP1 @76MW [WEBSMS] | CVIS
4/5/2024 5:36:14 AM | [NSO Update] Luzon Grid-04/05/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14036MW, PK=11524MW, RR=436MW, NetOpMargin: AM=2077, PM=1246, EVE=1304 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: N/A [WEBSMS] | CLUZ
4/5/2024 4:48:19 AM | [NSO Update] Mindanao Grid-04/05/2024 04:53: Weather Update: Trough of a Low Pressure Area (LPA) affecting Mindanao. Ridge of a High Pressure Area (HPA) extending over the eastern section of Northern Luzon. [WEBSMS] | CMIN
4/5/2024 4:48:01 AM | [NSO Update] Visayas Grid-04/05/2024 04:48: Weather Update: Trough of a Low Pressure Area (LPA) affecting Mindanao. Ridge of a High Pressure Area (HPA) extending over the eastern section of Northern Luzon. [WEBSMS] | CVIS
4/5/2024 4:47:43 AM | [NSO Update] Luzon Grid-04/05/2024 04:47: Weather Update: Trough of a Low Pressure Area (LPA) affecting Mindanao. Ridge of a High Pressure Area (HPA) extending over the eastern section of Northern Luzon. [WEBSMS] | CLUZ
4/5/2024 4:21:58 AM | Luzon Grid-04/05/2024 04:22: Binan - Balibago 115kV Line restored at 0421H (Planned Outage) [WEBSMS] | CLUZ
4/5/2024 4:19:27 AM | Mindanao Grid-04/05/2024 04:24: TALOMO 1 Unit 1 online at 0049H (Unplanned Outage) [WEBSMS] | CMIN
4/5/2024 4:18:48 AM | Mindanao Grid-04/05/2024 04:24: TALOMO 1 Unit 1 with 0.5MW load shutdown at 0003H as required by DLPC to facilitate safe restoration of busted fuse along their Malagos Line System (Unplanned Outage). [WEBSMS] | CMIN
4/5/2024 3:01:17 AM | Luzon Grid-04/05/2024 03:01: Ilijan GT2-1 online at 0259H (Unplanned Outage) [WEBSMS] | CLUZ
4/5/2024 12:51:37 AM | Luzon Grid-04/05/2024 00:51: Binan - Balibago 115kV Line de-energized at 0036H (Planned Outage) [WEBSMS] | CLUZ
4/5/2024 12:49:41 AM | Luzon Grid-04/05/2024 00:49: Ilijan B ST2 online at 0044H (Unplanned Outage) [WEBSMS] | CLUZ
4/4/2024 11:33:08 PM | Luzon Grid-04/04/2024 23:33: Ilijan B GT2-2 online at 2328H (Unplanned Outage) [WEBSMS] | CLUZ
4/4/2024 11:13:42 PM | Mindanao Grid-04/04/2024 23:19: TALOMO 1 Unit 1 online at 2220H (Unplanned Outage) [WEBSMS] | CMIN
4/4/2024 11:12:55 PM | Mindanao Grid-04/04/2024 23:18: TALOMO 1 Unit 1 with 0.51MW load isolated at 2133H due to loss of feedback power brought by DLPC Malagos Recloser Tripping (Unplanned Outage). [WEBSMS] | CMIN
4/4/2024 9:45:47 PM | Mindanao Grid-04/04/2024 21:51: WMPC DG10 shutdown at 2144H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/4/2024 8:15:51 PM | Mindanao Grid-04/04/2024 20:21: WMPC DG08 shutdown at 2014H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/4/2024 7:51:33 PM | Luzon Grid-04/04/2024 19:51: San Gabriel shutdown at 1950H (LNG Commissioning) [WEBSMS] | CLUZ
4/4/2024 5:59:28 PM | Mindanao Grid-04/04/2024 18:04: WMPC DG06 online at 1310H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/4/2024 5:58:05 PM | Mindanao Grid-04/04/2024 18:03: ASIGA Hydro online at 1431H (Unplanned Outage) [WEBSMS] | CMIN
4/4/2024 5:54:27 PM | [NSO Update] Mindanao Grid-04/04/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3089MW, PK=2364MW, RR=96MW, NetOpMargin: EVE=629 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @83MW, AG7 @20MW, PG4 @76MW [WEBSMS] | CMIN
4/4/2024 5:53:05 PM | [NSO Update] Visayas Grid-04/04/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2646MW, PK=2292MW, RR=61MW, NetOpMargin: EVE=294 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 333MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/4/2024 5:51:50 PM | [NSO Update] Luzon Grid-04/04/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12998MW, PK=11830MW, RR=449MW, NetOpMargin: EVE=719 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: N/A [WEBSMS] | CLUZ
4/4/2024 5:48:20 PM | Mindanao Grid-04/04/2024 17:53: Baloi SS Power Transformer # 3 re-energized at 1731H. From P&E emergency request (PO/Non-GOMP). [WEBSMS] | CMIN
4/4/2024 5:20:56 PM | Visayas Grid-04/04/2024 17:21: Compostela SS TR2 150MVA 230/138/13.8 energized at 1718H. (Planned Outage) [WEBSMS] | CVIS
4/4/2024 4:51:16 PM | [NSO Update] Visayas Grid-04/04/2024 16:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1642H with power going to Luzon. [WEBSMS] | CVIS
4/4/2024 4:50:56 PM | [NSO Update] Luzon Grid-04/04/2024 16:51: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1642H with power going to Luzon. [WEBSMS] | CLUZ
4/4/2024 4:49:22 PM | Luzon Grid-04/04/2024 16:49: Affected ALD feeders of NGCP and MERALCO both restored at 1637H. [WEBSMS] | CLUZ
4/4/2024 4:46:44 PM | [NSO Update] Visayas Grid-04/04/2024 16:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1632H from reverse power direction. [WEBSMS] | CVIS
4/4/2024 4:46:30 PM | [NSO Update] Luzon Grid-04/04/2024 16:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1632H from reverse power direction. [WEBSMS] | CLUZ
4/4/2024 4:32:16 PM | Luzon Grid-04/04/2024 16:32: ALD occurred at NGCP and MERALCO feeders at 1626H due to tripping of Ilijan GT1-2, ST-1, GT2-1, GT2-2 and ST-2. Lowest system frequency is 58.925Hz. [WEBSMS] | CLUZ
4/4/2024 4:17:27 PM | Mindanao Grid-04/04/2024 16:22: WMPC DG06 shutdown at 1614H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/4/2024 3:29:06 PM | Mindanao Grid-04/04/2024 15:34: Baloi SS Power Transformer # 3 de-energized at 1240H. P&E emergency request (PO/Non--GOMP). [WEBSMS] | CMIN
4/4/2024 3:17:00 PM | Mindanao Grid-04/04/2024 15:22: WMPC DG01 shutdown at 1513H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/4/2024 2:29:17 PM | Mindanao Grid-04/04/2024 14:34: ASIGA Hydro with 3.6MW load tripped at 1259H. Cause: Isolation due to loss of feedback power brought by tripping Butuan-Santiago 69 kV feeder (Unplanned Outage). [WEBSMS] | CMIN
4/4/2024 2:00:03 PM | Mindanao Grid-04/04/2024 14:05: LAKE MAINIT Hydro online at 1345H (Unplanned Outage) [WEBSMS] | CMIN
4/4/2024 1:41:19 PM | Mindanao Grid-04/04/2024 13:46: WMPC DG01 online at 1329H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/4/2024 1:35:32 PM | Luzon Grid-04/04/2024 13:35: Calaca 8-04CB24CLC opened at 1332H (Unplanned Outage) [WEBSMS] | CLUZ
4/4/2024 1:28:08 PM | [NSO Update] Visayas Grid-04/04/2024 13:28: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1324H with power going to Visayas [WEBSMS] | CVIS
4/4/2024 1:27:27 PM | [NSO Update] Luzon Grid-04/04/2024 13:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1324H with power going to Visayas [WEBSMS] | CLUZ
4/4/2024 1:26:50 PM | Mindanao Grid-04/04/2024 13:32: SEC2 online at 1325H (Unplanned Outage) [WEBSMS] | CMIN
4/4/2024 1:17:18 PM | [NSO Update] Visayas Grid-04/04/2024 13:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1314H from forward power direction [WEBSMS] | CVIS
4/4/2024 1:16:38 PM | [NSO Update] Luzon Grid-04/04/2024 13:16: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1314H from forward power direction [WEBSMS] | CLUZ
4/4/2024 1:08:43 PM | Mindanao Grid-04/04/2024 13:14: LAKE MAINIT Hydro with 16.2MW load tripped at 1259H. Cause: Isolation due to loss of feedback power brought by tripping of Butuan-Santiago 69 kV feeder (Unplanned Outage). [WEBSMS] | CMIN
4/4/2024 12:52:28 PM | [NSO Update] Mindanao Grid-04/04/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3047MW, PK=2509MW, RR=99MW, NetOpMargin: PM=438, EVE=514 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @76MW [WEBSMS] | CMIN
4/4/2024 12:44:54 PM | [NSO Update] Luzon Grid-04/04/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13909MW, PK=12382MW, RR=484MW, NetOpMargin: PM=1043, EVE=1114 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @300MW [WEBSMS] | CLUZ
4/4/2024 12:34:50 PM | [NSO Update] Visayas Grid-04/04/2024 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2721MW, PK=2452MW, RR=55MW, NetOpMargin: PM=213, EVE=172 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @325MW, PGPP1 @76MW [WEBSMS] | CVIS
4/4/2024 12:00:10 PM | Mindanao Grid-04/04/2024 12:05: Tacurong SS 138kV Busbar # 2 re-energized at 1118H. From Planned Outage (Non-GOMP). [WEBSMS] | CMIN
4/4/2024 11:30:56 AM | Mindanao Grid-04/04/2024 11:36: SEC2 with 118.3MW load tripped at 1120H. Initial cause: Overexcitation (for verification). Frequency dipped at 59.3Hz. No ALD. (Unplanned Outage) [WEBSMS] | CMIN
4/4/2024 10:50:13 AM | Mindanao Grid-04/04/2024 10:55: Baloi-Lugait 138KV line re-energized at 1041H. P&E emergency request. Non-GOMP. [WEBSMS] | CMIN
4/4/2024 9:33:51 AM | Mindanao Grid-04/04/2024 09:39: WMPC DG08 online at 0931H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/4/2024 9:21:05 AM | Mindanao Grid-04/04/2024 09:26: WMPC DG10 online at 0917H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
4/4/2024 9:01:50 AM | Mindanao Grid-04/04/2024 09:07: Tacurong SS 138kV Busbar # 2 de-energized at 0824H. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
4/4/2024 8:56:36 AM | Luzon Grid-04/04/2024 08:56: San Gabriel online at 0852H (Unplanned Outage) [WEBSMS] | CLUZ
4/4/2024 7:59:03 AM | Mindanao Grid-04/04/2024 08:04: Baloi-Lugait 138KV line de-energized at 0735H. P&E emergency request. Non-GOMP. [WEBSMS] | CMIN
4/4/2024 7:56:10 AM | Luzon Grid-04/04/2024 07:56: Batangas 300MVA T04 & T05 parallel at 0753H (Unplanned Outage) [WEBSMS] | CLUZ
4/4/2024 7:52:29 AM | Luzon Grid-04/04/2024 07:52: San Lorenzo-Sta. Rita 230kV Bus 1 & 2 unloop at 0750H (Unplanned Outage). [WEBSMS] | CLUZ
4/4/2024 6:19:09 AM | Visayas Grid-04/04/2024 06:19: Compostela SS TR2 150MVA 230/138/13.8 de-energized at 0613H. (Planned Outage) [WEBSMS] | CVIS
4/4/2024 5:46:49 AM | [NSO Update] Mindanao Grid-04/04/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3167MW, PK=2511MW, RR=96MW, NetOpMargin: AM=560, PM=522, EVE=604 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @76MW [WEBSMS] | CMIN
4/4/2024 5:45:12 AM | [NSO Update] Visayas Grid-04/04/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2759MW, PK=2370MW, RR=52MW, NetOpMargin: AM=337, PM=236, EVE=200 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @333MW, PGPP1 @76MW [WEBSMS] | CVIS
4/4/2024 5:42:48 AM | [NSO Update] Luzon Grid-04/04/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14213MW, PK=11428MW, RR=463MW, NetOpMargin: AM=2322, PM=1415, EVE=1395 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @300MW [WEBSMS] | CLUZ
4/4/2024 4:47:31 AM | [NSO Update] Mindanao Grid-04/04/2024 04:52: Weather Update: Easterlies affecting Visayas and Mindanao. Ridge of High Pressure Area (HPA) extending over the eastern section of Northern Luzon. [WEBSMS] | CMIN
4/4/2024 4:47:17 AM | [NSO Update] Visayas Grid-04/04/2024 04:47: Weather Update: Easterlies affecting Visayas and Mindanao. Ridge of High Pressure Area (HPA) extending over the eastern section of Northern Luzon. [WEBSMS] | CVIS
4/4/2024 4:46:33 AM | [NSO Update] Luzon Grid-04/04/2024 04:46: Weather Update: Easterlies affecting Visayas and Mindanao. Ridge of High Pressure Area (HPA) extending over the eastern section of Northern Luzon. [WEBSMS] | CLUZ
4/4/2024 12:41:46 AM | Luzon Grid-04/04/2024 00:41: Binan - Balibago 115kV Line de-energized at 0037H (Planned Outage) [WEBSMS] | CLUZ
4/3/2024 9:16:54 PM | Mindanao Grid-04/03/2024 21:22: WMPC DG10 shutdown at 2114H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
4/3/2024 5:59:39 PM | [NSO Update] Mindanao Grid-04/03/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3093MW, PK=2459MW, RR=88MW, NetOpMargin: EVE=545 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @25MW, AG6 @83MW, AG7 @20MW, PG4 @76MW [WEBSMS] | CMIN
4/3/2024 5:57:53 PM | [NSO Update] Visayas Grid-04/03/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2533MW, PK=2251MW, RR=93MW, NetOpMargin: EVE=189 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 328MW, PGPP1 @ 76MW [WEBSMS] | CVIS
4/3/2024 5:56:47 PM | [NSO Update] Luzon Grid-04/03/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12854MW, PK=11221MW, RR=447MW, NetOpMargin: EVE=1186 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 2 @ 290MW, Ilijan A @ 170MW, Ilijan B @ 580MW [WEBSMS] | CLUZ
4/3/2024 5:46:02 PM | Mindanao Grid-04/03/2024 17:51: WMPC DG08 shutdown at 1744H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
4/3/2024 5:17:26 PM | Mindanao Grid-04/03/2024 17:22: Agus5 - Aurora 138kV Line energized at 1715H. (Unplanned Outage) [WEBSMS] | CMIN
4/3/2024 5:16:10 PM | Mindanao Grid-04/03/2024 17:21: WMPC DG06 shutdown at 1713H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
4/3/2024 5:12:13 PM | Mindanao Grid-04/03/2024 17:17: Balo-i - Agus6 138kV Line1 energized at 1707H. (Planned Outage) [WEBSMS] | CMIN
4/3/2024 5:07:41 PM | [NSO Update] Luzon Grid-04/03/2024 17:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1706H with power going to Luzon. [WEBSMS] | CLUZ
4/3/2024 5:07:26 PM | [NSO Update] Visayas Grid-04/03/2024 17:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1706H with power going to Luzon. [WEBSMS] | CVIS
4/3/2024 4:57:25 PM | [NSO Update] Visayas Grid-04/03/2024 16:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1656H from reverse power direction. [WEBSMS] | CVIS
4/3/2024 4:57:06 PM | [NSO Update] Luzon Grid-04/03/2024 16:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1656H from reverse power direction. [WEBSMS] | CLUZ
4/3/2024 3:15:34 PM | Mindanao Grid-04/03/2024 15:20: Pulangi4 Unit2 shutdown at 1509H. (Planned Outage) [WEBSMS] | CMIN
4/3/2024 2:58:05 PM | Mindanao Grid-04/03/2024 15:03: Agus5 U2 synchronized at 1346H from Unplanned Outage. [WEBSMS] | CMIN
4/3/2024 1:43:17 PM | [NSO Update] Visayas Grid-04/03/2024 13:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1341H with power going to Visayas [WEBSMS] | CVIS
4/3/2024 1:39:25 PM | Mindanao Grid-04/03/2024 13:44: Pulangi4 U1 online at 1332H for Test Run. (Planned Outage) [WEBSMS] | CMIN
4/3/2024 1:37:43 PM | [NSO Update] Visayas Grid-04/03/2024 13:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1331H from forward power direction [WEBSMS] | CVIS
4/3/2024 1:37:12 PM | [NSO Update] Luzon Grid-04/03/2024 13:37: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1331H from forward power direction [WEBSMS] | CLUZ
4/3/2024 1:13:02 PM | Mindanao Grid-04/03/2024 13:18: Balo-i - Agus6 138kV line1 de-energized at 1304H. (Planned Outage) [WEBSMS] | CMIN
4/3/2024 12:52:30 PM | [NSO Update] Mindanao Grid-04/03/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3131MW, PK=2527MW, RR=94MW, NetOpMargin: PM=510, EVE=598 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG6 @83MW, AG7 @20MW, PG4 @76MW [WEBSMS] | CMIN
4/3/2024 12:48:01 PM | [NSO Update] Visayas Grid-04/03/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2735MW, PK=2412MW, RR=97MW, NetOpMargin: PM=227, EVE=169 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @325MW, PGPP1 @76MW [WEBSMS] | CVIS
4/3/2024 12:44:38 PM | [NSO Update] Luzon Grid-04/03/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13825MW, PK=12064MW, RR=454MW, NetOpMargin: PM=1308, EVE=1224 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MASINLOC 2 @290MW [WEBSMS] | CLUZ
4/3/2024 12:10:44 PM | Mindanao Grid-04/03/2024 12:15: Balo-i - Agus5 138kV Line energized at 1202H. (Planned Outage) [WEBSMS] | CMIN
4/3/2024 11:50:45 AM | Visayas Grid-04/03/2024 11:50: VMC cut in at 1131H (Unplanned Outage) [WEBSMS] | CVIS
4/3/2024 11:14:32 AM | Mindanao Grid-04/03/2024 11:18: Tacurong SS 138kV Bus1 Re-energized at 1109H. (Planned Outage) [WEBSMS] | CMIN
4/3/2024 10:59:07 AM | Mindanao Grid-04/03/2024 11:03: WMPC DG06 online at 1055H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
4/3/2024 10:42:27 AM | Mindanao Grid-04/03/2024 10:46: Agus5 U2 with a load of 25MW tripped at 1030H (Unplanned Outage) [WEBSMS] | CMIN
4/3/2024 10:36:51 AM | Mindanao Grid-04/03/2024 10:41: Agus5 - Aurora 138kV Line tripped at 1030H. (Unplanned Outage) [WEBSMS] | CMIN
4/3/2024 10:00:25 AM | Mindanao Grid-04/03/2024 10:04: WMPC DG08 online at 0958H. RPS - System Voltage Requirement. [WEBSMS] [WEBSMS] | CMIN
4/3/2024 9:37:34 AM | Mindanao Grid-04/03/2024 09:41: WMPC DG10 online at 0930H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
4/3/2024 9:02:47 AM | Mindanao Grid-04/03/2024 09:07: Tacurong SS 138kV Bus1 de-energized at 0859H. (Planned Outage) [WEBSMS] | CMIN
4/3/2024 8:40:13 AM | Luzon Grid-04/03/2024 08:40: Bay SS PCB 8-05CB04BYZ de-energized at 0839H. (Unplanned Outage) [WEBSMS] | CLUZ
4/3/2024 7:53:40 AM | Mindanao Grid-04/03/2024 07:57: Balo-i - Agus5 138kV Line de-energized at 0751H (Planned Outage) [WEBSMS] | CMIN
4/3/2024 5:45:43 AM | [NSO Update] Mindanao Grid-04/03/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3178MW, PK=2398MW, RR=93MW, NetOpMargin: AM=687, PM=571, EVE=607 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @43MW, AG2 @56MW, AG4 @69MW, AG5 @21MW, AG6 @101MW, AG7 @20MW, PG4 @76MW [WEBSMS] | CMIN
4/3/2024 5:43:27 AM | [NSO Update] Luzon Grid-04/03/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14035MW, PK=11458MW, RR=467MW, NetOpMargin: AM=2110, PM=1171, EVE=1608 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MASINLOC 2 @290MW [WEBSMS] | CLUZ
4/3/2024 5:41:47 AM | [NSO Update] Visayas Grid-04/03/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2804MW, PK=2322MW, RR=94MW, NetOpMargin: AM=388, PM=191, EVE=171 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @325MW, PGPP1 @76MW [WEBSMS] | CVIS
4/3/2024 5:20:18 AM | Luzon Grid-04/03/2024 05:20: Concepcion-UPSI Concepcion BESS 69kV Line de-energized at 0518H (Planned Outage) [WEBSMS] | CLUZ
4/3/2024 5:18:59 AM | Luzon Grid-04/03/2024 05:18: Concepcion-Concepcion 1 Solar PP 69kV Line de-energized at 0517H (Planned Outage) [WEBSMS] | CLUZ
4/3/2024 4:16:39 AM | Visayas Grid-04/03/2024 04:16: Calong-calong- Daanlungsod 138KV line 1 energized at 0414H, hotspot correction.(Unplanned Outage) [WEBSMS] | CVIS
4/3/2024 4:02:18 AM | [NSO Update] Luzon Grid-04/03/2024 04:02: Weather Advisory: Ridge of High Pressure Area (HPA) extending over the eastern section of Luzon. [WEBSMS] | CLUZ
4/3/2024 4:02:15 AM | [NSO Update] Visayas Grid-04/03/2024 04:02: Weather Advisory: Ridge of High Pressure Area (HPA) extending over the eastern section of Luzon. [WEBSMS] | CVIS
4/3/2024 4:02:13 AM | [NSO Update] Mindanao Grid-04/03/2024 04:06: Weather Advisory: Ridge of High Pressure Area (HPA) extending over the eastern section of Luzon. [WEBSMS] | CMIN
4/3/2024 2:50:30 AM | Luzon Grid-04/03/2024 02:50: Quezon (Balintawak) 300MVA T01 restored at 0249H (Planned Outage) [WEBSMS] | CLUZ
4/3/2024 2:24:33 AM | Visayas Grid-04/03/2024 02:24: Calong-calong- Daanlungsod 138KV line 1 de-energized at 0206H, hotspot correction.(Unplanned Outage) [WEBSMS] | CVIS
4/2/2024 11:32:18 PM | Luzon Grid-04/02/2024 23:32: Quezon (Balintawak) 300MVA T01 de-energized at 2331H (Planned Outage) [WEBSMS] | CLUZ
4/2/2024 10:22:44 PM | Luzon Grid-04/02/2024 22:23: SCPC 4 with 120MW load tripped at 2219H. Lowest frequency at 59.6871Hz (Unplanned Outage) [WEBSMS] | CLUZ
4/2/2024 9:26:39 PM | Mindanao Grid-04/02/2024 21:31: WMPC DG10 shutdown at 2122H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/2/2024 9:04:46 PM | Mindanao Grid-04/02/2024 21:09: Bunawan - Davao 138KV Line 1 restored at 2100H (Planned Outage) [WEBSMS] | CMIN
4/2/2024 8:15:56 PM | Mindanao Grid-04/02/2024 20:20: WMPC DG06 shutdown at 2014H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/2/2024 6:10:39 PM | [NSO Update] Visayas Grid-04/02/2024 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2611MW, PK=2351MW, RR=90MW, NetOpMargin: EVE=170 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @70MW, LEYTE A @332MW, PGPP1 @76MW [WEBSMS] | CVIS
4/2/2024 5:51:19 PM | Mindanao Grid-04/02/2024 17:55: WMPC DG07 shutdown at 1744H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/2/2024 5:50:35 PM | [NSO Update] Mindanao Grid-04/02/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3139MW, PK=2410MW, RR=91MW, NetOpMargin: EVE=638 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @45MW, AG2 @55MW, AG4 @69MW, AG5 @25MW, AG6 @101MW, AG7 @22MW, PG4 @98MW [WEBSMS] | CMIN
4/2/2024 5:48:59 PM | [NSO Update] Luzon Grid-04/02/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13190MW, PK=11537MW, RR=427MW, NetOpMargin: EVE=1226 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: ILIJAN A @300MW [WEBSMS] | CLUZ
4/2/2024 4:30:27 PM | Luzon Grid-04/02/2024 16:30: La Trinidad SS 230kV Bus 2 restored at 1630H (Planned Outage) [WEBSMS] | CLUZ
4/2/2024 12:48:57 PM | [NSO Update] Mindanao Grid-04/02/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3202MW, PK=2529MW, RR=97MW, NetOpMargin: PM=576, EVE=651 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @45MW, AG2 @55MW, AG4 @69MW, AG5 @25MW, AG6 @101MW, AG7 @22MW, PG4 @98MW [WEBSMS] | CMIN
4/2/2024 12:48:51 PM | Mindanao Grid-04/02/2024 12:53: WMPC DG06 online at 1245H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/2/2024 12:46:32 PM | [NSO Update] Luzon Grid-04/02/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14406MW, PK=12062MW, RR=444MW, NetOpMargin: PM=1900, EVE=1725 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: MASINLOC 3 @310MW [WEBSMS] | CLUZ
4/2/2024 12:46:08 PM | [NSO Update] Visayas Grid-04/02/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2744MW, PK=2412MW, RR=93MW, NetOpMargin: PM=239, EVE=170 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @70MW, LEYTE A @355MW, PGPP1 @76MW [WEBSMS] | CVIS
4/2/2024 10:21:25 AM | Mindanao Grid-04/02/2024 10:25: WMPC DG07 online at 1016H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/2/2024 9:40:21 AM | Mindanao Grid-04/02/2024 09:44: WMPC DG10 online at 0928H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
4/2/2024 8:07:12 AM | Luzon Grid-04/02/2024 08:07: La Trinidad SS 230kV Bus 2 de-energized at 0807H. (Planned Outage) [WEBSMS] | CLUZ
4/2/2024 8:06:38 AM | Mindanao Grid-04/02/2024 08:11: AGUS 5 Unit 1 HEP shutdown at 0803H. PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
4/2/2024 6:46:09 AM | Mindanao Grid-04/02/2024 06:50: Bunawan - Davao 138KV Line 1 shutdown at 0638H (Planned Outage) [WEBSMS] | CMIN
4/2/2024 5:32:59 AM | [NSO Update] Luzon Grid-04/02/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14584MW, PK=11511MW, RR=436MW, NetOpMargin: AM=2636, PM=1758, EVE=1284 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: MSLC3 @310MW, ILIJAN A @300MW [WEBSMS] | CLUZ
4/2/2024 5:30:42 AM | [NSO Update] Visayas Grid-04/02/2024 05:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2858MW, PK=2328MW, RR=89MW, NetOpMargin: AM=441, PM=244, EVE=236 Highest Unit O/L: THVI 1&2 @ 168MW Derated Plant: TGPP @70MW, LEYTE A @356MW, PGPP1 @76MW [WEBSMS] | CVIS
4/2/2024 5:27:43 AM | [NSO Update] Mindanao Grid-04/02/2024 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3212MW, PK=2377MW, RR=93MW, NetOpMargin: AM=742, PM=612, EVE=702 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @45MW, AG2 @55MW, AG4 @69MW, AG5 @25MW, AG6 @101MW, AG7 @22MW, PG4 @98MW [WEBSMS] | CMIN
4/2/2024 4:21:13 AM | Luzon Grid-04/02/2024 04:21: Binan-Balibago 115kV Line restored at 0420H (Planned Outage) [WEBSMS] | CLUZ
4/2/2024 4:02:23 AM | [NSO Update] Luzon Grid-04/02/2024 04:02: Weather Update: Ridge of High Pressure Area (HPA) extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CLUZ
4/2/2024 4:02:10 AM | [NSO Update] Visayas Grid-04/02/2024 04:02: Weather Update: Ridge of High Pressure Area (HPA) extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CVIS
4/2/2024 4:01:47 AM | [NSO Update] Mindanao Grid-04/02/2024 04:06: Weather Update: Ridge of High Pressure Area (HPA) extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CMIN
4/2/2024 12:38:32 AM | Luzon Grid-04/02/2024 00:38: Binan-Balibago 115kV Line de-energized at 0038H (Planned Outage) [WEBSMS] | CLUZ
4/1/2024 7:16:04 PM | Mindanao Grid-04/01/2024 19:20: WMPC DG01 shutdown at 1913H. MO Dispatch. [WEBSMS] | CMIN
4/1/2024 6:57:10 PM | Luzon Grid-04/01/2024 18:57: Angat HEPP 115kV Bus 1 restored at 1855H (Planned Outage) [WEBSMS] | CLUZ
4/1/2024 6:01:42 PM | [NSO Update] Mindanao Grid-04/01/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3071MW, PK=2448MW, RR=75MW, NetOpMargin: EVE=548 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @42MW, AG2 @55MW, AG4 @68MW, AG5 @20MW, AG6 @82MW, AG7 @19MW, PG4 @60MW [WEBSMS] | CMIN
4/1/2024 5:56:38 PM | [NSO Update] Visayas Grid-04/01/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2668MW, PK=2332MW, RR=90MW, NetOpMargin: EVE=246 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @74MW, LEYTE A @358MW, PGPP1 @76MW [WEBSMS] | CVIS
4/1/2024 5:55:32 PM | [NSO Update] Luzon Grid-04/01/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13088MW, PK=11471MW, RR=287MW, NetOpMargin: EVE=1330 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @220MW, ILIJAN A @300MW [WEBSMS] | CLUZ
4/1/2024 4:59:09 PM | Mindanao Grid-04/01/2024 17:03: WMPC DG06 shutdown at 1644H. MO Dispatched. [WEBSMS] | CMIN
4/1/2024 4:33:21 PM | Mindanao Grid-04/01/2024 16:37: WMPC DG06 end of RPS at 1630H, and start of MO dispatch at 1631H at 5.5MW. [WEBSMS] | CMIN
4/1/2024 4:17:36 PM | Visayas Grid-04/01/2024 16:17: Leyte-A, EDC-Mahanagdong A unit #1 tripped at 1549H (Unplanned Outage) [WEBSMS] | CVIS
4/1/2024 4:09:50 PM | Mindanao Grid-04/01/2024 16:14: SPC Mati shutdown at 1605H. MO dispatched. [WEBSMS] | CMIN
4/1/2024 1:34:28 PM | Luzon Grid-04/01/2024 13:34: Batangas - San Lorenzo 230kV Line 2 restored at 1331H (Unplanned Outage) [WEBSMS] | CLUZ
4/1/2024 1:24:45 PM | Mindanao Grid-04/01/2024 13:29: Lake Mainit (AGC) HEP online at 1318H from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
4/1/2024 1:15:42 PM | Mindanao Grid-04/01/2024 13:20: Update: Peak Power San Francisco Unit 2 online 1306H. MO dispatched. [WEBSMS] | CMIN
4/1/2024 1:13:31 PM | Mindanao Grid-04/01/2024 13:17: Peak Power San Francisco Unit 2 online. MO Dispatched. [WEBSMS] | CMIN
4/1/2024 1:04:12 PM | Mindanao Grid-04/01/2024 13:08: WMPC DG6 online at 1300H- RPS, System Voltage Requirement. (Planned Outage). [WEBSMS] | CMIN
4/1/2024 1:02:11 PM | [NSO Update] Luzon Grid-04/01/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14008MW, PK=11898MW, RR=311MW, NetOpMargin: PM=1798, EVE=1483 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 1 @220MW [WEBSMS] | CLUZ
4/1/2024 1:00:31 PM | [NSO Update] Mindanao Grid-04/01/2024 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3134MW, PK=2514MW, RR=78MW, NetOpMargin: PM=541, EVE=575 Highest Unit O/L: GNPK 1,2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @42MW, AG2 @55MW, AG4 @68MW, AG5 @20MW, AG6 @82MW, AG7 @19MW, PG4 @60MW [WEBSMS] | CMIN
4/1/2024 12:57:39 PM | [NSO Update] Visayas Grid-04/01/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2685MW, PK=2422MW, RR=93MW, NetOpMargin: PM=170, EVE=170 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @74MW, LEYTE A @358MW, PGPP1 @76MW [WEBSMS] | CVIS
4/1/2024 12:42:43 PM | Mindanao Grid-04/01/2024 12:47: STEAG Unit 2 with 100MW load shutdown at 1100H due to turbine pressure sensing line leak. (Unplanned Outage) [WEBSMS] | CMIN
4/1/2024 12:17:49 PM | Mindanao Grid-04/01/2024 12:22: WMPC DG06 shutdown at 1213H from MOT raise. Follow RTD. [WEBSMS] | CMIN
4/1/2024 12:16:37 PM | Mindanao Grid-04/01/2024 12:21: WMPC DG06 online at 1057H. MOT raise. [WEBSMS] | CMIN
4/1/2024 10:29:14 AM | Mindanao Grid-04/01/2024 10:33: LAKE MAINIT Hydro tripped at 1007H. Affected by tripping of Butuan-Santiago 69kV Line. (Unplanned Outage) [WEBSMS] | CMIN
4/1/2024 10:27:45 AM | Luzon Grid-04/01/2024 10:27: Angat HEPP SS 115kV Bus 1 de-energized at 1027H (Planned Outage) [WEBSMS] | CLUZ
4/1/2024 10:02:18 AM | Mindanao Grid-04/01/2024 10:06: SPC Mati online at 1000H. MO dispatched. [WEBSMS] | CMIN
4/1/2024 9:57:40 AM | Mindanao Grid-04/01/2024 10:02: WMPC DG010 online at 0929H - RPS, System voltage requirement. [WEBSMS] | CMIN
4/1/2024 9:31:37 AM | Mindanao Grid-04/01/2024 09:36: MINERGY COAL BALINGASAG (MMC) unit 2 online at 0919H from reserve shutdown. (Unplanned Outage) [WEBSMS] | CMIN
4/1/2024 8:19:52 AM | Mindanao Grid-04/01/2024 08:24: AGUS 2 Unit 3 HEP shutdown at 0814H. PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
4/1/2024 6:27:08 AM | Luzon Grid-04/01/2024 06:27: Batangas - San Lorenzo 230kV Line 2 de-energized at 0627H (Unplanned Outage) [WEBSMS] | CLUZ
4/1/2024 5:41:49 AM | [NSO Update] Mindanao Grid-04/01/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3244MW, PK=2292MW, RR=77MW, NetOpMargin: AM=874, PM=704, EVE=763 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @42MW, AG2 @55MW, AG4 @68MW, AG5 @20MW, AG6 @82MW, AG7 @19MW, PG4 @60MW [WEBSMS] | CMIN
4/1/2024 5:39:06 AM | [NSO Update] Visayas Grid-04/01/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2845MW, PK=2233MW, RR=89MW, NetOpMargin: AM=524, PM=260, EVE=175 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @75MW, LEYTE A @375MW, PGPP1 @76MW [WEBSMS] | CVIS
4/1/2024 5:35:06 AM | [NSO Update] Luzon Grid-04/01/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14321MW, PK=10901MW, RR=296MW, NetOpMargin: AM=3124, PM=2412, EVE=2223 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC1 @210MW, ILIJAN A @300MW [WEBSMS] | CLUZ
4/1/2024 4:20:25 AM | [NSO Update] Mindanao Grid-04/01/2024 04:24: Weather Update: Ridge of High Pressure Area (HPA) extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CMIN
4/1/2024 4:19:44 AM | [NSO Update] Visayas Grid-04/01/2024 04:19: Weather Update: Ridge of High Pressure Area (HPA) extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CVIS
4/1/2024 4:19:20 AM | [NSO Update] Luzon Grid-04/01/2024 04:19: Weather Update: Ridge of High Pressure Area (HPA) extending over the eastern sections of Northern and Central Luzon. [WEBSMS] | CLUZ
4/1/2024 1:54:35 AM | Luzon Grid-04/01/2024 01:54: Masinloc 3 online at 0152H (Planned Outage) [WEBSMS] | CLUZ
4/1/2024 1:29:41 AM | Visayas Grid-04/01/2024 01:29: PEDC U2 cut in at 0125H (Unplanned Outage) [WEBSMS] | CVIS
3/31/2024 11:17:48 PM | Mindanao Grid-03/31/2024 23:22: Agus6 Unit 2 Emergency shutdown at 2233H due to oil contamination of lower guide bearing. Unplanned outage. [WEBSMS] | CMIN
3/31/2024 9:47:04 PM | Luzon Grid-03/31/2024 21:47: Dasmarinas 600MVA T04 restored at 2146H (Planned Outage) [WEBSMS] | CLUZ
3/31/2024 9:42:36 PM | Luzon Grid-03/31/2024 21:42: Dasmarinas 500kV Bus 1 restored at 2141H (Planned Outage) [WEBSMS] | CLUZ
3/31/2024 7:06:57 PM | Luzon Grid-03/31/2024 19:07: San Jose-San Rafael 230KV Line restored at 1906H (Planned Outage) [WEBSMS] | CLUZ
3/31/2024 5:57:16 PM | [NSO Update] Luzon Grid-03/31/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13153MW, PK=9737MW, RR=330MW, NetOpMargin: EVE=13153 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC1 @200MW, ILIJAN A @ 300MW [WEBSMS] | CLUZ
3/31/2024 5:42:30 PM | [NSO Update] Mindanao Grid-03/31/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3191MW, PK=2177MW, RR=74MW, NetOpMargin: EVE=940 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @45MW, AG2 @56MW, AG4 @69MW, AG5 @22MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
3/31/2024 5:41:15 PM | [NSO Update] Visayas Grid-03/31/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2554MW, PK=2037MW, RR=86MW, NetOpMargin: EVE=432 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @75MW, LEYTE A @356MW, PGPP1 @76MW [WEBSMS] | CVIS
3/31/2024 5:16:20 PM | Mindanao Grid-03/31/2024 17:20: Davao SS 138kV Power Transformer 1 energized at 1713H (Planned Outage) [WEBSMS] | CMIN
3/31/2024 12:34:10 PM | [NSO Update] Luzon Grid-03/31/2024 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13835MW, PK=8748MW, RR=339MW, NetOpMargin: PM=4748, EVE=3450 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 1 @210MW [WEBSMS] | CLUZ
3/31/2024 12:28:52 PM | [NSO Update] Visayas Grid-03/31/2024 12:29: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2444MW, PK=1879MW, RR=89MW, NetOpMargin: PM=475, EVE=289 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @74MW, LEYTE A @372MW, PGPP1 @76MW [WEBSMS] | CVIS
3/31/2024 12:28:49 PM | [NSO Update] Mindanao Grid-03/31/2024 12:33: GRID UPDATE AS OF 1:00 PM System Condition: CAP=3246MW, PK=1936MW, RR=77MW, NetOpMargin: PM=1233, EVE=1013 Highest Unit O/L: GNPK 1,2,3 &4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @45MW, AG2 @56MW, AG4 @69MW, AG5 @22MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
3/31/2024 11:21:37 AM | Mindanao Grid-03/31/2024 11:26: Kibawe - Davao 138kV L1 restored at 1119H. (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 10:07:53 AM | Mindanao Grid-03/31/2024 10:12: Kibawe - Davao 138kV L1 de-energized at 1002H. (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 9:41:46 AM | Luzon Grid-03/31/2024 09:41: Ilijan 9-01CB04ILJ closed at 0939H (Unplanned Outage) [WEBSMS] | CLUZ
3/31/2024 9:03:32 AM | Luzon Grid-03/31/2024 09:03: Ilijan 9-01CB04ILJ opened at 0901H (Unplanned Outage) [WEBSMS] | CLUZ
3/31/2024 8:09:43 AM | Luzon Grid-03/31/2024 08:09: San Jose-San Rafael 230KV Line de-energized at 0807H (Planned Outage) [WEBSMS] | CLUZ
3/31/2024 5:36:02 AM | [NSO Update] Mindanao Grid-03/31/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3260MW, PK=1779MW, RR=75MW, NetOpMargin: AM=1405, PM=1339, EVE=1194 Highest Unit O/L: GNPK 1, 2, 3, &4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @45MW, AG2 @56MW, AG4 @69MW, AG5 @22MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
3/31/2024 5:31:36 AM | Visayas Grid-03/31/2024 05:31: Gahit - Barotac 230kV Line 1 looped at Barotac side at 0529H (Planned Outage) [WEBSMS] | CVIS
3/31/2024 5:30:28 AM | [NSO Update] Visayas Grid-03/31/2024 05:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2562MW, PK=1806MW, RR=87MW, NetOpMargin: AM=668, PM=636, EVE=510 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @79MW, LEYTE A @375MW, PGPP1 @76MW [WEBSMS] | CVIS
3/31/2024 5:26:57 AM | [NSO Update] Luzon Grid-03/31/2024 05:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14039MW, PK=8254MW, RR=327MW, NetOpMargin: AM=5458, PM=4908, EVE=3767 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC1 @210MW, ILIJAN A @300MW [WEBSMS] | CLUZ
3/31/2024 4:35:43 AM | [NSO Update] Mindanao Grid-03/31/2024 04:40: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
3/31/2024 4:34:49 AM | [NSO Update] Visayas Grid-03/31/2024 04:34: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
3/31/2024 4:34:18 AM | [NSO Update] Luzon Grid-03/31/2024 04:34: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
3/31/2024 3:54:45 AM | Visayas Grid-03/31/2024 03:54: Gahit - Barotac 230kV Line 1 energized at Gahit side at 0353H (Planned Outage) [WEBSMS] | CVIS
3/31/2024 3:10:57 AM | Visayas Grid-03/31/2024 03:11: Gahit - Barotac 230kV Line 1 de-energized at 0305H to rectify hotspot at shunt reactor PCB Barotac side (PLANNED OUTAGE) [WEBSMS] | CVIS
3/31/2024 2:56:09 AM | Visayas Grid-03/31/2024 02:56: Gahit - Barotac 230kV Line 1 energized at Gahit side at 0252H (Planned Outage) [WEBSMS] | CVIS
3/31/2024 2:49:08 AM | Mindanao Grid-03/31/2024 02:53: TALOMO 3 Unit 2 online at 0111H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 2:48:37 AM | Mindanao Grid-03/31/2024 02:53: TALOMO 3 Unit 1 online at 0112H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 2:48:00 AM | Mindanao Grid-03/31/2024 02:52: TALOMO 2B Unit 1 online at 0125H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 2:47:25 AM | Mindanao Grid-03/31/2024 02:51: TALOMO 2A Unit 2 online at 0121H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 2:46:54 AM | Mindanao Grid-03/31/2024 02:51: TALOMO 2A Unit 1 online at 0114H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 2:46:11 AM | Mindanao Grid-03/31/2024 02:50: TALOMO 2 Unit 3 online at 0125H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 2:45:34 AM | Mindanao Grid-03/31/2024 02:49: TALOMO 2 Unit 2 online at 0120H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 2:44:59 AM | Mindanao Grid-03/31/2024 02:49: TALOMO 2 Unit 1 online at 0114H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 2:42:10 AM | Mindanao Grid-03/31/2024 02:46: TALOMO 2 Unit 1 (0.12MW), Unit 2 (0.16MW), Unit 3 (0.14MW), TALOMO 2A Unit 1 (0.3MW), Unit 2 (0.1MW), TALOMO 2B Unit 1 (0.29MW), TALOMO 3 Unit 1 (0.8MW), Unit 2 (0.67MW) isolated at 0015H due to loss of feedback power brought by tripping of DLPC Tugbok Recloser 1 (Unplanned Outage, outside management control). [WEBSMS] | CMIN
3/31/2024 2:09:26 AM | Mindanao Grid-03/31/2024 02:13: TALOMO 2A Unit 1 (0.32MW), Unit 2 (0.1MW), TALOMO 2B Unit 1 (0.2MW) isolated at 2329H due to loss of feedback power brought by tripping of DLPC Tugbok Recloser 1 (Unplanned Outage, outside management control). [WEBSMS] | CMIN
3/31/2024 2:06:41 AM | Mindanao Grid-03/31/2024 02:11: TALOMO 2B Unit 1 online at 2323H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 2:05:52 AM | Mindanao Grid-03/31/2024 02:10: TALOMO 2A Unit 2 online at 2249H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 2:05:10 AM | Mindanao Grid-03/31/2024 02:09: TALOMO 2A Unit 1 online at 2241H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 1:18:16 AM | Mindanao Grid-03/31/2024 01:22: (Correction) LIBERTAD POWER online at 0008H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 1:11:53 AM | Mindanao Grid-03/31/2024 01:16: LIBERTAD POWER online at 0009H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 1:11:16 AM | Mindanao Grid-03/31/2024 01:15: LIBERTAD POWER with 6MW load tripped at 2354H (on houseload). Indication: 50LBB, Rate of Change of Freq. (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 12:33:35 AM | Mindanao Grid-03/31/2024 00:37: Baloi SS 138 kV Bus1 energized at 0029H from unplanned outage (F.O/Non-GOMP.) [WEBSMS] | CMIN
3/31/2024 12:32:15 AM | Mindanao Grid-03/31/2024 00:36: TALOMO 3 Unit 2 online at 2344H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 12:31:42 AM | Mindanao Grid-03/31/2024 00:36: TALOMO 3 Unit 1 online at 2348H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 12:31:00 AM | Mindanao Grid-03/31/2024 00:35: TALOMO 2B Unit 1 online at 2357H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 12:30:23 AM | Mindanao Grid-03/31/2024 00:34: TALOMO 2A Unit 2 online at 2349H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 12:29:46 AM | Mindanao Grid-03/31/2024 00:34: TALOMO 2A Unit 1 online at 2343H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 12:28:57 AM | Mindanao Grid-03/31/2024 00:33: TALOMO 2 Unit 3 online at 2347H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 12:28:26 AM | Mindanao Grid-03/31/2024 00:32: TALOMO 2 Unit 2 online at 2340H (Unplanned Outage) [WEBSMS] | CMIN
3/31/2024 12:27:41 AM | Mindanao Grid-03/31/2024 00:32: TALOMO 2 Unit 1 online at 2338H (Unplanned Outage) [WEBSMS] | CMIN
3/30/2024 11:53:38 PM | Mindanao Grid-03/30/2024 23:58: TALOMO 2 Unit 1 (0.12MW), Unit 2 (0.16MW), Unit 3 (0.14MW), TALOMO 2A Unit 1 (0.27MW), Unit 2 (0.1MW), TALOMO 2B Unit 1 (0.21MW), TALOMO 3 Unit 1 (0.74MW), Unit 2 (0.61MW) isolated at 2213H due to loss of feedback power brought by tripping of DLPC Tugbok Recloser 1 (Unplanned Outage) [WEBSMS] | CMIN
3/30/2024 10:53:30 PM | Mindanao Grid-03/30/2024 22:57: BUBUNAWAN online at 1606H (Unplanned Outage) [WEBSMS] | CMIN
3/30/2024 10:52:21 PM | Mindanao Grid-03/30/2024 22:56: (Correction) BUBUNAWAN Plant shutdown at 1342H due to low water river flow (Unplanned outage, outside management control). [WEBSMS] | CMIN
3/30/2024 10:50:56 PM | Mindanao Grid-03/30/2024 22:55: BUBUNAWAN Plant shutdown due to low water river flow (Unplanned outage, outside management control). [WEBSMS] | CMIN
3/30/2024 10:43:16 PM | Mindanao Grid-03/30/2024 22:47: BBM with 1.95MW load tripped at 0928H. Cause: Inclined Chain Conveyor Trouble (Unplanned Outage) [WEBSMS] | CMIN
3/30/2024 9:23:25 PM | Mindanao Grid-03/30/2024 21:27: Baloi SS 138 kV Bus1 de-energized at 2122H. F.O/Non-GOMP [WEBSMS] | CMIN
3/30/2024 7:31:29 PM | Luzon Grid-03/30/2024 19:31: Las Pinas SS 230kV Tie Line restored at 1922H (Planned Outage) [WEBSMS] | CLUZ
3/30/2024 7:30:36 PM | Luzon Grid-03/30/2024 19:30: Las Pinas SS 300MVA T01, T02, T03, T04, & T05 restored at 1918H, 1916H, 1916H, 1925H, & 1926H, respectively. (Planned Outage) [WEBSMS] | CLUZ
3/30/2024 7:26:22 PM | Luzon Grid-03/30/2024 19:26: Dasmarinas-Las Pinas 230kV Line 1 and 2 restored at 1916 and 1924H, respectively. (Planned Outage) [WEBSMS] | CLUZ
3/30/2024 5:46:37 PM | [NSO Update] Mindanao Grid-03/30/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3169MW, PK=2014MW, RR=74MW, NetOpMargin: EVE=1081 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @42MW, AG2 @36MW, AG4 @68MW, AG5 @20MW, AG6 @100MW, AG7 @19MW, PG4 @60MW [WEBSMS] | CMIN
3/30/2024 5:42:21 PM | [NSO Update] Visayas Grid-03/30/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2268MW, PK=1937MW, RR=86MW, NetOpMargin: EVE=245 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @74MW, LEYTE A @375MW, PGPP1 @76MW [WEBSMS] | CVIS
3/30/2024 5:40:28 PM | [NSO Update] Luzon Grid-03/30/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13164MW, PK=9460MW, RR=330MW, NetOpMargin: EVE=3375 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC1 @210MW, ILIJAN A @300MW [WEBSMS] | CLUZ
3/30/2024 12:33:34 PM | [NSO Update] Luzon Grid-03/30/2024 12:33: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14261MW, PK=9151MW, RR=338MW, NetOpMargin: PM=4772, EVE=3550 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 210MW, Ilijan A @ 300MW [WEBSMS] | CLUZ
3/30/2024 12:25:32 PM | [NSO Update] Visayas Grid-03/30/2024 12:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2391MW, PK=1855MW, RR=89MW, NetOpMargin: PM=447, EVE=420 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @74MW, LEYTE A @375MW, PGPP1 @76MW [WEBSMS] | CVIS
3/30/2024 12:25:09 PM | [NSO Update] Mindanao Grid-03/30/2024 12:29: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3229MW, PK=1986MW, RR=77MW, NetOpMargin: PM=1165, EVE=1033 Highest Unit O/L: GNPK 1,2,3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @42MW, AG2 @36MW, AG4 @68MW, AG5 @20MW, AG6 @100MW, AG7 @19MW, PG4 @60MW [WEBSMS] | CMIN
3/30/2024 10:40:11 AM | Mindanao Grid-03/30/2024 10:44: Agus-2 Kibawe 138 kV L2 tripped due to line to ground fault (CN) at 0927H and Agus2 U2 simultaneously tripped with 20.1 MW load. (Note Agus-2 Kibawe 138 kV L2 energized at tower # 33 only to prevent pilferage). Attempted to energized the line at 0947H but failed due to SOTF . Advised to conduct line patrol. Unplanned Outage [WEBSMS] | CMIN
3/30/2024 10:09:37 AM | Mindanao Grid-03/30/2024 10:14: AGUS 2 HEP Unit 2 online at 1007H (Unplanned Outage) [WEBSMS] | CMIN
3/30/2024 10:04:53 AM | Mindanao Grid-03/30/2024 10:09: Agus-2 Kibawe 138 kV L2 tripped due to line to ground fault (CN) at 0927H and Agus2 U3 simultaneously tripped with 20.1 MW load. (Note Agus-2 Kibawe 138 kV L2 energized at tower # 33 only to prevent pilferage). Attempted to energized the line at 0947H but failed due to SOTF . Advised at conduct line patrol. [WEBSMS] | CMIN
3/30/2024 10:04:09 AM | Mindanao Grid-03/30/2024 10:08: (Correction) AGUS 2 HEP Unit 2 with 20.1MW load tripped at 0927H. Indication: 86T, 5C. Frequency dipped at 59.72Hz. (Unplanned Outage) [WEBSMS] | CMIN
3/30/2024 9:56:49 AM | Mindanao Grid-03/30/2024 10:01: AGUS 2 HEP Unit 2 tripped at 0927H. Indication: 86T, 5C. Frequency dipped at 59.72Hz. (Unplanned Outage) [WEBSMS] | CMIN
3/30/2024 9:01:15 AM | Luzon Grid-03/30/2024 09:01: SLPGC 2 shutdown at 0858H (Unplanned Outage) [WEBSMS] | CLUZ
3/30/2024 7:24:09 AM | Luzon Grid-03/30/2024 07:24: Dasmarinas-Las Pinas 230kV Line 2 de-energized at 0710H (Planned Outage) [WEBSMS] | CLUZ
3/30/2024 7:22:29 AM | Luzon Grid-03/30/2024 07:22: Las Pinas SS 300MVA T01, T02, T03 & T04 unloop @ 230kV side at 0713H, 0716, 0717H and 0709H, respectively (Planned Outage). [WEBSMS] | CLUZ
3/30/2024 7:17:41 AM | Luzon Grid-03/30/2024 07:17: Dasmarinas-Las Pinas 230kV Line 1 de-energized at 0716H (Planned Outage) [WEBSMS] | CLUZ
3/30/2024 7:16:11 AM | Luzon Grid-03/30/2024 07:16: Las Pinas SS 230kV Tie Line de-energized at 0713H (Planned Outage) [WEBSMS] | CLUZ
3/30/2024 7:11:29 AM | Luzon Grid-03/30/2024 07:11: Las Pinas SS 300MVA T05 de-energized at 0708H (Planned Outage) [WEBSMS] | CLUZ
3/30/2024 6:21:44 AM | Mindanao Grid-03/30/2024 06:26: Davao SS Power Transformer 1_7XF01DAV, 150 MVA de-energized at 0619H. P.O/Non-GOMP. [WEBSMS] | CMIN
3/30/2024 5:59:12 AM | Luzon Grid-03/30/2024 05:59: Sual Unit 2 online at 0557H. (Planned Outage) [WEBSMS] | CLUZ
3/30/2024 5:50:26 AM | [NSO Update] Mindanao Grid-03/30/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3241MW, PK=1840MW, RR=75MW, NetOpMargin: AM=1326, PM=1269, EVE=1150 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @42MW, AG2 @36MW, AG4 @68MW, AG5 @20MW, AG6 @100MW, AG7 @19MW, PG4 @60MW [WEBSMS] | CMIN
3/30/2024 5:48:07 AM | [NSO Update] Visayas Grid-03/30/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1854MW, RR=87MW, NetOpMargin: AM=562, PM=339, EVE=171 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 74MW, Leyte A @ 375MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/30/2024 5:46:30 AM | [NSO Update] Luzon Grid-03/30/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13324MW, PK=8380MW, RR=321MW, NetOpMargin: AM=4622, PM=4135, EVE=2851 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 210MW, SLPGC 2 @ 46MW, Sual 1 @ 320MW, Ilijan A @ 300MW [WEBSMS] | CLUZ
3/30/2024 4:08:23 AM | [NSO Update] Mindanao Grid-03/30/2024 04:12: Weather Advisory: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
3/30/2024 4:07:40 AM | [NSO Update] Luzon Grid-03/30/2024 04:07: Weather Advisory: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
3/30/2024 4:06:23 AM | [NSO Update] Visayas Grid-03/30/2024 04:06: Weather Advisory: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
3/30/2024 1:04:20 AM | Luzon Grid-03/30/2024 01:04: For info: Laoag Solar PP completed the energization of their 35MVA T01 and 40MVA T02 at 0101H. [WEBSMS] | CLUZ
3/30/2024 12:17:38 AM | Luzon Grid-03/30/2024 00:17: Dasmarinas 600MVA T04 and Dasmarinas 500kV Bus 1 were de-energized at 0010H and 0014H respectively. (Planned Outage) [WEBSMS] | CLUZ
3/29/2024 8:48:00 PM | Visayas Grid-03/29/2024 20:48: PEDC U2 shutdown at 2042H (Unplanned Outage) [WEBSMS] | CVIS
3/29/2024 7:01:25 PM | Luzon Grid-03/29/2024 19:01: Nagsaag-San Jose 500kV line 2 was restored at 1858H. (Planned Outage) [WEBSMS] | CLUZ
3/29/2024 6:20:26 PM | Luzon Grid-03/29/2024 18:20: San Jose 300MVA T03 was looped at 115kV side at 1811H to momentarily parallel T01, T02, and T03. San Jose 300MVA T01 was un-looped from the 230kV side at 1812H. (San Jose 300MVA T02 and T03 were left paralleled.) [WEBSMS] | CLUZ
3/29/2024 5:52:44 PM | [NSO Update] Mindanao Grid-03/29/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3196MW, PK=1888MW, RR=74.3MW, NetOpMargin: EVE=1233 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @42MW, AG2 @55MW, AG4 @69MW, AG5 @22MW, AG6 @104MW, AG7 @19MW, PG4 @60MW [WEBSMS] | CMIN
3/29/2024 5:51:56 PM | [NSO Update] Visayas Grid-03/29/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2325MW, PK=1893MW, RR=86MW, NetOpMargin: EVE=346 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 74MW, Leyte A @ 368MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/29/2024 5:50:35 PM | [NSO Update] Luzon Grid-03/29/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12653MW, PK=8830MW, RR=356MW, NetOpMargin: EVE=3466 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 210MW, SLPGC 2 @ 46MW, Ilijan A @ 300MW [WEBSMS] | CLUZ
3/29/2024 4:00:01 PM | Visayas Grid-03/29/2024 16:00: URC U2 emergency shutdown at 1529H (Unplanned Outage) [WEBSMS] | CVIS
3/29/2024 2:46:52 PM | Mindanao Grid-03/29/2024 14:51: SMC Unit 1 online at 1432H. (Unplanned Outage) [WEBSMS] | CMIN
3/29/2024 2:26:40 PM | Luzon Grid-03/29/2024 14:26: Tayabas-Mauban 230kV line 1 was restored at 1425H. (Unplanned Outage) [WEBSMS] | CLUZ
3/29/2024 2:23:01 PM | Luzon Grid-03/29/2024 14:23: Tayabas-Mauban 230kV line 1 was de-energized at 1419H. (Unplanned Outage) [WEBSMS] | CLUZ
3/29/2024 1:52:35 PM | Luzon Grid-03/29/2024 13:52: For Info: San Jose 300MVA TO1 looped at primary side (230kV) and San Jose 300MVA TO3 unlopped at secondary side (115kV) at 1342H. [WEBSMS] | CLUZ
3/29/2024 1:42:31 PM | Luzon Grid-03/29/2024 13:42: Correction: Hermosa-San Jose 230kV Line restored at 1335H (Unplanned Outage) [WEBSMS] | CLUZ
3/29/2024 1:36:08 PM | Luzon Grid-03/29/2024 13:36: Hermosa-San Jose 230kV Line restored at 1035H (Unplanned Outage) [WEBSMS] | CLUZ
3/29/2024 1:31:53 PM | Luzon Grid-03/29/2024 13:31: For Info: San Jose 300MVA TO3 looped at secondary side (115kV) at 1326H due to unlooping San Jose 300MVA TO1 at primary side (230kV line) at 1319H. [WEBSMS] | CLUZ
3/29/2024 1:24:06 PM | Luzon Grid-03/29/2024 13:24: Hermosa-San Jose 230kV Line tripped at 1319H (Unplanned Outage) [WEBSMS] | CLUZ
3/29/2024 12:50:15 PM | [NSO Update] Luzon Grid-03/29/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13205MW, PK=8335MW, RR=309MW, NetOpMargin: PM=4562, EVE=3033 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC1 @210MW, SLPGC 2 @46MW, ILIJAN A @300MW [WEBSMS] | CLUZ
3/29/2024 12:32:29 PM | Luzon Grid-03/29/2024 12:32: Bacman 230kV Bus 2 restored at 1232H (Unplanned Outage) [WEBSMS] | CLUZ
3/29/2024 12:32:11 PM | [NSO Update] Visayas Grid-03/29/2024 12:32: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2596MW, PK=1602MW, RR=89MW, NetOpMargin: PM=904, EVE=475 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @74MW, LEYTE A @375MW, PGPP1 @76MW [WEBSMS] | CVIS
3/29/2024 10:31:34 AM | Luzon Grid-03/29/2024 10:31: Bacman 230kV Bus 2 de-energized at 1031H (Unplanned Outage) [WEBSMS] | CLUZ
3/29/2024 6:14:02 AM | Luzon Grid-03/29/2024 06:14: San Jose-Nagsaag 500kV Line 2 de-energized at 0611H (Planned Outage) [WEBSMS] | CLUZ
3/29/2024 5:56:19 AM | [NSO Update] Luzon Grid-03/29/2024 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13491MW, PK=8024MW, RR=295MW, NetOpMargin: AM=5172, PM=4994, EVE=3389 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @210MW, SLPGC 2 @46MW, ILIJAN A @300MW [WEBSMS] | CLUZ
3/29/2024 5:34:19 AM | [NSO Update] Mindanao Grid-03/29/2024 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3130MW, PK=1675MW, RR=75MW, NetOpMargin: AM=1379, PM=1309, EVE=1368 Highest Unit O/L: GNPK 1, 2, 3 & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @42MW, AG2 @55MW, AG4 @69MW, AG5 @22MW, AG6 @104MW, AG7 @19MW, PG4 @60MW [WEBSMS] | CMIN
3/29/2024 5:28:21 AM | [NSO Update] Visayas Grid-03/29/2024 05:28: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2492MW, PK=1678MW, RR=87MW, NetOpMargin: AM=727, PM=698, EVE=428 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @74MW, LEYTE A @375MW, PGPP1 @76MW [WEBSMS] | CVIS
3/29/2024 4:19:06 AM | [NSO Update] Mindanao Grid-03/29/2024 04:23: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
3/29/2024 4:18:47 AM | [NSO Update] Visayas Grid-03/29/2024 04:18: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
3/29/2024 4:16:55 AM | [NSO Update] Luzon Grid-03/29/2024 04:16: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
3/29/2024 12:04:06 AM | Mindanao Grid-03/29/2024 00:08: TALOMO 1 Unit 1 online at 2248H (Unplanned Outage) [WEBSMS] | CMIN
3/29/2024 12:03:24 AM | Mindanao Grid-03/29/2024 00:07: TALOMO 1 Unit 2 online at 2240H (Unplanned Outage) [WEBSMS] | CMIN
3/28/2024 10:48:56 PM | Mindanao Grid-03/28/2024 22:53: ALAMADA Hydro online at 1605H (Unplanned Outage) [WEBSMS] | CMIN
3/28/2024 10:47:09 PM | Mindanao Grid-03/28/2024 22:51: ALAMADA Hydro with 0.7MW load isolated at 1534H due to loss of feedback power brought by tripping of COTELCO P. Palma feeder. (Unplanned Outage) [WEBSMS] | CMIN
3/28/2024 10:42:10 PM | Mindanao Grid-03/28/2024 22:46: TALOMO 1 Unit 1 with 0.15MW load shutdown at 1739H due to clogged weir intake (Unplanned Outage) [WEBSMS] | CMIN
3/28/2024 10:41:12 PM | Mindanao Grid-03/28/2024 22:45: (Correction) TALOMO 1 Unit 2 with 0.10MW load shutdown at 1710H due to clogged weir intake (Unplanned Outage) [WEBSMS] | CMIN
3/28/2024 10:39:44 PM | Mindanao Grid-03/28/2024 22:44: TALOMO 1 Unit 1 with 0.15MW load shutdown at 1710H due to clogged weir intake (Unplanned Outage) [WEBSMS] | CMIN
3/28/2024 7:36:41 PM | [NSO Update] Visayas Grid-03/28/2024 19:36: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1927H with power going to Luzon [WEBSMS] | CVIS
3/28/2024 7:36:02 PM | [NSO Update] Luzon Grid-03/28/2024 19:36: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1927H with power going to Luzon [WEBSMS] | CLUZ
3/28/2024 7:27:38 PM | [NSO Update] Visayas Grid-03/28/2024 19:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1917H from reverse power direction [WEBSMS] | CVIS
3/28/2024 7:26:58 PM | [NSO Update] Luzon Grid-03/28/2024 19:27: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1917H from reverse power direction [WEBSMS] | CLUZ
3/28/2024 7:16:26 PM | Luzon Grid-03/28/2024 19:16: Bay 230kV Bus 1 restored at 1915H (Planned Outage) [WEBSMS] | CLUZ
3/28/2024 7:08:30 PM | [NSO Update] Mindanao Grid-03/28/2024 19:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1905H with power going to Visayas [WEBSMS] | CMIN
3/28/2024 7:07:07 PM | [NSO Update] Visayas Grid-03/28/2024 19:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1905H with power going to Visayas [WEBSMS] | CVIS
3/28/2024 6:57:13 PM | [NSO Update] Mindanao Grid-03/28/2024 19:01: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1852H from reverse power direction [WEBSMS] | CMIN
3/28/2024 6:56:21 PM | [NSO Update] Visayas Grid-03/28/2024 18:56: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1852H from reverse power direction [WEBSMS] | CVIS
3/28/2024 6:55:37 PM | [NSO Update] Luzon Grid-03/28/2024 18:55: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1852H from reverse power direction [WEBSMS] | CLUZ
3/28/2024 6:10:05 PM | Mindanao Grid-03/28/2024 18:14: Kibawe Tacurong 138 kV Line restored at 1807H from unplanned outage [WEBSMS] | CMIN
3/28/2024 5:57:39 PM | [NSO Update] Luzon Grid-03/28/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12545MW, PK=9500MW, RR=326MW, NetOpMargin: EVE=2719 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @210MW, SLPGC 2 @46MW, ILIJAN A @300MW [WEBSMS] | CLUZ
3/28/2024 5:46:12 PM | Luzon Grid-03/28/2024 17:46: San Jose-Nagsaag 500kV Line 1 restored at 1746H (Planned Outage) [WEBSMS] | CLUZ
3/28/2024 5:46:00 PM | [NSO Update] Mindanao Grid-03/28/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2995MW, PK=2016MW, RR=74.3MW, NetOpMargin: EVE=906 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @45MW, AG2 @56MW, AG4 @69MW, AG5 @22MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
3/28/2024 5:42:24 PM | [NSO Update] Visayas Grid-03/28/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2474MW, PK=2041MW, RR=86MW, NetOpMargin: EVE=347 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @369MW, PGPP1 @76MW [WEBSMS] | CVIS
3/28/2024 5:14:33 PM | Luzon Grid-03/28/2024 17:14: Masinloc-Bolo 230kV Line 1 restored at 1711H (Planned Outage) [WEBSMS] | CLUZ
3/28/2024 4:49:31 PM | [NSO Update] Mindanao Grid-03/28/2024 16:53: MO Initiated Market Intervention has been lifted today 28 March 2024 at 1630H for Luzon, Visayas and Mindanao. Market operation will resume starting interval 1640H. [WEBSMS] | CMIN
3/28/2024 4:48:21 PM | [NSO Update] Visayas Grid-03/28/2024 16:48: MO Initiated Market Intervention has been lifted today 28 March 2024 at 1630H for Luzon, Visayas and Mindanao. Market operation will resume starting interval 1640H. [WEBSMS] | CVIS
3/28/2024 4:46:39 PM | [NSO Update] Luzon Grid-03/28/2024 16:46: MO Initiated Market Intervention has been lifted today 28 March 2024 at 1630H for Luzon, Visayas and Mindanao. Market operation will resume starting interval 1640H. [WEBSMS] | CLUZ
3/28/2024 4:42:17 PM | Mindanao Grid-03/28/2024 16:46: LAMSAN BIOMASS online at 1612H (Unplanned Outage) [WEBSMS] | CMIN
3/28/2024 4:41:36 PM | Mindanao Grid-03/28/2024 16:45: LAMSAN BIOMASS with 13.5MW tripped at 1603H. Indication: 50N-non-directional earth fault, 67N-directional earth fault. (Unplanned Outage) [WEBSMS] | CMIN
3/28/2024 4:35:07 PM | [NSO Update] Mindanao Grid-03/28/2024 16:39: MO-initiated Market Intervention is issued today, 28 March 2024, for Luzon, Visayas, & Mindanao Grid for interval 1635H due to RTD generation failure. [WEBSMS] | CMIN
3/28/2024 4:33:26 PM | [NSO Update] Luzon Grid-03/28/2024 16:33: MO-initiated Market Intervention is issued today, 28 March 2024, for Luzon, Visayas, & Mindanao Grid for interval 1635H due to RTD generation failure. [WEBSMS] | CLUZ
3/28/2024 4:30:53 PM | [NSO Update] Visayas Grid-03/28/2024 16:30: MO-initiated Market Intervention is issued today, 28 March 2024, for Luzon, Visayas, & Mindanao Grid for interval 1635H due to RTD generation failure. [WEBSMS] | CVIS
3/28/2024 4:19:38 PM | Mindanao Grid-03/28/2024 16:23: SUPREME POWER MATI was about to cut-in to grid, however, was advised by DORECO to stop operation at 1430H (from Unplanned Outage). [WEBSMS] | CMIN
3/28/2024 4:16:40 PM | Mindanao Grid-03/28/2024 16:21: SUPREME POWER MATI with 3.25MW load isolated at 1350H due to loss of feedback power brought by tripping of Maco-Banaybanay 69 kV line (Unplanned Outage). [WEBSMS] | CMIN
3/28/2024 3:46:07 PM | Mindanao Grid-03/28/2024 15:50: Kibawe Tacurong 138 kV Line auto tripped at 1532H due to L2 L3 fault. (Unplanned Outage) [WEBSMS] | CMIN
3/28/2024 3:42:25 PM | Visayas Grid-03/28/2024 15:42: URC U1 cut in at 1536H (Unplanned Outage) [WEBSMS] | CVIS
3/28/2024 3:03:21 PM | Luzon Grid-03/28/2024 15:03: Hermosa PCB 8-03CB04HER restored at 1502H (Unplanned Outage) [WEBSMS] | CLUZ
3/28/2024 1:34:53 PM | [NSO Update] Mindanao Grid-03/28/2024 13:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3310MW, PK=1999MW, RR=77MW, NetOpMargin: PM=1234, EVE=952 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @45MW, AG2 @56MW, AG4 @69MW, AG5 @22MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
3/28/2024 1:29:00 PM | Mindanao Grid-03/28/2024 13:33: SMC Unit 1 emergency shutdown at 1325H due to repair of leakage at steam-drum low-down main isolation valve. (Unplanned Outage) [WEBSMS] | CMIN
3/28/2024 1:17:35 PM | [NSO Update] Visayas Grid-03/28/2024 13:17: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2790MW, PK=1844MW, RR=89MW, NetOpMargin: PM=857, EVE=389 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @72MW, LEYTE A @370MW, PGPP1 @76MW [WEBSMS] | CVIS
3/28/2024 1:16:31 PM | [NSO Update] Luzon Grid-03/28/2024 13:16: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13165MW, PK=8552MW, RR=336MW, NetOpMargin: PM=4277, EVE=3275 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @210MW, SLPGC 2 @46MW, ILIJAN A @300MW [WEBSMS] | CLUZ
3/28/2024 9:46:19 AM | Luzon Grid-03/28/2024 09:46: San Jose-Nagsaag 500kV Line 1 de-energized at 0945H (Planned Outage) [WEBSMS] | CLUZ
3/28/2024 9:34:16 AM | Luzon Grid-03/28/2024 09:34: San Jose 750MVA T01 restored at 0934H (Planned Outage) [WEBSMS] | CLUZ
3/28/2024 9:11:03 AM | Luzon Grid-03/28/2024 09:11: Commissioning of New Binan 300MVA T01 completed at 0909H. [WEBSMS] | CLUZ
3/28/2024 8:59:27 AM | Visayas Grid-03/28/2024 08:59: 69KV Lapu-Lapu- Poog Feeder #5 energized @0856H.( Planned Outage ) [WEBSMS] | CVIS
3/28/2024 8:43:55 AM | Luzon Grid-03/28/2024 08:43: New Binan 300MVA T01 successfully energized and looped at 0839H. On going commissioning test (Planned Outage) [WEBSMS] | CLUZ
3/28/2024 8:30:55 AM | [NSO Update] Mindanao Grid-03/28/2024 08:35: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0828H with power going to Mindanao [WEBSMS] | CMIN
3/28/2024 8:30:34 AM | [NSO Update] Visayas Grid-03/28/2024 08:30: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0828H with power going to Mindanao [WEBSMS] | CVIS
3/28/2024 8:21:53 AM | [NSO Update] Mindanao Grid-03/28/2024 08:26: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0818H from forward power direction [WEBSMS] | CMIN
3/28/2024 8:21:26 AM | [NSO Update] Visayas Grid-03/28/2024 08:21: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0818H from forward power direction [WEBSMS] | CVIS
3/28/2024 8:19:00 AM | [NSO Update] Visayas Grid-03/28/2024 08:19: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0817H with power going to Visayas [WEBSMS] | CVIS
3/28/2024 8:18:55 AM | [NSO Update] Luzon Grid-03/28/2024 08:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0817H with power going to Visayas [WEBSMS] | CLUZ
3/28/2024 8:14:05 AM | [NSO Update] Luzon Grid-03/28/2024 08:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0806H from forward power direction [WEBSMS] | CLUZ
3/28/2024 8:13:39 AM | [NSO Update] Visayas Grid-03/28/2024 08:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0806H from forward power direction [WEBSMS] | CVIS
3/28/2024 7:58:15 AM | Visayas Grid-03/28/2024 07:58: LEYTE A Maha B cut-in at 0752H. ( Planned Outage ) [WEBSMS] | CVIS
3/28/2024 7:22:44 AM | Visayas Grid-03/28/2024 07:22: 69KV Lapu-Lapu- Poog Feeder #5 de-energized @0608H.( Planned Outage ) [WEBSMS] | CVIS
3/28/2024 7:16:24 AM | Luzon Grid-03/28/2024 07:16: Bay 230kV Bus 1 de-energized at 0716H (Planned Outage) [WEBSMS] | CLUZ
3/28/2024 7:13:29 AM | Luzon Grid-03/28/2024 07:13: Hermosa PCB 8-03CB04HER emergency shutdown at 0711H due to low SF6 (Unplanned Outage) [WEBSMS] | CLUZ
3/28/2024 6:46:30 AM | Luzon Grid-03/28/2024 06:46: Masinloc-Bolo 230kV Line 1 de-energized at 0644H (Planned Outage) [WEBSMS] | CLUZ
3/28/2024 5:47:51 AM | [NSO Update] Mindanao Grid-03/28/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3303MW, PK=1943MW, RR=75MW, NetOpMargin: AM=1285, PM=1075, EVE=855 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @45MW, AG2 @56MW, AG4 @69MW, AG5 @22MW, AG6 @101MW, AG7 @20MW, PG4 @56MW [WEBSMS] | CMIN
3/28/2024 5:46:48 AM | [NSO Update] Visayas Grid-03/28/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2827MW, PK=1901MW, RR=87MW, NetOpMargin: AM=838, PM=678, EVE=467 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 375MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/28/2024 5:45:41 AM | [NSO Update] Luzon Grid-03/28/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13308MW, PK=7936MW, RR=295MW, NetOpMargin: AM=5077, PM=4533, EVE=3466 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 210MW, SLPGC 2 @ 46MW, Ilijan A @ 300MW [WEBSMS] | CLUZ
3/28/2024 4:14:21 AM | [NSO Update] Mindanao Grid-03/28/2024 04:18: Weather Advisory: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
3/28/2024 4:14:04 AM | [NSO Update] Visayas Grid-03/28/2024 04:14: Weather Advisory: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
3/28/2024 4:13:23 AM | [NSO Update] Luzon Grid-03/28/2024 04:13: Weather Advisory: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
3/28/2024 3:27:30 AM | Luzon Grid-03/28/2024 03:27: Cayanga Solar-Laoag Solar 230kV lines 1 and 2 were looped at Laoag Solar side at 0303H and 0320H respectively. (On-going energization of Laoag Solar PP as load) [WEBSMS] | CLUZ
3/28/2024 3:06:23 AM | Luzon Grid-03/28/2024 03:06: Binan 300MVA T02 was restored at 0306H. (Planned Outage) [WEBSMS] | CLUZ
3/28/2024 12:29:18 AM | [NSO Update] Visayas Grid-03/28/2024 00:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0027H with power going to Luzon. [WEBSMS] | CVIS
3/28/2024 12:29:06 AM | [NSO Update] Luzon Grid-03/28/2024 00:29: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0027H with power going to Luzon. [WEBSMS] | CLUZ
3/28/2024 12:18:11 AM | [NSO Update] Visayas Grid-03/28/2024 00:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0017H from reverse power direction. [WEBSMS] | CVIS
3/28/2024 12:17:55 AM | [NSO Update] Luzon Grid-03/28/2024 00:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0017H from reverse power direction. [WEBSMS] | CLUZ
3/28/2024 12:04:33 AM | [NSO Update] Mindanao Grid-03/28/2024 00:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0000H with power going to Visayas. [WEBSMS] | CMIN
3/28/2024 12:04:13 AM | [NSO Update] Visayas Grid-03/28/2024 00:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0000H with power going to Visayas. [WEBSMS] | CVIS
3/27/2024 11:35:57 PM | Visayas Grid-03/27/2024 23:35: Carcon-Sangi 34.5 KV L3 tripped/restored at 2329H/2333H Carcon side upon energization of Carcon-Sangi 34.5 KV L2 Carcon side (Unplanned Outage) [WEBSMS] | CVIS
3/27/2024 10:56:21 PM | Visayas Grid-03/27/2024 22:56: Carcon-Sangi 34.5 KV L3 looped at 2252H (Unplanned Outage) [WEBSMS] | CVIS
3/27/2024 10:49:29 PM | Visayas Grid-03/27/2024 22:49: Nasulo re-online at 2241H (Planned Outage) [WEBSMS] | CVIS
3/27/2024 10:38:46 PM | Visayas Grid-03/27/2024 22:38: Carcon-Sangi 34.5 KV L2L3 tripped at 2227H (Unplanned Outage) [WEBSMS] | CVIS
3/27/2024 9:59:56 PM | Luzon Grid-03/27/2024 21:59: San Jose SS 750MVA T01 de-energized at 2159H (Planned Outage) [WEBSMS] | CLUZ
3/27/2024 9:47:27 PM | [NSO Update] Mindanao Grid-03/27/2024 21:51: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2146H from forward power direction. [WEBSMS] | CMIN
3/27/2024 9:47:12 PM | [NSO Update] Visayas Grid-03/27/2024 21:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2146H from forward power direction. [WEBSMS] | CVIS
3/27/2024 9:41:54 PM | [NSO Update] Mindanao Grid-03/27/2024 21:46: MO Initiated Market Intervention has been lifted today 27 March 2024 at 2130H for Luzon, Visayas and Mindanao. Market operation will resume starting interval 2140H. [WEBSMS] | CMIN
3/27/2024 9:41:40 PM | [NSO Update] Visayas Grid-03/27/2024 21:41: MO Initiated Market Intervention has been lifted today 27 March 2024 at 2130H for Luzon, Visayas and Mindanao. Market operation will resume starting interval 2140H. [WEBSMS] | CVIS
3/27/2024 9:41:23 PM | [NSO Update] Luzon Grid-03/27/2024 21:41: MO Initiated Market Intervention has been lifted today 27 March 2024 at 2130H for Luzon, Visayas and Mindanao. Market operation will resume starting interval 2140H. [WEBSMS] | CLUZ
3/27/2024 9:38:51 PM | [NSO Update] Mindanao Grid-03/27/2024 21:43: MO-initiated Market Intervention is issued today, 27 March 2024, for Luzon, Visayas, & Mindanao Grid for interval 2135H due to RTD generation failure. [WEBSMS] | CMIN
3/27/2024 9:38:23 PM | [NSO Update] Visayas Grid-03/27/2024 21:38: MO-initiated Market Intervention is issued today, 27 March 2024, for Luzon, Visayas, & Mindanao Grid for interval 2135H due to RTD generation failure. [WEBSMS] | CVIS
3/27/2024 9:38:03 PM | [NSO Update] Luzon Grid-03/27/2024 21:38: MO-initiated Market Intervention is issued today, 27 March 2024, for Luzon, Visayas, & Mindanao Grid for interval 2135H due to RTD generation failure. [WEBSMS] | CLUZ
3/27/2024 9:29:07 PM | Visayas Grid-03/27/2024 21:29: EDC-Mahanagdong U3 tripped at 2124H. (Unplanned Outage) [WEBSMS] | CVIS
3/27/2024 8:20:24 PM | Mindanao Grid-03/27/2024 20:24: AGUS4 Unit 3 shutdown at 2008H due to OMC-low forebay elevation. Unplanned Outage. [WEBSMS] | CMIN
3/27/2024 8:18:22 PM | [NSO Update] Visayas Grid-03/27/2024 20:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2017H with power going to Visayas. [WEBSMS] | CVIS
3/27/2024 8:18:07 PM | [NSO Update] Luzon Grid-03/27/2024 20:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2017H with power going to Visayas. [WEBSMS] | CLUZ
3/27/2024 8:17:34 PM | Luzon Grid-03/27/2024 20:17: Binan SS 300MVA T02 de-energized at 2017H (Planned Outage) [WEBSMS] | CLUZ
3/27/2024 8:04:56 PM | [NSO Update] Visayas Grid-03/27/2024 20:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2004H from forward power direction. [WEBSMS] | CVIS
3/27/2024 8:04:40 PM | [NSO Update] Luzon Grid-03/27/2024 20:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2004H from forward power direction. [WEBSMS] | CLUZ
3/27/2024 7:45:40 PM | Mindanao Grid-03/27/2024 19:49: WMPC DG10 shutdown at 1944H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/27/2024 6:04:31 PM | [NSO Update] Visayas Grid-03/27/2024 18:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1803H with power going to Luzon. [WEBSMS] | CVIS
3/27/2024 6:04:13 PM | [NSO Update] Luzon Grid-03/27/2024 18:04: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1803H with power going to Luzon. [WEBSMS] | CLUZ
3/27/2024 5:53:42 PM | [NSO Update] Mindanao Grid-03/27/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3227MW, PK=2290MW, RR=74.3MW, NetOpMargin: EVE=862 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @44MW, AG2 @60MW, AG4 @90MW, AG5 @22MW, AG6 @106MW, AG7 @20MW, PG4 @60MW [WEBSMS] | CMIN
3/27/2024 5:52:58 PM | Luzon Grid-03/27/2024 17:52: Bolo SS 600MVA T03 restored at 1751H (Planned Outage) [WEBSMS] | CLUZ
3/27/2024 5:52:46 PM | [NSO Update] Visayas Grid-03/27/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2655MW, PK=2142MW, RR=86MW, NetOpMargin: EVE=426 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 74MW, Leyte A @ 368MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/27/2024 5:51:40 PM | [NSO Update] Luzon Grid-03/27/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12517MW, PK=10068MW, RR=290MW, NetOpMargin: EVE=2159 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 210MW, Ilijan A @ 230MW [WEBSMS] | CLUZ
3/27/2024 5:46:31 PM | Mindanao Grid-03/27/2024 17:50: WMPC DG07 shutdown at 1743H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/27/2024 5:42:35 PM | [NSO Update] Visayas Grid-03/27/2024 17:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1740H from forward power direction. [WEBSMS] | CVIS
3/27/2024 5:42:02 PM | [NSO Update] Luzon Grid-03/27/2024 17:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1740H from forward power direction. [WEBSMS] | CLUZ
3/27/2024 2:02:38 PM | Mindanao Grid-03/27/2024 14:06: AGUS2 U2 online at 1350H. Planned Outage (GOMP) [WEBSMS] | CMIN
3/27/2024 1:12:36 PM | [NSO Update] Mindanao Grid-03/27/2024 13:16: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3279MW, PK=2495MW, RR=77MW, NetOpMargin: PM=707, EVE=644 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @44MW, AG2 @65MW, AG4 @90MW, AG5 @22MW, AG6 @106MW, AG7 @20MW, PG4 @60MW [WEBSMS] | CMIN
3/27/2024 1:11:48 PM | Luzon Grid-03/27/2024 13:11: GMEC Unit 1 online at 1309H (Unplanned Outage) [WEBSMS] | CLUZ
3/27/2024 1:10:54 PM | [NSO Update] Visayas Grid-03/27/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2721MW, PK=2256MW, RR=89MW, NetOpMargin: PM=376, EVE=325 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @72MW, LEYTE A @370MW, PGPP1 @76MW [WEBSMS] | CVIS
3/27/2024 1:06:30 PM | [NSO Update] Luzon Grid-03/27/2024 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13140MW, PK=11157MW, RR=352MW, NetOpMargin: PM=1631, EVE=1480 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 1 @210MW, ILIJAN A @230MW [WEBSMS] | CLUZ
3/27/2024 12:43:16 PM | Mindanao Grid-03/27/2024 12:47: WMPC DG07 online at 1241H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/27/2024 10:41:38 AM | Visayas Grid-03/27/2024 10:41: Complete loop Calatrava - Cadiz 230kV Line 2 in Cadiz side at 1037H. [WEBSMS] | CVIS
3/27/2024 10:12:11 AM | Mindanao Grid-03/27/2024 10:16: AGUS4 U3 online at 1000H. (Unplanned Outage). [WEBSMS] | CMIN
3/27/2024 10:06:05 AM | Visayas Grid-03/27/2024 10:06: Successfully energized 230kV Cadiz - Calatrava 230kV Line 2 at Calatrava side at 1001H. [WEBSMS] | CVIS
3/27/2024 9:33:21 AM | Mindanao Grid-03/27/2024 09:37: WMPC DG10 online at 0930H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/27/2024 8:58:41 AM | Luzon Grid-03/27/2024 08:58: Bolo SS 600MVA T03 de-energized at 0858H (Planned Outage) [WEBSMS] | CLUZ
3/27/2024 6:07:41 AM | [NSO Update] Luzon Grid-03/27/2024 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13224MW, PK=11334MW, RR=331MW, NetOpMargin: AM=1559, PM=1893, EVE=1996 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 1 @210MW, ILIJAN A @230MW [WEBSMS] | CLUZ
3/27/2024 5:29:04 AM | [NSO Update] Visayas Grid-03/27/2024 05:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2880MW, PK=2330MW, RR=92MW, NetOpMargin: AM=458, PM=488, EVE=522 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @72MW, LEYTE A @370MW, PGPP1 @76MW [WEBSMS] | CVIS
3/27/2024 5:28:02 AM | [NSO Update] Mindanao Grid-03/27/2024 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3284MW, PK=2358MW, RR=75MW, NetOpMargin: AM=851, PM=804, EVE=905 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @44MW, AG2 @65MW, AG4 @72MW, AG5 @22MW, AG6 @106MW, AG7 @20MW, PG4 @60MW [WEBSMS] | CMIN
3/27/2024 4:05:37 AM | [NSO Update] Luzon Grid-03/27/2024 04:05: Weather Advisory: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
3/27/2024 4:05:32 AM | [NSO Update] Visayas Grid-03/27/2024 04:05: Weather Advisory: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
3/27/2024 4:05:17 AM | [NSO Update] Mindanao Grid-03/27/2024 04:09: Weather Advisory: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
3/27/2024 2:45:48 AM | Luzon Grid-03/27/2024 02:46: Correction: Masinloc 1 with 274MW load tripped at 0230H. Lowest Freq=59.55Hz. (Unplanned Outage) [WEBSMS] | CLUZ
3/27/2024 2:43:47 AM | Luzon Grid-03/27/2024 02:44: Masinloc 3 with 274MW tripped at 0230H. Lowest Freq=59.55Hz (Unplanned Outage) [WEBSMS] | CLUZ
3/26/2024 11:43:21 PM | Luzon Grid-03/26/2024 23:43: Sual 2 shutdown at 2341H (Unplanned Outage). [WEBSMS] | CLUZ
3/26/2024 9:09:23 PM | [NSO Update] Luzon Grid-03/26/2024 21:09: MO-initiated Market Intervention is issued today, 26 March 2024, for Luzon, Visayas, & Mindanao Grid for intervals 1930H to 1940 due to RTD failure to publish results. Market resumption on interval 1945H. [WEBSMS] | CLUZ
3/26/2024 9:09:01 PM | [NSO Update] Visayas Grid-03/26/2024 21:09: undefined at 2100H MO-initiated Market Intervention is issued today, 26 March 2024, for Luzon, Visayas, & Mindanao Grid for intervals 1930H to 1940 due to RTD failure to publish results. Market resumption on interval 1945H. [WEBSMS] | CVIS
3/26/2024 9:08:48 PM | [NSO Update] Mindanao Grid-03/26/2024 21:13: undefined at 2100H MO-initiated Market Intervention is issued today, 26 March 2024, for Luzon, Visayas, & Mindanao Grid for intervals 1930H to 1940 due to RTD failure to publish results. Market resumption on interval 1945H. [WEBSMS] | CMIN
3/26/2024 8:14:04 PM | [NSO Update] Visayas Grid-03/26/2024 20:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2013H with power going to Luzon. [WEBSMS] | CVIS
3/26/2024 8:13:49 PM | [NSO Update] Luzon Grid-03/26/2024 20:14: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 2013H with power going to Luzon. [WEBSMS] | CLUZ
3/26/2024 8:07:18 PM | [NSO Update] Visayas Grid-03/26/2024 20:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2003H from reverse power direction. [WEBSMS] | CVIS
3/26/2024 8:07:14 PM | [NSO Update] Luzon Grid-03/26/2024 20:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 2003H from reverse power direction. [WEBSMS] | CLUZ
3/26/2024 7:54:35 PM | Luzon Grid-03/26/2024 19:55: Commissioning of new Main protection for Bay-Makban B 230kV L1 completed at 1949H [WEBSMS] | CLUZ
3/26/2024 7:48:06 PM | Mindanao Grid-03/26/2024 19:52: WMPC DG10 end of RPS and converted to EN=3.8MW (spot market) at 1945H. [WEBSMS] | CMIN
3/26/2024 7:15:23 PM | Luzon Grid-03/26/2024 19:15: Bay-Makban B 230kV L1 energized at 1914H. Ongoing commissioning of new Main protection (Planned Outage) [WEBSMS] | CLUZ
3/26/2024 6:57:22 PM | Mindanao Grid-03/26/2024 19:02: WMPC DG06 shutdown at 1850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/26/2024 6:08:05 PM | Mindanao Grid-03/26/2024 18:12: WMPC DG07 shutdown at 1644H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/26/2024 6:07:25 PM | [NSO Update] Visayas Grid-03/26/2024 18:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1806H with power going to Visayas. [WEBSMS] | CVIS
3/26/2024 6:06:55 PM | [NSO Update] Luzon Grid-03/26/2024 18:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1806H with power going to Visayas. [WEBSMS] | CLUZ
3/26/2024 5:58:15 PM | [NSO Update] Luzon Grid-03/26/2024 17:58: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1756H from forward power direction. [WEBSMS] | CLUZ
3/26/2024 5:57:43 PM | [NSO Update] Visayas Grid-03/26/2024 17:58: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1756H from forward power direction. [WEBSMS] | CVIS
3/26/2024 5:45:22 PM | [NSO Update] Luzon Grid-03/26/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12927MW, PK=10959MW, RR=290MW, NetOpMargin: EVE=1677 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 1 @150MW, MASINLOC 1 @315MW, ILIJAN A @165MW [WEBSMS] | CLUZ
3/26/2024 5:44:14 PM | Luzon Grid-03/26/2024 17:44: System Advisory: The Highest Luzon Grid Peak Load for the year 2024 is 11,687MW occurred at 1417H today, March 26, 2024, Tuesday. The previous highest peak was 11,615MW which occurred yesterday March 25, 2024, Monday at 1433H. [WEBSMS] | CLUZ
3/26/2024 5:33:35 PM | [NSO Update] Visayas Grid-03/26/2024 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2608MW, PK=2187MW, RR=86MW, NetOpMargin: EVE=335 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @67MW, LEYTE A @342MW, PGPP1 @76MW [WEBSMS] | CVIS
3/26/2024 5:33:32 PM | [NSO Update] Mindanao Grid-03/26/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3198MW, PK=2396MW, RR=72MW, NetOpMargin: EVE=729 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @45MW, AG2 @40MW, AG4 @74MW, AG5 @23MW, AG6 @109MW, AG7 @21MW, PG4 @60MW [WEBSMS] | CMIN
3/26/2024 5:19:45 PM | [NSO Update] Visayas Grid-03/26/2024 17:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1715H with power going to Luzon. [WEBSMS] | CVIS
3/26/2024 5:19:41 PM | [NSO Update] Luzon Grid-03/26/2024 17:20: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1715H with power going to Luzon. [WEBSMS] | CLUZ
3/26/2024 5:06:15 PM | [NSO Update] Luzon Grid-03/26/2024 17:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1705H from reverse power direction. [WEBSMS] | CLUZ
3/26/2024 5:06:09 PM | [NSO Update] Visayas Grid-03/26/2024 17:06: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1705H from reverse power direction. [WEBSMS] | CVIS
3/26/2024 5:00:58 PM | Luzon Grid-03/26/2024 17:01: Ilijan ST1 online at 1659H (Unplanned Outage) [WEBSMS] | CLUZ
3/26/2024 4:50:10 PM | Visayas Grid-03/26/2024 16:50: Colon-Toledo 138KV Line energized 1650H.(Planned Outage) [WEBSMS] | CVIS
3/26/2024 4:49:34 PM | Luzon Grid-03/26/2024 16:50: MPGC 2 online at 1648H (Planned Outage) [WEBSMS] | CLUZ
3/26/2024 3:42:19 PM | Mindanao Grid-03/26/2024 15:47: ASIGA Hydro online at 1517H (Unplanned Outage) [WEBSMS] | CMIN
3/26/2024 3:35:36 PM | [NSO Update] Luzon Grid-03/26/2024 15:36: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1533H with power going to Visayas. [WEBSMS] | CLUZ
3/26/2024 3:34:55 PM | [NSO Update] Visayas Grid-03/26/2024 15:35: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1533H with power going to Visayas [WEBSMS] | CVIS
3/26/2024 3:06:17 PM | Luzon Grid-03/26/2024 15:06: Ilijan GT1-2 online at 1459H (Unplanned Outage) [WEBSMS] | CLUZ
3/26/2024 2:54:07 PM | Mindanao Grid-03/26/2024 14:58: LAKE MAINIT Hydro online at 1442H (Unplanned Outage) [WEBSMS] | CMIN
3/26/2024 2:51:05 PM | Mindanao Grid-03/26/2024 14:55: ASIGA Hydro with 4MW load isolated again at 1347H due to loss of feedback power brought by tripping of customer-owned Butuan-Santiago 69 kV line (Unplanned Outage). [WEBSMS] | CMIN
3/26/2024 2:48:40 PM | Mindanao Grid-03/26/2024 14:53: ASIGA Hydro online at 1338H (Unplanned Outage) [WEBSMS] | CMIN
3/26/2024 2:45:04 PM | [NSO Update] Visayas Grid-03/26/2024 14:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1444H from forward power direction. [WEBSMS] | CVIS
3/26/2024 2:44:59 PM | [NSO Update] Luzon Grid-03/26/2024 14:45: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1444H from forward power direction. [WEBSMS] | CLUZ
3/26/2024 2:01:58 PM | Mindanao Grid-03/26/2024 14:06: WMPC DG02 declared available at 1400H. [WEBSMS] | CMIN
3/26/2024 1:56:50 PM | Mindanao Grid-03/26/2024 14:01: ASIGA Hydro with 4MW load isolated at 1300H due to loss of feedback power brought by tripping of customer-owned Butuan-Santiago 69 kV line (Unplanned Outage). [WEBSMS] | CMIN
3/26/2024 1:55:59 PM | Mindanao Grid-03/26/2024 14:00: LAKE MAINIT Hydro with 17MW load isolated at 1300H due to loss of feedback power brought by tripping of customer-owned Butuan-Santiago 69 kV line (Unplanned Outage). [WEBSMS] | CMIN
3/26/2024 1:42:40 PM | Luzon Grid-03/26/2024 13:43: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1342H. (Planned Outage) [WEBSMS] | CLUZ
3/26/2024 1:14:56 PM | Mindanao Grid-03/26/2024 13:19: WMPC DG07 online at 1312H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/26/2024 12:54:06 PM | [NSO Update] Mindanao Grid-03/26/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3258MW, PK=2456MW, RR=77MW, NetOpMargin: PM=725, EVE=758 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @45MW, AG2 @40MW, AG4 @74MW, AG5 @23MW, AG6 @109MW, AG7 @21MW, PG4 @60MW [WEBSMS] | CMIN
3/26/2024 12:53:09 PM | [NSO Update] Visayas Grid-03/26/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2726MW, PK=2250MW, RR=89MW, NetOpMargin: PM=387, EVE=387 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @67MW, LEYTE A @335MW, PGPP1 @76MW [WEBSMS] | CVIS
3/26/2024 12:51:39 PM | [NSO Update] Luzon Grid-03/26/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13690MW, PK=11284MW, RR=352MW, NetOpMargin: PM=2054, EVE=2037 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @200MW, MSLC1 @315MW [WEBSMS] | CLUZ
3/26/2024 12:32:19 PM | [NSO Update] Visayas Grid-03/26/2024 12:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1227H with power going to Luzon [WEBSMS] | CVIS
3/26/2024 12:32:01 PM | [NSO Update] Luzon Grid-03/26/2024 12:32: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1227H with power going to Luzon [WEBSMS] | CLUZ
3/26/2024 12:17:57 PM | [NSO Update] Visayas Grid-03/26/2024 12:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1211H from forward power direction [WEBSMS] | CVIS
3/26/2024 12:17:19 PM | [NSO Update] Luzon Grid-03/26/2024 12:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1211H from forward power direction [WEBSMS] | CLUZ
3/26/2024 10:03:58 AM | Mindanao Grid-03/26/2024 10:08: WMPC DG06 online at 1000H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/26/2024 9:52:28 AM | [NSO Update] Visayas Grid-03/26/2024 09:52: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0950H with power going to Luzon [WEBSMS] | CVIS
3/26/2024 9:52:06 AM | [NSO Update] Luzon Grid-03/26/2024 09:52: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0950H with power going to Luzon [WEBSMS] | CLUZ
3/26/2024 9:46:06 AM | [NSO Update] Visayas Grid-03/26/2024 09:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0937H from reverse power direction [WEBSMS] | CVIS
3/26/2024 9:45:42 AM | [NSO Update] Luzon Grid-03/26/2024 09:46: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0937H from reverse power direction [WEBSMS] | CLUZ
3/26/2024 9:44:11 AM | Luzon Grid-03/26/2024 09:44: Ilijan B GT2-2 online at 0943H. (Unplanned Outage) [WEBSMS] | CLUZ
3/26/2024 9:18:29 AM | Luzon Grid-03/26/2024 09:18: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0917H. (Planned Outage) [WEBSMS] | CLUZ
3/26/2024 9:03:25 AM | [NSO Update] Mindanao Grid-03/26/2024 09:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0901H with power going to Visayas [WEBSMS] | CMIN
3/26/2024 9:02:59 AM | [NSO Update] Visayas Grid-03/26/2024 09:03: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0901H with power going to Visayas [WEBSMS] | CVIS
3/26/2024 8:37:25 AM | Luzon Grid-03/26/2024 08:37: Masinloc 3 shutdown at 0834H. (Planned Outage) [WEBSMS] | CLUZ
3/26/2024 8:26:20 AM | [NSO Update] Visayas Grid-03/26/2024 08:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0825H with power going to Visayas [WEBSMS] | CVIS
3/26/2024 8:26:01 AM | [NSO Update] Luzon Grid-03/26/2024 08:26: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 0825H with power going to Visayas [WEBSMS] | CLUZ
3/26/2024 8:18:30 AM | [NSO Update] Luzon Grid-03/26/2024 08:18: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0815H from forward power direction [WEBSMS] | CLUZ
3/26/2024 8:16:55 AM | [NSO Update] Visayas Grid-03/26/2024 08:17: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 0815H from forward power direction [WEBSMS] | CVIS
3/26/2024 7:57:14 AM | Luzon Grid-03/26/2024 07:57: Ilijan B ST-2 online at 0756H. (Unplanned Outage) [WEBSMS] | CLUZ
3/26/2024 7:56:01 AM | Visayas Grid-03/26/2024 07:56: Colon-Toledo 138KV Line de-energized 0735H.(Planned Outage) [WEBSMS] | CVIS
3/26/2024 7:07:14 AM | [NSO Update] Visayas Grid-03/26/2024 07:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0702H from forward power direction. [WEBSMS] | CVIS
3/26/2024 7:06:58 AM | [NSO Update] Mindanao Grid-03/26/2024 07:11: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0702H from forward power direction. [WEBSMS] | CMIN
3/26/2024 6:37:02 AM | Luzon Grid-03/26/2024 06:37: Binan 300MVA T03 restored at 0637H. (Planned Outage) [WEBSMS] | CLUZ
3/26/2024 6:34:20 AM | Luzon Grid-03/26/2024 06:34: SCPC 2 online at 0632H. (Unplanned Outage) [WEBSMS] | CLUZ
3/26/2024 6:14:54 AM | Luzon Grid-03/26/2024 06:15: Ilijan B GT2-1 online at 0612H. (Unplanned Outage) [WEBSMS] | CLUZ
3/26/2024 5:44:03 AM | [NSO Update] Luzon Grid-03/26/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13530MW, PK=11130MW, RR=341MW, NetOpMargin: AM=2059, PM=1813, EVE=1554 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC1 @200MW, MSLC1 @315MW, MSLC3 @120MW [WEBSMS] | CLUZ
3/26/2024 5:34:22 AM | [NSO Update] Visayas Grid-03/26/2024 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2875MW, PK=2196MW, RR=87MW, NetOpMargin: AM=592, PM=577, EVE=407 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @67MW, LEYTE A @348MW, PGPP1 @76MW [WEBSMS] | CVIS
3/26/2024 5:33:51 AM | [NSO Update] Mindanao Grid-03/26/2024 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3288MW, PK=2402MW, RR=75MW, NetOpMargin: AM=811, PM=715, EVE=787 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @45MW, AG2 @60MW, AG4 @74MW, AG5 @23MW, AG6 @109MW, AG7 @21MW, PG4 @60MW [WEBSMS] | CMIN
3/26/2024 4:01:16 AM | [NSO Update] Mindanao Grid-03/26/2024 04:06: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
3/26/2024 4:01:05 AM | [NSO Update] Visayas Grid-03/26/2024 04:01: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
3/26/2024 4:00:48 AM | [NSO Update] Luzon Grid-03/26/2024 04:01: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
3/26/2024 3:36:58 AM | Luzon Grid-03/26/2024 03:37: San Jose SS 83 MVA T01 (CO) restored at 0334H (Planned Outage) [WEBSMS] | CLUZ
3/26/2024 12:50:35 AM | Luzon Grid-03/26/2024 00:51: San Jose 83MVA T01 de-energized at 0049H (Planned Outage) [WEBSMS] | CLUZ
3/25/2024 10:24:41 PM | Luzon Grid-03/25/2024 22:25: Bay SS 230 kV Bus 2 restored at 2224H (Planned Outage) [WEBSMS] | CLUZ
3/25/2024 9:46:05 PM | Luzon Grid-03/25/2024 21:46: Binan 300MVA T03 de-energized at 2146H (Planned Outage) [WEBSMS] | CLUZ
3/25/2024 9:37:10 PM | Mindanao Grid-03/25/2024 21:41: WMPC DG10 cut-out at 2013H from RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/25/2024 8:12:35 PM | Luzon Grid-03/25/2024 20:13: Bolo-Cayanga 230kV Line 1 restored at 2012H (Planned Outage) [WEBSMS] | CLUZ
3/25/2024 7:29:38 PM | Luzon Grid-03/25/2024 19:30: System Advisory: The Highest Luzon Grid Peak Load for the year 2024 is 11,615MW occurred at 1433H today, March 25, 2024, Monday. The previous highest peak was 11,595MW which occurred last March 06, 2024, Wednesday at 1451H. [WEBSMS] | CLUZ
3/25/2024 7:14:46 PM | Mindanao Grid-03/25/2024 19:19: WMPC DG06 shutdown at 1913H from RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/25/2024 7:01:17 PM | Mindanao Grid-03/25/2024 19:06: TM2 U1 shutdown at 1831H from MO Dispatched. Follow RTD. [WEBSMS] | CMIN
3/25/2024 6:36:32 PM | Mindanao Grid-03/25/2024 18:41: WMPC DG06 online at 1818H as RPS replacement for WMPC DG02. [WEBSMS] | CMIN
3/25/2024 6:25:33 PM | Mindanao Grid-03/25/2024 18:30: TM2 U1 online at 1801H. MO Dispatched. [WEBSMS] | CMIN
3/25/2024 5:50:44 PM | [NSO Update] Mindanao Grid-03/25/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3224MW, PK=2358MW, RR=74MW, NetOpMargin: EVE=792 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @46MW, AG2 @61MW, AG4 @76MW, AG5 @23MW, AG6 @111MW, AG7 @21MW, PG4 @60MW [WEBSMS] | CMIN
3/25/2024 5:50:39 PM | [NSO Update] Visayas Grid-03/25/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2694MW, PK=2058MW, RR=86MW, NetOpMargin: EVE=549 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @79.5MW, LEYTE A @348MW, PGPP1 @76MW [WEBSMS] | CVIS
3/25/2024 5:50:33 PM | [NSO Update] Luzon Grid-03/25/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12652MW, PK=11016MW, RR=370MW, NetOpMargin: EVE=1266 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 220MW, Masinloc 1 @ 315MW, Masinloc 3 @ 305MW [WEBSMS] | CLUZ
3/25/2024 5:19:46 PM | Mindanao Grid-03/25/2024 17:24: Toril - Matanao 138kV Line 2 energized & looped at 1715H. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
3/25/2024 4:55:51 PM | Mindanao Grid-03/25/2024 17:00: TM2 U1 shutdown at 1648H from MO Dispatched. Follow RTD. [WEBSMS] | CMIN
3/25/2024 4:49:59 PM | Mindanao Grid-03/25/2024 16:54: WMPC DG06 shutdown at 1644H from RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/25/2024 4:46:56 PM | Mindanao Grid-03/25/2024 16:51: WMPC DG04 and DG07 shutdown at 1622H from MO dispatched. Follow RTD. [WEBSMS] | CMIN
3/25/2024 4:10:45 PM | Mindanao Grid-03/25/2024 16:15: Peak Power SOCCSARGEN Shutdown at 1607H, from MO Dispatched. Follow RTD. [WEBSMS] | CMIN
3/25/2024 3:31:43 PM | Mindanao Grid-03/25/2024 15:36: WMPC DG04 online at 1529H. MO dispatched. [WEBSMS] | CMIN
3/25/2024 3:19:53 PM | Mindanao Grid-03/25/2024 15:24: Peak Power SOCCSARGEN Online at 1515H, MO Dispatched. [WEBSMS] | CMIN
3/25/2024 3:07:57 PM | Mindanao Grid-03/25/2024 15:12: TM2 U1 online at 1501H. MO Dispatched. [WEBSMS] | CMIN
3/25/2024 2:42:09 PM | Mindanao Grid-03/25/2024 14:46: WMPC DG07 online at 1439H. MO dispatched. [WEBSMS] | CMIN
3/25/2024 2:29:53 PM | Luzon Grid-03/25/2024 14:30: Lal-lo-Cagayan North Solar 69kV Line 1 and Line 2 restored at 1422H and 1429H, respectively [WEBSMS] | CLUZ
3/25/2024 2:18:15 PM | Luzon Grid-03/25/2024 14:18: Lal-lo-UPSI Magapit BESS 69kV Line restored at 1413H (Unplanned Outage) [WEBSMS] | CLUZ
3/25/2024 1:39:51 PM | Mindanao Grid-03/25/2024 13:44: WMPC DG06 online at 1335H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/25/2024 1:26:26 PM | Mindanao Grid-03/25/2024 13:31: Davao-Kibawe 138kV L1 auto-tripped and auto-reclosed at 1319H. Unplanned Outage. [WEBSMS] | CMIN
3/25/2024 12:54:50 PM | [NSO Update] Luzon Grid-03/25/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13296MW, PK=11223MW, RR=399MW, NetOpMargin: PM=1674, EVE=1397 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 210MW, Masinloc 1 @ 315MW, Masinloc 3 @ 305MW, SLTEC 1 @ 116MW, SLTEC 2 @ 117MW [WEBSMS] | CLUZ
3/25/2024 12:53:13 PM | [NSO Update] Mindanao Grid-03/25/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3271MW, PK=2445MW, RR=77MW, NetOpMargin: PM=748, EVE=788 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @46MW, AG2 @61MW, AG4 @76MW, AG5 @23MW, AG6 @111MW, AG7 @21MW, PG4 @60MW [WEBSMS] | CMIN
3/25/2024 12:52:09 PM | [NSO Update] Visayas Grid-03/25/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2695MW, PK=2236MW, RR=91MW, NetOpMargin: PM=368, EVE=373 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 67MW, Leyte A @ 343MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/25/2024 12:49:55 PM | Luzon Grid-03/25/2024 12:50: Lal-lo-Cagayan North Solar 69kV Line 1 and Line 2 de-energized at 1248H and 1249H, respectively (Unplanned Outage) [WEBSMS] | CLUZ
3/25/2024 12:34:14 PM | Luzon Grid-03/25/2024 12:34: Lal-lo-UPSI Magapit BESS 69kV Line de-energized at 1234H. (Unplanned Outage) [WEBSMS] | CLUZ
3/25/2024 11:33:39 AM | Mindanao Grid-03/25/2024 11:38: MCC U1 (Minergy Coal Balingasag) Online at 1121H, from Reserved Shutdown. [WEBSMS] | CMIN
3/25/2024 10:19:02 AM | Luzon Grid-03/25/2024 10:19: For info: Ilijan-EERI 500kV line 2 was looped at 1016H at EERI side. [WEBSMS] | CLUZ
3/25/2024 10:04:48 AM | Mindanao Grid-03/25/2024 10:09: WMPC DG02 online at 1000H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/25/2024 10:03:19 AM | Mindanao Grid-03/25/2024 10:08: SPC Mati online at 1000H. MO dispatched. [WEBSMS] | CMIN
3/25/2024 9:46:51 AM | Mindanao Grid-03/25/2024 09:51: Toril - Matanao 138kV Line2 de-energized at 0945H (Planned Outage) [WEBSMS] | CMIN
3/25/2024 9:37:55 AM | Mindanao Grid-03/25/2024 09:42: WMPC DG10 online at 0933H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/25/2024 9:29:12 AM | Luzon Grid-03/25/2024 09:29: For info: LRCC resumed normal dispatch function at 0928H. [WEBSMS] | CLUZ
3/25/2024 9:02:08 AM | Luzon Grid-03/25/2024 09:02: For your information: LRCC was evacuated at 0901H in participation in the First Quarter Nationwide Simultaneous Earthquake Drill (NSED). The dispatch function was performed at the MDC building. ACCs were informed and advised to monitor the transmission lines and equipment under their area of responsibility (AOR). [WEBSMS] | CLUZ
3/25/2024 7:54:15 AM | Luzon Grid-03/25/2024 07:54: Bay SS 230kV Bus 2 de-energized at 0753H. (Planned Outage) [WEBSMS] | CLUZ
3/25/2024 6:22:27 AM | Mindanao Grid-03/25/2024 06:27: NagaMin SS 138kV 100MVA Transformer No.1 energized at 0614H. (Planned Outage) [WEBSMS] | CMIN
3/25/2024 6:13:40 AM | Luzon Grid-03/25/2024 06:14: Bolo-Cayanga 230kV Line 1 (CO) de-energized at 0613H. (Planned Outage) [WEBSMS] | CLUZ
3/25/2024 5:47:56 AM | [NSO Update] Mindanao Grid-03/25/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3286MW, PK=2321MW, RR=75MW, NetOpMargin: AM=890, PM=787, EVE=857 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @46MW, AG2 @61MW, AG4 @76MW, AG5 @23MW, AG6 @111MW, AG7 @21MW, PG4 @50MW [WEBSMS] | CMIN
3/25/2024 5:46:13 AM | [NSO Update] Visayas Grid-03/25/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2925MW, PK=2111MW, RR=87MW, NetOpMargin: AM=726, PM=393, EVE=368 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @79.5MW, LEYTE A @348MW, PGPP1 @76MW [WEBSMS] | CVIS
3/25/2024 5:43:40 AM | [NSO Update] Luzon Grid-03/25/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13861MW, PK=10992MW, RR=381MW, NetOpMargin: AM=2488, PM=2475, EVE=1708 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC1 @210MW, MSLC1 @315MW, MSLC3 @305MW [WEBSMS] | CLUZ
3/25/2024 5:20:52 AM | Luzon Grid-03/25/2024 05:21: Correction: Muntinlupa 115 kV Bus 2 restored at 0434H (Planned Outage) [WEBSMS] | CLUZ
3/25/2024 4:37:14 AM | Luzon Grid-03/25/2024 04:37: Muntinlupa 115kV Bus 2 restored at 0334H (Planned Outage) [WEBSMS] | CLUZ
3/25/2024 4:06:19 AM | [NSO Update] Mindanao Grid-03/25/2024 04:11: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
3/25/2024 4:06:06 AM | [NSO Update] Luzon Grid-03/25/2024 04:06: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
3/25/2024 4:05:48 AM | [NSO Update] Visayas Grid-03/25/2024 04:06: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
3/25/2024 1:19:29 AM | Luzon Grid-03/25/2024 01:19: Bolo - Cayanga 230kV Line 2 (CO) energized at 0118H (Planned Outage) [WEBSMS] | CLUZ
3/25/2024 1:04:25 AM | Luzon Grid-03/25/2024 01:04: Binan 300MVA T01 energized on high side at 0103H (On Commissioning/For soaking) [WEBSMS] | CLUZ
3/25/2024 12:32:01 AM | Luzon Grid-03/25/2024 00:32: Binan 300MVA T01 de-energized at 0031H (On Commissioning) [WEBSMS] | CLUZ
3/25/2024 12:10:09 AM | Mindanao Grid-03/25/2024 00:14: PULANGI 4 HEP Unit 2 online at 0001H from OMC Outage -affected by the Planned Outage at Maramag SS requested by the P&E. (Unplanned Outage) [WEBSMS] | CMIN
3/25/2024 12:08:44 AM | Luzon Grid-03/25/2024 00:09: Binan 300MVA T01 energized on high side at 0006H (On Commissioning/For soaking) [WEBSMS] | CLUZ
3/25/2024 12:05:55 AM | Mindanao Grid-03/25/2024 00:10: Maramag-Pulangi4 138kV Line 2 energized at 0001H. (Planned Outage) [WEBSMS] | CMIN
3/25/2024 12:00:56 AM | Luzon Grid-03/25/2024 00:01: Muntinlupa 115kV Bus 2 de-energized at 1201H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 11:47:18 PM | Luzon Grid-03/24/2024 23:47: Muntinlupa 115kV Bus 1 restored at 2340H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 11:19:28 PM | Luzon Grid-03/24/2024 23:19: Santiago - Magat HEPP 230kV Line 2 energized at 2316H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 10:58:34 PM | Mindanao Grid-03/24/2024 23:03: San Francisco-Bislig 138kV Line energized and looped at 2250H. (Planned Outage) [WEBSMS] | CMIN
3/24/2024 9:58:26 PM | Mindanao Grid-03/24/2024 22:03: Nagamin SS 138kV Bus No.1 energized at 2157H. (Planned Outage) [WEBSMS] | CMIN
3/24/2024 7:40:44 PM | Luzon Grid-03/24/2024 19:41: Muntinlupa 115kV Bus 1 de-energized at 1935H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 7:05:18 PM | Luzon Grid-03/24/2024 19:05: Taytay 300MVA T05 restored at 1905H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 5:53:33 PM | Mindanao Grid-03/24/2024 17:58: Maramag SS 138kV Bus No. 1 energized at 1742H. (Planned Outage) [WEBSMS] | CMIN
3/24/2024 5:52:24 PM | [NSO Update] Mindanao Grid-03/24/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3221MW, PK=2196MW, RR=74MW, NetOpMargin: EVE=951 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @47MW, AG2 @63MW, AG4 @94.5MW, AG5 @24MW, AG6 @114MW, AG7 @22MW, PG4 @45MW [WEBSMS] | CMIN
3/24/2024 5:50:26 PM | [NSO Update] Visayas Grid-03/24/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2641MW, PK=1959MW, RR=86MW, NetOpMargin: EVE=597 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @348MW, PGPP1 @76MW [WEBSMS] | CVIS
3/24/2024 5:45:45 PM | [NSO Update] Luzon Grid-03/24/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12474MW, PK=9972MW, RR=290MW, NetOpMargin: EVE=2212 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 1 @210MW, MASINLOC 1 @315MW, MASINLOC 3 @305MW, SUAL 2 @450MW [WEBSMS] | CLUZ
3/24/2024 5:25:26 PM | Luzon Grid-03/24/2024 17:25: Duhat-Hermosa 230kV Line restored at 1725H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 4:31:52 PM | Mindanao Grid-03/24/2024 16:36: San Francisco SS 138kV 50MVA Transformer No.1 energized at 1628H. (Planned Outage) [WEBSMS] | CMIN
3/24/2024 3:53:17 PM | Luzon Grid-03/24/2024 15:53: SCPC 2 with 150MW load tripped at 1547H. Lowest Frequency is 59.73Hz (Unplanned Outage) [WEBSMS] | CLUZ
3/24/2024 3:51:17 PM | Visayas Grid-03/24/2024 15:51: Cebu SS 100MVA TR 4 energized at 1531H (Planned Outage) [WEBSMS] | CVIS
3/24/2024 2:44:54 PM | Luzon Grid-03/24/2024 14:45: Dasmarinas PCB 9-03CB24DAS energized at 1444H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 1:54:27 PM | Luzon Grid-03/24/2024 13:54: Dasmarinas-Amadeo 230kV Line 2 restored at 1354H. Dasmarinas-Las Pinas 230kV Line 1 looped at 1351H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 1:01:03 PM | [NSO Update] Mindanao Grid-03/24/2024 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3281MW, PK=1963MW, RR=77MW, NetOpMargin: PM=1241, EVE=966 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @47MW, AG2 @63MW, AG4 @94.5MW, AG5 @24MW, AG6 @114MW, AG7 @22MW, PG4 @45MW [WEBSMS] | CMIN
3/24/2024 12:59:31 PM | [NSO Update] Visayas Grid-03/24/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2605MW, PK=1799MW, RR=88MW, NetOpMargin: PM=718, EVE=331 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @340MW, PGPP1 @76MW [WEBSMS] | CVIS
3/24/2024 12:58:18 PM | [NSO Update] Luzon Grid-03/24/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13466MW, PK=9328MW, RR=309MW, NetOpMargin: PM=3830, EVE=2267 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @220MW, MSLC1 @315MW, MSLC3 @305MW, SUAL 2 @450MW, MPGC 1 @150MW [WEBSMS] | CLUZ
3/24/2024 11:28:35 AM | Mindanao Grid-03/24/2024 11:33: Maramag-Kibawe 138kV Line 2 energized at 1121H. (Planned Outage) [WEBSMS] | CMIN
3/24/2024 9:27:27 AM | Mindanao Grid-03/24/2024 09:32: Maramag-Kibawe 138kV Line 2 shutdown at 0913H. (Planned Outage) [WEBSMS] | CMIN
3/24/2024 8:18:20 AM | Luzon Grid-03/24/2024 08:18: Taytay 300MVA T05 de-energized at 0818H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 8:11:49 AM | Visayas Grid-03/24/2024 08:12: Cebu SS 100MVA TR 4 de-energized at 0804H (Planned Outage) [WEBSMS] | CVIS
3/24/2024 7:54:56 AM | Luzon Grid-03/24/2024 07:55: Dasmarinas PCB 9-03CB24DAS de-energized at 0754H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 7:37:41 AM | Mindanao Grid-03/24/2024 07:42: NagaMin 138kV BUS No.1 shutdown at 0732H. (Planned Outage) [WEBSMS] | CMIN
3/24/2024 7:26:23 AM | Mindanao Grid-03/24/2024 07:31: Maramag SS 138kV BUS No.1 shutdown at 0706H. (Planned Outage) [WEBSMS] | CMIN
3/24/2024 7:22:30 AM | Mindanao Grid-03/24/2024 07:27: Maramag-Pulangi 138kV L2 shutdown at 0601H. (Planned Outage) [WEBSMS] | CMIN
3/24/2024 7:01:24 AM | Luzon Grid-03/24/2024 07:01: Santiago-Magat HEPP 230kV Line 2 de-energized at 0701H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 6:50:16 AM | Mindanao Grid-03/24/2024 06:54: PULANGI HEP Unit 2 with 24.0MW load shutdown at 0601H. Affected by the Planned Outage at Maramag SS requested by the P&E. (OMC Outage) [WEBSMS] | CMIN
3/24/2024 6:38:18 AM | Luzon Grid-03/24/2024 06:38: Dasmarinas-Amadeo 230kV Line 2 de-energized at 0634H. Dasmarinas-Las Pinas 230kV Line 1 on floating status at 0633H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 6:31:49 AM | Mindanao Grid-03/24/2024 06:36: San Francisco-Bislig 138kV Line shutdown at 0614H. (Planned Outage) [WEBSMS] | CMIN
3/24/2024 6:30:16 AM | Mindanao Grid-03/24/2024 06:34: San Francisco 50MVA 138kV Transformer No.1 shutdown at 0612H. Planned Outage. [WEBSMS] | CMIN
3/24/2024 6:14:24 AM | Luzon Grid-03/24/2024 06:14: Duhat-Hermosa 230kV Line de-energized at 0613H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 6:13:13 AM | Luzon Grid-03/24/2024 06:13: Bolo-Cayanga 230kV Line 2 (CO) de-energized at 0611H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 6:12:12 AM | [NSO Update] Luzon Grid-03/24/2024 06:12: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13715MW, PK=8821MW, RR=301MW, NetOpMargin: AM=4593, PM=4060, EVE=2545 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC 1 @220MW, MSLC1 @315MW, MSLC3 @305MW [WEBSMS] | CLUZ
3/24/2024 5:39:01 AM | [NSO Update] Mindanao Grid-03/24/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3260MW, PK=1865MW, RR=75MW, NetOpMargin: AM=1320, PM=1145, EVE=873 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @47MW, AG2 @63MW, AG4 @78MW, AG5 @24MW, AG6 @114MW, AG7 @22MW, PG4 @56MW [WEBSMS] | CMIN
3/24/2024 5:32:00 AM | [NSO Update] Visayas Grid-03/24/2024 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2668MW, PK=1853MW, RR=87MW, NetOpMargin: AM=728, PM=696, EVE=322 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @67MW, LEYTE A @348MW, PGPP1 @76MW [WEBSMS] | CVIS
3/24/2024 4:23:34 AM | [NSO Update] Mindanao Grid-03/24/2024 04:28: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
3/24/2024 4:22:55 AM | [NSO Update] Visayas Grid-03/24/2024 04:23: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
3/24/2024 4:22:35 AM | [NSO Update] Luzon Grid-03/24/2024 04:22: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
3/24/2024 2:56:52 AM | Visayas Grid-03/24/2024 02:57: Calatrava - Magdugo 230KV Line 1 energized at 0246H,(Unplanned Outage) [WEBSMS] | CVIS
3/24/2024 2:53:52 AM | Visayas Grid-03/24/2024 02:54: Calatrava SS 230KV Bus 1 energized at 0132H.(Planned Outage) [WEBSMS] | CVIS
3/24/2024 2:00:39 AM | Luzon Grid-03/24/2024 02:01: San Jose SS 300MVA T03 restored at 0157H (Planned Outage) [WEBSMS] | CLUZ
3/24/2024 1:24:23 AM | Mindanao Grid-03/24/2024 01:29: TUDAYA 1 Unit 1 (3.2MW) shutdown at 0008H (Unplanned Outage). Affected by DLPC 69 kV line interruption due to stringing activities for new 69 kV Toril-Binugao line. [WEBSMS] | CMIN
3/24/2024 1:23:41 AM | Mindanao Grid-03/24/2024 01:28: SIBULAN B Unit 1 (5.5MW) shutdown at 0005H (Unplanned Outage). Affected by DLPC 69 kV line interruption due to stringing activities for new 69 kV Toril-Binugao line. [WEBSMS] | CMIN
3/24/2024 1:22:58 AM | Mindanao Grid-03/24/2024 01:27: SIBULAN A Unit 1 (3MW) & Unit 2 (5MW) shutdown at 0003H (Unplanned Outage). Affected by DLPC 69 kV line interruption due to stringing activities for new 69 kV Toril-Binugao line. [WEBSMS] | CMIN
3/24/2024 1:22:01 AM | Mindanao Grid-03/24/2024 01:26: SIBULAN B Unit 2 (4.75MW) shutdown at 0002H (Unplanned Outage). Affected by DLPC 69 kV line interruption due to stringing activities for new 69 kV Toril-Binugao line. [WEBSMS] | CMIN
3/24/2024 12:08:00 AM | Visayas Grid-03/24/2024 00:08: Nasulo Plant cut-out from the system at 0004H (Planned Outage) [WEBSMS] | CVIS
3/23/2024 11:37:46 PM | Visayas Grid-03/23/2024 23:38: Calatrava SS 230KV Bus 1 de-energized at 2308H.(Planned Outage) [WEBSMS] | CVIS
3/23/2024 11:07:29 PM | Visayas Grid-03/23/2024 23:07: Calatrava - Magdugo 230KV Line 1 de-energized at 2244H, hotspot correction at Calatrava SS.(Unplanned Outage) [WEBSMS] | CVIS
3/23/2024 10:39:50 PM | Luzon Grid-03/23/2024 22:40: Hermosa-BCCPP 230kV Line 3 restored at 2239H (Planned Outage) [WEBSMS] | CLUZ
3/23/2024 8:30:15 PM | [NSO Update] Luzon Grid-03/23/2024 20:30: For information, the observance of Earth Hour has started at 2030H. [WEBSMS] | CLUZ
3/23/2024 8:30:11 PM | [NSO Update] Visayas Grid-03/23/2024 20:30: For information, the observance of Earth Hour has started at 2030H. [WEBSMS] | CVIS
3/23/2024 8:30:05 PM | [NSO Update] Mindanao Grid-03/23/2024 20:34: For information, the observance of Earth Hour has started at 2030H. [WEBSMS] | CMIN
3/23/2024 7:49:19 PM | Mindanao Grid-03/23/2024 19:54: WMPC DG10 shutdown at 1943H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/23/2024 7:15:29 PM | Mindanao Grid-03/23/2024 19:20: TALOMO 1 Unit 2 with 0.21 MW load shutdown at 1901H due to insufficient water supply (Unplanned Outage). [WEBSMS] | CMIN
3/23/2024 6:45:06 PM | Mindanao Grid-03/23/2024 18:49: WMPC DG08 shutdown at 1716H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/23/2024 6:28:08 PM | Luzon Grid-03/23/2024 18:28: Hermosa 230kV Bus 1 restored at 1827H (Planned Outage) [WEBSMS] | CLUZ
3/23/2024 6:08:04 PM | Luzon Grid-03/23/2024 18:08: San Jose SS 300MVA T03 de-energized at 1808H (Planned Outage) [WEBSMS] | CLUZ
3/23/2024 6:03:30 PM | Mindanao Grid-03/23/2024 18:08: General Santos SS 138kV/69kV/13.8kV 100MVA Power Transformer No.4 (7XF04GSA) energized/restored at 1758H. From Planned Outage-GOMP. [WEBSMS] | CMIN
3/23/2024 5:59:47 PM | Luzon Grid-03/23/2024 18:00: Nagsaag-Binga 230kV Line 1 restored at 1759H (Planned Outage) [WEBSMS] | CLUZ
3/23/2024 5:53:07 PM | [NSO Update] Mindanao Grid-03/23/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3249MW, PK=2324MW, RR=74MW, NetOpMargin: EVE=850 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @48MW, AG2 @64MW, AG4 @79MW, AG5 @25MW, AG6 @116MW, AG7 @22MW, PG4 @56MW [WEBSMS] | CMIN
3/23/2024 5:51:59 PM | [NSO Update] Visayas Grid-03/23/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2620MW, PK=2145MW, RR=86MW, NetOpMargin: EVE=389 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @79.5MW, LEYTE A @350MW, PGPP1 @76MW [WEBSMS] | CVIS
3/23/2024 5:48:51 PM | [NSO Update] Luzon Grid-03/23/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12595MW, PK=9838MW, RR=380MW, NetOpMargin: EVE=2377 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: MSLC1 @310MW, MSLC3 @310MW [WEBSMS] | CLUZ
3/23/2024 5:42:56 PM | Luzon Grid-03/23/2024 17:43: Ilijan GT1-2 shutdown at 1738H (Unplanned Outage) [WEBSMS] | CLUZ
3/23/2024 5:28:32 PM | Luzon Grid-03/23/2024 17:28: Ilijan ST1 shutdown at 1727H (Unplanned Outage) [WEBSMS] | CLUZ
3/23/2024 5:19:58 PM | Luzon Grid-03/23/2024 17:20: For info: Ilijan GT2-1 and ST2 shutdown at 1648H and 1625H, respectively (Unplanned Outage). [WEBSMS] | CLUZ
3/23/2024 5:17:45 PM | Luzon Grid-03/23/2024 17:18: Ilijan GT1-1 shutdown at 1716H (Unplanned Outage) [WEBSMS] | CLUZ
3/23/2024 4:50:26 PM | Luzon Grid-03/23/2024 16:50: San Jose 115kV Bus 1 restored at 1649H (Planned Outage) [WEBSMS] | CLUZ
3/23/2024 4:38:35 PM | Visayas Grid-03/23/2024 16:38: Samboan SS 69 kV Ginatilan Feeder energized at 1637H (Planned Outage) [WEBSMS] | CVIS
3/23/2024 4:18:43 PM | Luzon Grid-03/23/2024 16:19: Hermosa-BCCPP 230kV Line 3 de-energized at 1616H (Planned Outage) [WEBSMS] | CLUZ
3/23/2024 3:48:58 PM | Mindanao Grid-03/23/2024 15:53: Jasaan SS 138kV/69kV/13.8kV 100MVA Power Transformer No.1 (7XF01JAS) energized/restored at 1541H. From Planned Outage-GOMP. [WEBSMS] | CMIN
3/23/2024 2:34:52 PM | Mindanao Grid-03/23/2024 14:39: NagaMin SS 138kV Bus No.1 (7BS01NAA) successfully energized/restored at 1423H. From Unplanned Outage. [WEBSMS] | CMIN
3/23/2024 2:04:35 PM | Mindanao Grid-03/23/2024 14:09: NagaMin SS 138kV Bus No.1 (7BS01NAA) auto-tripped at 1356H. Unplanned Outage. (Note: No connected 138kV/69kV TLs, Power Transformers, and Power customers were affected.) [WEBSMS] | CMIN
3/23/2024 1:11:53 PM | Luzon Grid-03/23/2024 13:12: Dasmarinas-Amadeo 230kV Line 1 restored at 1312H (Planned Outage) [WEBSMS] | CLUZ
3/23/2024 12:54:59 PM | Mindanao Grid-03/23/2024 12:59: WMPC DG08 online at 1244H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/23/2024 12:45:06 PM | [NSO Update] Mindanao Grid-03/23/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3287MW, PK=2212MW, RR=77MW, NetOpMargin: PM=998, EVE=901 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @48MW, AG2 @64MW, AG4 @79MW, AG5 @25MW, AG6 @116MW, AG7 @22MW, PG4 @56MW [WEBSMS] | CMIN
3/23/2024 12:41:10 PM | [NSO Update] Visayas Grid-03/23/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2921MW, PK=2124MW, RR=88MW, NetOpMargin: PM=709, EVE=406 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @79.5MW, LEYTE A @340MW, PGPP1 @76MW [WEBSMS] | CVIS
3/23/2024 12:38:50 PM | [NSO Update] Luzon Grid-03/23/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14300MW, PK=10301MW, RR=399MW, NetOpMargin: PM=3600, EVE=1981 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: GNPD 2 @334MW, MASINLOC 1 @310MW, MASINLOC 3 @300MW, SLTEC 2 @109MW, ILIJAN B @300MW [WEBSMS] | CLUZ
3/23/2024 12:24:36 PM | Luzon Grid-03/23/2024 12:24: Hermosa 230kV Bus 1 de-energized at 1224H (Planned Outage) [WEBSMS] | CLUZ
3/23/2024 12:12:05 PM | Mindanao Grid-03/23/2024 12:16: LAKE MAINIT Hydro online at 1201H (Unplanned Outage) [WEBSMS] | CMIN
3/23/2024 12:02:54 PM | Mindanao Grid-03/23/2024 12:07: ASIGA Hydro online at 1158H (Unplanned Outage) [WEBSMS] | CMIN
3/23/2024 11:46:26 AM | Mindanao Grid-03/23/2024 11:51: TALOMO 3 Unit 2 online at 0908H (Unplanned Outage) [WEBSMS] | CMIN
3/23/2024 11:45:56 AM | Mindanao Grid-03/23/2024 11:50: TALOMO 3 Unit 1 online at 0854H (Unplanned Outage) [WEBSMS] | CMIN
3/23/2024 11:45:23 AM | Mindanao Grid-03/23/2024 11:50: TALOMO 2A Unit 2 online at 0722H (Unplanned Outage) [WEBSMS] | CMIN
3/23/2024 11:44:51 AM | Mindanao Grid-03/23/2024 11:49: TALOMO 2A Unit 1 online at 0718H (Unplanned Outage) [WEBSMS] | CMIN
3/23/2024 11:43:23 AM | Mindanao Grid-03/23/2024 11:48: TALOMO 2B Unit 1 online at 0717H (Unplanned Outage) [WEBSMS] | CMIN
3/23/2024 11:42:38 AM | Mindanao Grid-03/23/2024 11:47: TALOMO 2 Unit 2 online at 0715H (Unplanned Outage) [WEBSMS] | CMIN
3/23/2024 11:41:53 AM | Mindanao Grid-03/23/2024 11:46: TALOMO 2 Unit 1 online at 0714H (Unplanned Outage) [WEBSMS] | CMIN
3/23/2024 11:41:05 AM | Mindanao Grid-03/23/2024 11:45: TALOMO 2 Unit 3 online at 0713H (Unplanned Outage) [WEBSMS] | CMIN
3/23/2024 11:36:10 AM | Mindanao Grid-03/23/2024 11:40: ASIGA Hydro with 4MW load isolated at 1122H (Unplanned Outage). Cause: Loss of feedback power brought by tripping of customer-owned Butuan-Santiago 69 kV feeder. [WEBSMS] | CMIN
3/23/2024 11:35:19 AM | Mindanao Grid-03/23/2024 11:40: LAKE MAINIT Hydro with 17MW load isolated at 1122H (Unplanned Outage). Cause: Loss of feedback power brought by tripping of customer-owned Butuan-Santiago 69 kV feeder. [WEBSMS] | CMIN
3/23/2024 11:15:38 AM | Mindanao Grid-03/23/2024 11:20: Kibawe-Davao 138kV L2 energized/restored at 1110H. From Planned Outage/Non-GOMP. Approved P&E requested activity. [WEBSMS] | CMIN
3/23/2024 11:14:13 AM | Mindanao Grid-03/23/2024 11:18: SEC2 online at 1111H (Unplanned Outage) [WEBSMS] | CMIN
3/23/2024 9:47:50 AM | Mindanao Grid-03/23/2024 09:52: WMPC DG10 online at 0946H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/23/2024 9:10:04 AM | Mindanao Grid-03/23/2024 09:14: Kibawe-Davao 138kV Line 2 shutdown at 0903H (Planned Outage). P&E related activity. [WEBSMS] | CMIN
3/23/2024 8:51:09 AM | Mindanao Grid-03/23/2024 08:55: TALOMO 2 Unit 1 (0.14MW), Unit 2 (0.19MW), Unit 3 (0.15MW), TALOMO 2A Unit 1 (0.31MW), Unit 2 (0.1MW), TALOMO 2B Unit 1 (0.25MW), TALOMO 3 Unit 1 (0.73MW), Unit 2 (0.66MW) tripped at 0619H (Unplanned Outage). Affected by tripping of DLPC Tugbok line recloser 1. [WEBSMS] | CMIN
3/23/2024 7:10:01 AM | Visayas Grid-03/23/2024 07:10: Samboan SS 30MVA TR 1 de-energized at 0708H (Planned Outage) [WEBSMS] | CVIS
3/23/2024 7:07:46 AM | Visayas Grid-03/23/2024 07:08: Samboan SS 69 kV Ginatilan Feeder de-energized at 0704H (Planned Outage) [WEBSMS] | CVIS
3/23/2024 7:06:54 AM | Luzon Grid-03/23/2024 07:07: Nagsaag-Binga 230kV Line 1 de-energized at 0706H (Planned Outage) [WEBSMS] | CLUZ
3/23/2024 6:38:04 AM | Mindanao Grid-03/23/2024 06:42: Gensan SS transformer #4, 100 MVA) (7XF04GSA) de-energized at 0636H. P.O/GOMP. [WEBSMS] | CMIN
3/23/2024 6:36:26 AM | Luzon Grid-03/23/2024 06:36: Dasmarinas-Amadeo 230kV Line 1 de-energized at 0636H (Planned Outage) [WEBSMS] | CLUZ
3/23/2024 6:21:30 AM | Luzon Grid-03/23/2024 06:21: San Jose 115kV Bus 1 de-energized at 0618H (Planned Outage) [WEBSMS] | CLUZ
3/23/2024 6:11:46 AM | Mindanao Grid-03/23/2024 06:16: Jasaan SS transformer #1, 100 MVA) (7XF01JAS) de-energized at 0608H. P.O/GOMP. [WEBSMS] | CMIN
3/23/2024 5:54:53 AM | [NSO Update] Mindanao Grid-03/23/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3201MW, PK=2101MW, RR=75MW, NetOpMargin: AM=1025, PM=847, EVE=731 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @48MW, AG2 @64MW, AG4 @79MW, AG5 @25MW, AG6 @116MW, AG7 @22MW, PG4 @56MW [WEBSMS] | CMIN
3/23/2024 5:52:16 AM | [NSO Update] Visayas Grid-03/23/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2866MW, PK=2018MW, RR=87MW, NetOpMargin: AM=760, PM=700, EVE=284 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @79.5MW, LEYTE A @340MW, PGPP1 @76MW [WEBSMS] | CVIS
3/23/2024 5:48:33 AM | [NSO Update] Luzon Grid-03/23/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14579MW, PK=9891MW, RR=391MW, NetOpMargin: AM=4297, PM=3894, EVE=2805 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: MSLC1 @310MW, MSLC3 @295MW, GNPD 2 @334, ILIJAN B @300MW [WEBSMS] | CLUZ
3/23/2024 5:47:15 AM | Luzon Grid-03/23/2024 05:47: Sual 1 230kV Bus 1 restored at 0547H. (Unplanned Outage) [WEBSMS] | CLUZ
3/23/2024 5:33:09 AM | Luzon Grid-03/23/2024 05:33: Binan SS 230kV Bus 1 restored at 0533H. (Planned Outage) [WEBSMS] | CLUZ
3/23/2024 5:26:17 AM | Luzon Grid-03/23/2024 05:26: Sual 1 230kV Bus 1 de-energized at 0526H. (Unplanned Outage) [WEBSMS] | CLUZ
3/23/2024 4:22:50 AM | [NSO Update] Mindanao Grid-03/23/2024 04:27: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
3/23/2024 4:22:07 AM | [NSO Update] Visayas Grid-03/23/2024 04:22: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
3/23/2024 4:20:29 AM | [NSO Update] Luzon Grid-03/23/2024 04:20: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
3/22/2024 8:29:50 PM | Mindanao Grid-03/22/2024 20:34: WMPC DG04 shutdown at 2024H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/22/2024 8:05:27 PM | Luzon Grid-03/22/2024 20:05: Bacman 230kV Bus 2 restored at 2004H. (Planned Outage) [WEBSMS] | CLUZ
3/22/2024 7:23:04 PM | [NSO Update] Luzon Grid-03/22/2024 19:23: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1921H with power going to Luzon [WEBSMS] | CLUZ
3/22/2024 7:22:25 PM | [NSO Update] Visayas Grid-03/22/2024 19:22: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1921H with power going to Luzon [WEBSMS] | CVIS
3/22/2024 7:12:46 PM | [NSO Update] Visayas Grid-03/22/2024 19:13: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1910H from reverse power direction [WEBSMS] | CVIS
3/22/2024 7:12:04 PM | [NSO Update] Luzon Grid-03/22/2024 19:12: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1910H from reverse power direction [WEBSMS] | CLUZ
3/22/2024 7:08:37 PM | Mindanao Grid-03/22/2024 19:13: KEGI MARAMAG shutdown at 1905H. MO dispatched. [WEBSMS] | CMIN
3/22/2024 6:38:51 PM | Luzon Grid-03/22/2024 18:39: Binan SS 230kV Bus 1 de-energized at 1837H. (Planned Outage) [WEBSMS] | CLUZ
3/22/2024 5:47:13 PM | [NSO Update] Mindanao Grid-03/22/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3043MW, PK=2379MW, RR=74MW, NetOpMargin: EVE=590 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @48MW, AG2 @64MW, AG4 @79MW, AG5 @25MW, AG6 @116MW, AG7 @10MW, PG4 @56MW [WEBSMS] | CMIN
3/22/2024 5:45:28 PM | [NSO Update] Visayas Grid-03/22/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2479MW, PK=2185MW, RR=86MW, NetOpMargin: EVE=207 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @79.5MW, LEYTE A @345MW, PGPP1 @76MW [WEBSMS] | CVIS
3/22/2024 5:43:37 PM | [NSO Update] Luzon Grid-03/22/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13386MW, PK=9927MW, RR=370MW, NetOpMargin: EVE=3089 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: MSLC1 @310MW, MSLC3 @310MW, ILIJAN B @300MW [WEBSMS] | CLUZ
3/22/2024 5:38:39 PM | Mindanao Grid-03/22/2024 17:43: Baloi SS transformer T1, 300 MVA ( 8XF01BLO) energized at 1730H. P.O/Non-GOMP. [WEBSMS] | CMIN
3/22/2024 5:37:19 PM | Mindanao Grid-03/22/2024 17:41: Balo-i SS 230kV 300MVA Power Transformer No. 1 (8XF01BLO) energized at 1730H. Planned Outage. [WEBSMS] | CMIN
3/22/2024 5:27:48 PM | Mindanao Grid-03/22/2024 17:32: LAMSAN Biomass (LSK) online at 1719H from F.O Unplanned Outage. [WEBSMS] | CMIN
3/22/2024 5:26:12 PM | Mindanao Grid-03/22/2024 17:30: Update: LAMSAN Biomass (LSK) with 5.5MW load tripped at 1705H. Indication: 50N Directional Earth Fault. Unplanned Outage. [WEBSMS] | CMIN
3/22/2024 5:23:29 PM | Mindanao Grid-03/22/2024 17:28: LAMSAN Biomass (LSK) with 5.5MW load tripped at 1705H. Indication: 50N Directional Earth Fault. Planned Outage. [WEBSMS] | CMIN
3/22/2024 5:18:07 PM | Mindanao Grid-03/22/2024 17:22: WMPC DG08 shutdown at 1715H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/22/2024 4:45:33 PM | Luzon Grid-03/22/2024 16:45: San Jose-Angat 115kV line 1 looped at Angat side at 1645H via PCB 6-03CB24ANG. (Planned Outage) [WEBSMS] | CLUZ
3/22/2024 4:44:52 PM | Mindanao Grid-03/22/2024 16:49: SEC 1 online at 1643H from Forced Outage. (Unplanned outage). [WEBSMS] | CMIN
3/22/2024 3:37:40 PM | Mindanao Grid-03/22/2024 15:42: WMPC DG10 declared available at 1525H from force outage (Unplanned Outage) [WEBSMS] | CMIN
3/22/2024 3:17:15 PM | Luzon Grid-03/22/2024 15:17: GMEC 1 shutdown at 1515H. (Unplanned Outage) [WEBSMS] | CLUZ
3/22/2024 2:45:36 PM | Mindanao Grid-03/22/2024 14:50: Pulangi 4 HEP Online at 1438H from OMC-low forebay elevation. Unplanned Outage. [WEBSMS] | CMIN
3/22/2024 2:42:26 PM | Mindanao Grid-03/22/2024 14:47: SPC Mati, with 3.0MW load on Emergency Shutdown at 1419H due to engine problem. (Unplanned Outage) [WEBSMS] | CMIN
3/22/2024 1:52:20 PM | [NSO Update] Luzon Grid-03/22/2024 13:52: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1351H with power going to Visayas. [WEBSMS] | CLUZ
3/22/2024 1:52:16 PM | [NSO Update] Visayas Grid-03/22/2024 13:52: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1351H with power going to Visayas. [WEBSMS] | CVIS
3/22/2024 1:43:30 PM | [NSO Update] Visayas Grid-03/22/2024 13:43: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1341H from forward power direction. [WEBSMS] | CVIS
3/22/2024 1:42:30 PM | [NSO Update] Luzon Grid-03/22/2024 13:42: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1341H from forward power direction. [WEBSMS] | CLUZ
3/22/2024 1:22:53 PM | Luzon Grid-03/22/2024 13:23: San Jose-Angat 115kV line 1 was unlooped in Angat side at 1317H due to the Planned Outage of PCB 6-03CB24ANG. (Planned Outage) [WEBSMS] | CLUZ
3/22/2024 1:07:57 PM | Mindanao Grid-03/22/2024 13:12: Sibulan B HEP Unit 2 online at 1227H from PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
3/22/2024 1:01:51 PM | Mindanao Grid-03/22/2024 13:06: Sibulan B HEP Unit 1 online at 1204H from PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
3/22/2024 12:47:45 PM | [NSO Update] Luzon Grid-03/22/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14573MW, PK=10675MW, RR=402MW, NetOpMargin: PM=3496, EVE=3065 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: GMEC 1 @150MW, MASINLOC 1 @310MW, MASINLOC 3 @310MW, SLTEC 2 @109MW, ILIJAN B @300MW [WEBSMS] | CLUZ
3/22/2024 12:47:20 PM | [NSO Update] Visayas Grid-03/22/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2732MW, PK=2321MW, RR=89MW, NetOpMargin: PM=322, EVE=230 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @345MW, PGPP1 @76MW [WEBSMS] | CVIS
3/22/2024 12:47:12 PM | [NSO Update] Mindanao Grid-03/22/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3015MW, PK=2363MW, RR=77MW, NetOpMargin: PM=575, EVE=625 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @48MW, AG2 @64MW, AG4 @79MW, AG5 @25MW, AG6 @116MW, AG7 @10MW, PG4 @24MW [WEBSMS] | CMIN
3/22/2024 12:07:29 PM | Luzon Grid-03/22/2024 12:07: Sual CFTPP 230kV Bus 1 was energized at 1206H. (Unplanned Outage) [WEBSMS] | CLUZ
3/22/2024 12:02:40 PM | Luzon Grid-03/22/2024 12:02: Sual CFTPP 230kV Bus 1 was de-energized at 1201H. (Unplanned Outage) [WEBSMS] | CLUZ
3/22/2024 11:09:39 AM | Mindanao Grid-03/22/2024 11:14: SEC1 tripped with 114.19 MW load at 1054H. Cause: Master Fuel Trip. Lowest system frequency recorded was 59.547Hz. SOC 2 SIPS activated with a total load drop of 76.9 MW (Gensan - Lledo 37.9 MW, Gensan - Tupi 27.3MW and GSA -Kamanga -11.70 mw). [WEBSMS] | CMIN
3/22/2024 10:46:43 AM | Mindanao Grid-03/22/2024 10:51: Update: Lake Mainit HEP Unit 2 with 5.6MW tripped at 1032H. Indication: Digital Governor Trip Unplanned Outage [WEBSMS] | CMIN
3/22/2024 10:41:01 AM | Mindanao Grid-03/22/2024 10:45: Lake Mainit HEP Unit 2 with 5.6MW tripped at 1032H. Unplanned Outage [WEBSMS] | CMIN
3/22/2024 10:19:09 AM | Mindanao Grid-03/22/2024 10:23: WMPC DG08 online at 1016H. RPS-System Voltage Requirement [WEBSMS] | CMIN
3/22/2024 9:40:38 AM | Mindanao Grid-03/22/2024 09:45: WMPC DG04 online at 0938H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/22/2024 9:32:22 AM | Mindanao Grid-03/22/2024 09:37: WMPC DG10 with 8.5MW load tripped at 0926H. Indication: HT low pressure stop. (Unplanned Outage) [WEBSMS] | CMIN
3/22/2024 9:24:35 AM | Mindanao Grid-03/22/2024 09:29: Baloi SS transformer T1, 300 MVA ( 8XF01BLO) de-energized at 0923H. P.O/Non-GOMP. [WEBSMS] | CMIN
3/22/2024 9:16:04 AM | Mindanao Grid-03/22/2024 09:20: WMPC DG10 online at 0914H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/22/2024 7:31:32 AM | Mindanao Grid-03/22/2024 07:36: NagaMin SS Transformer No1.,100 MVA (7XF01NAA) de-energized at 0731H. PO/Non-GOMP. [WEBSMS] | CMIN
3/22/2024 6:14:06 AM | [NSO Update] Luzon Grid-03/22/2024 06:14: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15023MW, PK=10357MW, RR=381MW, NetOpMargin: AM=4285, PM=3877, EVE=3159 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @310MW, MSLC3 @310MW, ILIJAN B @300MW [WEBSMS] | CLUZ
3/22/2024 5:44:33 AM | [NSO Update] Mindanao Grid-03/22/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3146MW, PK=2310MW, RR=75MW, NetOpMargin: AM=760, PM=740, EVE=789 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @48MW, AG2 @64MW, AG4 @79MW, AG5 @25MW, AG6 @116MW, AG7 @17MW, PG4 @24MW [WEBSMS] | CMIN
3/22/2024 5:42:36 AM | [NSO Update] Visayas Grid-03/22/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2792MW, PK=2173MW, RR=87MW, NetOpMargin: AM=532, PM=501, EVE=357 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @345MW, PGPP1 @76MW [WEBSMS] | CVIS
3/22/2024 5:41:01 AM | Luzon Grid-03/22/2024 05:41: Binan SS 230kV Bus 2 was restored at 0536H (Planned Outage) [WEBSMS] | CLUZ
3/22/2024 4:18:46 AM | [NSO Update] Mindanao Grid-03/22/2024 04:23: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
3/22/2024 4:18:13 AM | [NSO Update] Visayas Grid-03/22/2024 04:18: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
3/22/2024 4:16:44 AM | [NSO Update] Luzon Grid-03/22/2024 04:17: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/22/2024 4:14:55 AM | Mindanao Grid-03/22/2024 04:19: BUBUNAWAN online at 0306H (Unplanned Outage) [WEBSMS] | CMIN
3/22/2024 1:34:16 AM | Luzon Grid-03/22/2024 01:34: Balsik-San Marcelino 230kV Lines 1 and 2 were restored at 0122H and 0130H, respectively. (Planned Outage) [WEBSMS] | CLUZ
3/22/2024 1:07:36 AM | Mindanao Grid-03/22/2024 01:12: BUBUNAWAN shutdown at 0020H (Unplanned Outage). Outside management control (low water river flow). [WEBSMS] | CMIN
3/21/2024 10:28:06 PM | Mindanao Grid-03/21/2024 22:32: NagaMin - Zamboanga 138kV L2 restored at 2225H. (Unplanned Outage) [WEBSMS] | CMIN
3/21/2024 10:15:03 PM | Mindanao Grid-03/21/2024 22:19: NagaMin - Zamboanga 138kV L2 tripped at 2209H. (Unplanned Outage) [WEBSMS] | CMIN
3/21/2024 7:47:55 PM | Mindanao Grid-03/21/2024 19:52: WMPC DG10 shutdown at 1944H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/21/2024 7:25:54 PM | Mindanao Grid-03/21/2024 19:30: Jasaan - Nasipit 138kV line restored at 1925H (Unplanned Outage) [WEBSMS] | CMIN
3/21/2024 7:07:52 PM | [NSO Update] Visayas Grid-03/21/2024 19:08: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1905H with power going to Luzon. [WEBSMS] | CVIS
3/21/2024 7:07:23 PM | [NSO Update] Luzon Grid-03/21/2024 19:07: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1905H with power going to Luzon. [WEBSMS] | CLUZ
3/21/2024 6:58:27 PM | [NSO Update] Visayas Grid-03/21/2024 18:58: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1853H from reverse power direction. [WEBSMS] | CVIS
3/21/2024 6:57:17 PM | [NSO Update] Luzon Grid-03/21/2024 18:57: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1853H from reverse power direction. [WEBSMS] | CLUZ
3/21/2024 6:48:02 PM | Mindanao Grid-03/21/2024 18:52: TALOMO 3 Unit 1 online at 1548H (Unplanned Outage) [WEBSMS] | CMIN
3/21/2024 6:47:25 PM | Mindanao Grid-03/21/2024 18:52: TALOMO 3 Unit 1 online at 1536H (Unplanned Outage) [WEBSMS] | CMIN
3/21/2024 6:46:49 PM | Mindanao Grid-03/21/2024 18:51: TALOMO 2B Unit 1 online at 1539H (Unplanned Outage) [WEBSMS] | CMIN
3/21/2024 6:46:08 PM | Mindanao Grid-03/21/2024 18:50: TALOMO 2A Unit 1 & Unit 2 online at 1522H (Unplanned Outage) [WEBSMS] | CMIN
3/21/2024 6:25:23 PM | [NSO Update] Luzon Grid-03/21/2024 18:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1821H with power going to Visayas. [WEBSMS] | CLUZ
3/21/2024 6:24:51 PM | [NSO Update] Visayas Grid-03/21/2024 18:25: Ormoc-Naga 350kV HVDC (Visayas-Luzon) de-blocked at 1821H with power going to Visayas. [WEBSMS] | CVIS
3/21/2024 6:22:17 PM | [NSO Update] Luzon Grid-03/21/2024 18:22: undefined at 1808H Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1808H from forward power direction [WEBSMS] | CLUZ
3/21/2024 6:21:34 PM | [NSO Update] Visayas Grid-03/21/2024 18:21: Ormoc-Naga 350kV HVDC (Visayas-Luzon) blocked at 1808H from forward power direction [WEBSMS] | CVIS
3/21/2024 6:15:33 PM | [NSO Update] Luzon Grid-03/21/2024 18:15: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13633MW, PK=10045MW, RR=290MW, NetOpMargin: EVE=3298 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MSLC1 @310MW, MSLC3 @305MW, GNPD 2 @608MW, ILIJAN B @300MW [WEBSMS] | CLUZ
3/21/2024 6:13:33 PM | Luzon Grid-03/21/2024 18:13: Binan SS 230kV Bus 2 de-energized at 1812H (Planned Outage) [WEBSMS] | CLUZ
3/21/2024 6:03:54 PM | Mindanao Grid-03/21/2024 18:08: TALOMO 2 Unit 2 & Unit 3 online at 1601H (Unplanned Outage) [WEBSMS] | CMIN
3/21/2024 6:03:17 PM | Mindanao Grid-03/21/2024 18:07: TALOMO 2 Unit 1 online at 1527H (Unplanned Outage) [WEBSMS] | CMIN
3/21/2024 6:02:28 PM | [NSO Update] Mindanao Grid-03/21/2024 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3087MW, PK=2313MW, RR=74.3MW, NetOpMargin: EVE=699 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @49MW, AG2 @66MW, AG4 @80MW, AG5 @26MW, AG6 @120MW, AG7 @17MW, PG4 @24MW [WEBSMS] | CMIN
3/21/2024 6:00:37 PM | Mindanao Grid-03/21/2024 18:05: TALOMO 2 Unit 1 (0.18MW), Unit 2 (0.2MW), Unit 3 (0.18), TALOMO 2A Unit 1 (0.29MW), Unit 2 (0.11MW), TALOMO 2 B Unit 1 (0.26MW), TALOMO 3 Unit 1 (0.71MW), Unit 2 (0.62MW) tripped at 1506H (Unplanned Outage). TUDAYA 1 Unit 1 at 1352H (Unplanned Outage). Affected by tripping of DLPCs Tugbok Feeder. [WEBSMS] | CMIN
3/21/2024 5:58:26 PM | [NSO Update] Visayas Grid-03/21/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2494MW, PK=2145MW, RR=91MW, NetOpMargin: EVE=258 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @338MW, PGPP1 @76MW [WEBSMS] | CVIS
3/21/2024 5:57:27 PM | Mindanao Grid-03/21/2024 18:02: Jasaan - Nasipit 138kV line tripped at 1746H. (Unplanned Outage) [WEBSMS] | CMIN
3/21/2024 5:50:47 PM | Mindanao Grid-03/21/2024 17:55: (Correction) TUDAYA 1 Unit 1 tripped at 1352H (Unplanned Outage). Affected by tripping of customer-owned DLPC ERA T2 CB5. [WEBSMS] | CMIN
3/21/2024 5:48:20 PM | Mindanao Grid-03/21/2024 17:52: SIBULAN A Unit 1 & Unit 2 online at 1614H (Unplanned Outage) [WEBSMS] | CMIN
3/21/2024 5:47:37 PM | Mindanao Grid-03/21/2024 17:52: TUDAYA 1 Unit 1 online at 1412H (Unplanned Outage) [WEBSMS] | CMIN
3/21/2024 5:46:21 PM | Mindanao Grid-03/21/2024 17:50: TUDAYA 1 Unit 1 at 1352H (Unplanned Outage). Affected by tripping of customer-owned DLPC ERA T2 CB5. [WEBSMS] | CMIN
3/21/2024 5:30:21 PM | Mindanao Grid-03/21/2024 17:34: PULANGI 4 Unit 2 emergency shutdown at 1728H (Unplanned Outage). Outside management control (insufficient water supply/ low forebay elevation). [WEBSMS] | CMIN
3/21/2024 5:29:13 PM | Luzon Grid-03/21/2024 17:29: Balsik-San Marcelino 230kV Lines 1 and 2 were de-energized at 1726H and 1727H, respectively. (Planned Outage) [WEBSMS] | CLUZ
3/21/2024 5:16:28 PM | Mindanao Grid-03/21/2024 17:21: WMPC DG07 shutdown at 1715H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/21/2024 4:55:12 PM | Luzon Grid-03/21/2024 16:55: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1654H (Planned Outage) [WEBSMS] | CLUZ
3/21/2024 4:47:15 PM | Mindanao Grid-03/21/2024 16:51: WMPC DG01 shutdown at 1644H. RPS-System Voltage Requirement [WEBSMS] | CMIN
3/21/2024 4:25:19 PM | Mindanao Grid-03/21/2024 16:29: SIBULAN A Unit 1 & Unit 2 tripped at 1352H (Unplanned Outage). Affected by tripping of customer-owned DLPC ERA T2 CB5. [WEBSMS] | CMIN
3/21/2024 3:33:59 PM | Luzon Grid-03/21/2024 15:34: Labo-Naga 230kV Line 2 restored at 1534H (Planned Outage) [WEBSMS] | CLUZ
3/21/2024 2:33:41 PM | Mindanao Grid-03/21/2024 14:38: AGUS 4 Unit 3 with 24.4MW load shutdown at 1426H. OMC - insufficient water supply. (Unplanned Outage). [WEBSMS] | CMIN
3/21/2024 1:56:19 PM | Mindanao Grid-03/21/2024 14:00: Kibawe - Tacurong 138kV line tripped and auto-reclosed at 1344H. (Unplanned Outage) [WEBSMS] | CMIN
3/21/2024 12:52:41 PM | Mindanao Grid-03/21/2024 12:57: WMPC DG01 online at 1249H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/21/2024 12:51:14 PM | [NSO Update] Mindanao Grid-03/21/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3184MW, PK=2450MW, RR=77MW, NetOpMargin: PM=656, EVE=729 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @49MW, AG2 @66MW, AG4 @80MW, AG5 @26MW, AG6 @120MW, AG7 @23MW, PG4 @56MW [WEBSMS] | CMIN
3/21/2024 12:47:14 PM | [NSO Update] Visayas Grid-03/21/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2662MW, PK=2233MW, RR=89MW, NetOpMargin: PM=340, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @338MW, PGPP1 @76MW [WEBSMS] | CVIS
3/21/2024 12:43:52 PM | [NSO Update] Luzon Grid-03/21/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14702MW, PK=10756MW, RR=312MW, NetOpMargin: PM=3634, EVE=3159 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @310MW, MSLC3 @305MW, ILIJAN B @300MW [WEBSMS] | CLUZ
3/21/2024 11:41:53 AM | Visayas Grid-03/21/2024 11:42: Colon - Dumanjug 138 kV Line 2 re-energized at 1141H. (Unplanned Outage) [WEBSMS] | CVIS
3/21/2024 11:33:13 AM | Mindanao Grid-03/21/2024 11:37: Agus 4 Unit 1 HEP online at 1129H (Unplanned Outage). [WEBSMS] | CMIN
3/21/2024 10:49:33 AM | Mindanao Grid-03/21/2024 10:54: WMPC DG07 online at 1046H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/21/2024 10:34:09 AM | Luzon Grid-03/21/2024 10:34: Bay-Makban B 230kV L1 de-energized at 1033H (Planned Outage) [WEBSMS] | CLUZ
3/21/2024 10:20:07 AM | Visayas Grid-03/21/2024 10:20: Colon - Dumanjug 138 kV Line 2 tripped at 1015H. (Unplanned Outage) [WEBSMS] | CVIS
3/21/2024 9:45:05 AM | Mindanao Grid-03/21/2024 09:49: WMPC DG10 online at 0943H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/21/2024 9:25:18 AM | Luzon Grid-03/21/2024 09:25: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0924H (Planned Outage) [WEBSMS] | CLUZ
3/21/2024 6:09:02 AM | Luzon Grid-03/21/2024 06:09: Labo-Naga 230kV Line 2 de-energized at 0608H (Planned Outage) [WEBSMS] | CLUZ
3/21/2024 5:55:31 AM | [NSO Update] Mindanao Grid-03/21/2024 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3184MW, PK=2317MW, RR=75MW, NetOpMargin: AM=792, PM=724, EVE=767 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @49MW, AG2 @66MW, AG4 @80MW, AG5 @26MW, AG6 @120MW, AG7 @11MW, PG4 @56MW [WEBSMS] | CMIN
3/21/2024 5:48:57 AM | [NSO Update] Visayas Grid-03/21/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2707MW, PK=2293MW, RR=87MW, NetOpMargin: AM=327, PM=370, EVE=307 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 336MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/21/2024 5:47:53 AM | [NSO Update] Luzon Grid-03/21/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14754MW, PK=10866MW, RR=301MW, NetOpMargin: AM=3587, PM=3087, EVE=2689 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 310MW, Masinloc 3 @ 305MW, SLTEC 1 @ 113MW, SLTEC 2 @ 105MW, Ilijan A @ 570MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
3/21/2024 5:42:02 AM | Luzon Grid-03/21/2024 05:42: Taytay SS 300MVA T05 restored at 0541H (Planned Outage) [WEBSMS] | CLUZ
3/21/2024 4:20:40 AM | [NSO Update] Mindanao Grid-03/21/2024 04:25: Weather Advisory: Northeast Monsoon affecting Luzon. Easterlies affecting Visayas and Mindanao. [WEBSMS] | CMIN
3/21/2024 4:20:26 AM | [NSO Update] Luzon Grid-03/21/2024 04:20: Weather Advisory: Northeast Monsoon affecting Luzon. Easterlies affecting Visayas and Mindanao. [WEBSMS] | CLUZ
3/21/2024 4:20:10 AM | [NSO Update] Visayas Grid-03/21/2024 04:20: Weather Advisory: Northeast Monsoon affecting Luzon. Easterlies affecting Visayas and Mindanao. [WEBSMS] | CVIS
3/21/2024 12:36:43 AM | Luzon Grid-03/21/2024 00:36: Taytay SS 300MVA T05 2 de-energized at 0036H (Planned Outage) [WEBSMS] | CLUZ
3/21/2024 12:18:36 AM | Visayas Grid-03/21/2024 00:18: CEDC U2 synchronized at 0016H (Unplanned Outage) [WEBSMS] | CVIS
3/20/2024 10:40:28 PM | Luzon Grid-03/20/2024 22:40: Bay-Makban B 230kV L2 commissioned at 2240H (Planned Outage) [WEBSMS] | CLUZ
3/20/2024 9:56:37 PM | Luzon Grid-03/20/2024 21:56: Bay-Makban 230kV L2 restored at 2154H, on commissioning. [WEBSMS] | CLUZ
3/20/2024 9:43:47 PM | Luzon Grid-03/20/2024 21:44: Muntinlupa-Gardner 115kV Tie Line 3 restored at 2143H (Planned Outage) [WEBSMS] | CLUZ
3/20/2024 8:31:53 PM | Mindanao Grid-03/20/2024 20:36: WMPC DG10 with 10MW load shutdown 2027H - MO Dispatch. [WEBSMS] | CMIN
3/20/2024 8:05:26 PM | Mindanao Grid-03/20/2024 20:10: WMPC DG10 End of RPS at 2000H. System voltage requirement. [WEBSMS] | CMIN
3/20/2024 7:32:37 PM | Visayas Grid-03/20/2024 19:32: SNBP tripped with 15.9MW load at 1921H (Unplanned Outage) [WEBSMS] | CVIS
3/20/2024 6:50:24 PM | Luzon Grid-03/20/2024 18:50: Muntinlupa-Gardner 115kV Tie Line 3 de-energized at 1850H (Planned Outage) [WEBSMS] | CLUZ
3/20/2024 6:39:00 PM | Luzon Grid-03/20/2024 18:39: Lal-lo-Cagayan North Solar 69kV Line 1 and Line 2 restored at 1836H and 1838H, respectively (Planned Outage) [WEBSMS] | CLUZ
3/20/2024 6:03:48 PM | Luzon Grid-03/20/2024 18:04: Lal-lo-UPSI Magapit BESS 69kV Line restored at 1803H (Planned Outage) [WEBSMS] | CLUZ
3/20/2024 5:54:00 PM | [NSO Update] Mindanao Grid-03/20/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3125MW, PK=2282MW, RR=74.3MW, NetOpMargin: EVE=768 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @51MW, AG2 @70MW, AG4 @78MW, AG5 @24MW, AG6 @125MW, AG7 @12MW, PG4 @56MW [WEBSMS] | CMIN
3/20/2024 5:53:02 PM | [NSO Update] Luzon Grid-03/20/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13738MW, PK=10601MW, RR=380MW, NetOpMargin: EVE=2757 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 310MW, Masinloc 3 @ 310MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
3/20/2024 5:52:28 PM | [NSO Update] Visayas Grid-03/20/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2525MW, PK=2128MW, RR=89MW, NetOpMargin: EVE=308 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 336MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/20/2024 5:41:51 PM | Mindanao Grid-03/20/2024 17:46: Agus6 transformer No.2 (7XF02AG6) energized at 1736H. P.O/GOMP [WEBSMS] | CMIN
3/20/2024 5:33:38 PM | Visayas Grid-03/20/2024 17:33: Compostela SS 150MVA TR6 230/138/13.8KV energized at 1724H. (Planned Outage) [WEBSMS] | CVIS
3/20/2024 5:19:50 PM | Mindanao Grid-03/20/2024 17:24: WMPC DG07 shutdown at 1714H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/20/2024 4:29:57 PM | Luzon Grid-03/20/2024 16:30: Labo-Naga 230kV Line 1 restored at 1629H (Planned Outage) [WEBSMS] | CLUZ
3/20/2024 12:53:16 PM | [NSO Update] Mindanao Grid-03/20/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3185MW, PK=2472MW, RR=77MW, NetOpMargin: PM=637, EVE=696 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @51MW, AG2 @70MW, AG4 @78MW, AG5 @24MW, AG6 @125MW, AG7 @12MW, PG4 @56MW [WEBSMS] | CMIN
3/20/2024 12:52:11 PM | [NSO Update] Visayas Grid-03/20/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2599MW, PK=2218MW, RR=92MW, NetOpMargin: PM=289, EVE=252 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @330MW, PGPP1 @76MW [WEBSMS] | CVIS
3/20/2024 12:50:48 PM | [NSO Update] Luzon Grid-03/20/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14720MW, PK=11134MW, RR=402MW, NetOpMargin: PM=3184, EVE=2723 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @310MW, MSLC3 @310MW, ILIJAN B @300MW [WEBSMS] | CLUZ
3/20/2024 12:47:28 PM | Mindanao Grid-03/20/2024 12:52: AGUS 7 Unit 2 with 9MW load shutdown at 1242H. OMC - insufficient water supply. (Unplanned Outage) [WEBSMS] | CMIN
3/20/2024 11:10:37 AM | Mindanao Grid-03/20/2024 11:15: WMPC DG07 online at 1016H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/20/2024 9:22:43 AM | Mindanao Grid-03/20/2024 09:27: WMPC DG10 online at 0919H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/20/2024 8:07:13 AM | Mindanao Grid-03/20/2024 08:11: AGUS 4 Unit 1 with 29.8MW load shutdown at 0802H. OMC - insufficient water supply. (Unplanned Outage) [WEBSMS] | CMIN
3/20/2024 6:59:49 AM | Mindanao Grid-03/20/2024 07:04: Agus6 transformer No.2 (7XF02AG6) de-energized at 0654H. P.O/GOMP [WEBSMS] | CMIN
3/20/2024 6:41:07 AM | Luzon Grid-03/20/2024 06:41: Lal-lo-Cagayan North Solar 69kV Line 1 and Line 2 de-energized at 0639H and 0640H, respectively. (Planned Outage) [WEBSMS] | CLUZ
3/20/2024 6:31:38 AM | [NSO Update] Mindanao Grid-03/20/2024 06:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3212MW, PK=2327MW, RR=75MW, NetOpMargin: AM=809, PM=660, EVE=720 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @51MW, AG2 @70MW, AG4 @78MW, AG5 @27MW, AG6 @125MW, AG7 @24MW, PG4 @56MW [WEBSMS] | CMIN
3/20/2024 6:30:59 AM | [NSO Update] Visayas Grid-03/20/2024 06:31: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2668MW, PK=2136MW, RR=87MW, NetOpMargin: AM=445, PM=272, EVE=255 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @336MW, PGPP1 @76MW [WEBSMS] | CVIS
3/20/2024 6:30:29 AM | Visayas Grid-03/20/2024 06:30: Compostela SS 150MVA TR6 230/138/13.8KV de-energized at 0625H. (Planned Outage) [WEBSMS] | CVIS
3/20/2024 6:30:08 AM | [NSO Update] Luzon Grid-03/20/2024 06:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14719MW, PK=10855MW, RR=391MW, NetOpMargin: AM=3473, PM=2967, EVE=2629 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MASINLOC 1 @310MW, MASINLOC 3 @310MW, SLTEC 2 @112MW, ILIJAN B @300MW [WEBSMS] | CLUZ
3/20/2024 6:26:10 AM | Luzon Grid-03/20/2024 06:26: Labo-Naga 230kV Line 1 de-energized at 0622H (Planned Outage) [WEBSMS] | CLUZ
3/20/2024 6:15:14 AM | Luzon Grid-03/20/2024 06:15: Lal-lo-UPSI Magapit BESS 69kV Line de-energized at 0611H (Planned Outage) [WEBSMS] | CLUZ
3/20/2024 4:30:04 AM | [NSO Update] Mindanao Grid-03/20/2024 04:34: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
3/20/2024 4:29:38 AM | [NSO Update] Visayas Grid-03/20/2024 04:29: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
3/20/2024 4:29:22 AM | [NSO Update] Luzon Grid-03/20/2024 04:29: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/20/2024 12:44:01 AM | Luzon Grid-03/20/2024 00:44: Balsik-San Marcelino 230kV lines 1 and 2 were restored at 0039H and 0041H respectively. (Planned Outage) [WEBSMS] | CLUZ
3/20/2024 12:01:26 AM | Mindanao Grid-03/20/2024 00:06: SEC2 shutdown at 2357H (Unplanned Outage). Emergency shutdown to facilitate repair of electrostatic precipitator. Implemented gradual unloading thru RTD. [WEBSMS] | CMIN
3/19/2024 9:20:44 PM | Visayas Grid-03/19/2024 21:20: CABI PP cut in at 2023H (Unplanned Outage) [WEBSMS] | CVIS
3/19/2024 8:44:30 PM | Mindanao Grid-03/19/2024 20:49: Surallah Power Generation (SPGI) online at 1849H (Unplanned Outage). [WEBSMS] | CMIN
3/19/2024 8:00:40 PM | Visayas Grid-03/19/2024 20:00: CABI PP tripped at 1945H (Unplanned Outage) [WEBSMS] | CVIS
3/19/2024 7:47:49 PM | Mindanao Grid-03/19/2024 19:52: WMPC DG04 shutdown at 1713H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/19/2024 7:30:31 PM | Visayas Grid-03/19/2024 19:30: VMC Cogen cut in at 1814H (Unplanned Outage) [WEBSMS] | CVIS
3/19/2024 7:16:11 PM | Mindanao Grid-03/19/2024 19:20: WMPC DG10 shutdown at 1914H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/19/2024 6:06:26 PM | [NSO Update] Luzon Grid-03/19/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13627MW, PK=10478MW, RR=290MW, NetOpMargin: EVE=2859 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: GMEC 2 @220MW, MASINLOC 1 @310MW, MASINLOC 3 @305MW, ILIJAN B @300MW [WEBSMS] | CLUZ
3/19/2024 5:49:11 PM | Visayas Grid-03/19/2024 17:49: Compostela SS 150MVA Transformer 3 energized at 1745H (Planned Outage) [WEBSMS] | CVIS
3/19/2024 5:43:40 PM | [NSO Update] Visayas Grid-03/19/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2493MW, PK=2153MW, RR=91MW, NetOpMargin: EVE=249 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @336MW, PGPP1 @76MW [WEBSMS] | CVIS
3/19/2024 5:43:35 PM | [NSO Update] Mindanao Grid-03/19/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3313MW, PK=2383MW, RR=72MW, NetOpMargin: EVE=858 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @38.5MW, MA2 @48MW, AG1 @53MW, AG2 @72MW, AG4 @124MW, AG5 @28MW, AG6 @130MW, AG7 @25MW, PG4 @66MW [WEBSMS] | CMIN
3/19/2024 5:28:49 PM | Luzon Grid-03/19/2024 17:29: Balsik-San Marcelino 230kV lines 2 and 1 were de-energized at 1726H and 1727H respectively. (Planned Outage) [WEBSMS] | CLUZ
3/19/2024 4:50:56 PM | Mindanao Grid-03/19/2024 16:55: WMPC DG07 shutdown at 1644H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/19/2024 4:20:03 PM | Mindanao Grid-03/19/2024 16:24: Talomo 1 Unit 2 with 0.2MW load shutdown at 1611H (Unplanned Outage). Insufficient water supply (outside management control). [WEBSMS] | CMIN
3/19/2024 1:51:50 PM | Mindanao Grid-03/19/2024 13:56: WMPC DG04 online at 1342H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/19/2024 12:54:40 PM | [NSO Update] Mindanao Grid-03/19/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3377MW, PK=2452MW, RR=77MW, NetOpMargin: PM=848, EVE=910 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @38.5MW, MA2 @48MW, AG1 @53MW, AG2 @72MW, AG4 @124MW, AG5 @28MW, AG6 @130MW, AG7 @25MW, PG4 @66MW [WEBSMS] | CMIN
3/19/2024 12:39:45 PM | Mindanao Grid-03/19/2024 12:44: WMPC DG07 online at 1238H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/19/2024 12:39:18 PM | [NSO Update] Visayas Grid-03/19/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2670MW, PK=2212MW, RR=93MW, NetOpMargin: PM=366, EVE=251 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @79.5MW, LEYTE A @336MW, PGPP1 @55MW [WEBSMS] | CVIS
3/19/2024 12:36:56 PM | [NSO Update] Luzon Grid-03/19/2024 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14709MW, PK=11284MW, RR=312MW, NetOpMargin: PM=3113, EVE=2502 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: GMEC 2 @250MW, MSLC1 @310MW, MSLC3 @305MW, ILIJAN B @300MW [WEBSMS] | CLUZ
3/19/2024 12:22:49 PM | Luzon Grid-03/19/2024 12:23: San Roque Unit 3 (70MW) tripped at 1214H (Unplanned Outage) [WEBSMS] | CLUZ
3/19/2024 12:20:51 PM | Luzon Grid-03/19/2024 12:21: San Roque Unit 3 (70MW) tripped at 1214H (Unplanned Outage) [WEBSMS] | CLUZ
3/19/2024 9:51:18 AM | Mindanao Grid-03/19/2024 09:55: WMPC DG10 online at 0948H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/19/2024 5:44:30 AM | [NSO Update] Mindanao Grid-03/19/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3386MW, PK=2230MW, RR=75MW, NetOpMargin: AM=1081, PM=961, EVE=1000 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @38.5MW, MA2 @48MW, AG1 @53MW, AG2 @72MW, AG4 @124MW, AG5 @28MW, AG6 @130MW, AG7 @25MW, PG4 @66MW [WEBSMS] | CMIN
3/19/2024 5:43:38 AM | [NSO Update] Visayas Grid-03/19/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2906MW, PK=2163MW, RR=91MW, NetOpMargin: AM=653, PM=476, EVE=342 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 79.5MW, Leyte A @ 336MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/19/2024 5:41:41 AM | [NSO Update] Luzon Grid-03/19/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14759MW, PK=10717MW, RR=301MW, NetOpMargin: AM=3740, PM=2915, EVE=2457 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: GMEC 2 @ 190MW, Masinloc 1 @ 310MW, Masinloc 3 @ 310MW, Ilijan A @ 570MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
3/19/2024 4:08:07 AM | [NSO Update] Mindanao Grid-03/19/2024 04:12: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
3/19/2024 4:07:55 AM | [NSO Update] Visayas Grid-03/19/2024 04:08: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
3/19/2024 4:07:39 AM | [NSO Update] Luzon Grid-03/19/2024 04:07: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
3/19/2024 2:28:06 AM | Luzon Grid-03/19/2024 02:28: SLPGC 1 online at 0227H (Unplanned Outage). [WEBSMS] | CLUZ
3/18/2024 9:55:32 PM | Luzon Grid-03/18/2024 21:55: SLPGC 1 with 150MW load tripped at 2153H (Unplanned Outage). [WEBSMS] | CLUZ
3/18/2024 8:57:24 PM | Visayas Grid-03/18/2024 20:57: MAHA A Unit 2 cut out at 2036H (Unplanned Outage) [WEBSMS] | CVIS
3/18/2024 7:47:06 PM | Mindanao Grid-03/18/2024 19:51: WMPC DG10 shutdown at 1943H. RPS-System Voltage Requirement [WEBSMS] | CMIN
3/18/2024 6:20:36 PM | Visayas Grid-03/18/2024 18:20: Cebu-Umapad 230kV Line 2 (underground XLPE cable portion) de-energized at 1802H after 24 hour soaking (Planned Outage) [WEBSMS] | CVIS
3/18/2024 5:48:35 PM | [NSO Update] Mindanao Grid-03/18/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3285MW, PK=2315MW, RR=74.3MW, NetOpMargin: EVE=895 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @55MW, AG2 @74MW, AG4 @78MW, AG5 @30MW, AG6 @136MW, AG7 @26MW, PG4 @66MW [WEBSMS] | CMIN
3/18/2024 5:47:42 PM | [NSO Update] Visayas Grid-03/18/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2619MW, PK=2113MW, RR=91MW, NetOpMargin: EVE=415 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 80MW, Leyte A @ 325MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/18/2024 5:46:22 PM | [NSO Update] Luzon Grid-03/18/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13279MW, PK=10621MW, RR=340MW, NetOpMargin: EVE=2318 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: GMEC 2 @ 220MW, Masinloc 1 @ 310MW, Masinloc 3 @ 310MW, Ilijan A @ 570MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
3/18/2024 4:49:18 PM | Mindanao Grid-03/18/2024 16:53: WMPC DG06 shutdown at 1643H. RPS-System Voltage Requirement [WEBSMS] | CMIN
3/18/2024 4:20:13 PM | Mindanao Grid-03/18/2024 16:24: New Bataan HEP (NBT) with 1.3MW load tripped at 1529H. Indication: for further investigation (Unplanned Outage) [WEBSMS] | CMIN
3/18/2024 2:04:58 PM | Mindanao Grid-03/18/2024 14:09: SPC Mati, with 3.0MW load on Emergency Shutdown at 1356H due to lube oil high temperature. (Unplanned Outage) [WEBSMS] | CMIN
3/18/2024 1:47:36 PM | Mindanao Grid-03/18/2024 13:52: SPC Mati online at 1344H MO Dispatch. (Unplanned Outage). [WEBSMS] | CMIN
3/18/2024 1:26:59 PM | Mindanao Grid-03/18/2024 13:31: SPC Mati, with 3.0MW load on Emergency Shutdown at 1314H due to engine problem. (Unplanned Outage) [WEBSMS] | CMIN
3/18/2024 1:02:39 PM | [NSO Update] Mindanao Grid-03/18/2024 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3350MW, PK=2386MW, RR=77MW, NetOpMargin: PM=886, EVE=918 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @55MW, AG2 @74MW, AG4 @78MW, AG5 @30MW, AG6 @136MW, AG7 @26MW, PG4 @66MW [WEBSMS] | CMIN
3/18/2024 12:59:50 PM | [NSO Update] Visayas Grid-03/18/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2822MW, PK=2187MW, RR=93MW, NetOpMargin: PM=542, EVE=373 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80MW, LEYTE A @325MW, PGPP1 @76MW [WEBSMS] | CVIS
3/18/2024 12:59:06 PM | Mindanao Grid-03/18/2024 13:03: WMPC DG06 online at 1256H. RPS-System Voltage Requirement [WEBSMS] | CMIN
3/18/2024 12:57:59 PM | [NSO Update] Luzon Grid-03/18/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14557MW, PK=11228MW, RR=362MW, NetOpMargin: PM=2967, EVE=2234 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: GMEC 2 @220MW, MSLC1 @310MW, MSLC3 @310MW, ILIJAN A @570MW, ILIJAN B @165MW [WEBSMS] | CLUZ
3/18/2024 11:49:25 AM | Visayas Grid-03/18/2024 11:49: Leyte-A Mahanagdong Unit 1 re-online @1134H, ( Planned Outage ) [WEBSMS] | CVIS
3/18/2024 10:24:23 AM | Visayas Grid-03/18/2024 10:24: CEDC unit# 2 emergency out @1020H, boiler back pass tube leak. ( Unplanned Outage ) [WEBSMS] | CVIS
3/18/2024 9:47:04 AM | Mindanao Grid-03/18/2024 09:51: MINERGY Coal (MCC) Unit 3 online at 0944H from FO. (Unplanned Outage) [WEBSMS] | CMIN
3/18/2024 9:28:12 AM | Mindanao Grid-03/18/2024 09:32: WMPC DG10 online at 0926H. RPS-System Voltage Requirement [WEBSMS] | CMIN
3/18/2024 5:35:49 AM | [NSO Update] Mindanao Grid-03/18/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3287MW, PK=2235MW, RR=75MW, NetOpMargin: AM=976, PM=915, EVE=986 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @55MW, AG2 @74MW, AG4 @58MW, AG5 @30MW, AG6 @136MW, AG7 @26MW, PG4 @66MW [WEBSMS] | CMIN
3/18/2024 5:34:15 AM | [NSO Update] Visayas Grid-03/18/2024 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2847MW, PK=2123MW, RR=89MW, NetOpMargin: AM=635, PM=480, EVE=335 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @297MW, PGPP1 @76MW [WEBSMS] | CVIS
3/18/2024 5:32:30 AM | [NSO Update] Luzon Grid-03/18/2024 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14400MW, PK=10899MW, RR=351MW, NetOpMargin: AM=3151, PM=2707, EVE=1974 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: GMEC 2 @220MW, MSLC1 @310MW, MSLC3 @310MW, ILIJAN A @570MW, ILIJAN B @165MW [WEBSMS] | CLUZ
3/18/2024 4:04:05 AM | [NSO Update] Luzon Grid-03/18/2024 04:04: Weather Update: Easterlies affecting the country [WEBSMS] | CLUZ
3/18/2024 4:03:50 AM | [NSO Update] Visayas Grid-03/18/2024 04:03: Weather Update: Easterlies affecting the country [WEBSMS] | CVIS
3/18/2024 4:03:26 AM | [NSO Update] Mindanao Grid-03/18/2024 04:07: Weather Update: Easterlies affecting the country [WEBSMS] | CMIN
3/18/2024 3:10:19 AM | Mindanao Grid-03/18/2024 03:14: Agus 2 U3 online at 0306H. Unplanned Outage. [WEBSMS] | CMIN
3/18/2024 1:59:06 AM | Luzon Grid-03/18/2024 01:59: San Jose 230kV Bus 2 restored at 0158H (Planned Outage) [WEBSMS] | CLUZ
3/18/2024 1:45:21 AM | Visayas Grid-03/18/2024 01:45: PEDC U2 cut in at 0144H (Unplanned Outage) [WEBSMS] | CVIS
3/18/2024 1:02:42 AM | Luzon Grid-03/18/2024 01:02: Balsik-San Marcelino 230kV Line 2 restored at 0102H (Planned Outage) [WEBSMS] | CLUZ
3/18/2024 1:00:18 AM | Luzon Grid-03/18/2024 01:00: Balsik-San Marcelino 230kV Line 1 restored at 0059H (Planned Outage) [WEBSMS] | CLUZ
3/17/2024 10:48:27 PM | Mindanao Grid-03/17/2024 22:52: Agus 2 U3 tripped at 2239H. Unplanned Outage. [WEBSMS] | CMIN
3/17/2024 9:51:07 PM | Luzon Grid-03/17/2024 21:51: San Jose 230kV Bus 2 de-energized at 2150H (Planned Outage) [WEBSMS] | CLUZ
3/17/2024 8:47:18 PM | Visayas Grid-03/17/2024 20:47: Quiot SS 100 MVA TR1 energized at 2045H (Planned Outage) [WEBSMS] | CVIS
3/17/2024 6:25:07 PM | Luzon Grid-03/17/2024 18:25: Correction: Ambuklao - Bayombong 230kV Line 2 energized at 1759H (Planned Outage) [WEBSMS] | CLUZ
3/17/2024 6:00:25 PM | Luzon Grid-03/17/2024 18:00: Ambuklao - Bayombong 230kV Line 2 energized at 0559H (Planned Outage) [WEBSMS] | CLUZ
3/17/2024 5:56:57 PM | [NSO Update] Luzon Grid-03/17/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13018MW, PK=9417MW, RR=210MW, NetOpMargin: EVE=3391 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: GMEC 2 @200MW, MSLC1 @310MW, MSLC3 @310MW, ILIJAN A @570MW ILIJAN B @165MW [WEBSMS] | CLUZ
3/17/2024 5:54:37 PM | Visayas Grid-03/17/2024 17:54: Toledo SS 138KV Bus 1 energized at 1749H. (Planned Outage) [WEBSMS] | CVIS
3/17/2024 5:47:57 PM | Luzon Grid-03/17/2024 17:48: San Lorenzo 230kV Bus 1 restored at 1747H (Planned Outage) [WEBSMS] | CLUZ
3/17/2024 5:45:58 PM | Luzon Grid-03/17/2024 17:46: Balsik-San Marcelino 230kV Line 1 de-energized at 1745H (Planned Outage) [WEBSMS] | CLUZ
3/17/2024 5:41:21 PM | Luzon Grid-03/17/2024 17:41: Botolan-Subic 230kV Line restored at 1741H (Planned Outage) [WEBSMS] | CLUZ
3/17/2024 5:34:01 PM | [NSO Update] Mindanao Grid-03/17/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3301MW, PK=2053MW, RR=74MW, NetOpMargin: EVE=1173 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @55MW, AG2 @74MW, AG4 @93MW, AG5 @30MW, AG6 @136MW, AG7 @26MW, PG4 @66MW [WEBSMS] | CMIN
3/17/2024 5:31:22 PM | [NSO Update] Visayas Grid-03/17/2024 17:31: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2527MW, PK=2085MW, RR=86MW, NetOpMargin: EVE=356 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @288MW, PGPP1 @76MW [WEBSMS] | CVIS
3/17/2024 5:31:08 PM | Luzon Grid-03/17/2024 17:31: Balsik-San Marcelino 230kV Line 2 de-energized at 1730H (Planned Outage) [WEBSMS] | CLUZ
3/17/2024 5:15:26 PM | Luzon Grid-03/17/2024 17:15: San Rafael 230kV Bus 1 restored at 1714H (Planned Outage) [WEBSMS] | CLUZ
3/17/2024 5:06:16 PM | Mindanao Grid-03/17/2024 17:10: LAMSAN Biomass (LSK) online at 1701H. Planned Outage. [WEBSMS] | CMIN
3/17/2024 4:47:09 PM | Mindanao Grid-03/17/2024 16:51: LAMSAN Biomass (LSK) shutdown at 1642H. Planned Outage. [WEBSMS] | CMIN
3/17/2024 4:24:57 PM | Mindanao Grid-03/17/2024 16:29: Kibawe-Sultan Kudarat 138 kV Line 1(7LI1KIB-SKU) energized at 1621H. P.O/GOMP. [WEBSMS] | CMIN
3/17/2024 12:42:33 PM | [NSO Update] Mindanao Grid-03/17/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3352MW, PK=1843MW, RR=77MW, NetOpMargin: PM=1432, EVE=1191 Highest Unit O/L: GNPK 1, 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @55MW, AG2 @74MW, AG4 @93MW, AG5 @30MW, AG6 @136MW, AG7 @26MW, PG4 @66MW [WEBSMS] | CMIN
3/17/2024 12:41:13 PM | [NSO Update] Visayas Grid-03/17/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2673MW, PK=1825MW, RR=89MW, NetOpMargin: PM=759, EVE=276 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @297MW, PGPP1 @76MW [WEBSMS] | CVIS
3/17/2024 12:39:07 PM | [NSO Update] Luzon Grid-03/17/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14435MW, PK=9118MW, RR=229MW, NetOpMargin: PM=5088, EVE=3457 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: GMEC 2 @210MW, MSLC1 @310MW, MSLC3 @310MW [WEBSMS] | CLUZ
3/17/2024 8:05:37 AM | Luzon Grid-03/17/2024 08:05: Botolan-Subic 230kV Line de-energized at 0805H (Planned Outage) [WEBSMS] | CLUZ
3/17/2024 7:36:37 AM | Luzon Grid-03/17/2024 07:36: San Rafael SS 230kV Bus 1 de-energized at 0736H (Planned Outage) [WEBSMS] | CLUZ
3/17/2024 7:04:22 AM | Mindanao Grid-03/17/2024 07:08: LAMSAN Biomass (LSK) online at 0700H. Planned Outage. [WEBSMS] | CMIN
3/17/2024 6:47:50 AM | Mindanao Grid-03/17/2024 06:52: Sultan Kudarat 138 kV Line 1(7LI1KIB-SKU) de-energized at 0642H. P.O/GOMP. [WEBSMS] | CMIN
3/17/2024 6:32:17 AM | Luzon Grid-03/17/2024 06:32: Ambuklao-Bayombong 230kV Line 2 de-energized at 0632H (Planned Outage) [WEBSMS] | CLUZ
3/17/2024 6:07:35 AM | Mindanao Grid-03/17/2024 06:12: Davao SS 138kV 150MVA Transformer # 1 successfully restored at 0547H. From Unplanned Outage. [WEBSMS] | CMIN
3/17/2024 6:04:47 AM | Mindanao Grid-03/17/2024 06:09: LAMSAN Biomass (LSK) shutdown at 0600H. Planned Outage. [WEBSMS] | CMIN
3/17/2024 5:50:00 AM | [NSO Update] Luzon Grid-03/17/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14328MW, PK=8884MW, RR=221MW, NetOpMargin: AM=5222, PM=4812, EVE=3426 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: GMEC 2 @210MW, MASINLOC 1 @310MW, MASINLOC 3 @310MW, MPGC 1 @90MW, ILIJAN B @ 300MW [WEBSMS] | CLUZ
3/17/2024 5:38:30 AM | Visayas Grid-03/17/2024 05:38: Quiot SS 100 MVA TR1 de-energized at 0538H (Planned Outage) [WEBSMS] | CVIS
3/17/2024 5:36:45 AM | [NSO Update] Visayas Grid-03/17/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2595MW, PK=1726MW, RR=87MW, NetOpMargin: AM=782, PM=735, EVE=260 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @297MW, PGPP1 @76MW [WEBSMS] | CVIS
3/17/2024 5:36:39 AM | [NSO Update] Mindanao Grid-03/17/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3371MW, PK=1847MW, RR=75MW, NetOpMargin: AM=1449, PM=1313, EVE=1072 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @55MW, AG2 @74MW, AG4 @93MW, AG5 @30MW, AG6 @136MW, AG7 @26MW, PG4 @66MW [WEBSMS] | CMIN
3/17/2024 4:04:53 AM | [NSO Update] Mindanao Grid-03/17/2024 04:09: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CMIN
3/17/2024 4:04:29 AM | [NSO Update] Visayas Grid-03/17/2024 04:04: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CVIS
3/17/2024 4:04:13 AM | [NSO Update] Luzon Grid-03/17/2024 04:04: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CLUZ
3/17/2024 3:00:31 AM | Luzon Grid-03/17/2024 03:00: For info: Ilijan ST2 online at 0145H (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2024 1:04:40 AM | Mindanao Grid-03/17/2024 01:09: Davao SS 138kV 150MVA Transformer # 1 on emergency shutdown at 2354H for correction of oil leaking at phase B 69KV bushing. Unplanned Outage. [WEBSMS] | CMIN
3/17/2024 12:03:35 AM | Luzon Grid-03/17/2024 00:03: Ilijan GT 2-1 online at 0001H (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2024 12:02:21 AM | Visayas Grid-03/17/2024 00:02: PEDC U2 emergency shutdown at 0000H (Unplanned Outage) [WEBSMS] | CVIS
3/16/2024 11:38:42 PM | Mindanao Grid-03/16/2024 23:43: Manolo Fortich-Maramag 138kV L2 (7LI2MNO-MRM) re-energized at 2316H. From Planned Outage / GOMP. [WEBSMS] | CMIN
3/16/2024 10:19:23 PM | Luzon Grid-03/16/2024 22:19: Cayanga Solar Plant 230kV Bus 1 restored at 2219H (Planned Outage) [WEBSMS] | CLUZ
3/16/2024 7:44:39 PM | Visayas Grid-03/16/2024 19:44: Sta. Barbara SS 3x33.33 MVA Mobile Transformer energized without load at 1940H. (Temporary Replacement of Sta. Barbara 50 MVA TR2) [WEBSMS] | CVIS
3/16/2024 7:16:36 PM | Mindanao Grid-03/16/2024 19:21: Matanao-Gensan 138kV L1 re-energized at 1847H. From P&E request (Planned Outage /Non-GOMP). [WEBSMS] | CMIN
3/16/2024 7:14:25 PM | Mindanao Grid-03/16/2024 19:18: General Santos SS 138kV Busbar # 1 (7BS01GSA) re-energized at 1839H. From P&E request (Planned outage / N-GOMP). [WEBSMS] | CMIN
3/16/2024 7:04:07 PM | Visayas Grid-03/16/2024 19:04: East Asia Utilities Corp. (EAUC) plant maintenance completed at 1900H (Planned Outage) [WEBSMS] | CVIS
3/16/2024 6:50:55 PM | Luzon Grid-03/16/2024 18:51: Taytay 300MVA T02 restored at 1850H (Planned Outage) [WEBSMS] | CLUZ
3/16/2024 6:26:22 PM | Luzon Grid-03/16/2024 18:26: SCPC 4 online at 1819H (Planned Outage) [WEBSMS] | CLUZ
3/16/2024 5:50:46 PM | Mindanao Grid-03/16/2024 17:55: Aurora SS 138kV Power Transformer No. 2 (7XFO2AUR) re-energized at 1737H. From Planned Outage / GOMP. [WEBSMS] | CMIN
3/16/2024 5:49:13 PM | Visayas Grid-03/16/2024 17:49: Toledo SS 138 kV Bus 1 energized at 1744H. (Planned Outage) [WEBSMS] | CVIS
3/16/2024 5:36:57 PM | [NSO Update] Luzon Grid-03/16/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13172MW, PK=10216MW, RR=340MW, NetOpMargin: EVE=2616 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 310MW, Masinloc 3 @ 310MW, MPGC 1 @ 60MW [WEBSMS] | CLUZ
3/16/2024 5:36:53 PM | [NSO Update] Visayas Grid-03/16/2024 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2657MW, PK=2101MW, RR=86MW, NetOpMargin: EVE=470 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @293MW, PGPP1 @76MW [WEBSMS] | CVIS
3/16/2024 5:36:42 PM | [NSO Update] Mindanao Grid-03/16/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3244MW, PK=2228MW, RR=74MW, NetOpMargin: EVE=942 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @94MW, AG5 @30MW, AG6 @138MW, AG7 @27MW, PG4 @66MW [WEBSMS] | CMIN
3/16/2024 5:00:36 PM | Visayas Grid-03/16/2024 17:00: Colon - Dumanjug 138 KV Line 2 energized at 1657H. (Planned Outage) [WEBSMS] | CVIS
3/16/2024 4:15:19 PM | Mindanao Grid-03/16/2024 16:19: WMPC DG10 shutdown at 1614H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/16/2024 3:32:02 PM | Luzon Grid-03/16/2024 15:32: For Info: San Marcelino 100MVAR Capacitor Bank # 1 & 2 completed commissioning test at 1240H & 1518H, respectively [WEBSMS] | CLUZ
3/16/2024 2:58:10 PM | Luzon Grid-03/16/2024 14:58: Naga-Daraga 230kV Line restored at 1456H (Planned Outage) [WEBSMS] | CLUZ
3/16/2024 1:51:49 PM | Luzon Grid-03/16/2024 13:51: Casecnan-Nagsaag 230kV Line 1 restored at 1350H (Planned Outage) [WEBSMS] | CLUZ
3/16/2024 1:36:07 PM | Luzon Grid-03/16/2024 13:36: For Info: San Marcelino 100MVAR Capacitor Bank # 2 successfully energized at 1334H. On going commissioning test [WEBSMS] | CLUZ
3/16/2024 1:35:04 PM | Mindanao Grid-03/16/2024 13:39: WMPC DG10 online at 1330H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/16/2024 1:23:32 PM | Mindanao Grid-03/16/2024 13:28: Aurora SS 138kV Busbar # 1 re-energized at 1251H. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
3/16/2024 12:49:03 PM | [NSO Update] Mindanao Grid-03/16/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: CAP=3302MW, PK=2176MW, RR=77MW, NetOpMargin: PM=1048, EVE=958 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @55MW, AG2 @74MW, AG4 @93MW, AG5 @30MW, AG6 @138MW, AG7 @27MW, PG4 @66MW [WEBSMS] | CMIN
3/16/2024 12:47:11 PM | [NSO Update] Visayas Grid-03/16/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2864MW, PK=2077MW, RR=89MW, NetOpMargin: PM=698, EVE=348 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 297MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/16/2024 12:39:49 PM | [NSO Update] Luzon Grid-03/16/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14373MW, PK=10238MW, RR=362MW, NetOpMargin: PM=3773, EVE=2750 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 310MW, Masinloc 3 @ 310MW, MPGC 1 @ 60MW [WEBSMS] | CLUZ
3/16/2024 11:32:15 AM | Luzon Grid-03/16/2024 11:32: For Info: San Marcelino 100MVAR Capacitor Bank # 1 successfully energized at 1129H. On going commissioning test [WEBSMS] | CLUZ
3/16/2024 11:10:49 AM | Mindanao Grid-03/16/2024 11:15: FDC Unit 2 online at 1040H. From PMS (GOMP). [WEBSMS] | CMIN
3/16/2024 9:13:15 AM | Luzon Grid-03/16/2024 09:13: San Jose-Angat 115kV Line 2 restored at 0912H (Planned Outage) [WEBSMS] | CLUZ
3/16/2024 8:25:30 AM | Mindanao Grid-03/16/2024 08:29: Matanao-Gensan 138kV L1 de-energized at 0738H. P&E request. Planned Outage /Non-GOMP. [WEBSMS] | CMIN
3/16/2024 8:03:55 AM | Mindanao Grid-03/16/2024 08:08: General Santos SS 138kV Bus 1 (7BS01GSA) de-energized at 0752H. Planned outage / N-GOMP. [WEBSMS] | CMIN
3/16/2024 8:01:21 AM | Luzon Grid-03/16/2024 08:01: Cayanga Solar Plant 230kV Bus 1 de-energized at 0801H (Planned Outage) [WEBSMS] | CLUZ
3/16/2024 8:00:49 AM | Mindanao Grid-03/16/2024 08:05: Matanao-General Santos 138kV Line 1 (7LI1MAT-GSA) de-energized at 0738H. Planned outage / N-GOMP. [WEBSMS] | CMIN
3/16/2024 7:33:55 AM | Visayas Grid-03/16/2024 07:34: Toledo SS 138KV Bus 1 de-energized at 0731H. (Planned Outage) [WEBSMS] | CVIS
3/16/2024 7:07:01 AM | Luzon Grid-03/16/2024 07:07: Taytay 300MVA T02 de-energized at 0706H (Planned Outage) [WEBSMS] | CLUZ
3/16/2024 6:47:51 AM | Luzon Grid-03/16/2024 06:47: San Jose SS 115kV Bus 2 restored at 0647H (Planned Outage) [WEBSMS] | CLUZ
3/16/2024 6:45:43 AM | Mindanao Grid-03/16/2024 06:50: Aurora SS 138kV Bus #1 (7BS01AUR) de-energized at 0636H. Planned outage / N-GOMP. [WEBSMS] | CMIN
3/16/2024 6:43:02 AM | Visayas Grid-03/16/2024 06:43: East Asia Utilities Corp. (EAUC) on total plant maintenance shutdown GOMP at 0637H (Planned Outage) [WEBSMS] | CVIS
3/16/2024 6:26:31 AM | Luzon Grid-03/16/2024 06:26: San Lorenzo 230kV Bus 1 de-energized at 0621H (Planned Outage) [WEBSMS] | CLUZ
3/16/2024 6:13:25 AM | Mindanao Grid-03/16/2024 06:17: Aurora 138kV transformer No.2 (7XF02AUR) de-energized at 0608H. P.O/GOMP [WEBSMS] | CMIN
3/16/2024 6:10:42 AM | Luzon Grid-03/16/2024 06:10: Naga-Daraga 230kV Line de-energized at 0610H (Planned Outage) [WEBSMS] | CLUZ
3/16/2024 6:03:10 AM | [NSO Update] Mindanao Grid-03/16/2024 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3174MW, PK=2072MW, RR=75MW, NetOpMargin: AM=1026, PM=885, EVE=787 Highest Unit O/L: GNPK 1,2,3&4 & 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @55MW, AG2 @74MW, AG4 @93MW, AG5 @30MW, AG6 @138MW, AG7 @27MW, PG4 @66MW [WEBSMS] | CMIN
3/16/2024 5:59:39 AM | [NSO Update] Visayas Grid-03/16/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2855MW, PK=1987MW, RR=87MW, NetOpMargin: AM=781, PM=641, EVE=264 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @297MW, PGPP1 @76MW [WEBSMS] | CVIS
3/16/2024 5:54:08 AM | [NSO Update] Luzon Grid-03/16/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14376MW, PK=9961MW, RR=351MW, NetOpMargin: AM=4064, PM=3767, EVE=2687 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: GMEC 2 @150MW, MSLC1 @310MW, MSLC3 @310MW [WEBSMS] | CLUZ
3/16/2024 5:47:35 AM | Mindanao Grid-03/16/2024 05:52: Manolo- Maramag 138 kV L2 (7LI2MNO-MRM) de-energized at 0539H. P.O/GOMP. [WEBSMS] | CMIN
3/16/2024 5:45:16 AM | Visayas Grid-03/16/2024 05:45: Colon-Dumanjug 138 KV Line 2 de-energized at 0544H (Planned Outage) [WEBSMS] | CVIS
3/16/2024 4:26:25 AM | [NSO Update] Mindanao Grid-03/16/2024 04:30: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
3/16/2024 4:25:12 AM | [NSO Update] Visayas Grid-03/16/2024 04:25: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
3/16/2024 4:24:46 AM | [NSO Update] Luzon Grid-03/16/2024 04:24: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/16/2024 2:53:10 AM | Luzon Grid-03/16/2024 02:53: Balsik-San Marcelino 230kV Line 1 and 2 restored at 0237H and 0252H, respectively. (Planned Outage) [WEBSMS] | CLUZ
3/16/2024 1:09:50 AM | Luzon Grid-03/16/2024 01:09: San Jose-Angat 115kV Line 2 de-energized at 0109H (Planned Outage) [WEBSMS] | CLUZ
3/16/2024 12:28:44 AM | Luzon Grid-03/16/2024 00:28: San Jose SS 115kV Bus 2 de-energized at 0028H (Planned Outage) [WEBSMS] | CLUZ
3/15/2024 11:49:01 PM | Luzon Grid-03/15/2024 23:49: Batangas SS 230kV Bus 2 restored at 2348H (Planned Outage) [WEBSMS] | CLUZ
3/15/2024 11:03:51 PM | Mindanao Grid-03/15/2024 23:08: Baloi- Agus6 138 kV L1 (7LI1BLO-AG6) energized at Baloi side 2233H and looped at Agus6 side 2300H. Note: Above said line was transferred/swing to bay 4 (7-04CB04AG6/7-04CB24AG6 from bay 2 (7-02CB08AG6/ 7-02CD24AG6). P.O/Non-GOMP. [WEBSMS] | CMIN
3/15/2024 9:31:08 PM | Visayas Grid-03/15/2024 21:31: Nasulo re-online at 2127H (Unplanned Outage) [WEBSMS] | CVIS
3/15/2024 7:45:07 PM | Mindanao Grid-03/15/2024 19:49: WMPC DG10 shutdown at 1943H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/15/2024 7:36:16 PM | Luzon Grid-03/15/2024 19:36: Batangas SS 230kV Bus 2 de-energized at 1935H (Planned Outage) [WEBSMS] | CLUZ
3/15/2024 6:06:43 PM | Luzon Grid-03/15/2024 18:06: Balsik-San Marcelino 230kV Line 1 de-energized at 1806H (Planned Outage) [WEBSMS] | CLUZ
3/15/2024 5:42:35 PM | [NSO Update] Mindanao Grid-03/15/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3094MW, PK=2298MW, RR=74MW, NetOpMargin: EVE=722 Highest Unit O/L: GNPK 1,2,3&4 & 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @94MW, AG5 @30MW, AG6 @138MW, AG7 @27MW, PG4 @66MW [WEBSMS] | CMIN
3/15/2024 5:41:40 PM | [NSO Update] Visayas Grid-03/15/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2479MW, PK=2156MW, RR=86MW, NetOpMargin: EVE=237 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @297MW, PGPP1 @76MW [WEBSMS] | CVIS
3/15/2024 5:39:54 PM | [NSO Update] Luzon Grid-03/15/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13103MW, PK=9785MW, RR=340MW, NetOpMargin: EVE=2977 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: MSLC1 @310MW, MSLC3 @320MW [WEBSMS] | CLUZ
3/15/2024 5:16:42 PM | Mindanao Grid-03/15/2024 17:21: WMPC DG01 shutdown at 1714H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/15/2024 5:16:35 PM | Luzon Grid-03/15/2024 17:16: Balsik-San Marcelino 230kV Line 2 de-energized at 1715H (Planned Outage) [WEBSMS] | CLUZ
3/15/2024 5:12:46 PM | Luzon Grid-03/15/2024 17:12: San Manuel 300MVA T01 commissioned at 1710H. [WEBSMS] | CLUZ
3/15/2024 4:49:15 PM | Luzon Grid-03/15/2024 16:49: San Manuel 300MVA T01 loop at 0446H, on commissioning test. [WEBSMS] | CLUZ
3/15/2024 4:45:55 PM | Luzon Grid-03/15/2024 16:45: San Jose-Angat 115kV L1 loop at 1644H (Unplanned Outage) [WEBSMS] | CLUZ
3/15/2024 3:52:44 PM | Luzon Grid-03/15/2024 15:52: Bacman-Palayan Binary Plant 230kV Tie Line restored at 1551H (Planned Outage) [WEBSMS] | CLUZ
3/15/2024 3:35:11 PM | Visayas Grid-03/15/2024 15:35: Nasulo tripped at 1525H (Unplanned Outage) [WEBSMS] | CVIS
3/15/2024 1:03:47 PM | Luzon Grid-03/15/2024 13:03: San Jose-Angat 115kV L1 unloop at 1301H (Unplanned Outage) [WEBSMS] | CLUZ
3/15/2024 12:54:57 PM | [NSO Update] Luzon Grid-03/15/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14282MW, PK=10806MW, RR=362MW, NetOpMargin: PM=3114, EVE=2596 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: MASINLOC 1 @310MW, MASINLOC 3 @320MW [WEBSMS] | CLUZ
3/15/2024 12:49:44 PM | [NSO Update] Visayas Grid-03/15/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2788MW, PK=2225MW, RR=90MW, NetOpMargin: PM=473, EVE=283 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @286MW, PGPP1 @38MW [WEBSMS] | CVIS
3/15/2024 12:39:31 PM | [NSO Update] Mindanao Grid-03/15/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3147MW, PK=2337MW, RR=77MW, NetOpMargin: PM=732, EVE=730 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @94MW, AG5 @30MW, AG6 @138MW, AG7 @27MW, PG4 @66MW [WEBSMS] | CMIN
3/15/2024 12:33:31 PM | Mindanao Grid-03/15/2024 12:37: Agus 6 Unit 5 online at 1226H. (Unplanned Outage) [WEBSMS] | CMIN
3/15/2024 12:27:57 PM | Visayas Grid-03/15/2024 12:28: Colon-Dumanjug 138KV Line 1 energized at 1220HH. (Unplanned Outage) [WEBSMS] | CVIS
3/15/2024 11:40:34 AM | Visayas Grid-03/15/2024 11:40: Colon-Dumanjug 138KV Line 1 tripped at 1136H. (Unplanned Outage) [WEBSMS] | CVIS
3/15/2024 11:36:59 AM | Visayas Grid-03/15/2024 11:37: Barotac SS 230KV Bus 2 energized at 1135H.(Unplanned Outage) [WEBSMS] | CVIS
3/15/2024 11:07:09 AM | Mindanao Grid-03/15/2024 11:11: Agus 6 Unit 5 shutdown at 1103H. (Unplanned Outage) [WEBSMS] | CMIN
3/15/2024 10:54:48 AM | Mindanao Grid-03/15/2024 10:59: WMPC DG01 online at 1048H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/15/2024 10:47:15 AM | Visayas Grid-03/15/2024 10:47: Barotac SS 230KV Bus 2 tripped at 1030H.(Unplanned Outage) [WEBSMS] | CVIS
3/15/2024 10:00:58 AM | Visayas Grid-03/15/2024 10:01: Cadiz-Gahit 230KV line 2 de-energized at 0957H. (Planned Outage) [WEBSMS] | CVIS
3/15/2024 9:35:20 AM | Luzon Grid-03/15/2024 09:35: Bacman-Palayan Binary Plant 230kV Tie Line de-energized at 0829H (Planned Outage) [WEBSMS] | CLUZ
3/15/2024 9:30:47 AM | Mindanao Grid-03/15/2024 09:35: WMPC DG10 online at 0929H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/15/2024 6:34:40 AM | Mindanao Grid-03/15/2024 06:39: Agus6-Balo-i 138 kV L1 de-energized at 0629H. P.O/Non-GOMP. [WEBSMS] | CMIN
3/15/2024 5:43:11 AM | [NSO Update] Mindanao Grid-03/15/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3164MW, PK=2190MW, RR=75MW, NetOpMargin: AM=899, PM=822, EVE=837 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @94MW, AG5 @30MW, AG6 @138MW, AG7 @27MW, PG4 @66MW [WEBSMS] | CMIN
3/15/2024 5:40:11 AM | [NSO Update] Visayas Grid-03/15/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2925MW, PK=2205MW, RR=87MW, NetOpMargin: AM=633, PM=508, EVE=385 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @297MW, PGPP1 @76MW [WEBSMS] | CVIS
3/15/2024 5:35:28 AM | [NSO Update] Luzon Grid-03/15/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14311MW, PK=10605MW, RR=351MW, NetOpMargin: AM=3355, PM=3008, EVE=2642 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: MSLC1 @310MW, MSLC3 @320MW [WEBSMS] | CLUZ
3/15/2024 4:22:06 AM | [NSO Update] Visayas Grid-03/15/2024 04:22: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CVIS
3/15/2024 4:21:22 AM | [NSO Update] Mindanao Grid-03/15/2024 04:25: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
3/15/2024 4:14:03 AM | [NSO Update] Luzon Grid-03/15/2024 04:14: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
3/14/2024 11:11:52 PM | Luzon Grid-03/14/2024 23:11: Batangas 230kV Bus 1 was energized at 2311H. (Planned Outage) [WEBSMS] | CLUZ
3/14/2024 8:08:42 PM | Luzon Grid-03/14/2024 20:08: Batangas 230kV Bus 1 was de-energized at 2007H. (Planned Outage) [WEBSMS] | CLUZ
3/14/2024 7:21:11 PM | Mindanao Grid-03/14/2024 19:25: WMPC DG10 shutdown at 1915H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/14/2024 6:19:30 PM | Mindanao Grid-03/14/2024 18:23: Agus 6 SS 138kV Bus No. 1 restored at 1818H. (Planned Outage) [WEBSMS] | CMIN
3/14/2024 5:45:43 PM | [NSO Update] Mindanao Grid-03/14/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3157MW, PK=2319MW, RR=74MW, NetOpMargin: EVE=764 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @41MW, MA2 @50MW, AG1 @57MW, AG2 @78MW, AG4 @97MW, AG5 @31MW, AG6 @139MW, AG7 @27MW, PG4 @66MW [WEBSMS] | CMIN
3/14/2024 5:44:02 PM | [NSO Update] Visayas Grid-03/14/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2614MW, PK=2156MW, RR=91MW, NetOpMargin: EVE=367 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @288MW, PGPP1 @76MW [WEBSMS] | CVIS
3/14/2024 5:42:09 PM | [NSO Update] Visayas Grid-03/14/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2614MW, PK=2156MW, RR=91MW, NetOpMargin: EVE=91 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @288MW, PGPP1 @76MW [WEBSMS] | CVIS
3/14/2024 5:40:16 PM | [NSO Update] Luzon Grid-03/14/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13412MW, PK=10549MW, RR=380MW, NetOpMargin: EVE=2483 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: MSLC1 @310MW, MSLC3 @320MW [WEBSMS] | CLUZ
3/14/2024 5:08:55 PM | Luzon Grid-03/14/2024 17:08: Lamao-SCPC 230kV tie line 4 was restored at 1708H. (Planned Outage) [WEBSMS] | CLUZ
3/14/2024 4:47:10 PM | Mindanao Grid-03/14/2024 16:51: WMPC DG01 shutdown at 1645H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/14/2024 3:48:04 PM | Luzon Grid-03/14/2024 15:48: San Manuel 300MVA T01 was energized at high side(230kV side) at 1531H. (On-going commissioning and energization.) [WEBSMS] | CLUZ
3/14/2024 3:32:44 PM | Luzon Grid-03/14/2024 15:32: For information: Batangas 300MVA T04 and T05 were unparalleled at 1527H while Sta Rita-San Lorenzo 230kV Busses were looped at 1529H. [WEBSMS] | CLUZ
3/14/2024 3:13:50 PM | [NSO Update] Luzon Grid-03/14/2024 15:13: Naga-Ormoc 350kV HVDC (Luzon-Visayas) de-blocked at 1503H with power going to Luzon (Unplanned Outage) [WEBSMS] | CLUZ
3/14/2024 3:13:47 PM | [NSO Update] Visayas Grid-03/14/2024 15:13: Naga-Ormoc 350kV HVDC (Luzon-Visayas) de-blocked at 1503H with power going to Luzon (Unplanned Outage) [WEBSMS] | CVIS
3/14/2024 3:08:35 PM | [NSO Update] Luzon Grid-03/14/2024 15:08: Naga-Ormoc 350kV HVDC (Luzon-Visayas) tripped at 1451H with power going to Luzon (Unplanned Outage) [WEBSMS] | CLUZ
3/14/2024 3:04:07 PM | [NSO Update] Visayas Grid-03/14/2024 15:04: Naga-Ormoc 350kV HVDC (Luzon-Visayas) tripped at 1451H with power going to Luzon (Unplanned Outage) [WEBSMS] | CVIS
3/14/2024 3:03:00 PM | Luzon Grid-03/14/2024 15:03: Luzon-Visayas HVDC auto-tripped at 1451H from an estimated load of 187MW(Visayas to Luzon power flow direction). The Luzon Grid lowest system frequency was 59.554Hz. (Unplanned Outage) [WEBSMS] | CLUZ
3/14/2024 1:13:56 PM | Mindanao Grid-03/14/2024 13:18: WMPC DG01 online at 1303H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/14/2024 12:54:14 PM | [NSO Update] Mindanao Grid-03/14/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3211MW, PK=2278MW, RR=77MW, NetOpMargin: PM=855, EVE=852 Highest Unit O/L: GNPK 1-4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @41MW, MA2 @50MW, AG1 @57MW, AG2 @78MW, AG4 @97MW, AG5 @31MW, AG6 @139MW, AG7 @27MW, PG4 @66MW [WEBSMS] | CMIN
3/14/2024 12:52:56 PM | [NSO Update] Visayas Grid-03/14/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3012MW, PK=2251MW, RR=93MW, NetOpMargin: PM=668, EVE=441 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @287MW, PGPP1 @76MW [WEBSMS] | CVIS
3/14/2024 12:51:47 PM | [NSO Update] Luzon Grid-03/14/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14694MW, PK=10893MW, RR=402MW, NetOpMargin: PM=3399, EVE=2815 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @310MW, MSLC3 @320MW [WEBSMS] | CLUZ
3/14/2024 11:33:51 AM | Luzon Grid-03/14/2024 11:33: Sta. Rita 230kV Bus 1 restored at 1133H (Unplanned Outage) [WEBSMS] | CLUZ
3/14/2024 10:33:34 AM | Mindanao Grid-03/14/2024 10:37: WMPC DG10 online at 0952H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/14/2024 8:21:03 AM | Mindanao Grid-03/14/2024 08:25: AGUS2 U2 shutdown at 0815H. Planned Outage (GOMP) [WEBSMS] | CMIN
3/14/2024 6:45:19 AM | Mindanao Grid-03/14/2024 06:49: Agus 6 SS 138kV Bus No. 1 de-energized at 0638H. (Planned Outage) [WEBSMS] | CMIN
3/14/2024 6:33:17 AM | Luzon Grid-03/14/2024 06:33: Sta. Rita 230kV Bus 1 de-energized at 0632H (Unplanned Outage) [WEBSMS] | CLUZ
3/14/2024 5:48:56 AM | [NSO Update] Mindanao Grid-03/14/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3227MW, PK=2149MW, RR=75MW, NetOpMargin: AM=1003, PM=781, EVE=822 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @38.5MW, MA2 @50MW, AG1 @57MW, AG2 @78MW, AG4 @97MW, AG5 @31MW, AG6 @143MW, AG7 @27MW, PG4 @66MW [WEBSMS] | CMIN
3/14/2024 5:48:01 AM | [NSO Update] Visayas Grid-03/14/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2835MW, PK=2147MW, RR=90MW, NetOpMargin: AM=598, PM=342, EVE=204 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 297MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/14/2024 5:46:54 AM | [NSO Update] Luzon Grid-03/14/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14530MW, PK=10624MW, RR=391MW, NetOpMargin: AM=3515, PM=2877, EVE=2497 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 310MW, Masinloc 3 @ 320MW [WEBSMS] | CLUZ
3/14/2024 4:15:42 AM | Luzon Grid-03/14/2024 04:15: San Jose SS 300MVA T03 energized at 0410H (Planned Outage) [WEBSMS] | CLUZ
3/14/2024 4:07:42 AM | [NSO Update] Mindanao Grid-03/14/2024 04:12: Weather Advisory: Shear Line affecting the eastern sections of Central and Southern Luzon. Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
3/14/2024 4:07:20 AM | [NSO Update] Visayas Grid-03/14/2024 04:07: Weather Advisory: Shear Line affecting the eastern sections of Central and Southern Luzon. Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
3/14/2024 4:06:58 AM | [NSO Update] Luzon Grid-03/14/2024 04:07: Weather Advisory: Shear Line affecting the eastern sections of Central and Southern Luzon. Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
3/14/2024 2:04:43 AM | Mindanao Grid-03/14/2024 02:09: STEAG U1 online at 0157H. Planned Outage. [WEBSMS] | CMIN
3/14/2024 12:35:44 AM | Luzon Grid-03/14/2024 00:36: Balsik-San Marcelino 230kV Line 2 restored at 0035H (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 11:59:14 PM | Luzon Grid-03/13/2024 23:59: Ilijan GT2-1 shutdown at 2358H (Unplanned Outage). [WEBSMS] | CLUZ
3/13/2024 11:42:00 PM | Luzon Grid-03/13/2024 23:42: Ilijan ST2 shutdown at 2341H (Unplanned Outage). [WEBSMS] | CLUZ
3/13/2024 9:02:57 PM | Luzon Grid-03/13/2024 21:03: San Jose SS 300MVA T03 de-energized at 2102H. (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 7:41:27 PM | Luzon Grid-03/13/2024 19:41: Hermosa-Calaguiman 69kV Line restored at 1939H. (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 7:17:51 PM | Mindanao Grid-03/13/2024 19:22: WMPC DG10 shutdown at 1915H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/13/2024 6:38:29 PM | Luzon Grid-03/13/2024 18:38: Ilijan B GT2-2 shutdown at 1838H. (Unplanned Outage) [WEBSMS] | CLUZ
3/13/2024 6:10:45 PM | Luzon Grid-03/13/2024 18:11: San Manuel SS 230kV Bus 1 restored at 1810H. (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 6:02:57 PM | Visayas Grid-03/13/2024 18:03: Compostela SS 150MVA TR 1 energized at 1759H (Planned Outage) [WEBSMS] | CVIS
3/13/2024 5:56:19 PM | Luzon Grid-03/13/2024 17:56: Gumaca-Labo 230kV Line 2 restored at 1756H. (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 5:54:03 PM | [NSO Update] Mindanao Grid-03/13/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3048MW, PK=2231MW, RR=74.3MW, NetOpMargin: EVE=743 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @57MW, AG2 @79MW, AG4 @98MW, AG5 @31MW, AG6 @143MW, AG7 @27MW, PG4 @76MW [WEBSMS] | CMIN
3/13/2024 5:52:57 PM | [NSO Update] Visayas Grid-03/13/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2574MW, PK=2199MW, RR=89MW, NetOpMargin: EVE=286 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 220MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/13/2024 5:51:22 PM | [NSO Update] Luzon Grid-03/13/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13988MW, PK=9927MW, RR=380MW, NetOpMargin: EVE=3681 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 310MW, Masinloc 3 @ 320MW [WEBSMS] | CLUZ
3/13/2024 5:07:28 PM | Luzon Grid-03/13/2024 17:07: Balsik-San Marcelino 230kV Line 2 de-energized at 1707H. (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 4:12:35 PM | Luzon Grid-03/13/2024 16:12: Hermosa-Calaguiman 69kV Line de-energized at 1610H (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 3:19:42 PM | Luzon Grid-03/13/2024 15:19: Angat HEPP SS 115kV Bus 1 restored at 1517H. (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 12:45:24 PM | [NSO Update] Mindanao Grid-03/13/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3090MW, PK=2283MW, RR=77MW, NetOpMargin: PM=730, EVE=761 Highest Unit O/L: GNPK 1,2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @57MW, AG2 @79MW, AG4 @98MW, AG5 @31MW, AG6 @139MW, AG7 @27MW, PG4 @76MW [WEBSMS] | CMIN
3/13/2024 12:43:16 PM | [NSO Update] Luzon Grid-03/13/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14911MW, PK=11035MW, RR=399MW, NetOpMargin: PM=3477, EVE=3133 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @310MW, MSLC3 @320MW [WEBSMS] | CLUZ
3/13/2024 12:41:22 PM | [NSO Update] Visayas Grid-03/13/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2731MW, PK=2272MW, RR=68MW, NetOpMargin: PM=392, EVE=227 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @210MW, PGPP1 @76MW [WEBSMS] | CVIS
3/13/2024 10:41:25 AM | Visayas Grid-03/13/2024 10:41: MAHA A U2 tripped at 1038H (Unplanned Outage) [WEBSMS] | CVIS
3/13/2024 10:25:59 AM | Mindanao Grid-03/13/2024 10:30: WMPC DG01 online at 1021H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/13/2024 9:29:59 AM | Mindanao Grid-03/13/2024 09:34: WMPC DG10 online at 0922H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/13/2024 8:16:18 AM | Luzon Grid-03/13/2024 08:16: Taytay SS 300MVA T05 restored at 0816H. (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 7:55:49 AM | Visayas Grid-03/13/2024 07:56: UMPP U3 emergency shutdown at 0743H (Unplanned Outage) [WEBSMS] | CVIS
3/13/2024 6:36:02 AM | Luzon Grid-03/13/2024 06:36: Gumaca-Labo 230kV Line 2 de-energized at 0635H. (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 6:35:24 AM | Visayas Grid-03/13/2024 06:35: Compostela SS 150MVA TR 1 de-energized at 0629H (Planned Outage) [WEBSMS] | CVIS
3/13/2024 6:02:47 AM | Luzon Grid-03/13/2024 06:03: San Manuel SS 230kV Bus 1 de-energized at 0602H (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 5:52:45 AM | [NSO Update] Mindanao Grid-03/13/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3111MW, PK=2312MW, RR=75MW, NetOpMargin: AM=723, PM=608, EVE=661 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @57MW, AG2 @79MW, AG4 @98MW, AG5 @31MW, AG6 @139MW, AG7 @27MW, PG4 @76MW [WEBSMS] | CMIN
3/13/2024 5:47:44 AM | [NSO Update] Visayas Grid-03/13/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2725MW, PK=2207MW, RR=88MW, NetOpMargin: AM=430, PM=237, EVE=175 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @286MW, PGPP1 @76MW [WEBSMS] | CVIS
3/13/2024 5:44:42 AM | [NSO Update] Luzon Grid-03/13/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14475MW, PK=11159MW, RR=391MW, NetOpMargin: AM=2925, PM=2484, EVE=2272 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @310MW, MSLC3 @320MW, ILIJAN A @370MW, ILIJAN B @385MW [WEBSMS] | CLUZ
3/13/2024 5:41:00 AM | Luzon Grid-03/13/2024 05:41: Hermosa-Calaguiman 69kV Line energized at 0534H (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 5:11:45 AM | Luzon Grid-03/13/2024 05:11: Hermosa-Calaguiman 69kV Line de-energized at 0511H (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 4:30:20 AM | [NSO Update] Mindanao Grid-03/13/2024 04:34: Weather Update: Shear Line affecting the eastern sections of Central and Southern Luzon. Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
3/13/2024 4:29:45 AM | [NSO Update] Visayas Grid-03/13/2024 04:29: Weather Update: Shear Line affecting the eastern sections of Central and Southern Luzon. Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
3/13/2024 4:29:30 AM | [NSO Update] Luzon Grid-03/13/2024 04:29: Weather Update: Shear Line affecting the eastern sections of Central and Southern Luzon. Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
3/13/2024 3:36:21 AM | Luzon Grid-03/13/2024 03:36: MPGC 3 online at 0335H (Unplanned Outage) [WEBSMS] | CLUZ
3/13/2024 2:37:16 AM | Luzon Grid-03/13/2024 02:37: Ilijan GT2-2 online at 0232H (Unplanned Outage) [WEBSMS] | CLUZ
3/13/2024 2:22:53 AM | Luzon Grid-03/13/2024 02:23: QPPL online at 0216H (Planned Outage) [WEBSMS] | CLUZ
3/13/2024 12:53:01 AM | Luzon Grid-03/13/2024 00:53: Taytay SS 300MVA T05 de-energized at 0052H (Planned Outage) [WEBSMS] | CLUZ
3/12/2024 11:31:41 PM | Luzon Grid-03/12/2024 23:31: Concepcion-San Manuel 230kV Line 2 restored at 2328H (Planned Outage) [WEBSMS] | CLUZ
3/12/2024 8:21:24 PM | Mindanao Grid-03/12/2024 20:26: WMPC DG10 shutdown at 2019H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/12/2024 6:18:51 PM | Luzon Grid-03/12/2024 18:19: Dasmarinas-TMC II (Ternate) 115kV Line energized at 1818H (Planned Outage) [WEBSMS] | CLUZ
3/12/2024 6:02:16 PM | Luzon Grid-03/12/2024 18:02: Gumaca-Labo 230kV Line 1 restored at 1802H (Planned Outage) [WEBSMS] | CLUZ
3/12/2024 5:59:37 PM | [NSO Update] Mindanao Grid-03/12/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2996MW, PK=2211MW, RR=74.3MW, NetOpMargin: EVE=711 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @58MW, AG2 @80MW, AG4 @99MW, AG5 @31MW, AG6 @145MW, AG7 @28MW, PG4 @68MW [WEBSMS] | CMIN
3/12/2024 5:56:23 PM | [NSO Update] Visayas Grid-03/12/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2513MW, PK=2152MW, RR=92MW, NetOpMargin: EVE=269 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @290MW, PGPP1 @76MW [WEBSMS] | CVIS
3/12/2024 5:52:44 PM | Mindanao Grid-03/12/2024 17:57: Agus 5 - Aurora 138kV Line successfully energized/restored at 1748H. From Planned Outage (Non-GOMP). Note: P & E requested shutdown activity. [WEBSMS] | CMIN
3/12/2024 5:52:02 PM | [NSO Update] Luzon Grid-03/12/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13063MW, PK=10714MW, RR=380MW, NetOpMargin: EVE=1969 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @310MW, MSLC3 @320MW, ILIJAN A @570MW, ILIJAN B @165MW [WEBSMS] | CLUZ
3/12/2024 4:45:19 PM | Mindanao Grid-03/12/2024 16:49: WMPC DG04 shutdown at 1643H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/12/2024 1:19:26 PM | Mindanao Grid-03/12/2024 13:24: Updated: Minergy Coal Power Plant (MCC) Unit #3 with a gross generation of 54.64W auto-tripped at 1255H, with CEPALCO SIPS activation of about 50.04MW ( 9-feeders of CEPALCOs system). Lowest system frequency recorded was 59.78Hz. No ALD. (Unplanned Outage). [WEBSMS] | CMIN
3/12/2024 1:17:44 PM | Mindanao Grid-03/12/2024 13:22: undefined at 1255H Minergy Coal Power Plant (MCC) Unit #3 with a gross generation of 54.64W auto-tripped at 1255H, with CEPALCO SIPS activation of about 50.04MW ( 9-feeders of CEPALCOs system). Lowest system frequency recorded was 59.78Hz. No ALD. (Unplanned Outage). [WEBSMS] | CMIN
3/12/2024 12:46:56 PM | [NSO Update] Mindanao Grid-03/12/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2984MW, PK=2400MW, RR=77MW, NetOpMargin: PM=506, EVE=570 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @58MW, AG2 @80MW, AG4 @99MW, AG5 @31MW, AG6 @145MW, AG7 @28MW, PG4 @68MW [WEBSMS] | CMIN
3/12/2024 12:44:39 PM | [NSO Update] Visayas Grid-03/12/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2670MW, PK=2259MW, RR=91MW, NetOpMargin: PM=320, EVE=221 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @292MW, PGPP1 @76MW [WEBSMS] | CVIS
3/12/2024 12:39:06 PM | [NSO Update] Luzon Grid-03/12/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13694MW, PK=11351MW, RR=399MW, NetOpMargin: PM=1944, EVE=1777 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @310MW, MSLC3 @320MW, ILIJAN A @570MW, ILIJAN B @165MW [WEBSMS] | CLUZ
3/12/2024 11:54:25 AM | Mindanao Grid-03/12/2024 11:59: STEAG Unit 2 online at 1103H (from PMS, NON-GOMP). (Planned Outage) [WEBSMS] | CMIN
3/12/2024 10:42:45 AM | Mindanao Grid-03/12/2024 10:47: WMPC DG04 online at 1040H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/12/2024 9:58:02 AM | Mindanao Grid-03/12/2024 10:02: WMPC DG10 online at 0935H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/12/2024 9:15:05 AM | Visayas Grid-03/12/2024 09:15: PEDC U3 online at 0914H. (Unplanned Outage) [WEBSMS] | CVIS
3/12/2024 8:45:10 AM | Luzon Grid-03/12/2024 08:45: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0845H. (Planned Outage) [WEBSMS] | CLUZ
3/12/2024 7:18:33 AM | Visayas Grid-03/12/2024 07:18: PEDC U3 tripped at 0716H. (Unplanned Outage) [WEBSMS] | CVIS
3/12/2024 6:41:56 AM | Mindanao Grid-03/12/2024 06:46: Agus 5 - Aurora 138kV Line deenergized at 0618H. Planned Outage (Non-GOMP). Note: P & E requested shutdown activity. [WEBSMS] | CMIN
3/12/2024 6:35:08 AM | Luzon Grid-03/12/2024 06:35: Gumaca-Labo 230kV Line 1 de-energized at 0635H. (Planned Outage) [WEBSMS] | CLUZ
3/12/2024 6:28:20 AM | Luzon Grid-03/12/2024 06:28: Concepcion-San Manuel 230kV Line 2 de-energized at 0628H. (Planned Outage) [WEBSMS] | CLUZ
3/12/2024 6:18:51 AM | Mindanao Grid-03/12/2024 06:23: Agus5 - Aurora 138kV line de-energized at 0618H. (Planned Outage) [WEBSMS] | CMIN
3/12/2024 5:55:03 AM | [NSO Update] Luzon Grid-03/12/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14100MW, PK=10933MW, RR=391MW, NetOpMargin: AM=2776, PM=2471, EVE=2062 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: MASINLOC 1 @310MW, MASINLOC 2 @300MW, MASINLOC 3 @315MW, ILIJAN A @570MW, ILIJAN B@165MW [WEBSMS] | CLUZ
3/12/2024 5:50:23 AM | Luzon Grid-03/12/2024 05:50: Balsik-San Marcelino 230kV line 2 was restored at 0547H. (Planned Outage) [WEBSMS] | CLUZ
3/12/2024 5:39:13 AM | [NSO Update] Visayas Grid-03/12/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2790MW, PK=2232MW, RR=92MW, NetOpMargin: AM=466, PM=347, EVE=182 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @292MW, PGPP1 @76MW [WEBSMS] | CVIS
3/12/2024 5:39:07 AM | [NSO Update] Mindanao Grid-03/12/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3014MW, PK=2290MW, RR=75MW, NetOpMargin: AM=649, PM=533, EVE=579 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @58MW, AG2 @80MW, AG4 @99MW, AG5 @31MW, AG6 @145MW, AG7 @28MW, PG4 @68MW [WEBSMS] | CMIN
3/12/2024 4:10:45 AM | Luzon Grid-03/12/2024 04:10: Balsik-San Marcelino 230kV line 2 was de-energized at 0407H (Planned Outage) [WEBSMS] | CLUZ
3/12/2024 4:08:55 AM | [NSO Update] Visayas Grid-03/12/2024 04:09: Weather Advisory: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
3/12/2024 4:08:38 AM | [NSO Update] Mindanao Grid-03/12/2024 04:13: Weather Advisory: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
3/12/2024 4:08:22 AM | [NSO Update] Luzon Grid-03/12/2024 04:08: Weather Advisory: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/12/2024 2:57:37 AM | Luzon Grid-03/12/2024 02:57: Balsik-San Marcelino 230kV line 2 was restored at 0254H (Planned Outage) [WEBSMS] | CLUZ
3/11/2024 8:51:21 PM | Mindanao Grid-03/11/2024 20:55: Marawi SS 138kV 50MVA Power Transformer tripped at 2041H. (Unplanned Outage) [WEBSMS] | CMIN
3/11/2024 7:52:14 PM | Luzon Grid-03/11/2024 19:52: MPGC Unit 3 tripped at 1948H from 150MW load. The lowest system frequency was 59.653Hz. (Unplanned Outage-The unit is under commissioning test.) [WEBSMS] | CLUZ
3/11/2024 7:16:27 PM | Mindanao Grid-03/11/2024 19:21: WMPC DG10 shutdown at 1914H. RPS-System Voltage Reqyirement. [WEBSMS] | CMIN
3/11/2024 5:43:36 PM | [NSO Update] Luzon Grid-03/11/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13031MW, PK=10115MW, RR=380MW, NetOpMargin: EVE=2536 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 310MW, Masinloc 3 @ 320MW, Ilijan A @ 570MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
3/11/2024 5:29:55 PM | [NSO Update] Visayas Grid-03/11/2024 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2450MW, PK=2200MW, RR=65MW, NetOpMargin: EVE=185 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @285MW, PGPP1 @76MW [WEBSMS] | CVIS
3/11/2024 5:29:50 PM | [NSO Update] Mindanao Grid-03/11/2024 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3007MW, PK=2338MW, RR=74MW, NetOpMargin: EVE=595 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @59MW, AG2 @82MW, AG4 @102MW, AG5 @32MW, AG6 @149MW, AG7 @29MW, PG4 @94MW [WEBSMS] | CMIN
3/11/2024 5:11:48 PM | Luzon Grid-03/11/2024 17:11: Balsik-San Marcelino 230kV line 2 was de-energized at 1710H. (Planned Outage) [WEBSMS] | CLUZ
3/11/2024 5:05:58 PM | Luzon Grid-03/11/2024 17:06: Mauban-QPPL 230kV line 1(Customer Owned and Maintained Line) was restored at 1702H (Planned Outage) [WEBSMS] | CLUZ
3/11/2024 4:52:05 PM | Mindanao Grid-03/11/2024 16:56: Agus5 SS 138kV Bus #2 restored at 1645H (Planned Outage) [WEBSMS] | CMIN
3/11/2024 4:46:24 PM | Mindanao Grid-03/11/2024 16:50: WMPC DG04 shutdown at 1643H. RPS-System Voltage Requirement [WEBSMS] | CMIN
3/11/2024 3:36:47 PM | Luzon Grid-03/11/2024 15:36: Makban B-Makban D 230kV tie line(Customer Owned and Maintained Line) was restored at 1534H. (Planned Outage) [WEBSMS] | CLUZ
3/11/2024 1:28:14 PM | Mindanao Grid-03/11/2024 13:32: WMPC DG04 online at 1322H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/11/2024 12:51:29 PM | [NSO Update] Mindanao Grid-03/11/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3069MW, PK=2342MW, RR=77MW, NetOpMargin: PM=650, EVE=644 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @59MW, AG2 @82MW, AG4 @102MW, AG5 @32MW, AG6 @149MW, AG7 @29MW, PG4 @94MW [WEBSMS] | CMIN
3/11/2024 12:48:27 PM | [NSO Update] Visayas Grid-03/11/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: CAP=2620MW, PK=2266MW, RR=92MW, NetOpMargin: PM=262, EVE=187 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 284MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/11/2024 12:45:00 PM | [NSO Update] Luzon Grid-03/11/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14103MW, PK=10675MW, RR=392MW, NetOpMargin: PM=3036, EVE=2404 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 310MW, Masinloc 3 @ 320MW, Ilijan A @ 570MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
3/11/2024 11:44:43 AM | Mindanao Grid-03/11/2024 11:49: Zamboanga SS 138kV Bus No. 2 restored at 1142H. (Planned Outage) [WEBSMS] | CMIN
3/11/2024 10:32:20 AM | Mindanao Grid-03/11/2024 10:36: WMPC DG10 online at 1028H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/11/2024 10:28:58 AM | Luzon Grid-03/11/2024 10:29: Bay-Makban Plant B 230kV Line 2 de-energized at 1024H (Planned Outage) [WEBSMS] | CLUZ
3/11/2024 8:47:08 AM | Mindanao Grid-03/11/2024 08:51: Zamboanga SS 138kV Bus No. 2 de-energized at 0841H. (Planned Outage) [WEBSMS] | CMIN
3/11/2024 8:44:30 AM | Mindanao Grid-03/11/2024 08:49: Agus 5 SS 138kV Bus No. 2 de-energized at 0836H. (Planned Outage) [WEBSMS] | CMIN
3/11/2024 8:36:59 AM | Luzon Grid-03/11/2024 08:37: Casecnan-Nagsaag 230kV Line 1 de-energized at 0836H (Planned Outage) [WEBSMS] | CLUZ
3/11/2024 8:22:43 AM | Luzon Grid-03/11/2024 08:22: Angat HEPP SS 115kV Bus 1 de-energized at 0820H (Planned Outage). [WEBSMS] | CLUZ
3/11/2024 5:48:03 AM | [NSO Update] Mindanao Grid-03/11/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3103MW, PK=2223MW, RR=75MW, NetOpMargin: AM=805, PM=677, EVE=696 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @59MW, AG2 @82MW, AG4 @102MW, AG5 @32MW, AG6 @149MW, AG7 @29MW, PG4 @117MW [WEBSMS] | CMIN
3/11/2024 5:47:12 AM | [NSO Update] Visayas Grid-03/11/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2758MW, PK=2151MW, RR=92MW, NetOpMargin: AM=514, PM=302, EVE=236 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 315MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/11/2024 5:45:53 AM | [NSO Update] Luzon Grid-03/11/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14222MW, PK=10426MW, RR=381MW, NetOpMargin: AM=3415, PM=2835, EVE=2223 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Masinloc 1 @ 310MW, Masinloc 3 @ 320MW, Ilijan A @ 570MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
3/11/2024 4:26:48 AM | [NSO Update] Luzon Grid-03/11/2024 04:26: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/11/2024 4:25:32 AM | [NSO Update] Mindanao Grid-03/11/2024 04:30: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
3/11/2024 4:25:18 AM | [NSO Update] Visayas Grid-03/11/2024 04:25: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
3/11/2024 12:05:37 AM | Luzon Grid-03/11/2024 00:05: For info: Sta Rita and San Lorenzo 230kV Bus A and B were unlooped at 2356H of March 10, 2024 while Batangas 300MVA T04 and T05 were looped at 0002H. This was due to hotspots found at Disconnect switch of bus 1 tie breakers at San Lorenzo and Sta. Rita. [WEBSMS] | CLUZ
3/10/2024 11:49:11 PM | Luzon Grid-03/10/2024 23:49: MPGC 2 shutdown at 2346H. On commissioning Test (Planned Outage) [WEBSMS] | CLUZ
3/10/2024 11:01:13 PM | Visayas Grid-03/10/2024 23:01: PGPP 2 SOG 1 cut in at 2255H (Unplanned Outage) [WEBSMS] | CVIS
3/10/2024 10:53:55 PM | Visayas Grid-03/10/2024 22:54: Malitbog U3 cut in at 2230H (Unplanned Outage) [WEBSMS] | CVIS
3/10/2024 10:45:02 PM | Visayas Grid-03/10/2024 22:45: FFHC shutdown at 2209H (Unplanned Outage) [WEBSMS] | CVIS
3/10/2024 7:54:10 PM | Luzon Grid-03/10/2024 19:54: Lumban-Malaya 230kV Line 2 restored at 1949H. On-going commissioning test for its swinging from Bay 84 to new Bay 85 at Malaya side (Planned Outage) [WEBSMS] | CLUZ
3/10/2024 7:16:13 PM | Visayas Grid-03/10/2024 19:16: Cebu SS 300MVA 230/138/13.8KV TR3 energized at 1856H.(Planned Outage) [WEBSMS] | CVIS
3/10/2024 7:12:10 PM | Luzon Grid-03/10/2024 19:12: Balingueo 230kV Bus 2 restored at 1911H (Planned Outage) [WEBSMS] | CLUZ
3/10/2024 6:46:17 PM | Luzon Grid-03/10/2024 18:46: Batangas-San Lorenzo 230kV line 2 restored at 1844H (Planned Outage) [WEBSMS] | CLUZ
3/10/2024 6:41:11 PM | Luzon Grid-03/10/2024 18:41: Batangas-San Lorenzo 230kV line 1 restored at 1840H (Planned Outage) [WEBSMS] | CLUZ
3/10/2024 5:58:20 PM | [NSO Update] Mindanao Grid-03/10/2024 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2993MW, PK=2137MW, RR=74.3MW, NetOpMargin: EVE=782 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @59MW, AG2 @82MW, AG4 @102MW, AG5 @32MW, AG6 @149MW, AG7 @29MW, PG4 @87MW [WEBSMS] | CMIN
3/10/2024 5:57:23 PM | [NSO Update] Visayas Grid-03/10/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2498MW, PK=1967MW, RR=86MW, NetOpMargin: EVE=445 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 309MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/10/2024 5:56:27 PM | [NSO Update] Luzon Grid-03/10/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12556MW, PK=9224MW, RR=290MW, NetOpMargin: EVE=3042 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Masinloc 1 @ 310MW, Masinloc 3 @ 320MW, Ilijan A @ 570MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
3/10/2024 5:51:55 PM | Mindanao Grid-03/10/2024 17:56: Pitogo SS 138kV Bus No. 2 (7BS02PIT) energized/restored at 1745H. From Planned Outage (Non-GOMP). Note: MTD-A requested Shutdown. [WEBSMS] | CMIN
3/10/2024 5:50:13 PM | Mindanao Grid-03/10/2024 17:54: Pitogo SS 138kV/69kV/13.8kV 100MVA Power Transformer No.1 (7XF01PIT) energized/restored at 1744H. From Planned Outage (Non-GOMP). Note: P&E requested Shutdown under MSUP, Stage 1. [WEBSMS] | CMIN
3/10/2024 5:41:46 PM | Luzon Grid-03/10/2024 17:41: Taytay 300MVA T01 restored at 1740H (Planned Outage) [WEBSMS] | CLUZ
3/10/2024 5:34:23 PM | Luzon Grid-03/10/2024 17:34: Cabanatuan-Pantabangan 230kV Line restored at 1734H (Planned Outage) [WEBSMS] | CLUZ
3/10/2024 4:46:54 PM | Luzon Grid-03/10/2024 16:47: GNPD 2 online at 1646H (Unplanned Outage) [WEBSMS] | CLUZ
3/10/2024 3:38:40 PM | Mindanao Grid-03/10/2024 15:43: Nasipit-TM2 138kV L2 (7LI2NAS-TM2) successfully energized/ restored at 1533H. From Planned Outage (GOP). Note: Requested shutdown by Therma Marine (TM2) Management) [WEBSMS] | CMIN
3/10/2024 3:32:19 PM | Mindanao Grid-03/10/2024 15:36: Placer SS 50MVA Power Transformer No. 2 (7XF02PLA) energized back to the Mindanao Grid at 1527H from Planned Outage (Non-GOMP). [WEBSMS] | CMIN
3/10/2024 3:27:43 PM | Mindanao Grid-03/10/2024 15:32: Jasaan-Butuan 138kV Line successfully energized and completely looped to the Mindanao Grid at 1518H. From Planned Outage (GOMP). [WEBSMS] | CMIN
3/10/2024 3:25:53 PM | Luzon Grid-03/10/2024 15:26: GNPD 2 which online at 1454H tripped at 1519H with 149MW load. Lowest Frequency is 59.58Hz (Unplanned Outage) [WEBSMS] | CLUZ
3/10/2024 1:42:35 PM | Mindanao Grid-03/10/2024 13:47: Placer SS 50MVA Power Transformer No. 2 (7XF02PLA) de-energized at 1331H. Planned Outage (Non-GOMP0. Note: This is approved Shutdown request by MD4 SS. [WEBSMS] | CMIN
3/10/2024 1:28:28 PM | Mindanao Grid-03/10/2024 13:33: Pitogo SS 138kV Bus No. 2 (7BS02PIT) de-energized at 1320H. Planned Outage (Non-GOMP). Note: MTD-A requested Shutdown. [WEBSMS] | CMIN
3/10/2024 1:25:11 PM | Mindanao Grid-03/10/2024 13:29: Pitogo SS 138kV 100MVA Power Transformer No.1 (7XF01PIT) de-energized at 1314H. Planned Outage (Non-GOMP). Note: P&E requested Shutdown under MSUP, Stage 1. [WEBSMS] | CMIN
3/10/2024 1:03:20 PM | [NSO Update] Mindanao Grid-03/10/2024 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3045MW, PK=1971MW, RR=77MW, NetOpMargin: PM=997, EVE=725 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @59MW, AG2 @82MW, AG4 @102MW, AG5 @32MW, AG6 @149MW, AG7 @29MW, PG4 @87MW [WEBSMS] | CMIN
3/10/2024 12:58:01 PM | [NSO Update] Visayas Grid-03/10/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2738MW, PK=1705MW, RR=88MW, NetOpMargin: PM=944, EVE=526 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @312MW, PGPP1 @76MW [WEBSMS] | CVIS
3/10/2024 12:49:51 PM | [NSO Update] Luzon Grid-03/10/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13495MW, PK=8984MW, RR=299MW, NetOpMargin: PM=4212, EVE=2683 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MSLC1 @310MW, MSLC3 @270MW, ILIJAN A @570MW, ILIJAN B @165MW [WEBSMS] | CLUZ
3/10/2024 9:27:54 AM | Luzon Grid-03/10/2024 09:28: Amadeo PCB 8-02CB04AMA was de-energized at 0913H. (Planned Outage) [WEBSMS] | CLUZ
3/10/2024 8:16:51 AM | Mindanao Grid-03/10/2024 08:21: Nasipit-TM2 138kV L2 (7LI2NAS-TM2) de-energized at 0808H. Planned Outage (GOP). Note: Approved request by Therma Marine (TM2) Management) [WEBSMS] | CMIN
3/10/2024 8:03:57 AM | Luzon Grid-03/10/2024 08:04: Balingueo 230kV Bus 2 was de-energized at 0802H. (Planned Outage) [WEBSMS] | CLUZ
3/10/2024 7:59:33 AM | Luzon Grid-03/10/2024 07:59: GNPD Unit 2 tripped at 0756H from 133MW load. The lowest system frequency was 59.586Hz. (Unplanned Outage) [WEBSMS] | CLUZ
3/10/2024 7:45:46 AM | Mindanao Grid-03/10/2024 07:50: Jasaan-Butuan 138kV Line de-energized at 0742H. Planned Outage (GOMP). [WEBSMS] | CMIN
3/10/2024 7:43:36 AM | Luzon Grid-03/10/2024 07:43: GNPD Unit 2 online at 0741H. (Unplanned Outage) [WEBSMS] | CLUZ
3/10/2024 7:06:47 AM | Luzon Grid-03/10/2024 07:06: Taytay 300MVA T01 was de-energized at 0706H. (Planned Outage) [WEBSMS] | CLUZ
3/10/2024 6:36:15 AM | Luzon Grid-03/10/2024 06:36: Cabanatuan-Pantabangan 230kV line was de-energized at 0635H. (Planned Outage) [WEBSMS] | CLUZ
3/10/2024 6:21:55 AM | Luzon Grid-03/10/2024 06:22: Batangas-San Lorenzo 230kV line 1 and 2 were de-energized at 0616H and 0618H respectively. (Planned Outage) [WEBSMS] | CLUZ
3/10/2024 6:09:15 AM | Luzon Grid-03/10/2024 06:09: Correction: GNPD 2 shutdown at 0601H to perform necessary repairs for its turbine bearing no.5 high vibration issue (Unplanned Outage) [WEBSMS] | CLUZ
3/10/2024 6:02:41 AM | Luzon Grid-03/10/2024 06:02: GNPD 1 shutdown at 0601H to perform necessary repairs for its turbine bearing no.5 high vibration issue (Unplanned Outage) [WEBSMS] | CLUZ
3/10/2024 5:46:17 AM | [NSO Update] Mindanao Grid-03/10/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3067MW, PK=1849MW, RR=75MW, NetOpMargin: AM=1142, PM=1073, EVE=764 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @59MW, AG2 @82MW, AG4 @102MW, AG5 @32MW, AG6 @149MW, AG7 @29MW, PG4 @87MW [WEBSMS] | CMIN
3/10/2024 5:45:03 AM | [NSO Update] Visayas Grid-03/10/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2513MW, PK=1745MW, RR=87MW, NetOpMargin: AM=681, PM=798, EVE=236 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @312MW, PGPP1 @76MW [WEBSMS] | CVIS
3/10/2024 5:44:35 AM | [NSO Update] Luzon Grid-03/10/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13513MW, PK=8491MW, RR=291MW, NetOpMargin: AM=4731, PM=4269, EVE=2731 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MSLC1 @310MW, MSLC3 @245MW, ILIJAN B @165MW [WEBSMS] | CLUZ
3/10/2024 4:06:13 AM | [NSO Update] Luzon Grid-03/10/2024 04:06: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/10/2024 4:00:50 AM | [NSO Update] Visayas Grid-03/10/2024 04:00: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
3/10/2024 4:00:25 AM | [NSO Update] Mindanao Grid-03/10/2024 04:04: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
3/10/2024 1:34:22 AM | Luzon Grid-03/10/2024 01:34: Ilijan GT2-2 shutdown at 2327H of March 9, 2024. Note: No initial information from the plant regarding their unit shutdown (Unplanned Outage) [WEBSMS] | CLUZ
3/10/2024 1:22:54 AM | Luzon Grid-03/10/2024 01:23: Malaya 230kV Bus 2 restored at 0122H (Planned Outage) [WEBSMS] | CLUZ
3/10/2024 1:21:23 AM | Luzon Grid-03/10/2024 01:21: SBPL online at 0117H (Unplanned Outage) [WEBSMS] | CLUZ
3/10/2024 12:12:14 AM | Mindanao Grid-03/10/2024 00:16: TM2 U2 Shutdown at 0008H. Planned Outage. [WEBSMS] | CMIN
3/9/2024 9:05:59 PM | Luzon Grid-03/09/2024 21:06: Ilijan GT1-1 online at 2104H (Unplanned Outage) [WEBSMS] | CLUZ
3/9/2024 8:17:56 PM | Mindanao Grid-03/09/2024 20:22: Pulangi 4 U1 shutdown at 2016H. Unplanned Outage [WEBSMS] | CMIN
3/9/2024 5:51:42 PM | Mindanao Grid-03/09/2024 17:56: Matanao - General Santos 138kV L2 restored at 1749H. (Planned Outage) [WEBSMS] | CMIN
3/9/2024 5:46:04 PM | [NSO Update] Mindanao Grid-03/09/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2996MW, PK=2288MW, RR=74MW, NetOpMargin: EVE=634 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @60MW, AG2 @83MW, AG4 @103MW, AG5 @33MW, AG6 @150MW, AG7 @29MW, PG4 @87MW [WEBSMS] | CMIN
3/9/2024 5:44:43 PM | Mindanao Grid-03/09/2024 17:49: Lugait SS 138kV Power Transformer No. 2 restored at 1743H. (Planned Outage) [WEBSMS] | CMIN
3/9/2024 5:42:28 PM | [NSO Update] Visayas Grid-03/09/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2393MW, PK=2045MW, RR=90MW, NetOpMargin: EVE=259 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @305MW, PGPP1 @76MW [WEBSMS] | CVIS
3/9/2024 5:39:16 PM | [NSO Update] Luzon Grid-03/09/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12510MW, PK=9686MW, RR=380MW, NetOpMargin: EVE=2444 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: GMEC 1 @ 155MW, Masinloc 1 @ 310MW, Masinloc 3 @ 325MW, Ilijan A @ 230MW [WEBSMS] | CLUZ
3/9/2024 5:16:43 PM | Mindanao Grid-03/09/2024 17:21: Baloi-Marawi 69kV Line 2 re-energized at 1712H (Planned Outage). [WEBSMS] | CMIN
3/9/2024 5:16:16 PM | Mindanao Grid-03/09/2024 17:20: WMPC DG10 shutdown at 1713H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/9/2024 3:37:35 PM | Luzon Grid-03/09/2024 15:37: Bay-Batangas 230kV line 1 restored at 1536H (Planned Outage) [WEBSMS] | CLUZ
3/9/2024 3:37:16 PM | Visayas Grid-03/09/2024 15:37: Cebu SS 100MVA TR2 energized at 1531H (Planned Outage) [WEBSMS] | CVIS
3/9/2024 3:27:03 PM | Visayas Grid-03/09/2024 15:27: Petrowind online at 1457H (Planned Outage) [WEBSMS] | CVIS
3/9/2024 2:56:28 PM | Mindanao Grid-03/09/2024 15:00: Pulangi 4 U2 online at 1452H. Planned Outage. [WEBSMS] | CMIN
3/9/2024 1:44:32 PM | Mindanao Grid-03/09/2024 13:49: WMPC DG10 online at 1342H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/9/2024 1:40:22 PM | Mindanao Grid-03/09/2024 13:44: NagaMin SS 138kV Power Transformer No. 1 restored at 1336H. (Planned Outage) [WEBSMS] | CMIN
3/9/2024 12:46:12 PM | [NSO Update] Mindanao Grid-03/09/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3043MW, PK=2193MW, RR=77MW, NetOpMargin: PM=773, EVE=680 Highest Unit O/L: GNPK 1, 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @60MW, AG2 @83MW, AG4 @103MW, AG5 @33MW, AG6 @150MW, AG7 @29MW, PG4 @87MW [WEBSMS] | CMIN
3/9/2024 12:45:03 PM | [NSO Update] Visayas Grid-03/09/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2746MW, PK=2021MW, RR=88MW, NetOpMargin: PM=637, EVE=463 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 305MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/9/2024 12:43:01 PM | [NSO Update] Luzon Grid-03/09/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13762MW, PK=10340MW, RR=402MW, NetOpMargin: PM=3020, EVE=2146 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: GMEC 1 @ 155MW, Masinloc 1 @ 310MW, Masinloc 3 @ 325MW, Pagbilao 1 @ 300MW, Ilijan A @ 230MW [WEBSMS] | CLUZ
3/9/2024 12:21:53 PM | Luzon Grid-03/09/2024 12:21: San Jose-North Caloocan 115kV line was de-energized at 1220H. (Planned Outage) [WEBSMS] | CLUZ
3/9/2024 12:20:05 PM | Luzon Grid-03/09/2024 12:20: San Jose-Camarin 115kV line was restored at 1113H. (Planned Outage) [WEBSMS] | CLUZ
3/9/2024 11:08:07 AM | Luzon Grid-03/09/2024 11:08: MPGC Unit 3 online at 1100H. (On-going Commissioning for new generating unit) [WEBSMS] | CLUZ
3/9/2024 11:04:35 AM | Luzon Grid-03/09/2024 11:04: Mauban-SBPL 230kV line 1(Customer Owned and Maintained Line) also auto-tripped at 1056H. (Unplanned Outage) [WEBSMS] | CLUZ
3/9/2024 11:00:40 AM | Luzon Grid-03/09/2024 11:00: SBPL Generating Unit tripped at 1056H from 180MW load. The lowest system frequency was 59.678Hz. (Unplanned Outage) [WEBSMS] | CLUZ
3/9/2024 9:36:52 AM | Luzon Grid-03/09/2024 09:36: Makban B-Makban D 230kV Tie Line was de-energized at 0926H. (Planned Outage) [WEBSMS] | CLUZ
3/9/2024 8:39:37 AM | Luzon Grid-03/09/2024 08:39: Calaca-BCF(Batangas Cola Fired Power Plant) 230kV line 3 was de-energized at 0837H. (Planned Outage) [WEBSMS] | CLUZ
3/9/2024 8:12:02 AM | Mindanao Grid-03/09/2024 08:16: Baloi-Marawi 69kV Line 2 shutdown at 0803H to facilitate massive clearing by D2-TL and ride-on activities by D2-SS and MTD-A. Planned Outage. [WEBSMS] | CMIN
3/9/2024 7:46:05 AM | Luzon Grid-03/09/2024 07:46: San Jose-Camarin 115kV line was de-energized at 0744H. (Planned Outage) [WEBSMS] | CLUZ
3/9/2024 7:30:23 AM | Luzon Grid-03/09/2024 07:30: Lumban-Malaya 230kV line 2 was de-energized at 0728H. (Planned Outage) [WEBSMS] | CLUZ
3/9/2024 7:08:39 AM | Mindanao Grid-03/09/2024 07:13: NagaMin SS 138kV Power Transformer No. 1 de-energized at 0706H. (Planned Outage) [WEBSMS] | CMIN
3/9/2024 7:08:23 AM | Luzon Grid-03/09/2024 07:08: Malaya 230kV Bus 2 was de-energized at 0707H. (Planned Outage) [WEBSMS] | CLUZ
3/9/2024 7:03:58 AM | Mindanao Grid-03/09/2024 07:08: Lugait SS 138kV Power Transformer No. 2 de-energized at 0702H. (Planned Outage) [WEBSMS] | CMIN
3/9/2024 6:59:41 AM | Luzon Grid-03/09/2024 06:59: Bay-Batangas 230kV line 1 was de-energized at 0659H. (Planned Outage) [WEBSMS] | CLUZ
3/9/2024 6:55:18 AM | Luzon Grid-03/09/2024 06:55: For info: Batangas 300MVA T04 and T05 were unparalleled at 0644H, while San Lorenzo-Sta Rita 230kV Busses were looped at 0651H. [WEBSMS] | CLUZ
3/9/2024 6:41:04 AM | Mindanao Grid-03/09/2024 06:45: Matanao - General Santos 138kV L2 de-energized at 0637H. (Planned Outage) [WEBSMS] | CMIN
3/9/2024 6:37:51 AM | Visayas Grid-03/09/2024 06:37: Cebu SS 100MVA TR2 de-energized at 0637H (Planned Outage) [WEBSMS] | CVIS
3/9/2024 6:32:17 AM | Mindanao Grid-03/09/2024 06:36: ASIGA HEP online at 0551H. Unplanned Outage. [WEBSMS] | CMIN
3/9/2024 5:50:41 AM | [NSO Update] Mindanao Grid-03/09/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3053MW, PK=2103MW, RR=75MW, NetOpMargin: AM=875, PM=829, EVE=733 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @60MW, AG2 @83MW, AG4 @103MW, AG5 @33MW, AG6 @150MW, AG7 @29MW, PG4 @87MW [WEBSMS] | CMIN
3/9/2024 5:49:10 AM | [NSO Update] Visayas Grid-03/09/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2898MW, PK=2032MW, RR=87MW, NetOpMargin: AM=779, PM=693, EVE=368 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
3/9/2024 5:49:07 AM | [NSO Update] Luzon Grid-03/09/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14196MW, PK=10175MW, RR=391MW, NetOpMargin: AM=3629, PM=3415, EVE=2651 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: GMEC 1 @155MW, MASINLOC 1 @310MW, MASINLOC 3 @325MW, PAGBILAO 1 @300MW, ILIJAN A@230MW [WEBSMS] | CLUZ
3/9/2024 5:37:15 AM | Luzon Grid-03/09/2024 05:37: Dona Imelda SS 300MVA T03 restored at 0535H (Planned Outage) [WEBSMS] | CLUZ
3/9/2024 5:04:35 AM | Mindanao Grid-03/09/2024 05:09: Lake Mainit (AGC) HEP online at 0436H. (Unplanned Outage) [WEBSMS] | CMIN
3/9/2024 4:28:48 AM | Luzon Grid-03/09/2024 04:28: MERALCO San Jose SS 83MVA T01 restored at 0426H (Planned Outage) [WEBSMS] | CLUZ
3/9/2024 4:27:47 AM | Mindanao Grid-03/09/2024 04:32: ASIGA (ASG) HEP with 5.7MW load isolated at 0351H affected by the tripping of Butuan-Santiago 69kV STL (ANECOs owned and maintained line). (Unplanned Outage) [WEBSMS] | CMIN
3/9/2024 4:25:53 AM | Mindanao Grid-03/09/2024 04:30: Lake Mainit (AGC) HEP with 16.3MW load isolated at 0351H affected by the tripping of Butuan-Santiago 69kV STL (ANECOs owned and maintained line). (Unplanned Outage) [WEBSMS] | CMIN
3/9/2024 4:04:46 AM | [NSO Update] Luzon Grid-03/09/2024 04:04: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/9/2024 4:03:21 AM | [NSO Update] Mindanao Grid-03/09/2024 04:07: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
3/9/2024 4:03:03 AM | [NSO Update] Visayas Grid-03/09/2024 04:03: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
3/9/2024 1:11:50 AM | Luzon Grid-03/09/2024 01:11: MERALCO San Jose SS 83MVA T01 de-energized at 0110H (Planned Outage) [WEBSMS] | CLUZ
3/9/2024 1:03:45 AM | Luzon Grid-03/09/2024 01:03: For info: Sta Rita and San Lorenzo 230kV Bus A and B were unlooped at 0100H while Batangas 300MVA T04 and T05 were looped at 0103H. [WEBSMS] | CLUZ
3/8/2024 10:30:11 PM | Luzon Grid-03/08/2024 22:30: Dona Imelda SS 300MVA T03 de-energized at 2227H (Planned Outage) [WEBSMS] | CLUZ
3/8/2024 8:49:11 PM | Mindanao Grid-03/08/2024 20:53: WMPC DG10 shutdown at 2043H. RPS-System Voltage Requirement [WEBSMS] | CMIN
3/8/2024 7:20:34 PM | Visayas Grid-03/08/2024 19:20: Petrowind on line at 1804H. (Planned Outage) [WEBSMS] | CVIS
3/8/2024 6:06:27 PM | Mindanao Grid-03/08/2024 18:10: Kidapawan SS 138kV Bus #2 (7BS02KID) successfully restored/energized back to the Mindanao Grid at 1801H. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
3/8/2024 6:01:54 PM | [NSO Update] Luzon Grid-03/08/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12884MW, PK=10448MW, RR=280MW, NetOpMargin: EVE=2156 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: GMEC 1 @155MW, MSLC1 @310MW, MSLC3 @325MW, PBL1 @300MW, ILIJAN A @230MW [WEBSMS] | CLUZ
3/8/2024 5:54:52 PM | [NSO Update] Mindanao Grid-03/08/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3033MW, PK=2262MW, RR=72MW, NetOpMargin: EVE=698 Highest Unit O/L: GNPK 1,2, 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @60MW, AG2 @83MW, AG4 @103MW, AG5 @33MW, AG6 @180MW, AG7 @29MW, PG4 @87MW [WEBSMS] | CMIN
3/8/2024 5:52:32 PM | [NSO Update] Visayas Grid-03/08/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2499MW, PK=2128MW, RR=90MW, NetOpMargin: EVE=282 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
3/8/2024 5:16:32 PM | Mindanao Grid-03/08/2024 17:21: WMPC DG04 shutdown at 1713H. RPS-System Voltage Requirement [WEBSMS] | CMIN
3/8/2024 4:30:48 PM | Mindanao Grid-03/08/2024 16:35: Lake Mainit HEP Unit 2 with 6.2MW tripped at 1604H. (Unplanned Outage) [WEBSMS] | CMIN
3/8/2024 3:24:56 PM | Luzon Grid-03/08/2024 15:24: Tayabas 230kV Bus 1 restored at 1522H (Planned Outage) [WEBSMS] | CLUZ
3/8/2024 1:03:23 PM | [NSO Update] Mindanao Grid-03/08/2024 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3095MW, PK=2346MW, RR=77MW, NetOpMargin: PM=672, EVE=682 Highest Unit O/L: GNPK 1-4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @60MW, AG2 @83MW, AG4 @103MW, AG5 @33MW, AG6 @175MW, AG7 @29MW, PG4 @87MW [WEBSMS] | CMIN
3/8/2024 1:02:12 PM | [NSO Update] Visayas Grid-03/08/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2786MW, PK=2298MW, RR=95MW, NetOpMargin: PM=393, EVE=273 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @322MW, PGPP1 @76MW [WEBSMS] | CVIS
3/8/2024 1:00:09 PM | [NSO Update] Luzon Grid-03/08/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13901MW, PK=11237MW, RR=302MW, NetOpMargin: PM=2362, EVE=1730 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: GMEC 1 @155MW, MSLC1 @310MW, MSLC3 @320MW, PBL1 @300MW, ILIJAN A @230MW [WEBSMS] | CLUZ
3/8/2024 10:32:01 AM | Mindanao Grid-03/08/2024 10:36: WMPC DG04 online at 1029H. RPS-System Voltage Requirement [WEBSMS] | CMIN
3/8/2024 9:51:15 AM | Mindanao Grid-03/08/2024 09:55: WMPC DG10 online at 0947H. RPS-System Voltage Requirement [WEBSMS] | CMIN
3/8/2024 8:39:29 AM | Mindanao Grid-03/08/2024 08:43: TALOMO 2B unit 1 online at 0725H. (Unplanned Outage) [WEBSMS] | CMIN
3/8/2024 8:37:11 AM | Mindanao Grid-03/08/2024 08:41: Kidapawan SS 138kV Bus #2 (7BS02KID) de-energized at 0827H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
3/8/2024 8:36:35 AM | Mindanao Grid-03/08/2024 08:41: TALOMO 2B Unit 1 with 0.27MW load tripped at 0717H. Indication: Wicket gate signal failure. (Unplanned Outage) [WEBSMS] | CMIN
3/8/2024 6:43:22 AM | Luzon Grid-03/08/2024 06:43: Tayabas 230kV Bus 1 was de-energized at 0642H. (Planned Outage) [WEBSMS] | CLUZ
3/8/2024 6:06:48 AM | [NSO Update] Luzon Grid-03/08/2024 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14035MW, PK=10980MW, RR=291MW, NetOpMargin: AM=2765, PM=1955, EVE=1590 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: GMEC 1 @155MW, MSLC1 @310MW, PBL1 @300MW, ILIJAN A @230MW [WEBSMS] | CLUZ
3/8/2024 5:56:37 AM | Luzon Grid-03/08/2024 05:56: La Trinidad-Bauang 230kV line 2 was restored at 0554H. (Planned Outage) [WEBSMS] | CLUZ
3/8/2024 5:42:44 AM | Luzon Grid-03/08/2024 05:42: Bacman 230kV Bus 2 was de-energized at 0538H. (Planned Outage) [WEBSMS] | CLUZ
3/8/2024 5:34:58 AM | [NSO Update] Mindanao Grid-03/08/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3102MW, PK=2311MW, RR=75MW, NetOpMargin: AM=715, PM=696, EVE=691 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @60MW, AG2 @83MW, AG4 @103MW, AG5 @33MW, AG6 @175MW, AG7 @29MW, PG4 @87MW [WEBSMS] | CMIN
3/8/2024 5:28:32 AM | [NSO Update] Visayas Grid-03/08/2024 05:28: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2758MW, PK=2217MW, RR=91MW, NetOpMargin: AM=451, PM=294, EVE=230 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @322MW, PGPP1 @76MW [WEBSMS] | CVIS
3/8/2024 5:27:04 AM | Visayas Grid-03/08/2024 05:27: Quiot 100 MVA TR2 de-energized/energized at 0302H/0457H. (Unplanned Outage) [WEBSMS] | CVIS
3/8/2024 4:22:20 AM | [NSO Update] Mindanao Grid-03/08/2024 04:26: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
3/8/2024 4:21:33 AM | [NSO Update] Luzon Grid-03/08/2024 04:21: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/8/2024 4:20:40 AM | [NSO Update] Visayas Grid-03/08/2024 04:20: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
3/8/2024 12:03:34 AM | Mindanao Grid-03/08/2024 00:08: STEAG U1 shutdown at 0000H. Planned Outage. [WEBSMS] | CMIN
3/7/2024 11:58:17 PM | Luzon Grid-03/07/2024 23:58: Botolan-Subic Hanjin 230kV line was restored at 2357H. (Unplanned Outage) [WEBSMS] | CLUZ
3/7/2024 11:43:46 PM | Luzon Grid-03/07/2024 23:43: Botolan-Subic Hanjin 230kV line auto-tripped/auto-reclosed but auto-tripped again at 2337H. (Unplanned Outage) [WEBSMS] | CLUZ
3/7/2024 10:52:35 PM | Luzon Grid-03/07/2024 22:52: La Trinidad-Bauang 230kV line 2 was de-energized at 2245H. (Planned Outage) [WEBSMS] | CLUZ
3/7/2024 9:55:36 PM | Mindanao Grid-03/07/2024 22:00: Butuan - Placer 138kV Line 1 re-energized at 2148H (Planned Outage). [WEBSMS] | CMIN
3/7/2024 9:42:12 PM | Visayas Grid-03/07/2024 21:42: Calatrava - Cadiz 230 kV Line 1 energized from Cadiz SS at 2038H, closed loop at Calatrava SS at 2140H. (Test and Commissioning) [WEBSMS] | CVIS
3/7/2024 8:38:49 PM | Visayas Grid-03/07/2024 20:38: Calatrava - Cadiz 230 kV Line 1 energized from Cadiz SS at 2038H. (Test and Commissioning) [WEBSMS] | CVIS
3/7/2024 8:30:07 PM | Visayas Grid-03/07/2024 20:30: Calatrava - Cadiz 230 kV Line 1 de-energized at 2029H. (Test and Commissioning) [WEBSMS] | CVIS
3/7/2024 8:28:03 PM | Mindanao Grid-03/07/2024 20:32: WMPC DG10 shutdown at 2019H. RPS-System Voltage Requirement [WEBSMS] | CMIN
3/7/2024 8:06:10 PM | Visayas Grid-03/07/2024 20:06: Calatrava - Cadiz 230 kV Line 1 energized from Calatrava SS at 2004H. (Test and Commissioning) [WEBSMS] | CVIS
3/7/2024 7:37:06 PM | Luzon Grid-03/07/2024 19:36: Tayabas SS PCB 8Z-03CB08TAY closed at 1936H, commissioned. [WEBSMS] | CLUZ
3/7/2024 6:04:53 PM | [NSO Update] Luzon Grid-03/07/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12780MW, PK=11057MW, RR=370MW, NetOpMargin: EVE=1353 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: GMEC 1 @155MW, MSLC1 @310MW, PBL1 @270MW, ILIJAN A @230MW [WEBSMS] | CLUZ
3/7/2024 6:02:44 PM | [NSO Update] Visayas Grid-03/07/2024 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2562MW, PK=2296MW, RR=86MW, NetOpMargin: EVE=181 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @300MW, PGPP1 @76MW [WEBSMS] | CVIS
3/7/2024 5:57:29 PM | [NSO Update] Mindanao Grid-03/07/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3120MW, PK=2364MW, RR=74MW, NetOpMargin: EVE=681 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @59MW, AG2 @81MW, AG4 @101MW, AG5 @32MW, AG6 @162MW, AG7 @28MW, PG4 @87MW [WEBSMS] | CMIN
3/7/2024 5:25:29 PM | Visayas Grid-03/07/2024 17:25: EDC-Malitbog U3 tripped at 1718H. (Unplanned Outage) [WEBSMS] | CVIS
3/7/2024 5:03:18 PM | Mindanao Grid-03/07/2024 17:07: WMPC DG04 shutdown at 1658H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/7/2024 4:51:00 PM | Mindanao Grid-03/07/2024 16:55: Agus 6 U4 online at 1642H. Unplanned Outage. [WEBSMS] | CMIN
3/7/2024 4:04:53 PM | Visayas Grid-03/07/2024 16:04: EDC-Malitbog U3 online at 1547H. (Unplanned Outage) [WEBSMS] | CVIS
3/7/2024 2:50:29 PM | Visayas Grid-03/07/2024 14:50: EDC-Upper Mahiao U4 online at 1444H. (Unplanned Outage) [WEBSMS] | CVIS
3/7/2024 2:15:51 PM | Visayas Grid-03/07/2024 14:15: EDC-Upper Mahiao U4 emergency shutdown at 1405H. (Unplanned Outage) [WEBSMS] | CVIS
3/7/2024 2:14:39 PM | Visayas Grid-03/07/2024 14:14: EDC-Malitbog U3 tripped at 1411H. (Unplanned Outage) [WEBSMS] | CVIS
3/7/2024 1:58:58 PM | Luzon Grid-03/07/2024 13:58: Quezon - Mexico 230kV Line restored at 1357H. (Unplanned Outage) [WEBSMS] | CLUZ
3/7/2024 1:57:46 PM | Luzon Grid-03/07/2024 13:57: Quezon - Mexico 230kV Line tripped at 1353H. (Unplanned Outage) [WEBSMS] | CLUZ
3/7/2024 1:06:17 PM | Mindanao Grid-03/07/2024 13:10: WMPC DG04 online at 1243H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/7/2024 12:52:29 PM | [NSO Update] Visayas Grid-03/07/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2728MW, PK=2335MW, RR=91MW, NetOpMargin: PM=303, EVE=218 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @319MW, PGPP1 @76MW [WEBSMS] | CVIS
3/7/2024 12:50:01 PM | [NSO Update] Luzon Grid-03/07/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13953MW, PK=11340MW, RR=392MW, NetOpMargin: PM=2220, EVE=1365 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: GMEC 1 @155MW, MASINLOC 1 @310MW, PAGBILAO 1 @270MW, ILIJAN A @230MW [WEBSMS] | CLUZ
3/7/2024 12:46:48 PM | [NSO Update] Mindanao Grid-03/07/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3166MW, PK=2418MW, RR=77MW, NetOpMargin: PM=671, EVE=673 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @59MW, AG2 @81MW, AG4 @101MW, AG5 @32MW, AG6 @152MW, AG7 @28MW, PG4 @87MW [WEBSMS] | CMIN
3/7/2024 9:48:14 AM | Mindanao Grid-03/07/2024 09:52: WMPC DG10 online at 0944H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
3/7/2024 9:29:01 AM | Mindanao Grid-03/07/2024 09:33: MCC U2 (CEPALCO Balingasag) online at 0903H. Follow RTD. [WEBSMS] | CMIN
3/7/2024 8:09:33 AM | Mindanao Grid-03/07/2024 08:13: (IACC) Iligan-MCN 13.8kV line re-energized up to watershed only at 0711H. Watershed cut-out fuse closed at 0806H. [WEBSMS] | CMIN
3/7/2024 6:05:48 AM | Luzon Grid-03/07/2024 06:05: Bakun HEPP 60MVA Main Transformer T01 (Customer Owned) de-energized at 0602H (Planned Outage) [WEBSMS] | CLUZ
3/7/2024 5:52:36 AM | [NSO Update] Luzon Grid-03/07/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14229MW, PK=11042MW, RR=381MW, NetOpMargin: AM=2806, PM=2123, EVE=1517 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC2 @180MW, MSLC1 @310MW, PBL1 @270MW, ILIJAN A @230MW [WEBSMS] | CLUZ
3/7/2024 5:48:54 AM | [NSO Update] Mindanao Grid-03/07/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3206MW, PK=2279MW, RR=75MW, NetOpMargin: AM=851, PM=678, EVE=654 Highest Unit O/L: GNPK 1,2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @59MW, AG2 @81MW, AG4 @101MW, AG5 @32MW, AG6 @178MW, AG7 @28MW, PG4 @87MW [WEBSMS] | CMIN
3/7/2024 5:48:09 AM | Mindanao Grid-03/07/2024 05:52: (IACC) Iligan-MCN 13.8kV line tripped with indication ABN at 0538H, LD=0.908MW (Unplanned Outage) [WEBSMS] | CMIN
3/7/2024 5:46:03 AM | [NSO Update] Visayas Grid-03/07/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2860MW, PK=2331MW, RR=88MW, NetOpMargin: AM=440, PM=280, EVE=276 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @319MW, PGPP1 @76MW [WEBSMS] | CVIS
3/7/2024 5:16:51 AM | Mindanao Grid-03/07/2024 05:21: Butuan - Placer 136kV Line1 shutdown at 0506H (Planned Outage) [WEBSMS] | CMIN
3/7/2024 4:28:25 AM | [NSO Update] Mindanao Grid-03/07/2024 04:32: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
3/7/2024 4:28:01 AM | [NSO Update] Luzon Grid-03/07/2024 04:28: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
3/7/2024 4:27:35 AM | [NSO Update] Visayas Grid-03/07/2024 04:27: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
3/7/2024 4:11:27 AM | Mindanao Grid-03/07/2024 04:16: SEC 1 (SMF) online at 0403H from FO. (Unplanned Outage) [WEBSMS] | CMIN
3/7/2024 2:51:24 AM | Mindanao Grid-03/07/2024 02:56: Updated: Minergy Coal Plant (MCC) U3 online at 0230H from FO. (Unplanned Outage) [WEBSMS] | CMIN
3/7/2024 2:44:17 AM | Mindanao Grid-03/07/2024 02:49: Minergy Coal Plant (MCC) U3 online from FO. Unplanned Outage. [WEBSMS] | CMIN
3/7/2024 12:55:45 AM | Luzon Grid-03/07/2024 00:56: Calaca 2 shutdown at 2351H (Planned Outage) [WEBSMS] | CLUZ
3/6/2024 8:23:46 PM | Mindanao Grid-03/06/2024 20:28: Minergy Coal Plant (MCC) U3 with a gross generation of 55MW tripped at 1958H with CEPALCO SIPS activation (Unplanned Outage). The lowest frequency reached was 59.72 Hz. Details to follow. [WEBSMS] | CMIN
3/6/2024 6:07:24 PM | Mindanao Grid-03/06/2024 18:12: Update 1: SEC Unit 1 with 118MW load tripped at 1738H with SIPS activation lowest frequency dip at 59.533Hz. Indication: For investigation. (Unplanned outage.) [WEBSMS] | CMIN
3/6/2024 5:55:20 PM | [NSO Update] Mindanao Grid-03/06/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3056MW, PK=2331MW, RR=72MW, NetOpMargin: EVE=653 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @59MW, AG2 @81MW, AG4 @101MW, AG5 @32MW, AG6 @122MW, AG7 @28MW, PG4 @66MW [WEBSMS] | CMIN
3/6/2024 5:53:26 PM | [NSO Update] Visayas Grid-03/06/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2732MW, PK=2252MW, RR=88MW, NetOpMargin: EVE=392 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
3/6/2024 5:52:25 PM | [NSO Update] Luzon Grid-03/06/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13203MW, PK=11080MW, RR=370MW, NetOpMargin: EVE=1753 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC2 @180MW, MSLC1 @310MW, PBL1 @300MW, SLPGC 1 @110MW, ILIJAN A @300MW [WEBSMS] | CLUZ
3/6/2024 5:49:34 PM | Mindanao Grid-03/06/2024 17:54: SEC-1 (SMF) with gross generation of 118MW tripped at 17:38:39H. (Unplanned Outage). [WEBSMS] | CMIN
3/6/2024 4:23:52 PM | Mindanao Grid-03/06/2024 16:28: Nasipit-Therma Marine Mobile 2 138kV Line 1 re-energized at 1621H (Planned Outage) [WEBSMS] | CMIN
3/6/2024 3:16:38 PM | Mindanao Grid-03/06/2024 15:21: WMPC DG02 with 3.0MW load tripped at 1510H. Indication: For further investigation. (Unplanned Outage) [WEBSMS] | CMIN
3/6/2024 3:06:05 PM | Mindanao Grid-03/06/2024 15:10: WMPC DG06 online at 1503H. MO Dispatch. [WEBSMS] | CMIN
3/6/2024 3:03:10 PM | Mindanao Grid-03/06/2024 15:07: WMPC DG02 online at 1441H. MO Dispatch. [WEBSMS] | CMIN
3/6/2024 3:02:33 PM | Mindanao Grid-03/06/2024 15:07: WMPC DG07 online at 1441H. MO Dispatch. [WEBSMS] | CMIN
3/6/2024 3:01:51 PM | Visayas Grid-03/06/2024 15:02: Colon SS 138/69/13.8 kV 50 MVA TR1 energized at 1458H. (Planned Outage) [WEBSMS] | CVIS
3/6/2024 1:15:09 PM | Visayas Grid-03/06/2024 13:15: Nabas SS 13/69 KV TR1 Secondary side 69KV auto-tripped at 1304H load involved 47MW. (Unplanned Outage) [WEBSMS] | CVIS
3/6/2024 1:06:15 PM | Mindanao Grid-03/06/2024 13:10: WMPC DG01 online at 1301H. MO Dispatch. [WEBSMS] | CMIN
3/6/2024 12:48:50 PM | [NSO Update] Mindanao Grid-03/06/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3122MW, PK=2416MW, RR=74MW, NetOpMargin: PM=631, EVE=647 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @59MW, AG2 @81MW, AG4 @101MW, AG5 @32MW, AG6 @147MW, AG7 @28MW, PG4 @66MW [WEBSMS] | CMIN
3/6/2024 12:46:32 PM | [NSO Update] Visayas Grid-03/06/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2675MW, PK=2309MW, RR=90MW, NetOpMargin: PM=276, EVE=204 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @305MW, PGPP1 @76MW [WEBSMS] | CVIS
3/6/2024 12:44:39 PM | [NSO Update] Luzon Grid-03/06/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14000MW, PK=11158MW, RR=389MW, NetOpMargin: PM=2453, EVE=1905 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @180MW, GMEC 1 @155MW, MSLC1 @310MW, PBL1 @300MW, SLPGC 1 @110MW, ILIJAN A @300MW [WEBSMS] | CLUZ
3/6/2024 10:53:17 AM | Mindanao Grid-03/06/2024 10:58: WMPC DG4 online at 1048H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
3/6/2024 10:10:27 AM | Luzon Grid-03/06/2024 10:10: For info: Sta Rita and San Lorenzo 230kV Busses were looped at 1010H. [WEBSMS] | CLUZ
3/6/2024 8:51:43 AM | Mindanao Grid-03/06/2024 08:56: WMPC DG10 online at 0849H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
3/6/2024 8:31:09 AM | Visayas Grid-03/06/2024 08:31: Colon SS 138/69KV 50MVA TR1 de-energized at 0827H. (Planned Outage) [WEBSMS] | CVIS
3/6/2024 7:41:18 AM | Mindanao Grid-03/06/2024 07:46: Nasipit-Therma Marine Mobile 2 138kV Line 1 shutdown at 0733H (Planned Outage) [WEBSMS] | CMIN
3/6/2024 7:13:24 AM | Luzon Grid-03/06/2024 07:13: For info: Batangas 300MVA T04 and T05 on split configuration at 0709H for preparation of looping of Sta. Rita and San Lorenzo 230kV Bus. [WEBSMS] | CLUZ
3/6/2024 6:42:48 AM | Luzon Grid-03/06/2024 06:43: GMEC Unit 1 online at 0636H. (Unplanned Outage) [WEBSMS] | CLUZ
3/6/2024 5:55:18 AM | Luzon Grid-03/06/2024 05:55: For info: Sta Rita-San Lorenzo 230kV Busses were unlooped at 0548H while Batangas 300MVA T04 and T05 were paralleled at 0551H. [WEBSMS] | CLUZ
3/6/2024 5:50:52 AM | [NSO Update] Luzon Grid-03/06/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14052MW, PK=10808MW, RR=391MW, NetOpMargin: AM=2837, PM=2494, EVE=1877 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 180MW, Masinloc 1 @ 310MW, Pagbilao 1 @ 300MW, Ilijan A @ 300MW [WEBSMS] | CLUZ
3/6/2024 5:46:06 AM | [NSO Update] Mindanao Grid-03/06/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3119MW, PK=2302MW, RR=72MW, NetOpMargin: AM=745, PM=672, EVE=687 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @59MW, AG2 @81MW, AG4 @101MW, AG5 @32MW, AG6 @122MW, AG7 @28MW, PG4 @66MW [WEBSMS] | CMIN
3/6/2024 5:45:13 AM | [NSO Update] Visayas Grid-03/06/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2724MW, PK=2220MW, RR=87MW, NetOpMargin: AM=417, PM=468, EVE=298 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 319MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/6/2024 4:25:19 AM | Mindanao Grid-03/06/2024 04:30: Agus 6 Unit#4 manually shutdown at 0412H. Unplanned Outage. [WEBSMS] | CMIN
3/6/2024 4:10:44 AM | [NSO Update] Mindanao Grid-03/06/2024 04:15: Weather Advisory: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
3/6/2024 4:10:30 AM | [NSO Update] Visayas Grid-03/06/2024 04:10: Weather Advisory: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
3/6/2024 4:09:41 AM | [NSO Update] Luzon Grid-03/06/2024 04:09: Weather Advisory: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
3/6/2024 12:23:20 AM | Mindanao Grid-03/06/2024 00:28: TM2 U1 shutdown at 0014H. Planned Outage (GOMP) [WEBSMS] | CMIN
3/5/2024 10:11:45 PM | Luzon Grid-03/05/2024 22:12: GNPD Unit 2 synchronized at 2210H. (Planned Outage) [WEBSMS] | CLUZ
3/5/2024 7:56:29 PM | Luzon Grid-03/05/2024 19:56: San Jose-Angat 115kV line 3 was looped at 1954H in Angat HEPP side. (Unplanned Outage - The equipment involved is under the AOR of Angat HEPP.) [WEBSMS] | CLUZ
3/5/2024 6:17:38 PM | Luzon Grid-03/05/2024 18:17: Angat HEPP 115kV Bus 1, and Angat HEPP 37MVA T03 were energized at 1815H and 1817H respectively. (Unplanned Outage - Under the AOR of Angat HEPP) [WEBSMS] | CLUZ
3/5/2024 6:05:34 PM | [NSO Update] Luzon Grid-03/05/2024 18:05: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12449MW, PK=10822MW, RR=380MW, NetOpMargin: EVE=1247 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @315MW [WEBSMS] | CLUZ
3/5/2024 5:54:20 PM | [NSO Update] Mindanao Grid-03/05/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3142MW, PK=2261MW, RR=70MW, NetOpMargin: EVE=810 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @59MW, AG2 @81MW, AG4 @101MW, AG5 @32MW, AG6 @121MW, AG7 @28MW, PG4 @96MW [WEBSMS] | CMIN
3/5/2024 5:46:53 PM | [NSO Update] Visayas Grid-03/05/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2736MW, PK=2243MW, RR=86MW, NetOpMargin: EVE=408 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
3/5/2024 5:25:26 PM | Luzon Grid-03/05/2024 17:25: San Jose-Angat 115kV line 3 was unlooped at Angat HEPP side due to the recurrence of auto-tripping of Angat HEPP 115kV Bus 1, Angat HEPP 37MVA T03 and Units 5, and 7 at 1716H. (Unplanned Outage - The equipment involved is under the AOR of Angat HEPP) [WEBSMS] | CLUZ
3/5/2024 5:02:35 PM | Luzon Grid-03/05/2024 17:02: Angat HEPP 115kV Bus 1, and Angat HEPP 37MVA T03 were energized at 1657H and 1659H respectively while San Jose-Angat 115kV line 3 was looped at Angat HEPP side at 1659H. (Unplanned Outage) [WEBSMS] | CLUZ
3/5/2024 4:41:40 PM | Luzon Grid-03/05/2024 16:41: For info: San Jose-Angat 115kV line 3 was unlooped at Angat HEPP side due to the auto-tripping of Angat HEPP 115kV Bus 1, Angat HEPP 37MVA T03 and Units 5, and 7 at 1614H. (Unplanned Outage) [WEBSMS] | CLUZ
3/5/2024 3:26:22 PM | Luzon Grid-03/05/2024 15:26: Dasmarinas-TMC II (Ternate) 115kV line (Customer Owned) was energized at 1524H. (Planned Outage) [WEBSMS] | CLUZ
3/5/2024 3:08:09 PM | Mindanao Grid-03/05/2024 15:12: WMPC DG09 tripped at 1500H. Unplanned Outage. [WEBSMS] | CMIN
3/5/2024 12:39:52 PM | [NSO Update] Mindanao Grid-03/05/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3188MW, PK=2352MW, RR=74MW, NetOpMargin: PM=762, EVE=774 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @59MW, AG2 @81MW, AG4 @101MW, AG5 @32MW, AG6 @121MW, AG7 @28MW, PG4 @96MW [WEBSMS] | CMIN
3/5/2024 12:36:14 PM | [NSO Update] Visayas Grid-03/05/2024 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2822MW, PK=2236MW, RR=89MW, NetOpMargin: PM=497, EVE=428 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @312MW, PGPP1 @76MW [WEBSMS] | CVIS
3/5/2024 12:34:49 PM | [NSO Update] Luzon Grid-03/05/2024 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13295MW, PK=11200MW, RR=362MW, NetOpMargin: PM=1733, EVE=1171 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @315MW, MSLC3 @300MW [WEBSMS] | CLUZ
3/5/2024 11:48:42 AM | Luzon Grid-03/05/2024 11:48: Ilijan A ST 1 online at 1146H (Planned Outage) [WEBSMS] | CLUZ
3/5/2024 9:08:13 AM | Mindanao Grid-03/05/2024 09:12: Agus 6 U1 shutdown at 0901H. Planned Outage. [WEBSMS] | CMIN
3/5/2024 8:48:12 AM | Luzon Grid-03/05/2024 08:48: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0845H (Planned Outage) [WEBSMS] | CLUZ
3/5/2024 8:47:05 AM | Mindanao Grid-03/05/2024 08:51: FDC U1 online at 0839H. Unplanned Outage. [WEBSMS] | CMIN
3/5/2024 8:07:54 AM | Luzon Grid-03/05/2024 08:07: Ilijan A1-2 online at 0805H (Unplanned Outage) [WEBSMS] | CLUZ
3/5/2024 7:06:57 AM | Mindanao Grid-03/05/2024 07:11: Pulangi 4 U2 shutdown at 0702H. Planned Outage. [WEBSMS] | CMIN
3/5/2024 6:18:33 AM | Mindanao Grid-03/05/2024 06:23: FDC U1 with 132MW gross generation tripped at 0608H. Unplanned Outage. [WEBSMS] | CMIN
3/5/2024 6:08:45 AM | [NSO Update] Luzon Grid-03/05/2024 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13129MW, PK=10813MW, RR=351MW, NetOpMargin: AM=1965, PM=1675, EVE=1328 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Calaca 2 @ 180MW, Masinloc 1 @ 315MW, Masinloc 3 @ 300MW [WEBSMS] | CLUZ
3/5/2024 6:00:02 AM | [NSO Update] Mindanao Grid-03/05/2024 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3218MW, PK=2198MW, RR=72MW, NetOpMargin: AM=948, PM=849, EVE=919 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @59MW, AG2 @81MW, AG4 @101MW, AG5 @32MW, AG6 @121MW, AG7 @28MW, PG4 @104MW [WEBSMS] | CMIN
3/5/2024 5:58:55 AM | [NSO Update] Visayas Grid-03/05/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2815MW, PK=2146MW, RR=87MW, NetOpMargin: AM=582, PM=514, EVE=492 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 319MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/5/2024 5:06:04 AM | Mindanao Grid-03/05/2024 05:10: Sultan Kudarat SS 138kV Power Transformer No. 3 de-energized at 0503H for decommissioning. (Planned Outage) [WEBSMS] | CMIN
3/5/2024 4:08:16 AM | [NSO Update] Luzon Grid-03/05/2024 04:08: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CLUZ
3/5/2024 4:07:57 AM | [NSO Update] Mindanao Grid-03/05/2024 04:12: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CMIN
3/5/2024 4:07:36 AM | [NSO Update] Visayas Grid-03/05/2024 04:07: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CVIS
3/4/2024 11:54:27 PM | Luzon Grid-03/04/2024 23:54: SLPGC Unit 1 online at 2349H (Unplanned Outage) [WEBSMS] | CLUZ
3/4/2024 10:46:05 PM | Mindanao Grid-03/04/2024 22:50: Davao-Bunawan 138kV L2 energized at 2239H. (Planned Outage) [WEBSMS] | CMIN
3/4/2024 10:40:32 PM | Luzon Grid-03/04/2024 22:40: Pagbilao Unit 1 online at 2237H (Unplanned Outage) [WEBSMS] | CLUZ
3/4/2024 5:54:17 PM | [NSO Update] Mindanao Grid-03/04/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3187MW, PK=2167MW, RR=74MW, NetOpMargin: EVE=946 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
3/4/2024 5:49:00 PM | [NSO Update] Visayas Grid-03/04/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2645MW, PK=2202MW, RR=87MW, NetOpMargin: EVE=357 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @313MW, PGPP1 @76MW [WEBSMS] | CVIS
3/4/2024 5:39:59 PM | [NSO Update] Luzon Grid-03/04/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11654MW, PK=10334MW, RR=380MW, NetOpMargin: EVE=940 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @330MW, MSLC3 @330MW, Sual 2 @320MW [WEBSMS] | CLUZ
3/4/2024 4:56:06 PM | Mindanao Grid-03/04/2024 17:00: WMPC DG10 with 8.5MW load tripped at 1642H. Indication: Oil mist concentration high stop. (Unplanned Outage) [WEBSMS] | CMIN
3/4/2024 4:49:56 PM | Luzon Grid-03/04/2024 16:50: SLPGC Unit 1 tripped at 1641H from 40MW while on load stabilization. (Unplanned Outage) [WEBSMS] | CLUZ
3/4/2024 4:36:44 PM | Mindanao Grid-03/04/2024 16:41: WMPC DG03 shutdown at 1622H. MO Dispatch. [WEBSMS] | CMIN
3/4/2024 4:31:56 PM | Mindanao Grid-03/04/2024 16:36: Libertad Power online at 1609H. (Unplanned Outage) [WEBSMS] | CMIN
3/4/2024 4:31:20 PM | Mindanao Grid-03/04/2024 16:36: Libertad Power (LPE) with 6MW load tripped at 1604H. Indication: For further investigation. (Unplanned Outage) [WEBSMS] | CMIN
3/4/2024 3:37:52 PM | Mindanao Grid-03/04/2024 15:42: WMPC DG03 online at 1531H. MO dispatched. [WEBSMS] | CMIN
3/4/2024 3:00:10 PM | Mindanao Grid-03/04/2024 15:04: TMI 1 Unit 2 online at 1454H. MO Dispatch. [WEBSMS] | CMIN
3/4/2024 1:10:48 PM | Luzon Grid-03/04/2024 13:11: GNPD 855MVA Transformer No. 3(Customer Owned) was de-energized at 1304H. (Unplanned Outage requested by GNPD to facilitate the testing of metering equipment.) [WEBSMS] | CLUZ
3/4/2024 12:58:11 PM | Mindanao Grid-03/04/2024 13:02: WMPC DG01 online at 1255H. MO dispatched. [WEBSMS] | CMIN
3/4/2024 12:57:35 PM | Mindanao Grid-03/04/2024 13:02: Bunawan SS 138kV Bus No. 2 energized at 1255H. (Planned Outage) [WEBSMS] | CMIN
3/4/2024 12:48:46 PM | [NSO Update] Mindanao Grid-03/04/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3247MW, PK=2272MW, RR=77MW, NetOpMargin: PM=898, EVE=913 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
3/4/2024 12:45:08 PM | [NSO Update] Visayas Grid-03/04/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2215MW, RR=89MW, NetOpMargin: PM=586, EVE=409 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @305MW, PGPP1 @76MW [WEBSMS] | CVIS
3/4/2024 12:43:12 PM | [NSO Update] Luzon Grid-03/04/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12846MW, PK=10885MW, RR=399MW, NetOpMargin: PM=1562, EVE=1194 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @330MW, MSLC3 @325MW [WEBSMS] | CLUZ
3/4/2024 12:26:31 PM | Mindanao Grid-03/04/2024 12:31: TM2 U1 online at 1218H. MO Dispatch. (Unplanned Outage) [WEBSMS] | CMIN
3/4/2024 12:23:18 PM | Mindanao Grid-03/04/2024 12:27: Libertad Power (LPE) online at 1218H (Unplanned Outage). [WEBSMS] | CMIN
3/4/2024 12:18:29 PM | Mindanao Grid-03/04/2024 12:23: Libertad Power (LPE) with 6MW tripped at 1208H. Indication: For further investigation. Unplanned Outage. [WEBSMS] | CMIN
3/4/2024 11:46:48 AM | Luzon Grid-03/04/2024 11:47: SLPGC Unit 1 online at 1143H. (Unplanned Outage) [WEBSMS] | CLUZ
3/4/2024 10:40:18 AM | Luzon Grid-03/04/2024 10:40: San Jose - Angat 115kV line 3 was looped at Angat HEPP side at 1033H. (Related to Angat HEPP Upgrading Project) [WEBSMS] | CLUZ
3/4/2024 10:09:40 AM | Mindanao Grid-03/04/2024 10:14: WMPC DG10 online at 1007H. MO dispatched. [WEBSMS] | CMIN
3/4/2024 10:03:58 AM | Mindanao Grid-03/04/2024 10:08: SPC Mati online at 1000H. MO dispatched. [WEBSMS] | CMIN
3/4/2024 8:38:58 AM | Mindanao Grid-03/04/2024 08:43: Bunawan SS 138kV Bus 2 de-energized/shutdown at 0811H (Planned Outage) [WEBSMS] | CMIN
3/4/2024 5:40:02 AM | [NSO Update] Luzon Grid-03/04/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13055MW, PK=10404MW, RR=391MW, NetOpMargin: AM=2260, PM=1785, EVE=1390 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: CALACA 2 @180MW, MASINLOC 1 @330MW, MASINLOC 3 @320MW [WEBSMS] | CLUZ
3/4/2024 5:36:47 AM | [NSO Update] Mindanao Grid-03/04/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3253MW, PK=2104MW, RR=75MW, NetOpMargin: AM=1075, PM=903, EVE=929 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
3/4/2024 5:34:38 AM | [NSO Update] Visayas Grid-03/04/2024 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2945MW, PK=2108MW, RR=87MW, NetOpMargin: AM=750, PM=659, EVE=510 Highest Unit O/L: THVI 1 & 2 @169MW Derated Plant: LEYTE A @312MW, PGPP1 @76MW [WEBSMS] | CVIS
3/4/2024 5:25:17 AM | Mindanao Grid-03/04/2024 05:29: Attempted to energize Baloi -IDPP ( Mapalad) 138 kV Line at 0502H but failed with SOTF relay indication. Advised SEOD on duty at Baloi to inform TL Engr to conduct line patrol. [WEBSMS] | CMIN
3/4/2024 5:03:36 AM | Mindanao Grid-03/04/2024 05:08: Baloi -IDPP ( Mapalad) 138 kV Line tripped at 0423H (Unplanned Outage) [WEBSMS] | CMIN
3/4/2024 4:17:08 AM | [NSO Update] Visayas Grid-03/04/2024 04:17: Weather Advisory: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
3/4/2024 4:16:54 AM | [NSO Update] Mindanao Grid-03/04/2024 04:21: Weather Advisory: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
3/4/2024 4:16:37 AM | [NSO Update] Luzon Grid-03/04/2024 04:16: Weather Advisory: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/4/2024 2:55:15 AM | Luzon Grid-03/04/2024 02:55: Ilijan GT2-1 online at 0254H (Unplanned Outage). [WEBSMS] | CLUZ
3/4/2024 1:39:39 AM | Luzon Grid-03/04/2024 01:39: Ilijan ST2 online at 0138H (Unplanned Outage) [WEBSMS] | CLUZ
3/4/2024 1:21:48 AM | Mindanao Grid-03/04/2024 01:26: TUDAYA 2 Unit 2 online at 0049H (Unplanned Outage) [WEBSMS] | CMIN
3/4/2024 12:47:29 AM | Luzon Grid-03/04/2024 00:47: Ilijan GT 2-2 online at 0045H (Unplanned Outage) [WEBSMS] | CLUZ
3/4/2024 12:23:24 AM | Luzon Grid-03/04/2024 00:23: Tayabas-San Jose 500kV Line 1 restored at 0021H (Unplanned Outage) [WEBSMS] | CLUZ
3/3/2024 11:54:00 PM | Mindanao Grid-03/03/2024 23:58: TUDAYA 2 Unit 2 with 2.6MW load shutdown at 2102H for dewatering of Tudaya 2 Unit 2 Tailrace to facilitate Unit 1 installation of Draft Tube. (Unplanned Outage) [WEBSMS] | CMIN
3/3/2024 9:39:13 PM | Luzon Grid-03/03/2024 21:39: SLPGC Unit 1 (150MW) tripped at 2135H. Lowest system frequency was 59.563Hz. [WEBSMS] | CLUZ
3/3/2024 9:21:07 PM | Luzon Grid-03/03/2024 21:21: San Jose SS 300MVA T01 restored at 2120H (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 9:16:13 PM | Luzon Grid-03/03/2024 21:16: Sta. Rita Module 40 online at 2113H (Unplanned Outage) [WEBSMS] | CLUZ
3/3/2024 8:10:25 PM | Mindanao Grid-03/03/2024 20:15: LAMSAN Biomass online at 2004H (from shutdown/ outside management control). Follow RTD. [WEBSMS] | CMIN
3/3/2024 7:37:57 PM | Mindanao Grid-03/03/2024 19:42: LAMSAN Biomass shutdown at 1925H. End of MRU. [WEBSMS] | CMIN
3/3/2024 7:11:35 PM | Mindanao Grid-03/03/2024 19:16: Sultan Kudarat 138 kV Power Transformer No.3, 75 MVA (7XF03SKU) energized back at 1902H from Planned Outage/ Non-GOMP. [WEBSMS] | CMIN
3/3/2024 7:08:17 PM | Mindanao Grid-03/03/2024 19:12: Sultan Kudarat 138 kV Power Transformer No.2 (7XF02SKU energized back at 1903H from Planned Outage/ Non-GOMP. [WEBSMS] | CMIN
3/3/2024 6:52:58 PM | Mindanao Grid-03/03/2024 18:57: Kibawe-Sultan Kudarat (SKU) 138kVL energized at 1850H from Planned Outage/Non-GOMP. [WEBSMS] | CMIN
3/3/2024 6:45:08 PM | Mindanao Grid-03/03/2024 18:49: Balo-i-Agus2 138kV L2 energized back at 1840H from Planned Outage/GOMP. [WEBSMS] | CMIN
3/3/2024 6:27:48 PM | Mindanao Grid-03/03/2024 18:32: Maco SS 138kV 100MVA Power Transformer No.2 energized at 1824H from Planned Outage/GOMP. [WEBSMS] | CMIN
3/3/2024 5:51:45 PM | Mindanao Grid-03/03/2024 17:56: (Updated) Kibawe-Tacurong 138kVL energized at 1747H from Planned Outage/Non-GOMP. [WEBSMS] | CMIN
3/3/2024 5:49:49 PM | [NSO Update] Mindanao Grid-03/03/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3285MW, PK=2072MW, RR=74MW, NetOpMargin: EVE=1139 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
3/3/2024 5:49:00 PM | Mindanao Grid-03/03/2024 17:53: Kibawe-Tacurong 138kVL energized at 1750H from Planned Outage/Non-GOMP. [WEBSMS] | CMIN
3/3/2024 5:48:56 PM | [NSO Update] Visayas Grid-03/03/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2723MW, PK=2040MW, RR=86MW, NetOpMargin: EVE=597 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 313MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/3/2024 5:47:51 PM | [NSO Update] Luzon Grid-03/03/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11190MW, PK=9206MW, RR=290MW, NetOpMargin: EVE=1694 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Calaca 2 @ 180MW, Masinloc 1 @ 300MW, Masinloc 3 @ 305MW [WEBSMS] | CLUZ
3/3/2024 5:17:19 PM | Luzon Grid-03/03/2024 17:17: Hermosa-Balsik 230kV Line 2 restored at 1716H (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 5:16:01 PM | Luzon Grid-03/03/2024 17:16: Ilijan PCB 9-01CB08ILJ & PCB 9-01CB24ILJ restored at 1713H (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 5:13:38 PM | Luzon Grid-03/03/2024 17:13: Tayabas PCB 9-03CB04TAY & PCB 9-03CB24TAY (formerly Tayabas-San Jose 500kV Line 2) restored at 1710H & 1711H, respectively. (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 5:04:04 PM | Mindanao Grid-03/03/2024 17:08: Manolo Fortich SS 138kV 50MVA Power Transformer No.1 energized at 1700H from Planned Outage/GOMP. [WEBSMS] | CMIN
3/3/2024 4:52:03 PM | Luzon Grid-03/03/2024 16:52: Calaca-Sta. Rita 230kV Line 2 restored at 1650H (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 4:06:57 PM | Luzon Grid-03/03/2024 16:07: Ilijan PCB 9-01CB08ILJ & PCB 9-01CB24ILJ de-energized at 1604H (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 3:23:37 PM | Luzon Grid-03/03/2024 15:23: Lamao-SCPC 230kV Tie Line 4 de-energized at 1520H (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 3:16:56 PM | Visayas Grid-03/03/2024 15:17: 230KV Cebu-Magdugo line 1 energized @1511H. ( Planned Outage ) [WEBSMS] | CVIS
3/3/2024 1:07:31 PM | [NSO Update] Mindanao Grid-03/03/2024 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3348MW, PK=1850MW, RR=77MW, NetOpMargin: PM=1420, EVE=1168 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
3/3/2024 1:04:11 PM | [NSO Update] Visayas Grid-03/03/2024 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2753MW, PK=1764MW, RR=89MW, NetOpMargin: PM=901, EVE=620 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
3/3/2024 10:43:21 AM | Mindanao Grid-03/03/2024 10:47: SIBULAN B Unit 1 online at 0949H (from shutdown affected by DLPC line activities, outside management control). [WEBSMS] | CMIN
3/3/2024 10:42:34 AM | Mindanao Grid-03/03/2024 10:47: TUDAYA 2 Unit 1 online at 0933H (from shutdown affected by DLPC line activities, outside management control). [WEBSMS] | CMIN
3/3/2024 10:41:13 AM | Mindanao Grid-03/03/2024 10:45: SIBULAN B Unit 2 online at 0928H (from shutdown affected by DLPC line activities, outside management control). [WEBSMS] | CMIN
3/3/2024 10:40:32 AM | Mindanao Grid-03/03/2024 10:45: TUDAYA 1 Unit 1 online at 0924H (from shutdown affected by DLPC line activities, outside management control). [WEBSMS] | CMIN
3/3/2024 10:39:44 AM | Mindanao Grid-03/03/2024 10:44: SIBULAN A Unit 1 online at 0911H (from shutdown affected by DLPC line activities, outside management control). [WEBSMS] | CMIN
3/3/2024 10:34:31 AM | Mindanao Grid-03/03/2024 10:39: (Correction) STEAG Unit 2 emergency shutdown at 1030H due to re-heater tube leak (Unplanned Outage). Gradual unloading implemented. [WEBSMS] | CMIN
3/3/2024 10:32:51 AM | Mindanao Grid-03/03/2024 10:37: STEAG Unit 1 emergency shutdown at 1030H due to re-heater tube leak. Implemented gradual unloading. [WEBSMS] | CMIN
3/3/2024 10:31:21 AM | Visayas Grid-03/03/2024 10:31: San Lorenzo Wind cut-in at 0947H. (Unplanned Outage) [WEBSMS] | CVIS
3/3/2024 10:04:53 AM | Mindanao Grid-03/03/2024 10:09: Kibawe-Sultan Kudarat 138kV L deenergized at 0638H (Planned Outage/Non-GOMP). [WEBSMS] | CMIN
3/3/2024 8:51:58 AM | Mindanao Grid-03/03/2024 08:56: Balo-i-Agus2 138kV L2 de-energized at 0848H. Planned Outage/GOMP. [WEBSMS] | CMIN
3/3/2024 8:51:30 AM | Visayas Grid-03/03/2024 08:51: San Lorenzo Wind tripped at 0612H. (Unplanned Outage) [WEBSMS] | CVIS
3/3/2024 8:18:50 AM | Luzon Grid-03/03/2024 08:19: San Jose SS 300MVA T01 de-energized at 0817H (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 7:51:42 AM | Mindanao Grid-03/03/2024 07:56: Kibawe-Tacurong 138kVL de-energized at 0749H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
3/3/2024 7:21:53 AM | Mindanao Grid-03/03/2024 07:26: Maco SS 138kV 100MVA Power Transformer No.2 de-energized at 0715H. Planned Outage/GOMP. [WEBSMS] | CMIN
3/3/2024 7:08:29 AM | Mindanao Grid-03/03/2024 07:13: LAMSAN Biomas online at 0702H (Planned Outage) [WEBSMS] | CMIN
3/3/2024 6:55:13 AM | Mindanao Grid-03/03/2024 06:59: Updated: Manolo Fortich SS 138kV 50MVA Power Transformer No.1 de-energized at 0538H. Planned Outage/GOMP. [WEBSMS] | CMIN
3/3/2024 6:48:24 AM | Mindanao Grid-03/03/2024 06:53: Kibawe-Sultan Kudarat (SKU) 138kVL de-energized at 0638H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
3/3/2024 6:43:37 AM | Luzon Grid-03/03/2024 06:43: Tayabas-San Jose 500kV Line 2 de-energized at 0643H (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 6:41:46 AM | Luzon Grid-03/03/2024 06:41: Tayabas-San Jose 500kV Line 1 de-energized at 0641H (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 6:39:49 AM | Luzon Grid-03/03/2024 06:39: Hermosa-Balsik 230kV Line 2 de-energized at 0639H (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 6:14:28 AM | Mindanao Grid-03/03/2024 06:19: LAMSAN Biomass shutdown at 0600H (Planned Outage) [WEBSMS] | CMIN
3/3/2024 5:49:58 AM | Visayas Grid-03/03/2024 05:50: Cebu SS 138KV Bus 2 energized at 0546H. (Planned Outage) [WEBSMS] | CVIS
3/3/2024 5:46:50 AM | Mindanao Grid-03/03/2024 05:51: Manolo Fortich SS 138kV/50MVA Power Transformer #1 de-energized/shutdown at 0538H (Planned Outage) [WEBSMS] | CMIN
3/3/2024 5:39:28 AM | [NSO Update] Luzon Grid-03/03/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12136MW, PK=8519MW, RR=301MW, NetOpMargin: AM=3315, PM=2772, EVE=1517 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: CALACA 2 @180MW, MASINLOC 1 @280MW, MASINLOC 3 @310MW [WEBSMS] | CLUZ
3/3/2024 5:35:51 AM | Luzon Grid-03/03/2024 05:36: San Jose SS 750MVA T05 restored at 0535H (Unplanned Outage) [WEBSMS] | CLUZ
3/3/2024 5:35:11 AM | [NSO Update] Mindanao Grid-03/03/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3343MW, PK=1717MW, RR=75MW, NetOpMargin: AM=1551, PM=1332, EVE=1114 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
3/3/2024 5:34:16 AM | Visayas Grid-03/03/2024 05:34: Cebu-Mandaue 138KV line 1 energized at 0534H. (Planned Outage) [WEBSMS] | CVIS
3/3/2024 5:31:30 AM | [NSO Update] Visayas Grid-03/03/2024 05:31: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2723MW, PK=1668MW, RR=87MW, NetOpMargin: AM=968, PM=886, EVE=667 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @319MW, PGPP1 @76MW [WEBSMS] | CVIS
3/3/2024 5:27:47 AM | Luzon Grid-03/03/2024 05:27: San Jose-Balsik 500kV Line restored at 0527H (Unplanned Outage) [WEBSMS] | CLUZ
3/3/2024 4:58:57 AM | Luzon Grid-03/03/2024 04:59: Ilijan GT2-2 shutdown at 0457H (Unplanned Outage) [WEBSMS] | CLUZ
3/3/2024 4:49:01 AM | Luzon Grid-03/03/2024 04:49: Ilijan ST2 shutdown at 0448H (Unplanned Outage) [WEBSMS] | CLUZ
3/3/2024 4:48:07 AM | Luzon Grid-03/03/2024 04:48: Ilijan GT2-1 shutdown at 0446H (Unplanned Outage) [WEBSMS] | CLUZ
3/3/2024 4:36:52 AM | [NSO Update] Mindanao Grid-03/03/2024 04:41: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
3/3/2024 4:36:36 AM | [NSO Update] Luzon Grid-03/03/2024 04:36: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/3/2024 4:36:32 AM | [NSO Update] Visayas Grid-03/03/2024 04:36: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
3/3/2024 4:11:42 AM | Luzon Grid-03/03/2024 04:11: Taytay (Dolores) - Masinag 115 kV Line (CO) restored at 0411H (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 2:15:24 AM | Luzon Grid-03/03/2024 02:15: Binan-San Pedro 115kV Line restored at 0214H (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 1:12:43 AM | Mindanao Grid-03/03/2024 01:17: Tudaya 2 HEP Unit 2 with 2.638MW load shutdown at 0005H, due to insufficient water supply. OMC. [WEBSMS] | CMIN
3/3/2024 1:11:13 AM | Mindanao Grid-03/03/2024 01:15: SIBULAN B HEP Unit 2 with 8.49MW load shutdown at 0012H, affected by the Planned outage of DLPC owned and maintained 69kV line. OMC [WEBSMS] | CMIN
3/3/2024 1:10:08 AM | Mindanao Grid-03/03/2024 01:14: SIBULAN B HEP Unit 1 with 7.03MW load shutdown at 0012H, affected by the Planned outage of DLPC owned and maintained 69kV line. OMC [WEBSMS] | CMIN
3/3/2024 1:09:05 AM | Mindanao Grid-03/03/2024 01:13: SIBULAN A HEP Unit 1 with 7.7MW load shutdown at 0010H, affected by the Planned outage of DLPC owned and maintained 69kV line. OMC [WEBSMS] | CMIN
3/3/2024 1:07:46 AM | Mindanao Grid-03/03/2024 01:12: Tudaya 1 HEP Unit 1 with 4.45MW load shutdown at 0002H, affected by the Planned outage of DLPC owned and maintained 69kV line. OMC [WEBSMS] | CMIN
3/3/2024 12:38:23 AM | Visayas Grid-03/03/2024 00:38: Cebu-Mandaue 138KV line 1 de-energized at 0035H. (Planned Outage) [WEBSMS] | CVIS
3/3/2024 12:18:00 AM | Luzon Grid-03/03/2024 00:18: Taytay (Dolores) - Masinag 115 kV Line (CO) de-energized at 0015H. (Planned Outage) [WEBSMS] | CLUZ
3/3/2024 12:13:18 AM | Visayas Grid-03/03/2024 00:13: Cebu SS 138KV Bus 2 de-energized at 0010H. (Planned Outage) [WEBSMS] | CVIS
3/2/2024 11:29:55 PM | Mindanao Grid-03/02/2024 23:34: Maco SS 138kV/100MVA Power Transformer No. 1 energized at 2324H (Planned Outage) [WEBSMS] | CMIN
3/2/2024 11:08:35 PM | Luzon Grid-03/02/2024 23:08: Binan-San Pedro 115kV Line de-energized at 2308H (Planned Outage) [WEBSMS] | CLUZ
3/2/2024 10:55:03 PM | Luzon Grid-03/02/2024 22:55: Concepcion-TERASU Solar PP 69kV Line restored at 2253H. (Planned Outage) [WEBSMS] | CLUZ
3/2/2024 10:26:01 PM | Luzon Grid-03/02/2024 22:26: Kalayaan Unit 1 tripped as pump at 2218H, highest frequency reached 60.59Hz. (Unplanned Outage) [WEBSMS] | CLUZ
3/2/2024 8:48:15 PM | Mindanao Grid-03/02/2024 20:52: SPC Mati shutdown at 2005H (Unplanned Outage). [WEBSMS] | CMIN
3/2/2024 7:35:54 PM | Luzon Grid-03/02/2024 19:36: Sta. Rita 40 shutdown at 1935H (Unplanned Outage) [WEBSMS] | CLUZ
3/2/2024 5:50:32 PM | [NSO Update] Mindanao Grid-03/02/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3278MW, PK=2199MW, RR=72MW, NetOpMargin: EVE=1007 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
3/2/2024 5:49:29 PM | [NSO Update] Visayas Grid-03/02/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2565MW, PK=2045MW, RR=86MW, NetOpMargin: EVE=433 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 306MW, PGPP1 @ 76MW [WEBSMS] | CVIS
3/2/2024 5:47:57 PM | [NSO Update] Luzon Grid-03/02/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11952MW, PK=9731MW, RR=380MW, NetOpMargin: EVE=1841 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Calaca 2 @ 180MW, Masinloc 1 @ 210MW, Masinloc 3 @ 300MW [WEBSMS] | CLUZ
3/2/2024 5:34:58 PM | [NSO Update] Luzon Grid-03/02/2024 17:35: Naga-Ormoc 350kV HVDC (Luzon-Visayas) de-blocked at 1718H with power going to Luzon (Planned Outage) [WEBSMS] | CLUZ
3/2/2024 5:34:08 PM | [NSO Update] Visayas Grid-03/02/2024 17:34: Naga-Ormoc 350kV HVDC (Luzon-Visayas) de-blocked at 1718H with power going to Luzon (Planned Outage) [WEBSMS] | CVIS
3/2/2024 4:18:33 PM | Luzon Grid-03/02/2024 16:18: Hermosa-BCCPP 230kV Line 2 restored at 1617H (Planned Outage) [WEBSMS] | CLUZ
3/2/2024 3:35:51 PM | Mindanao Grid-03/02/2024 15:40: Bunawan - Don Ramon 138kV Line 2 (DLPCs owned and maintained 138kV Line) energized/restored at 1529H from emergency shutdown. (Unplanned Outage) [WEBSMS] | CMIN
3/2/2024 1:14:29 PM | [NSO Update] Visayas Grid-03/02/2024 13:14: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2582MW, PK=1945MW, RR=89MW, NetOpMargin: PM=548, EVE=328 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @306MW, PGPP1 @76MW [WEBSMS] | CVIS
3/2/2024 1:09:52 PM | [NSO Update] Mindanao Grid-03/02/2024 13:14: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3324MW, PK=2084MW, RR=74MW, NetOpMargin: PM=1166, EVE=1046 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
3/2/2024 1:03:59 PM | [NSO Update] Luzon Grid-03/02/2024 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12568MW, PK=9950MW, RR=399MW, NetOpMargin: PM=2219, EVE=1733 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Derated Plant: CLC2 @180MW, MSLC1 @210MW, MSLC3 @300MW [WEBSMS] | CLUZ
3/2/2024 12:46:58 PM | Mindanao Grid-03/02/2024 12:51: Balo-i SS 230kV 300MVA Power Transformer #1 re-energized and loop at 1244H (Unplanned Outage) [WEBSMS] | CMIN
3/2/2024 12:32:49 PM | Mindanao Grid-03/02/2024 12:37: Bunawan - Don Ramon 138kV Line2 de-energized at 1226H (Unplanned Outage) [WEBSMS] | CMIN
3/2/2024 11:58:51 AM | Mindanao Grid-03/02/2024 12:03: Davao - Bunawan 138kV Line 2 de-energized at 0808H (Planned Outage) [WEBSMS] | CMIN
3/2/2024 11:02:04 AM | Mindanao Grid-03/02/2024 11:06: SPC Mati online at 1000H. MO dispatched. [WEBSMS] | CMIN
3/2/2024 8:58:25 AM | Visayas Grid-03/02/2024 08:58: PEDC U3 online at 0855H (Unplanned Outage) [WEBSMS] | CVIS
3/2/2024 8:54:52 AM | Mindanao Grid-03/02/2024 08:59: AGUS2 HEP Unit 2 online at 0852H. (Unplanned Outage) [WEBSMS] | CMIN
3/2/2024 8:21:47 AM | Mindanao Grid-03/02/2024 08:26: Agus 2 Unit 2 with 37MW load tripped at 0757H. Cause: To be determined. (Unplanned Outage) [WEBSMS] | CMIN
3/2/2024 8:17:37 AM | Mindanao Grid-03/02/2024 08:22: Balo-i SS 230kV Power Transformer #1 tripped at 0800H (Unplanned Outage) [WEBSMS] | CMIN
3/2/2024 8:02:53 AM | Luzon Grid-03/02/2024 08:03: San Jose-Balsik 500kV Line de-energized at 0801H (Planned Outage) [WEBSMS] | CLUZ
3/2/2024 7:53:40 AM | Luzon Grid-03/02/2024 07:53: San Jose SS 750MVA T05 de-energized at 0753H (Planned Outage) [WEBSMS] | CLUZ
3/2/2024 7:26:46 AM | Luzon Grid-03/02/2024 07:26: Calaca-Sta. Rita 230kV Line 2 de-energized at 0725H (Planned Outage) [WEBSMS] | CLUZ
3/2/2024 7:18:49 AM | Luzon Grid-03/02/2024 07:18: Hermosa-BCCPP 230kV Line 2 de-energized at 0718H (Planned Outage) [WEBSMS] | CLUZ
3/2/2024 6:52:17 AM | Luzon Grid-03/02/2024 06:52: Calaca-Binan 230kV Line restored at 0650H (Planned Outage) [WEBSMS] | CLUZ
3/2/2024 6:42:35 AM | Mindanao Grid-03/02/2024 06:47: Maco SS Power Transformer #1 shutdown at 0635H (Planned Outage) [WEBSMS] | CMIN
3/2/2024 6:33:36 AM | Mindanao Grid-03/02/2024 06:38: Talomo 1 Unit 1 online at 0548H. (Unplanned Outage) [WEBSMS] | CMIN
3/2/2024 6:32:40 AM | Mindanao Grid-03/02/2024 06:37: Talomo 1 Unit 2 online at 0514H. (Unplanned Outage) [WEBSMS] | CMIN
3/2/2024 6:24:54 AM | Luzon Grid-03/02/2024 06:25: Concepcion-TERASU Solar PP 69kV Line de-energized at 0622H (Planned Outage) [WEBSMS] | CLUZ
3/2/2024 6:10:37 AM | [NSO Update] Luzon Grid-03/02/2024 06:10: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12725MW, PK=9851MW, RR=391MW, NetOpMargin: AM=2483, PM=1783, EVE=1562 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @100MW, MSLC3 @305MW [WEBSMS] | CLUZ
3/2/2024 6:03:53 AM | [NSO Update] Mindanao Grid-03/02/2024 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3348MW, PK=2036MW, RR=72MW, NetOpMargin: AM=1240, PM=1142, EVE=1057 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
3/2/2024 5:47:20 AM | [NSO Update] Visayas Grid-03/02/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2392MW, PK=1898MW, RR=87MW, NetOpMargin: AM=407, PM=360, EVE=407 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @306MW, PGPP1 @76MW [WEBSMS] | CVIS
3/2/2024 5:40:57 AM | Mindanao Grid-03/02/2024 05:45: ASIGA Hydro with 8MW load tripped at 0518H. Indication: Restricted Earth Fault. Frequency dipped at 59.85Hz. (Unplanned Outage) [WEBSMS] | CMIN
3/2/2024 5:38:20 AM | Mindanao Grid-03/02/2024 05:42: TALOMO 1 Unit 1 (load=0.5MW) & Unit 2 (load=0.5MW) isolated at 0435H caused by tripping of DLPC-owned Calinan-Malagos line. [WEBSMS] | CMIN
3/2/2024 5:19:24 AM | Visayas Grid-03/02/2024 05:19: URC on islanding operation at 0516H. (Unplanned Outage) [WEBSMS] | CVIS
3/2/2024 5:10:33 AM | Visayas Grid-03/02/2024 05:10: URC synchronized at 0508H. (Unplanned Outage) [WEBSMS] | CVIS
3/2/2024 5:04:36 AM | Luzon Grid-03/02/2024 05:04: Calaca-Binan 230kV Line de-energized at 0504H (Planned Outage) [WEBSMS] | CLUZ
3/2/2024 4:55:30 AM | Visayas Grid-03/02/2024 04:55: URC on islanding operation at 0436H. (Unplanned Outage) [WEBSMS] | CVIS
3/2/2024 4:17:47 AM | [NSO Update] Mindanao Grid-03/02/2024 04:22: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
3/2/2024 4:17:23 AM | [NSO Update] Visayas Grid-03/02/2024 04:17: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
3/2/2024 4:16:59 AM | [NSO Update] Luzon Grid-03/02/2024 04:17: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/2/2024 4:03:48 AM | Luzon Grid-03/02/2024 04:03: LPI (SCPC) 4 shutdown at 0401H (Planned Outage) [WEBSMS] | CLUZ
3/2/2024 2:49:34 AM | Luzon Grid-03/02/2024 02:49: Masinloc 1 online at 0247H (Unplanned Outage). [WEBSMS] | CLUZ
3/2/2024 1:32:30 AM | Mindanao Grid-03/02/2024 01:37: Bunawan-DRA 138kV L2 (CO) energized at 0117H. From Unplanned Outage. (Requested by DLPC Management). [WEBSMS] | CMIN
3/2/2024 1:01:30 AM | Luzon Grid-03/02/2024 01:01: Ilijan GT2-1 online at 0037H (Unplanned Outage) [WEBSMS] | CLUZ
3/2/2024 12:45:45 AM | [NSO Update] Visayas Grid-03/02/2024 00:45: SO-initiated Market Intervention for Visayas has been lifted today at 0026H. Market operations will resume starting interval 0035H. [WEBSMS] | CVIS
3/1/2024 11:54:04 PM | Visayas Grid-03/01/2024 23:54: KSPC U1 cut in at 2345H. (Unplanned Outage) [WEBSMS] | CVIS
3/1/2024 11:29:49 PM | Visayas Grid-03/01/2024 23:29: PEDC U1 cut in at 2322H. (Unplanned Outage) [WEBSMS] | CVIS
3/1/2024 11:18:42 PM | Luzon Grid-03/01/2024 23:18: Ilijan ST2 online at 2317H (Unplanned Outage) [WEBSMS] | CLUZ
3/1/2024 10:39:56 PM | Luzon Grid-03/01/2024 22:40: Hermosa-BCCPP 230kV Line 3 restored at 2239H (Planned Outage) [WEBSMS] | CLUZ
3/1/2024 10:09:40 PM | Luzon Grid-03/01/2024 22:09: Ilijan GT2-2 online at 2206H (Unplanned Outage) [WEBSMS] | CLUZ
3/1/2024 10:08:36 PM | [NSO Update] Visayas Grid-03/01/2024 22:08: The Yellow Alert Notice issued for the Visayas Grid today, March 1, 2024, has been lifted effective 2201H. [WEBSMS] | CVIS
3/1/2024 9:56:35 PM | Visayas Grid-03/01/2024 21:56: PEDC U2 cut-in 2153H initial load 8.2MW(Unplanned Outage) [WEBSMS] | CVIS
3/1/2024 8:49:20 PM | [NSO Update] Visayas Grid-03/01/2024 20:49: Yellow Alert Notice issued for Visayas today, starting 1900H is extended up to 2200H Forced Outage:SCBP@19.5MW,HPC1@2MW,VMC1@2.5MW,VMC 2@21.5MW,SCBI@7.4MW, NBP@25MW,PCPC@135MW,KSPC1@103MW,PEDC1@83.7MW,PEDC2 @83.7MW,PEDC@150MW,PDPP3 @50MW,PDPP1@15MW,NWind @36MW,PGPP1@112.5MW,FFHC @21MW,PB101@32MW,TIMBA@18.9MW,PWIND @36MW,VSGA@8MW (Total: 962.7MW).De-rated: LeyteA@297MW,CEDC 3@75MW (Total: 200.1MW) [WEBSMS] | CVIS
3/1/2024 8:20:36 PM | Luzon Grid-03/01/2024 20:20: Clark 230kV Bus 4 energized at 2011H. Ongoing commissioning of Main 2 protection (Planned Outage) [WEBSMS] | CLUZ
3/1/2024 7:43:22 PM | Mindanao Grid-03/01/2024 19:47: WMPC DG10 shutdown at 1941H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
3/1/2024 7:34:31 PM | [NSO Update] Visayas Grid-03/01/2024 19:34: Yellow Alert Notice issued for Visayas today, 01-Mar 2024, for intervals 1900H-2100H.Force Outage:SCBP @19.5MW, HPC 1 @2MW, VMC 1 @2.5MW, VMC 2 @21.5MW, SCBI @7.4MW, SNBP @25MW, PCPC @135MW, KSPC 1 @103MW, PEDC 1 @83.7MW, PEDC 2 @83.7MW, PEDC 3 @150MW, PDPP3 @50MW, PDPP1 @15MW, Nabas Wind @36MW (Total: 734.3MW). De-rated: Leyte A @297MW, PGPP1 @76MW, CEDC U3 @75MW (Total: 234.7MW) [WEBSMS] | CVIS
3/1/2024 7:10:33 PM | Luzon Grid-03/01/2024 19:10: San Jose-Angat 115kV line 3 energized at 1908H at San Jose side (Unplanned Outage) [WEBSMS] | CLUZ
3/1/2024 7:07:29 PM | [NSO Update] Visayas Grid-03/01/2024 19:07: SO initiated Market Intervention for Visayas is issued today at starting interval 1900H due to partial blackout at Panay sub-grid [WEBSMS] | CVIS
3/1/2024 7:04:31 PM | Visayas Grid-03/01/2024 19:04: Total plant shutdown of PEDC at 1859H. [WEBSMS] | CVIS
3/1/2024 6:51:44 PM | Luzon Grid-03/01/2024 18:51: Masinloc 1 with 279MW load tripped at 1846H. Lowest Frequency is 59.42Hz (Unplanned Outage) [WEBSMS] | CLUZ
3/1/2024 6:29:19 PM | Luzon Grid-03/01/2024 18:29: San Jose-San Rafael 230kV Line restored at 1829H (Unplanned Outage) [WEBSMS] | CLUZ
3/1/2024 6:01:18 PM | Mindanao Grid-03/01/2024 18:05: SIBULAN A Unit 1 online at 1744H (Planned Outage) [WEBSMS] | CMIN
3/1/2024 5:46:20 PM | [NSO Update] Mindanao Grid-03/01/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3278MW, PK=2163MW, RR=72MW, NetOpMargin: EVE=1043 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
3/1/2024 5:42:37 PM | [NSO Update] Luzon Grid-03/01/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11751MW, PK=10281MW, RR=380MW, NetOpMargin: EVE=1090 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CALACA 2 @180MW, MASINLOC 1 @330MW, MASINLOC 3 @325MW [WEBSMS] | CLUZ
3/1/2024 5:40:56 PM | [NSO Update] Visayas Grid-03/01/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2614MW, PK=2112MW, RR=87MW, NetOpMargin: EVE=416 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @297MW, PGPP1 @76MW [WEBSMS] | CVIS
3/1/2024 3:31:38 PM | Luzon Grid-03/01/2024 15:31: San Jose-San Rafael 230kV Line tripped at 1529H (Unplanned Outage) [WEBSMS] | CLUZ
3/1/2024 3:19:36 PM | Luzon Grid-03/01/2024 15:19: Ilijan Block B with 600MW load tripped at 1511H. Lowest Frequency is 59.075Hz. No ALD (Unplanned Outage) [WEBSMS] | CLUZ
3/1/2024 2:17:24 PM | Visayas Grid-03/01/2024 14:17: KSPC unit #1 auto-tripped at 1414H load 103MW (Unplanned Outage) [WEBSMS] | CVIS
3/1/2024 1:59:43 PM | Luzon Grid-03/01/2024 13:59: Bolo-Cayanga Solar 230kV line 2 loop at 1356H (Unplanned Outage) [WEBSMS] | CLUZ
3/1/2024 12:56:39 PM | [NSO Update] Mindanao Grid-03/01/2024 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3325MW, PK=2185MW, RR=77MW, NetOpMargin: PM=1063, EVE=1083 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
3/1/2024 12:55:35 PM | [NSO Update] Visayas Grid-03/01/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2982MW, PK=2185MW, RR=89MW, NetOpMargin: PM=709, EVE=503 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @305MW, PGPP1 @76MW [WEBSMS] | CVIS
3/1/2024 12:54:19 PM | [NSO Update] Luzon Grid-03/01/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13172MW, PK=10653MW, RR=399MW, NetOpMargin: PM=2120, EVE=1577 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @330MW, MSLC3 @320MW, SCPC 2 @75MW [WEBSMS] | CLUZ
3/1/2024 10:31:18 AM | Mindanao Grid-03/01/2024 10:35: WMPC DG10 online at 1029H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
3/1/2024 9:16:02 AM | Luzon Grid-03/01/2024 09:16: Clark SS 230kV Bus 4 de-energized at 0913H (Planned Outage) [WEBSMS] | CLUZ
3/1/2024 8:15:32 AM | Luzon Grid-03/01/2024 08:15: Hermosa-BCCPP 230kV Line 3 de-energized at 0815H (Planned Outage) [WEBSMS] | CLUZ
3/1/2024 8:13:46 AM | Mindanao Grid-03/01/2024 08:18: Kidapawan SS 50MVA Power Transformer No. 2 de-energized at 0807H. (Planned Outage) [WEBSMS] | CMIN
3/1/2024 8:09:41 AM | Mindanao Grid-03/01/2024 08:14: ASIGA Hydro online at 0800H (Unplanned Outage) [WEBSMS] | CMIN
3/1/2024 7:47:05 AM | Mindanao Grid-03/01/2024 07:51: ASIGA Hydro with 8.1MW load tripped at 0735H. Indication: Restricted Earth Fault. Frequency dipped at 59.8Hz. (Unplanned Outage) [WEBSMS] | CMIN
3/1/2024 5:58:41 AM | [NSO Update] Mindanao Grid-03/01/2024 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3341MW, PK=2098MW, RR=75MW, NetOpMargin: AM=1168, PM=1045, EVE=1078 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @35.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
3/1/2024 5:56:53 AM | [NSO Update] Visayas Grid-03/01/2024 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2972MW, PK=2119MW, RR=87MW, NetOpMargin: AM=766, PM=625, EVE=592 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @305MW, PGPP1 @76MW [WEBSMS] | CVIS
3/1/2024 5:54:31 AM | [NSO Update] Luzon Grid-03/01/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13463MW, PK=10405MW, RR=391MW, NetOpMargin: AM=2667, PM=2180, EVE=1638 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @330MW, MSLC3 @320MW, SCPC 2 @75MW [WEBSMS] | CLUZ
3/1/2024 4:30:25 AM | Visayas Grid-03/01/2024 04:30: PEDC unit 2 cut-in to the system at 2343H, initial load 8.0MW. [WEBSMS] | CVIS
3/1/2024 4:14:41 AM | [NSO Update] Mindanao Grid-03/01/2024 04:19: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
3/1/2024 4:14:06 AM | [NSO Update] Visayas Grid-03/01/2024 04:14: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
3/1/2024 4:13:37 AM | [NSO Update] Luzon Grid-03/01/2024 04:13: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/1/2024 1:00:19 AM | Mindanao Grid-03/01/2024 01:04: Agusan Power Corporation online at 0053H from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
3/1/2024 12:22:00 AM | Mindanao Grid-03/01/2024 00:26: Lake Mainit HEP with 19.5MW load on emergency shutdown at 0014H. Cause: Load hunting. (Unplanned Outage) [WEBSMS] | CMIN
3/1/2024 12:05:24 AM | Mindanao Grid-03/01/2024 00:09: FDC unit 2 with 45MW tripped at 2348H. Lowest frequency dip at 59.622HZ, no ALD. Indication: Turbine stress trip. The generator unit is supposed ramp down and for PMS shutdown at 0001. (Unplanned Outage) [WEBSMS] | CMIN
2/29/2024 11:21:37 PM | Mindanao Grid-02/29/2024 23:26: Update: Libertad Power with 6MW tripped at 2201H and restored at 2207H. Indication: Rate of Change of Frequency Protection, Trip [WEBSMS] | CMIN
2/29/2024 10:57:26 PM | Mindanao Grid-02/29/2024 23:01: ASIGA HEP online at 2246H (Unplanned Outage) [WEBSMS] | CMIN
2/29/2024 10:56:47 PM | Mindanao Grid-02/29/2024 23:01: Lake Mainit HEP online at 2245H. (Unplanned Outage) [WEBSMS] | CMIN
2/29/2024 10:41:04 PM | Mindanao Grid-02/29/2024 22:45: Libertad Power with 6MW tripped at 2201H and restored at 2207H. Indication: for investigation. (Unplanned Outage) [WEBSMS] | CMIN
2/29/2024 10:00:33 PM | Mindanao Grid-02/29/2024 22:05: ASIGA HEP with 8MW load and Lake Mainit HEP with 19.5MW load Tripped/Isolated at 2150H. Affected by the tripping of Butuan-Santiago 69kV Line. Unplanned Outage [WEBSMS] | CMIN
2/29/2024 9:01:20 PM | Mindanao Grid-02/29/2024 21:05: Siguil HEP shutdown at 2048H. Test & Commissioning. [WEBSMS] | CMIN
2/29/2024 8:23:02 PM | Mindanao Grid-02/29/2024 20:27: WMPC DG10 shutdown at 2022H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/29/2024 8:18:17 PM | Mindanao Grid-02/29/2024 20:22: Siguil HEP online at 2014H. Test & Commissioning. [WEBSMS] | CMIN
2/29/2024 5:51:48 PM | [NSO Update] Mindanao Grid-02/29/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3399MW, PK=2180MW, RR=72MW, NetOpMargin: EVE=1146 Highest Unit O/L: GNPK 2,3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
2/29/2024 5:49:25 PM | [NSO Update] Visayas Grid-02/29/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2604MW, PK=2105MW, RR=85MW, NetOpMargin: EVE=413 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @305MW, PGPP1 @76MW, PEDC U3 @135MW [WEBSMS] | CVIS
2/29/2024 5:46:18 PM | [NSO Update] Luzon Grid-02/29/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12305MW, PK=10222MW, RR=417MW, NetOpMargin: EVE=1666 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: CALACA 2 @180MW, MASINLOC 1 @325MW [WEBSMS] | CLUZ
2/29/2024 3:20:22 PM | Luzon Grid-02/29/2024 15:20: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1518H (Planned Outage) [WEBSMS] | CLUZ
2/29/2024 12:45:09 PM | [NSO Update] Mindanao Grid-02/29/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3444MW, PK=2197MW, RR=74MW, NetOpMargin: PM=1173, EVE=1186 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
2/29/2024 12:41:08 PM | [NSO Update] Luzon Grid-02/29/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13480MW, PK=10666MW, RR=428MW, NetOpMargin: PM=2386, EVE=1747 Highest Unit O/L: GNPD 1@668MW Derated Plant: CALACA 2 @180MW [WEBSMS] | CLUZ
2/29/2024 12:40:57 PM | [NSO Update] Visayas Grid-02/29/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2834MW, PK=2146MW, RR=86MW, NetOpMargin: PM=601, EVE=441 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW, PEDC U3 @135MW [WEBSMS] | CVIS
2/29/2024 10:25:31 AM | Mindanao Grid-02/29/2024 10:30: WMPC DG10 Online at 1022H. RPS-System Voltage Requirement [WEBSMS] | CMIN
2/29/2024 9:21:02 AM | Luzon Grid-02/29/2024 09:21: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0920H. (Planned Outage) [WEBSMS] | CLUZ
2/29/2024 5:51:27 AM | [NSO Update] Luzon Grid-02/29/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13585MW, PK=10235MW, RR=422MW, NetOpMargin: AM=2929, PM=2186, EVE=1560 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CALACA 2 @180MW [WEBSMS] | CLUZ
2/29/2024 5:32:22 AM | [NSO Update] Mindanao Grid-02/29/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3460MW, PK=2058MW, RR=72MW, NetOpMargin: AM=1330, PM=1124, EVE=1104 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @109MW [WEBSMS] | CMIN
2/29/2024 5:28:52 AM | [NSO Update] Visayas Grid-02/29/2024 05:28: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2914MW, PK=2158MW, RR=84MW, NetOpMargin: AM=672, PM=467, EVE=414 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW, PEDC U3 @135MW [WEBSMS] | CVIS
2/29/2024 4:14:45 AM | [NSO Update] Luzon Grid-02/29/2024 04:14: Weather Update: Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
2/29/2024 4:13:32 AM | [NSO Update] Mindanao Grid-02/29/2024 04:18: Weather Update: Northeast Monsoon affecting Luzon. [WEBSMS] | CMIN
2/29/2024 4:12:11 AM | [NSO Update] Visayas Grid-02/29/2024 04:12: Weather Update: Northeast Monsoon affecting Luzon. [WEBSMS] | CVIS
2/29/2024 1:09:10 AM | Luzon Grid-02/29/2024 01:09: Pagbilao 1 emergency shutdown at 0104H due to boiler tube leak (Unplanned Outage) [WEBSMS] | CLUZ
2/29/2024 12:24:52 AM | Visayas Grid-02/29/2024 00:24: HPC U2 synchronized at 0010H. (Unplanned Outage) [WEBSMS] | CVIS
2/29/2024 12:22:49 AM | Visayas Grid-02/29/2024 00:22: HPC U2 isolated from the grid at 0007H. (Unplanned Outage) [WEBSMS] | CVIS
2/29/2024 12:20:53 AM | Visayas Grid-02/29/2024 00:20: NNBP U1 cut in at 2041H. (Unplanned Outage) [WEBSMS] | CVIS
2/28/2024 7:53:20 PM | Mindanao Grid-02/28/2024 19:57: WMPC DG10 shutdown at 1943H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/28/2024 6:01:08 PM | [NSO Update] Luzon Grid-02/28/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12629MW, PK=10142MW, RR=410MW, NetOpMargin: EVE=2077 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CALACA 2 @180MW, MASINLOC 1 @330MW, MASINLOC 2 @280MW [WEBSMS] | CLUZ
2/28/2024 5:54:52 PM | [NSO Update] Mindanao Grid-02/28/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3453MW, PK=2105MW, RR=72MW, NetOpMargin: EVE=1276 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @169MW [WEBSMS] | CMIN
2/28/2024 5:51:30 PM | [NSO Update] Visayas Grid-02/28/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2658MW, PK=2142MW, RR=85MW, NetOpMargin: EVE=431 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW, PEDC U3 @135MW [WEBSMS] | CVIS
2/28/2024 4:40:47 PM | Luzon Grid-02/28/2024 16:40: Naga 230kV Bus 2 restored at 1640H (Unplanned Outage) [WEBSMS] | CLUZ
2/28/2024 4:19:05 PM | Luzon Grid-02/28/2024 16:19: Naga 230kV Bus 2 emergency shutdown at 1616H due to lockout of Shunt Reactor 3 breaker 8CB08(8XR03NAG) Phase B. (Unplanned Outage) [WEBSMS] | CLUZ
2/28/2024 12:38:03 PM | [NSO Update] Mindanao Grid-02/28/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3500MW, PK=2181MW, RR=75MW, NetOpMargin: PM=1244, EVE=1244 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @169MW [WEBSMS] | CMIN
2/28/2024 12:36:18 PM | [NSO Update] Visayas Grid-02/28/2024 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2173MW, RR=86MW, NetOpMargin: PM=631, EVE=432 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @300MW, PGPP1 @76MW, PEDC U3 @135MW [WEBSMS] | CVIS
2/28/2024 12:33:20 PM | [NSO Update] Luzon Grid-02/28/2024 12:33: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13866MW, PK=10677MW, RR=427MW, NetOpMargin: PM=2762, EVE=1923 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CALACA 2 @180MW, MASINLOC 1 @330MW, MASINLOC 2 @280MW [WEBSMS] | CLUZ
2/28/2024 11:54:03 AM | Luzon Grid-02/28/2024 11:54: For info: Sta Rita and San Lorenzo 230kV Busses were looped at 1153H. [WEBSMS] | CLUZ
2/28/2024 11:52:05 AM | Luzon Grid-02/28/2024 11:52: For info: Batangas 300MVA T04 and T05 on split configuration at 1150H for preparation of looping of Sta. Rita and San Lorenzo 230kV Bus. [WEBSMS] | CLUZ
2/28/2024 11:43:00 AM | Luzon Grid-02/28/2024 11:43: San Lorenzo 230kV Bus 1 restored at 1142H (Unplanned Outage) [WEBSMS] | CLUZ
2/28/2024 10:33:08 AM | Mindanao Grid-02/28/2024 10:37: WMPC DG10 Online at 1030H. RPS-System Voltage Requirement [WEBSMS] | CMIN
2/28/2024 8:49:15 AM | Luzon Grid-02/28/2024 08:49: Mauban-QPPL 230kV Line 2 restored at 0847H. (Planned Outage) [WEBSMS] | CLUZ
2/28/2024 6:03:30 AM | [NSO Update] Mindanao Grid-02/28/2024 06:08: Weather Update: Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
2/28/2024 6:03:15 AM | [NSO Update] Visayas Grid-02/28/2024 06:03: Weather Update: Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
2/28/2024 6:02:52 AM | [NSO Update] Luzon Grid-02/28/2024 06:02: Weather Update: Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
2/28/2024 5:47:16 AM | [NSO Update] Mindanao Grid-02/28/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3517MW, PK=2096MW, RR=72MW, NetOpMargin: AM=1349, PM=1289, EVE=1296 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @169MW [WEBSMS] | CMIN
2/28/2024 5:44:04 AM | [NSO Update] Visayas Grid-02/28/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2882MW, PK=2095MW, RR=83MW, NetOpMargin: AM=705, PM=606, EVE=368 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW, PEDC U3 @135MW [WEBSMS] | CVIS
2/28/2024 5:41:26 AM | [NSO Update] Luzon Grid-02/28/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13858MW, PK=10317MW, RR=414MW, NetOpMargin: AM=3127, PM=2425, EVE=1833 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @330MW, MSLC2 @280MW [WEBSMS] | CLUZ
2/28/2024 5:11:16 AM | Luzon Grid-02/28/2024 05:11: San Lorenzo 230kV Bus 1 de-energized at 0510H (Unplanned Outage) [WEBSMS] | CLUZ
2/28/2024 4:17:29 AM | Visayas Grid-02/28/2024 04:17: PEDC unit #2 emergency shutdown @0408H.(Unplanned Outage ) [WEBSMS] | CVIS
2/27/2024 10:39:16 PM | Luzon Grid-02/27/2024 22:39: Hermosa-Balsik 230kV line 1 was restored at 2237H. (Planned Outage) [WEBSMS] | CLUZ
2/27/2024 7:09:31 PM | Mindanao Grid-02/27/2024 19:13: WMPC DG10 shutdown at 1908H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/27/2024 6:02:54 PM | Luzon Grid-02/27/2024 18:02: Bolo-Cayanga Solar 230kV line 2 was looped in Cayanga Solar side at 1800H. (Unplanned Outage) [WEBSMS] | CLUZ
2/27/2024 5:41:41 PM | [NSO Update] Mindanao Grid-02/27/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3375MW, PK=2135MW, RR=72MW, NetOpMargin: EVE=1167 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @120MW [WEBSMS] | CMIN
2/27/2024 5:40:25 PM | [NSO Update] Visayas Grid-02/27/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2688MW, PK=2092MW, RR=83MW, NetOpMargin: EVE=513 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @300MW, PGPP1 @76MW [WEBSMS] | CVIS
2/27/2024 5:38:23 PM | [NSO Update] Luzon Grid-02/27/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12711MW, PK=10021MW, RR=402MW, NetOpMargin: EVE=2288 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @330MW, MSLC2 @280MW [WEBSMS] | CLUZ
2/27/2024 5:18:42 PM | Luzon Grid-02/27/2024 17:18: San Jose-Angat 115kV line 3 was de-energized at 1717H. (Unplanned Outage requested by Angat HEPP) [WEBSMS] | CLUZ
2/27/2024 5:13:11 PM | Luzon Grid-02/27/2024 17:12: Hermosa-Balsik 230kV line 1 was de-energized at 1712H. (Planned Outage) [WEBSMS] | CLUZ
2/27/2024 4:55:20 PM | Luzon Grid-02/27/2024 16:55: San Jose-Tayabas 500kV line 2 was energized from Tayabas Substation side at 1653H. (Planned Outage) [WEBSMS] | CLUZ
2/27/2024 12:58:21 PM | [NSO Update] Luzon Grid-02/27/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13744MW, PK=10565MW, RR=426MW, NetOpMargin: PM=2752, EVE=2094 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Calaca 2 @ 180MW, Masinloc 1 @ 330MW, Masinloc 2 @ 280MW, Masinloc 3 @ 300MW [WEBSMS] | CLUZ
2/27/2024 12:51:58 PM | [NSO Update] Mindanao Grid-02/27/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3410MW, PK=2227MW, RR=74MW, NetOpMargin: PM=1109, EVE=1149 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @120MW [WEBSMS] | CMIN
2/27/2024 12:51:10 PM | [NSO Update] Visayas Grid-02/27/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2751MW, PK=2175MW, RR=84MW, NetOpMargin: PM=492, EVE=406 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 309MW, PGPP1 @ 76MW [WEBSMS] | CVIS
2/27/2024 12:29:53 PM | Visayas Grid-02/27/2024 12:29: PEDC U3 cut-in at 1227H. (Unplanned Outage) [WEBSMS] | CVIS
2/27/2024 10:29:31 AM | Mindanao Grid-02/27/2024 10:33: WMPC DG10 Online at 1023H. RPS-System Voltage Requirement [WEBSMS] | CMIN
2/27/2024 9:10:43 AM | Luzon Grid-02/27/2024 09:10: Lamao-UPSI Lamao BESS 230kV Line 1 (CO) restored at 0907H (Planned Outage) [WEBSMS] | CLUZ
2/27/2024 8:21:10 AM | Visayas Grid-02/27/2024 08:20: PEDC U3 tripped at 0816H. (Unplanned Outage) [WEBSMS] | CVIS
2/27/2024 7:11:28 AM | Luzon Grid-02/27/2024 07:11: Mauban-QPPL 230kV Line 2 de-energized at 0709H (Planned Outage) [WEBSMS] | CLUZ
2/27/2024 6:08:40 AM | Luzon Grid-02/27/2024 06:08: Lamao-UPSI Lamao BESS 230kV Line 1 (CO) de-energized at 0607H (Planned Outage) [WEBSMS] | CLUZ
2/27/2024 5:49:22 AM | [NSO Update] Mindanao Grid-02/27/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3437MW, PK=2167MW, RR=72MW, NetOpMargin: AM=1198, PM=1023, EVE=1094 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @120MW [WEBSMS] | CMIN
2/27/2024 5:46:29 AM | [NSO Update] Visayas Grid-02/27/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2916MW, PK=2119MW, RR=90MW, NetOpMargin: AM=707, PM=677, EVE=464 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW [WEBSMS] | CVIS
2/27/2024 5:42:52 AM | [NSO Update] Luzon Grid-02/27/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13825MW, PK=10358MW, RR=409MW, NetOpMargin: AM=3057, PM=2842, EVE=2279 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @330MW [WEBSMS] | CLUZ
2/27/2024 5:13:51 AM | Luzon Grid-02/27/2024 05:13: San Jose-Tayabas 500kV Line 2 de-energized at 0513H (Planned Outage) [WEBSMS] | CLUZ
2/27/2024 4:30:41 AM | [NSO Update] Luzon Grid-02/27/2024 04:30: Weather Update: Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
2/27/2024 4:24:58 AM | [NSO Update] Mindanao Grid-02/27/2024 04:29: Weather Update: Northeast Monsoon affecting Luzon. [WEBSMS] | CMIN
2/27/2024 4:24:31 AM | [NSO Update] Visayas Grid-02/27/2024 04:24: Weather Update: Northeast Monsoon affecting Luzon. [WEBSMS] | CVIS
2/26/2024 11:40:26 PM | Luzon Grid-02/26/2024 23:40: Kalayan 4 with -161MW load tripped as pump at 2330H. Highest Frequency is 60.51Hz (Unplanned Outage) [WEBSMS] | CLUZ
2/26/2024 8:09:06 PM | Luzon Grid-02/26/2024 20:08: Bolo-Cayanga Solar 230kV line 2(Customer Owned and Maintained) was unlooped from Cayanga side at 2006H. (Unplanned Outage requested by Cayanga Solar PP) [WEBSMS] | CLUZ
2/26/2024 7:50:40 PM | Mindanao Grid-02/26/2024 19:54: WMPC DG10 shutdown at 1943H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/26/2024 5:55:57 PM | [NSO Update] Mindanao Grid-02/26/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3483MW, PK=2195MW, RR=72MW, NetOpMargin: EVE=1216 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @169MW [WEBSMS] | CMIN
2/26/2024 5:50:52 PM | [NSO Update] Visayas Grid-02/26/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2724MW, PK=2095MW, RR=83MW, NetOpMargin: EVE=547 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @300MW, PGPP1 @76MW [WEBSMS] | CVIS
2/26/2024 5:47:40 PM | [NSO Update] Luzon Grid-02/26/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12737MW, PK=10103MW, RR=417MW, NetOpMargin: EVE=2217 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @330MW [WEBSMS] | CLUZ
2/26/2024 2:32:27 PM | Luzon Grid-02/26/2024 14:32: Pagbilao Unit 1 online at 1431H. (Unplanned Outage) [WEBSMS] | CLUZ
2/26/2024 1:02:03 PM | Visayas Grid-02/26/2024 13:01: NNBP cut-in at 1245H. ( Unplanned Outage ) [WEBSMS] | CVIS
2/26/2024 12:36:21 PM | [NSO Update] Mindanao Grid-02/26/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3536MW, PK=2278MW, RR=74MW, NetOpMargin: PM=1184, EVE=1210 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @169MW [WEBSMS] | CMIN
2/26/2024 12:35:00 PM | [NSO Update] Visayas Grid-02/26/2024 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3011MW, PK=2128MW, RR=88MW, NetOpMargin: PM=795, EVE=557 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW [WEBSMS] | CVIS
2/26/2024 12:33:12 PM | [NSO Update] Luzon Grid-02/26/2024 12:32: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13576MW, PK=10688MW, RR=426MW, NetOpMargin: PM=2462, EVE=1771 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @330MW [WEBSMS] | CLUZ
2/26/2024 10:33:36 AM | Mindanao Grid-02/26/2024 10:37: WMPC DG10 Online at 1030H. RPS-System Voltage Requirement [WEBSMS] | CMIN
2/26/2024 7:49:10 AM | Luzon Grid-02/26/2024 07:48: Batangas 300MVA T04 and T05 were paralleled at 0746H. (After the unlooping of Sta Rita-San Lorenzo 230kV Busses) [WEBSMS] | CLUZ
2/26/2024 7:43:51 AM | Luzon Grid-02/26/2024 07:43: Sta Rita-San Lorenzo 230kV Bus 2 Tie Breaker 8-02TB24SLO was opened at 0740H. (Requested by First Gas due to hotspot at the associated Disconnect Switch) [WEBSMS] | CLUZ
2/26/2024 7:10:08 AM | Luzon Grid-02/26/2024 07:09: Nagsaag PCB 8-05CB24NGS was de-energized at 0708H. (Planned Outage) [WEBSMS] | CLUZ
2/26/2024 5:59:45 AM | [NSO Update] Mindanao Grid-02/26/2024 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3557MW, PK=2212MW, RR=72MW, NetOpMargin: AM=1273, PM=1173, EVE=1201 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @169MW [WEBSMS] | CMIN
2/26/2024 5:58:21 AM | [NSO Update] Visayas Grid-02/26/2024 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3013MW, PK=2115MW, RR=86MW, NetOpMargin: AM=812, PM=708, EVE=489 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW [WEBSMS] | CVIS
2/26/2024 5:51:53 AM | [NSO Update] Luzon Grid-02/26/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14046MW, PK=10433MW, RR=425MW, NetOpMargin: AM=3188, PM=2450, EVE=1702 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @330MW [WEBSMS] | CLUZ
2/26/2024 4:19:57 AM | [NSO Update] Mindanao Grid-02/26/2024 04:24: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the rest of country. [WEBSMS] | CMIN
2/26/2024 4:19:43 AM | [NSO Update] Visayas Grid-02/26/2024 04:19: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the rest of country. [WEBSMS] | CVIS
2/26/2024 4:19:13 AM | [NSO Update] Luzon Grid-02/26/2024 04:18: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the rest of country. [WEBSMS] | CLUZ
2/26/2024 3:29:56 AM | Visayas Grid-02/26/2024 03:29: CEDC unit # 2 cut-in to the system @0206H. ( Un-planned Outage ) [WEBSMS] | CVIS
2/26/2024 3:08:56 AM | Mindanao Grid-02/26/2024 03:13: Libertad Power online at 0307H. (Unplanned Outage) [WEBSMS] | CMIN
2/26/2024 1:07:46 AM | Mindanao Grid-02/26/2024 01:11: SEC Unit 1 online at 0102H from Forced Outage: (Unplanned Outage) [WEBSMS] | CMIN
2/25/2024 11:38:23 PM | Mindanao Grid-02/25/2024 23:42: Toril - Matanao 138KV Line 2 re-energized at 2329H (Planned Outage) [WEBSMS] | CMIN
2/25/2024 10:23:46 PM | Luzon Grid-02/25/2024 22:23: Ilijan-Tayabas 500kV Line restored at 2222H (Planned Outage) [WEBSMS] | CLUZ
2/25/2024 7:46:49 PM | Luzon Grid-02/25/2024 19:46: Calaca-Sta. Rita 230kV Line 1 restored at 1944H (Planned Outage) [WEBSMS] | CLUZ
2/25/2024 6:29:27 PM | Luzon Grid-02/25/2024 18:29: Balsik 1000MVA T02 restored at 1827H (Planned Outage) [WEBSMS] | CLUZ
2/25/2024 6:15:40 PM | [NSO Update] Mindanao Grid-02/25/2024 18:19: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3362MW, PK=2069MW, RR=72MW, NetOpMargin: EVE=1221 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @192MW [WEBSMS] | CMIN
2/25/2024 6:01:49 PM | [NSO Update] Visayas Grid-02/25/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2637MW, PK=2007MW, RR=79MW, NetOpMargin: EVE=551 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW [WEBSMS] | CVIS
2/25/2024 5:58:06 PM | Luzon Grid-02/25/2024 17:57: Mexico-Quezon 230kV Line restored at 1757H (Planned Outage) [WEBSMS] | CLUZ
2/25/2024 5:56:39 PM | [NSO Update] Luzon Grid-02/25/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12127MW, PK=9273MW, RR=287MW, NetOpMargin: EVE=2567 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @330MW [WEBSMS] | CLUZ
2/25/2024 5:40:37 PM | Mindanao Grid-02/25/2024 17:44: SEC Unit 1 with 53.7MW load tripped at 1732H with SIPS activation. Indication: Induced draft Fan Tripped. Lowest Frequency dip at 59.604Hz, no ALD. (Unplanned Outage) [WEBSMS] | CMIN
2/25/2024 5:26:46 PM | Luzon Grid-02/25/2024 17:26: Dasmarinas-Ternate 115kV Line restored at 1724H (Unplanned Outage) [WEBSMS] | CLUZ
2/25/2024 5:04:15 PM | Luzon Grid-02/25/2024 17:03: Pagbilao EHV-Pagbilao PP 230kV Line 1 restored at 1702H (Planned Outage) [WEBSMS] | CLUZ
2/25/2024 4:48:17 PM | Mindanao Grid-02/25/2024 16:52: Pulangi Unit 2 shutdown at 0804H. On-line at 1503H. P&E activity: Installation of remaining parts of 7-08DS05MRM at Maramag SS. (Planned outage) [WEBSMS] | CMIN
2/25/2024 4:35:39 PM | Luzon Grid-02/25/2024 16:35: Balingueo 230kV Bus 1 restored at 1633H (Planned Outage) [WEBSMS] | CLUZ
2/25/2024 4:03:02 PM | Luzon Grid-02/25/2024 16:02: Tuguegarao 230kV Bus 1 restored at 1601H (Planned Outage) [WEBSMS] | CLUZ
2/25/2024 3:06:03 PM | Mindanao Grid-02/25/2024 15:10: Maramag - Pulangui 4 re-energized at 1503H (Planned Outage) [WEBSMS] | CMIN
2/25/2024 3:05:47 PM | Mindanao Grid-02/25/2024 15:09: Pulangi Unit 2 on-line at 1503H. Affected by P&E activity: Installation of remaining parts of 7-08DS05MRM. (Planned Outage) [WEBSMS] | CMIN
2/25/2024 2:23:20 PM | Mindanao Grid-02/25/2024 14:27: Baloi - Agus 6 138KV Line re-energized/looped at 1421H (Planned Outage) [WEBSMS] | CMIN
2/25/2024 12:58:07 PM | [NSO Update] Luzon Grid-02/25/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13122MW, PK=9054MW, RR=296MW, NetOpMargin: PM=3772, EVE=2288 Highest Unit O/L: GNPD 1@668MW Derated Plant: CALACA 2 @180MW, MASINLOC1 @330MW [WEBSMS] | CLUZ
2/25/2024 12:55:05 PM | [NSO Update] Mindanao Grid-02/25/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3437MW, PK=1808MW, RR=74MW, NetOpMargin: PM=1555, EVE=1280 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @104MW [WEBSMS] | CMIN
2/25/2024 12:48:28 PM | [NSO Update] Visayas Grid-02/25/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2873MW, PK=1831MW, RR=81MW, NetOpMargin: PM=961, EVE=542 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @307MW, PGPP1 @76MW [WEBSMS] | CVIS
2/25/2024 12:39:14 PM | Mindanao Grid-02/25/2024 12:43: Baloi - Agus 6 138KV Line 1 shutdown at 1228H (Planned Outage) [WEBSMS] | CMIN
2/25/2024 12:09:40 PM | Visayas Grid-02/25/2024 12:09: CEDC unit no 2 tripped 1204H, load 20.82MW (Unplanned Outage) [WEBSMS] | CVIS
2/25/2024 11:12:16 AM | Luzon Grid-02/25/2024 11:11: Dasmarinas-Ternate 115kV Line tripped at 1106H (Unplanned Outage) [WEBSMS] | CLUZ
2/25/2024 11:05:49 AM | Mindanao Grid-02/25/2024 11:10: Baloi - Agus 5 138KV Line re-energized/looped at 1100H (Planned Outage) [WEBSMS] | CMIN
2/25/2024 10:17:34 AM | Visayas Grid-02/25/2024 10:18: CEDC unit #2 cut-in to the system at 1014H, initial load 8.0MW (Unplanned Outage) [WEBSMS] | CVIS
2/25/2024 8:28:28 AM | Mindanao Grid-02/25/2024 08:33: Maramag - Pulangui 4 138KV Line 2 shutdown at 0804H (Planned Outage) [WEBSMS] | CMIN
2/25/2024 8:12:44 AM | Luzon Grid-02/25/2024 08:13: Pagbilao EHV-Pagbilao PP 230kV Line 1 de-energized at 0812H (Planned Outage) [WEBSMS] | CLUZ
2/25/2024 8:06:55 AM | Mindanao Grid-02/25/2024 08:12: Pulangi Unit 2 shutdown at 0804H. P&E Request: Installation of remaining parts of 7-08DS05MRM. (Planned Outage) [WEBSMS] | CMIN
2/25/2024 7:23:23 AM | Mindanao Grid-02/25/2024 07:28: Toril - Matanao 138KV Line 2 shutdown at 0717H (Planned Outage) [WEBSMS] | CMIN
2/25/2024 7:10:45 AM | Mindanao Grid-02/25/2024 07:15: Baloi - Agus 5 138KV Line deenergized at 0703H (Planned Outage) [WEBSMS] | CMIN
2/25/2024 7:09:52 AM | Luzon Grid-02/25/2024 07:10: Balsik SS 1000MVA T02 de-energized at 0709H (Planned Outage) [WEBSMS] | CLUZ
2/25/2024 6:46:01 AM | Luzon Grid-02/25/2024 06:46: Ilijan-Tayabas 500kV Line de-energized at 0646H (Planned Outage) [WEBSMS] | CLUZ
2/25/2024 6:12:12 AM | Luzon Grid-02/25/2024 06:12: Mexico-Quezon 230kV Line de-energized at 0611H (Planned Outage) [WEBSMS] | CLUZ
2/25/2024 5:44:15 AM | [NSO Update] Mindanao Grid-02/25/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3506MW, PK=1767MW, RR=72MW, NetOpMargin: AM=1667, PM=1526, EVE=1306 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @169MW [WEBSMS] | CMIN
2/25/2024 5:43:32 AM | Mindanao Grid-02/25/2024 05:48: TUDAYA2 Unit 1 with 4MW load emergency shutdown at 0529H due to high bearing temperature (Unplanned Outage) [WEBSMS] | CMIN
2/25/2024 5:39:03 AM | Luzon Grid-02/25/2024 05:39: Tuguegarao SS 230kV Bus 1 de-energized at 0539H. (Planned Outage) [WEBSMS] | CLUZ
2/25/2024 5:35:01 AM | [NSO Update] Visayas Grid-02/25/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3024MW, PK=1959MW, RR=79MW, NetOpMargin: AM=986, PM=1000, EVE=732 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW [WEBSMS] | CVIS
2/25/2024 5:29:46 AM | [NSO Update] Luzon Grid-02/25/2024 05:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13370MW, PK=9227MW, RR=295MW, NetOpMargin: AM=3848, PM=3810, EVE=2522 Highest Unit O/L: GNPD 1@668MW Derated Plant: CALACA 2 @180MW, MASINLOC1 @330MW [WEBSMS] | CLUZ
2/25/2024 5:20:22 AM | Mindanao Grid-02/25/2024 05:25: TUDAYA 2 Unit 1 online at 0424H (Unplanned Outage) [WEBSMS] | CMIN
2/25/2024 4:02:16 AM | [NSO Update] Luzon Grid-02/25/2024 04:02: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of country. [WEBSMS] | CLUZ
2/25/2024 4:01:55 AM | [NSO Update] Mindanao Grid-02/25/2024 04:07: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of country. [WEBSMS] | CMIN
2/25/2024 4:01:51 AM | [NSO Update] Visayas Grid-02/25/2024 04:02: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of country. [WEBSMS] | CVIS
2/25/2024 3:59:08 AM | Luzon Grid-02/25/2024 03:59: Dasmarinas SS 115kV Bus 1 energized at 0359H (Planned Outage) [WEBSMS] | CLUZ
2/25/2024 1:35:21 AM | Mindanao Grid-02/25/2024 01:40: Toril - Matanao 138kV Line1 energized and looped at 0129H (Planned Outage) [WEBSMS] | CMIN
2/25/2024 1:20:35 AM | Visayas Grid-02/25/2024 01:21: CEDC U2 emergency cut out at 0115H (Unplanned Outage) [WEBSMS] | CVIS
2/25/2024 12:24:11 AM | Luzon Grid-02/25/2024 00:24: Dasmarinas SS 115kV Bus 1 de-energized at 0015H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 11:56:23 PM | Mindanao Grid-02/25/2024 00:01: Zamboanga SS 138kV Power Transformer #1 energized at 2353H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 11:48:48 PM | Mindanao Grid-02/24/2024 23:53: Butuan SS 138kV Bus #2 energized at 2344H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 10:18:45 PM | Mindanao Grid-02/24/2024 22:23: Balo-i - Kauswagan 230kV Line 2 energize and loop at 2212H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 9:17:44 PM | Mindanao Grid-02/24/2024 21:22: Zamboanga SS 138kV Bus #1energized at 2114H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 9:13:34 PM | Luzon Grid-02/24/2024 21:14: San Jose SS 300MVA T03 energized at 2112H. (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 8:21:04 PM | Mindanao Grid-02/24/2024 20:26: LIBERTAD POWER with 6MW load emergency shutdown at 2018H due to steam drum leakage (Unplanned Outage) [WEBSMS] | CMIN
2/24/2024 7:26:05 PM | Luzon Grid-02/24/2024 19:26: San Jose SS 115kV Bus 1 restored at 1922H. (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 6:02:49 PM | Mindanao Grid-02/24/2024 18:07: Kibawe - Tacurong 138kV Line energized at 1759H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 5:52:31 PM | Luzon Grid-02/24/2024 17:53: Dasmarinas SS 500kV Bus 2 restored at 1752H. (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 5:42:38 PM | [NSO Update] Mindanao Grid-02/24/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3425MW, PK=2184MW, RR=72MW, NetOpMargin: EVE=1170 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @104MW [WEBSMS] | CMIN
2/24/2024 5:41:27 PM | [NSO Update] Visayas Grid-02/24/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2422MW, PK=2078MW, RR=83MW, NetOpMargin: EVE=261 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: Leyte A @ 309MW, PGPP1 @ 76MW, TPVI @ 27.5MW [WEBSMS] | CVIS
2/24/2024 5:39:00 PM | [NSO Update] Luzon Grid-02/24/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12085MW, PK=10053MW, RR=377MW, NetOpMargin: EVE=1655 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Calaca 2 @ 180MW, Masinloc 1 @ 325MW [WEBSMS] | CLUZ
2/24/2024 5:14:12 PM | Luzon Grid-02/24/2024 17:14: Daraga-Tiwi C 230kV Line restored at 1714H. (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 5:08:24 PM | Luzon Grid-02/24/2024 17:09: Daraga SS 230kV Bus 1 restored at 1707H. (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 5:07:06 PM | Luzon Grid-02/24/2024 17:07: Masinloc-Bolo 230kV Line 2 restored at 1707H. (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 4:23:44 PM | Luzon Grid-02/24/2024 16:24: Balsik SS 500kV Bus 2 restored at 1623H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 4:04:09 PM | Mindanao Grid-02/24/2024 16:09: Balo-i - Lugait 138kV Line energized and loop at 1555H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 3:15:42 PM | Mindanao Grid-02/24/2024 15:20: Manolo Fortich - Maramag 138kV Line 2 energized at 1513H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 1:35:19 PM | Luzon Grid-02/24/2024 13:35: Binga-Nagsaag 230kV L1 restored at 1335H (Unplanned Outage) [WEBSMS] | CLUZ
2/24/2024 1:27:57 PM | Luzon Grid-02/24/2024 13:28: Binga-Nagsaag 230kV L1 tripped at 1326H (Unplanned Outage) [WEBSMS] | CLUZ
2/24/2024 1:20:25 PM | Luzon Grid-02/24/2024 13:21: Binga-Nagsaag 230kV L2 restored at 1320H (Unplanned Outage) [WEBSMS] | CLUZ
2/24/2024 1:12:19 PM | Luzon Grid-02/24/2024 13:12: Binga-Nagsaag 230kV L2 tripped at 1308H (Unplanned Outage) [WEBSMS] | CLUZ
2/24/2024 1:10:34 PM | Mindanao Grid-02/24/2024 13:15: Balo-i - Lugait 138kV Line shutdown at 1307H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 12:45:48 PM | Mindanao Grid-02/24/2024 12:50: Kauswagan SS 230kV Bus #1 energized at 1241H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 12:41:36 PM | [NSO Update] Mindanao Grid-02/24/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3486MW, PK=2144MW, RR=75MW, NetOpMargin: PM=1267, EVE=1173 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @104MW [WEBSMS] | CMIN
2/24/2024 12:39:43 PM | [NSO Update] Visayas Grid-02/24/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2621MW, PK=2039MW, RR=80MW, NetOpMargin: PM=501, EVE=178 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW [WEBSMS] | CVIS
2/24/2024 12:36:04 PM | [NSO Update] Luzon Grid-02/24/2024 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13170MW, PK=10149MW, RR=386MW, NetOpMargin: PM=2635, EVE=1506 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @325MW [WEBSMS] | CLUZ
2/24/2024 12:17:04 PM | Mindanao Grid-02/24/2024 12:22: Balo-i SS 100MVA Power Transformer #3 energized at 1209H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 12:01:42 PM | Luzon Grid-02/24/2024 12:02: Calaca-Sta. Rita 230kV Line 1 de-energized at 1200H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 11:42:22 AM | Luzon Grid-02/24/2024 11:43: Masinloc-Bolo 230kV Line 2 de-energized at 1142H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 11:34:10 AM | Luzon Grid-02/24/2024 11:34: Masinloc-Bolo 230kV Line 1 restored at 1134H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 11:32:57 AM | Luzon Grid-02/24/2024 11:33: Sta. Rita-San Lorenzo 230kV Bus 1 & 2 loop at 1131H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 10:36:42 AM | Luzon Grid-02/24/2024 10:37: San Jose SS 115kV Bus 1 de-energized at 1037H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 10:10:15 AM | Luzon Grid-02/24/2024 10:10: San Jose SS PCB 9Z-01CB04SJO closed at 1010H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 10:06:23 AM | Luzon Grid-02/24/2024 10:07: Batangas T04 and T05 split at 1000H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 9:55:30 AM | Mindanao Grid-02/24/2024 10:00: Kauswagan SS 230kV Bus #1 shutdown at 0949H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 9:54:12 AM | Luzon Grid-02/24/2024 09:54: Sta. Rita 230kV Bus 2 restored at 0953H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 9:24:55 AM | Mindanao Grid-02/24/2024 09:30: Balo-i Power Transformer #3 shutdown at 0922H (Planned Outage). [WEBSMS] | CMIN
2/24/2024 9:00:24 AM | Mindanao Grid-02/24/2024 09:05: Balo-i 138kV Bus 1 energized at 0853H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 8:47:41 AM | Luzon Grid-02/24/2024 08:48: San Jose SS 300MVA T03 de-energized at 0846H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 8:27:27 AM | Mindanao Grid-02/24/2024 08:32: SEC2 online at 0825H. From PMS (Non-GOMP). [WEBSMS] | CMIN
2/24/2024 8:19:07 AM | Mindanao Grid-02/24/2024 08:24: Manolo Fortich - Maramag 138kV Line 2 shutdown at 0811H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 8:13:45 AM | Luzon Grid-02/24/2024 08:14: Balingueo SS 230kV Bus 1 de-energized at 0813H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 8:08:21 AM | Luzon Grid-02/24/2024 08:08: Balsik SS 500kV Bus 2 de-energized at 0807H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 7:54:17 AM | Mindanao Grid-02/24/2024 07:59: Toril - Matanao 138kV Line 1 shutdown at 0745H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 7:52:32 AM | Luzon Grid-02/24/2024 07:53: Daraga SS 230kV Bus 1 de-energized at 0752H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 7:48:59 AM | Luzon Grid-02/24/2024 07:49: Daraga-Tiwi C 230kV Line de-energized at 0749H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 7:35:46 AM | Luzon Grid-02/24/2024 07:36: Dasmarinas SS 500kV Bus 2 de-energized at 0735H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 7:24:48 AM | Luzon Grid-02/24/2024 07:25: Ilijan PP Block-1 GT\ST Main Transformer de-energized at 0718H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 7:15:28 AM | Mindanao Grid-02/24/2024 07:20: Balo-i - Kauswagan 230kV Line2 shutdown at 0629H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 7:13:43 AM | Mindanao Grid-02/24/2024 07:18: Kibawe-Tacurong 138kV Line 1 shutdown at 0706H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 7:01:55 AM | Luzon Grid-02/24/2024 07:02: San Jose SS PCB 9Z-01CB04SJO opened at 0700H (Unplanned Outage) [WEBSMS] | CLUZ
2/24/2024 6:55:40 AM | Luzon Grid-02/24/2024 06:56: San Jose SS 300MVA T03 unloop at 0652H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 6:53:52 AM | Luzon Grid-02/24/2024 06:54: San Jose SS 300MVA T02 loop at 0649H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 5:56:31 AM | Mindanao Grid-02/24/2024 06:01: Butuan SS 138KV Bus 2 shutdown at 0552H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 5:51:59 AM | [NSO Update] Luzon Grid-02/24/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13321MW, PK=10000MW, RR=384MW, NetOpMargin: AM=2937, PM=3128, EVE=1862 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: CALACA 2 @180MW, GMEC 2 @286MW [WEBSMS] | CLUZ
2/24/2024 5:38:31 AM | [NSO Update] Mindanao Grid-02/24/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3493MW, PK=2000MW, RR=72MW, NetOpMargin: AM=1421, PM=1286, EVE=1162 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @104MW [WEBSMS] | CMIN
2/24/2024 5:38:18 AM | Luzon Grid-02/24/2024 05:38: Masinloc-Bolo 230kV Line 1 de-energized at 0535H (Planned Outage) [WEBSMS] | CLUZ
2/24/2024 5:32:21 AM | [NSO Update] Visayas Grid-02/24/2024 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2624MW, PK=1994MW, RR=79MW, NetOpMargin: AM=551, PM=444, EVE=259 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW [WEBSMS] | CVIS
2/24/2024 5:22:56 AM | Visayas Grid-02/24/2024 05:23: TVI Unit # 1 cut-in @0520H. ( Planned Outage ). [WEBSMS] | CVIS
2/24/2024 5:20:21 AM | Mindanao Grid-02/24/2024 05:25: Baloi SS 138KV Bus 1 shutdown at 0517H (Planned Outage) [WEBSMS] | CMIN
2/24/2024 5:10:17 AM | Luzon Grid-02/24/2024 05:10: Sta. Rita 230kV Bus 2 de-energized at 0510H (Unplanned Outage) [WEBSMS] | CLUZ
2/24/2024 4:07:31 AM | [NSO Update] Luzon Grid-02/24/2024 04:08: Weather Advisory: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of country. [WEBSMS] | CLUZ
2/24/2024 4:07:27 AM | [NSO Update] Visayas Grid-02/24/2024 04:08: Weather Advisory: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of country. [WEBSMS] | CVIS
2/24/2024 4:07:24 AM | [NSO Update] Mindanao Grid-02/24/2024 04:12: Weather Advisory: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of country. [WEBSMS] | CMIN
2/23/2024 11:51:43 PM | Mindanao Grid-02/23/2024 23:56: Siguil HEP shutdwon at 2350H. Test & Commissioning [WEBSMS] | CMIN
2/23/2024 11:39:13 PM | Mindanao Grid-02/23/2024 23:44: Siguil HEP online at 2338H. Test & Commissioning. [WEBSMS] | CMIN
2/23/2024 11:07:28 PM | Luzon Grid-02/23/2024 23:08: Ilijan GT1-1 shutdown at 2307H (Planned Outage) [WEBSMS] | CLUZ
2/23/2024 10:47:24 PM | Mindanao Grid-02/23/2024 22:52: Siguil HEP with 14.63 MW tripped at 2245H. Test & Commissioning. [WEBSMS] | CMIN
2/23/2024 10:43:17 PM | Luzon Grid-02/23/2024 22:43: Ilijan ST1 shutdown at 2241H (Planned Outage) [WEBSMS] | CLUZ
2/23/2024 10:34:21 PM | Luzon Grid-02/23/2024 22:34: For info: Sta Rita and San Lorenzo 230kV Bus A and B were unlooped at 2216H while Batangas 300MVA T04 and T05 were looped at 2221H. This was due to hotspots found near the tie bus breakers at San Lorenzo and Sta. Rita. [WEBSMS] | CLUZ
2/23/2024 10:16:46 PM | Mindanao Grid-02/23/2024 22:21: Siguil HEP online at 2215H. Test & Commissioning. [WEBSMS] | CMIN
2/23/2024 10:03:09 PM | Mindanao Grid-02/23/2024 22:08: SEC Unit 2 shutdown at 2200H. (Planned Outage) [WEBSMS] | CMIN
2/23/2024 9:43:13 PM | Mindanao Grid-02/23/2024 21:48: Siguil HEP with 10.9MW load (75%) performed load rejection at 2142H. Test & Commissioning. [WEBSMS] | CMIN
2/23/2024 9:34:38 PM | Mindanao Grid-02/23/2024 21:39: Nagamin-Zamboanga 138KV line 1 re-energized at 2129H (Unplanned Outage) [WEBSMS] | CMIN
2/23/2024 9:25:11 PM | Mindanao Grid-02/23/2024 21:30: Nagamin Zamboanga 138KV Line 1 tripped at 2121H (Unplanned Outage) [WEBSMS] | CMIN
2/23/2024 9:13:09 PM | Mindanao Grid-02/23/2024 21:18: Siguil HEP online back at 2111H. Test & Commissioning. [WEBSMS] | CMIN
2/23/2024 9:01:22 PM | Mindanao Grid-02/23/2024 21:06: Siguil HEP with 7MW load performed load rejection at 2100H. [WEBSMS] | CMIN
2/23/2024 7:11:00 PM | Mindanao Grid-02/23/2024 19:16: Siguil HEP online at 1908H. Testing & commissioning. [WEBSMS] | CMIN
2/23/2024 6:00:58 PM | Mindanao Grid-02/23/2024 18:06: Tudaya 2 Unit 2 with 2.87MW shutdown at 1717H to facilitate tailrace runner inspection. (Unplanned Outage) [WEBSMS] | CMIN
2/23/2024 5:57:46 PM | [NSO Update] Mindanao Grid-02/23/2024 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3339MW, PK=2146MW, RR=70MW, NetOpMargin: EVE=1123 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @104MW [WEBSMS] | CMIN
2/23/2024 5:56:51 PM | [NSO Update] Visayas Grid-02/23/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2553MW, PK=2146MW, RR=83MW, NetOpMargin: EVE=324 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: Leyte A @ 309MW, PGPP1 @ 76MW [WEBSMS] | CVIS
2/23/2024 5:55:37 PM | [NSO Update] Luzon Grid-02/23/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12487MW, PK=10453MW, RR=417MW, NetOpMargin: EVE=1616 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Calaca 2 @ 180MW, Masinloc 1 @ 330MW, Ilijan A @ 300MW, Ilijan B @ 590MW [WEBSMS] | CLUZ
2/23/2024 5:42:18 PM | Mindanao Grid-02/23/2024 17:47: SEC Unit 1 online at 1739H from Forced Outage: (Unplanned Outage) [WEBSMS] | CMIN
2/23/2024 5:23:47 PM | Mindanao Grid-02/23/2024 17:28: SEC Unit 1 tripped again at 1721H after synchronization at 1719H. Indication to follow (Unplanned Outage) [WEBSMS] | CMIN
2/23/2024 5:20:44 PM | Mindanao Grid-02/23/2024 17:25: SEC Unit 1 online at 1719H from Forced Outage: Induced draft Fan Tripped.(Unplanned Outage) [WEBSMS] | CMIN
2/23/2024 4:44:05 PM | Mindanao Grid-02/23/2024 16:49: WMPC DG10 shutdown at 1644H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/23/2024 1:12:50 PM | [NSO Update] Mindanao Grid-02/23/2024 13:17: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3396MW, PK=2285MW, RR=75MW, NetOpMargin: PM=1036, EVE=1045 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @104MW [WEBSMS] | CMIN
2/23/2024 1:11:51 PM | [NSO Update] Visayas Grid-02/23/2024 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2772MW, PK=2213MW, RR=85MW, NetOpMargin: PM=475, EVE=275 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW [WEBSMS] | CVIS
2/23/2024 1:09:42 PM | [NSO Update] Luzon Grid-02/23/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13603MW, PK=11066MW, RR=441MW, NetOpMargin: PM=2097, EVE=1382 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @330MW, ILIJAN A @240MW, ILIJAN B @590MW [WEBSMS] | CLUZ
2/23/2024 11:39:31 AM | Mindanao Grid-02/23/2024 11:44: Update 2: SEC Unit 1 with 109.5MW load tripped at 1054H with SIPS activation: GenSan - Lledo 69kV Line with LD=38.07MW, GenSan - Pob Tupi 69kV Line with LD=27.91MW, and Kamanga - Kiamba 69kV Line with LD=9.14MW. Lowest frequency dip at 59.545Hz. Cause: Tripping of Induced Draft Fan. Unplanned outage. [WEBSMS] | CMIN
2/23/2024 11:07:20 AM | Mindanao Grid-02/23/2024 11:12: Update 1: SEC Unit 1 with 109.5MW load tripped at 1054H with SIPS activation lowest frequency dip at 59.545Hz. Indication: For investigation. Unplanned outage. [WEBSMS] | CMIN
2/23/2024 11:02:57 AM | Mindanao Grid-02/23/2024 11:08: SEC Unit 1 with 109.5MW load tripped at 1054H with SIPS activation. Indication: For investigation. Unplanned outage. [WEBSMS] | CMIN
2/23/2024 10:27:17 AM | Mindanao Grid-02/23/2024 10:32: WMPC DG10 Online at 1025H. RPS-System Voltage Requirement [WEBSMS] | CMIN
2/23/2024 8:28:22 AM | Mindanao Grid-02/23/2024 08:33: Tudaya 2 Unit 1 tripped at 0756H. Indication: Temp. Generator radial bearing too high (Unplanned Outage) [WEBSMS] | CMIN
2/23/2024 6:43:05 AM | Visayas Grid-02/23/2024 06:43: URC U2 cut-out at 0640H. (Unplanned Outage) [WEBSMS] | CVIS
2/23/2024 6:19:30 AM | Luzon Grid-02/23/2024 06:20: Tayabas 600MVA T04 was de-energized at 0614H. For decommissioning and to be transferred to Dasmarinas Substation and will be commissioned as Dasmarinas 600MVA Transformer No. 5. (Planned Outage) [WEBSMS] | CLUZ
2/23/2024 5:58:58 AM | [NSO Update] Luzon Grid-02/23/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13695MW, PK=10714MW, RR=428MW, NetOpMargin: AM=2553, PM=2308, EVE=1529 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CALACA 2 @180MW, MPGC 1 @286MW, MASINLOC 1 @330MW, ILIJAN A @240MW, ILIJAN B @ 590MW [WEBSMS] | CLUZ
2/23/2024 5:55:24 AM | [NSO Update] Visayas Grid-02/23/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2810MW, PK=2157MW, RR=81MW, NetOpMargin: AM=572, PM=601, EVE=362 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW [WEBSMS] | CVIS
2/23/2024 5:55:12 AM | [NSO Update] Mindanao Grid-02/23/2024 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3514MW, PK=2235MW, RR=72MW, NetOpMargin: AM=1208, PM=1225, EVE=1262 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @146MW, AG7 @28MW, PG4 @104MW [WEBSMS] | CMIN
2/23/2024 4:00:37 AM | [NSO Update] Visayas Grid-02/23/2024 04:01: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CVIS
2/23/2024 4:00:22 AM | [NSO Update] Mindanao Grid-02/23/2024 04:05: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CMIN
2/23/2024 4:00:18 AM | [NSO Update] Luzon Grid-02/23/2024 04:00: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CLUZ
2/23/2024 2:31:57 AM | Luzon Grid-02/23/2024 02:32: Binan-Muntinlupa 230kV Line 3 restored at 0229H (Planned Outage) [WEBSMS] | CLUZ
2/22/2024 7:46:41 PM | Mindanao Grid-02/22/2024 19:51: WMPC DG10 shutdown at 1943H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
2/22/2024 7:37:22 PM | Mindanao Grid-02/22/2024 19:42: Balo-i SS 138kV Bus #2 re-energized at 1924H (Unplanned Outage). [WEBSMS] | CMIN
2/22/2024 7:06:30 PM | Luzon Grid-02/22/2024 19:07: Binan-Muntinlupa 230kV Line 3 de-energized at 1906H. (Planned Outage) [WEBSMS] | CLUZ
2/22/2024 5:41:33 PM | [NSO Update] Mindanao Grid-02/22/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3222MW, PK=2140MW, RR=72MW, NetOpMargin: EVE=1009 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @129MW, AG7 @28MW, PG4 @104MW [WEBSMS] | CMIN
2/22/2024 5:39:40 PM | [NSO Update] Visayas Grid-02/22/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2491MW, PK=2139MW, RR=82MW, NetOpMargin: EVE=270 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @305MW, PGPP1 @38MW [WEBSMS] | CVIS
2/22/2024 5:39:23 PM | Mindanao Grid-02/22/2024 17:44: Balo-i SS 230kV 300MVA Transformer #1 re-energized and loop at 1735H (Unplanned Outage) [WEBSMS] | CMIN
2/22/2024 5:37:37 PM | [NSO Update] Luzon Grid-02/22/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12355MW, PK=10557MW, RR=413MW, NetOpMargin: EVE=1385 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CALACA 2 @180MW, GMEC 2 @286MW, MASINLOC 1 @330MW, ILIJAN A @240MW, ILIJAN B @ 590MW [WEBSMS] | CLUZ
2/22/2024 5:02:45 PM | Mindanao Grid-02/22/2024 17:07: ASIGA HEP online at 1642H. Unplanned Outage. [WEBSMS] | CMIN
2/22/2024 5:00:17 PM | Visayas Grid-02/22/2024 17:00: PGPP Unit#3 emergency out @ 1657H. ( Unplanned Outage ) [WEBSMS] | CVIS
2/22/2024 4:38:53 PM | Mindanao Grid-02/22/2024 16:43: Balo-i SS 230kV 300MVA Transformer #1 emergency shutdown at 1626H (Unplanned Outage). [WEBSMS] | CMIN
2/22/2024 4:34:28 PM | Mindanao Grid-02/22/2024 16:39: Balo-i SS 230kV 300MVA Transformer #2 re-energized and loop at 1619H (Unplanned Outage). [WEBSMS] | CMIN
2/22/2024 4:22:13 PM | Mindanao Grid-02/22/2024 16:27: ASIGA HEP with 8MW gross generation tripped at 1612H. Indication: Restricted Earth Fault. Unplanned Outage. [WEBSMS] | CMIN
2/22/2024 3:57:50 PM | Mindanao Grid-02/22/2024 16:02: ASIGA HEP online at 1435H. Unplanned Outage. [WEBSMS] | CMIN
2/22/2024 3:56:17 PM | Mindanao Grid-02/22/2024 16:01: Lake Mainit online at 1549H. Unplanned Outage. [WEBSMS] | CMIN
2/22/2024 3:17:50 PM | Luzon Grid-02/22/2024 15:18: For info: Commissioning and energization of San Jose 6-06CB24SJO and 6-06CB08SJO Stub Protection completed at 1514H. (End of Commissioning) [WEBSMS] | CLUZ
2/22/2024 2:59:17 PM | Mindanao Grid-02/22/2024 15:04: Balo-i SS 230kV 300MVA Transformer #2 emergency shutdown at 1442H (Unplanned Outage) [WEBSMS] | CMIN
2/22/2024 2:57:45 PM | Mindanao Grid-02/22/2024 15:02: Balo-i SS 138kV Busbar #2 emergency shutdown at 1420H (Unplanned Outage). [WEBSMS] | CMIN
2/22/2024 2:50:24 PM | Luzon Grid-02/22/2024 14:50: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1450H. (Planned Outage) [WEBSMS] | CLUZ
2/22/2024 1:40:13 PM | Mindanao Grid-02/22/2024 13:45: Lake Mainit HEP Tripped/Isolated at 1313H. Affected by the tripping of Butuan-Santiago 69kV Line. Unplanned Outage [WEBSMS] | CMIN
2/22/2024 1:38:19 PM | Mindanao Grid-02/22/2024 13:43: ASIGA HEP Tripped/Isolated at 1313H. Affected by the tripping of Butuan-Santiago 69kV Line. Unplanned Outage [WEBSMS] | CMIN
2/22/2024 12:47:10 PM | [NSO Update] Mindanao Grid-02/22/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3272MW, PK=2328MW, RR=74MW, NetOpMargin: PM=870, EVE=914 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @129MW, AG7 @28MW, PG4 @104MW [WEBSMS] | CMIN
2/22/2024 12:46:36 PM | Luzon Grid-02/22/2024 12:47: For info: Sta Rita and San Lorenzo 230kV Busses were looped at 1246H. [WEBSMS] | CLUZ
2/22/2024 12:45:31 PM | [NSO Update] Visayas Grid-02/22/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2756MW, PK=2236MW, RR=85MW, NetOpMargin: PM=435, EVE=298 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @305MW, PGPP1 @76MW [WEBSMS] | CVIS
2/22/2024 12:43:52 PM | [NSO Update] Luzon Grid-02/22/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13310MW, PK=11038MW, RR=426MW, NetOpMargin: PM=1846, EVE=1411 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, GMEC 2 @286MW, MSLC1 @325MW, ILIJAN A @230MW [WEBSMS] | CLUZ
2/22/2024 12:31:38 PM | Luzon Grid-02/22/2024 12:32: For info: Batangas 300MVA T04 and T05 on split configuration at 1229H for preparation of looping of Sta. Rita and San Lorenzo 230kV Bus. [WEBSMS] | CLUZ
2/22/2024 10:33:00 AM | Mindanao Grid-02/22/2024 10:38: WMPC DG10 Online at 1030H. RPS-System Voltage Requirement [WEBSMS] | CMIN
2/22/2024 9:04:54 AM | Luzon Grid-02/22/2024 09:05: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0904H. (Planned Outage) [WEBSMS] | CLUZ
2/22/2024 6:44:52 AM | Luzon Grid-02/22/2024 06:45: San Jose SS 115kV Bus 2 restored at 0644H. (Planned Outage) [WEBSMS] | CLUZ
2/22/2024 6:21:09 AM | Mindanao Grid-02/22/2024 06:26: Zamboanga Power Transformer #1 shutdown at 0607H (Planned Outage). P&E Request under MSRP Stage II Schedule IV. [WEBSMS] | CMIN
2/22/2024 5:42:50 AM | [NSO Update] Mindanao Grid-02/22/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3291MW, PK=2266MW, RR=72MW, NetOpMargin: AM=953, PM=934, EVE=977 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @32MW, AG6 @129MW, AG7 @28MW, PG4 @104MW [WEBSMS] | CMIN
2/22/2024 5:41:02 AM | [NSO Update] Visayas Grid-02/22/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2830MW, PK=2199MW, RR=83MW, NetOpMargin: AM=548, PM=594, EVE=380 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @305MW, PGPP1 @76MW [WEBSMS] | CVIS
2/22/2024 5:39:39 AM | [NSO Update] Luzon Grid-02/22/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13512MW, PK=10737MW, RR=417MW, NetOpMargin: AM=2358, PM=1979, EVE=1508 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @325MW, MPGC 1 @75MW, ILIJAN A @165MW, ILIJAN B @585 MW [WEBSMS] | CLUZ
2/22/2024 4:04:01 AM | [NSO Update] Luzon Grid-02/22/2024 04:04: Weather Update: Easterlies affecting the country [WEBSMS] | CLUZ
2/22/2024 4:02:29 AM | [NSO Update] Mindanao Grid-02/22/2024 04:07: Weather Update: Easterlies affecting the country [WEBSMS] | CMIN
2/22/2024 4:02:06 AM | [NSO Update] Visayas Grid-02/22/2024 04:02: Weather Update: Easterlies affecting the country [WEBSMS] | CVIS
2/22/2024 1:06:28 AM | Luzon Grid-02/22/2024 01:07: Pagbilao Unit 1 shutdown at 0106H (Planned Outage) [WEBSMS] | CLUZ
2/21/2024 11:36:45 PM | Luzon Grid-02/21/2024 23:37: San Gabriel shutdown at 2334H (Planned Outage) [WEBSMS] | CLUZ
2/21/2024 9:49:03 PM | Mindanao Grid-02/21/2024 21:54: SIBULAN A Unit 1 online at 2140H. Cause of tripping: Ground fault in auxiliary transformer (Unplanned Outage) [WEBSMS] | CMIN
2/21/2024 9:48:29 PM | Mindanao Grid-02/21/2024 21:53: SIBULAN A Unit 2 online at 2134H. Cause of tripping: Ground fault in auxiliary transformer (Unplanned Outage) [WEBSMS] | CMIN
2/21/2024 9:24:16 PM | Mindanao Grid-02/21/2024 21:29: TUDAYA 2 Unit 2 with 0.9MW load shutdown at 2106H. Insufficient water supply (Unplanned Outage) [WEBSMS] | CMIN
2/21/2024 9:22:35 PM | Mindanao Grid-02/21/2024 21:27: (Correction) SIBULAN A Unit 1 (load=4.85MW) and Unit 2 (load=4.5MW) tripped at 2033H. Cause: To be verified by DLPC. Frequency dipped at 59.81Hz. (Unplanned Outage) [WEBSMS] | CMIN
2/21/2024 9:21:16 PM | Mindanao Grid-02/21/2024 21:26: SIBULAN A Unit 1 (load=4.85MW) and Unit 2 (load=4.5MW) tripped at 0833H. Cause: To be verified by DLPC. Frequency dipped at 59.81Hz. (Unplanned Outage) [WEBSMS] | CMIN
2/21/2024 8:25:33 PM | Luzon Grid-02/21/2024 20:26: San Jose SS 115kV Bus 2 shutdown at 2023H (Planned Outage) [WEBSMS] | CLUZ
2/21/2024 5:39:28 PM | [NSO Update] Mindanao Grid-02/21/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3397MW, PK=2227MW, RR=72MW, NetOpMargin: EVE=1097 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @42MW, AG6 @146MW, AG7 @28MW, PG4 @99MW [WEBSMS] | CMIN
2/21/2024 5:36:30 PM | [NSO Update] Visayas Grid-02/21/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2563MW, PK=2147MW, RR=82MW, NetOpMargin: EVE=334 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @302MW, PGPP1 @76MW [WEBSMS] | CVIS
2/21/2024 5:34:46 PM | [NSO Update] Luzon Grid-02/21/2024 17:35: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13046MW, PK=10495MW, RR=327MW, NetOpMargin: EVE=2224 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Calaca 2 @ 180MW, Masinloc 1 @ 325MW, Ilijan A @ 165MW, Ilijan B @ 535MW [WEBSMS] | CLUZ
2/21/2024 5:16:26 PM | Mindanao Grid-02/21/2024 17:21: WMPC DG10 shutdown at 1714H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/21/2024 4:06:03 PM | Luzon Grid-02/21/2024 16:06: Tayabas 230kV Bus 2 restored at 1605H (Planned Outage) [WEBSMS] | CLUZ
2/21/2024 1:00:50 PM | Mindanao Grid-02/21/2024 13:05: WMPC DG10 online at 1258H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/21/2024 12:42:58 PM | [NSO Update] Mindanao Grid-02/21/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3448MW, PK=2360MW, RR=74MW, NetOpMargin: PM=1013, EVE=1058 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @42MW, AG6 @146MW, AG7 @28MW, PG4 @99MW [WEBSMS] | CMIN
2/21/2024 12:41:06 PM | [NSO Update] Visayas Grid-02/21/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2728MW, PK=2155MW, RR=86MW, NetOpMargin: PM=488, EVE=334 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: Leyte A @ 302MW, PGPP1 @ 76MW [WEBSMS] | CVIS
2/21/2024 12:38:46 PM | [NSO Update] Luzon Grid-02/21/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13971MW, PK=10885MW, RR=336MW, NetOpMargin: PM=2750, EVE=2223 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Calaca 2 @ 180MW, Masinloc 1 @ 325MW, Ilijan A @ 165MW, Ilijan B @ 535MW [WEBSMS] | CLUZ
2/21/2024 6:44:17 AM | Luzon Grid-02/21/2024 06:44: Tayabas SS 230kV Bus 2 de-energized at 0644H. (Planned Outage) [WEBSMS] | CLUZ
2/21/2024 5:50:39 AM | [NSO Update] Luzon Grid-02/21/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14416MW, PK=10570MW, RR=335MW, NetOpMargin: AM=3511, PM=2777, EVE=2376 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @325MW, ILIJAN A @165MW, ILIJAN B@535MW [WEBSMS] | CLUZ
2/21/2024 5:45:53 AM | Mindanao Grid-02/21/2024 05:50: ASIGA HEP online at 0526H. Unplanned Outage. [WEBSMS] | CMIN
2/21/2024 5:33:30 AM | [NSO Update] Mindanao Grid-02/21/2024 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3458MW, PK=2196MW, RR=72MW, NetOpMargin: AM=1190, PM=1074, EVE=1160 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @58MW, AG2 @81MW, AG4 @100MW, AG5 @30MW, AG6 @146MW, AG7 @28MW, PG4 @99MW [WEBSMS] | CMIN
2/21/2024 5:30:58 AM | [NSO Update] Visayas Grid-02/21/2024 05:31: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2892MW, PK=2059MW, RR=82MW, NetOpMargin: AM=751, PM=631, EVE=480 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @350MW, PGPP1 @76MW [WEBSMS] | CVIS
2/21/2024 5:15:21 AM | Mindanao Grid-02/21/2024 05:20: ASIGA HEP with 8.1MW gross generation tripped at 0504H. Indication: Restricted Earth Fault. Unplanned Outage [WEBSMS] | CMIN
2/21/2024 4:23:23 AM | Luzon Grid-02/21/2024 04:23: San Jose SS 300MVA T03 restored at 0421H (Planned Outage) [WEBSMS] | CLUZ
2/20/2024 11:33:27 PM | Visayas Grid-02/20/2024 23:33: Magdugo-Dumanjug 230kV Line 2 energized at 2325H. (Planned Outage) [WEBSMS] | CVIS
2/20/2024 8:50:18 PM | Luzon Grid-02/20/2024 20:50: Tayabas 600MVA T01 restored at 2045H (Planned Outage) [WEBSMS] | CLUZ
2/20/2024 8:20:27 PM | Luzon Grid-02/20/2024 20:20: San Jose SS 300MVA T03 de-energized at 2015H (Planned Outage) [WEBSMS] | CLUZ
2/20/2024 7:32:09 PM | Mindanao Grid-02/20/2024 19:37: Mt Apo U3 online at 1928H. Unplanned Outage. [WEBSMS] | CMIN
2/20/2024 5:46:16 PM | [NSO Update] Mindanao Grid-02/20/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3394MW, PK=2261MW, RR=72MW, NetOpMargin: EVE=1061 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @33MW, AG6 @152MW, AG7 @29MW, PG4 @90MW [WEBSMS] | CMIN
2/20/2024 5:45:15 PM | [NSO Update] Visayas Grid-02/20/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2556MW, PK=2095MW, RR=83MW, NetOpMargin: EVE=378 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @76MW [WEBSMS] | CVIS
2/20/2024 5:43:27 PM | Mindanao Grid-02/20/2024 17:48: ASIGA HEP with 7MW gross generation tripped at 1656H. Indication: For verification. Unplanned Outage. [WEBSMS] | CMIN
2/20/2024 5:41:50 PM | [NSO Update] Luzon Grid-02/20/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13021MW, PK=10429MW, RR=327MW, NetOpMargin: EVE=2265 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @325MW, ILIJAN A @165MW, ILIJAN B@535MW [WEBSMS] | CLUZ
2/20/2024 5:20:23 PM | Mindanao Grid-02/20/2024 17:25: ASIGA Hydro online at 1650H. (Unplanned Outage) [WEBSMS] | CMIN
2/20/2024 5:15:59 PM | Mindanao Grid-02/20/2024 17:21: WMPC DG10 shutdown at 1713H. RPS-System Voltage Requirement [WEBSMS] | CMIN
2/20/2024 4:32:04 PM | Mindanao Grid-02/20/2024 16:37: ASIGA HEP with 7.5MW gross generation tripped at 1626H. Indication: Restricted Earth Fault. Unplanned Outage. [WEBSMS] | CMIN
2/20/2024 3:04:33 PM | Luzon Grid-02/20/2024 15:05: Binga-Ambuklao 230kV Line 2 restored at 1502H (Unplanned Outage) [WEBSMS] | CLUZ
2/20/2024 2:44:46 PM | Luzon Grid-02/20/2024 14:45: Binga-Ambuklao 230kV Line 2 tripped at 1438H (Unplanned Outage) [WEBSMS] | CLUZ
2/20/2024 1:38:34 PM | Visayas Grid-02/20/2024 13:39: TGPP U3 tripped at 1336H (Unplanned Outage) [WEBSMS] | CVIS
2/20/2024 1:20:01 PM | Visayas Grid-02/20/2024 13:20: TGPP U3 online at 1315H (Unplanned Outage) [WEBSMS] | CVIS
2/20/2024 1:01:27 PM | Mindanao Grid-02/20/2024 13:06: WMPC DG10 online at 1258H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
2/20/2024 12:48:42 PM | [NSO Update] Luzon Grid-02/20/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14069MW, PK=10808MW, RR=336MW, NetOpMargin: PM=2925, EVE=2331 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @325MW, ILIJAN A @165MW, ILIJAN B@535MW [WEBSMS] | CLUZ
2/20/2024 12:44:54 PM | [NSO Update] Visayas Grid-02/20/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2612MW, PK=2084MW, RR=85MW, NetOpMargin: PM=443, EVE=319 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @350MW, PGPP1 @76MW [WEBSMS] | CVIS
2/20/2024 12:40:24 PM | [NSO Update] Mindanao Grid-02/20/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3349MW, PK=2316MW, RR=75MW, NetOpMargin: PM=958, EVE=983 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @33MW, AG6 @152MW, AG7 @29MW, PG4 @90MW [WEBSMS] | CMIN
2/20/2024 11:57:39 AM | Mindanao Grid-02/20/2024 12:02: Naga Mindanao SVC online at 1146H (Unplanned Outage). [WEBSMS] | CMIN
2/20/2024 11:52:31 AM | Mindanao Grid-02/20/2024 11:57: Sarangani Unit #1 (SEC 1) online at 1140H. Unplanned Outage. [WEBSMS] | CMIN
2/20/2024 11:50:46 AM | Mindanao Grid-02/20/2024 11:55: Naga Mindanao SVC tripped at 1117H (Unplanned Outage). [WEBSMS] | CMIN
2/20/2024 11:39:11 AM | Mindanao Grid-02/20/2024 11:44: Aurora - Naga Mindanao 138kV Line 2 tripped and auto-reclosed at 1117H (Unplanned Outage) [WEBSMS] | CMIN
2/20/2024 6:59:51 AM | Luzon Grid-02/20/2024 07:00: GMEC 1 with 285MW tripped at 0656H. Lowest system frequency was 59.471Hz. (Unplanned Outage) [WEBSMS] | CLUZ
2/20/2024 6:40:09 AM | Luzon Grid-02/20/2024 06:40: Tayabas SS 600MVA T01 de-energized at 0640H. (Planned Outage) [WEBSMS] | CLUZ
2/20/2024 6:20:33 AM | Visayas Grid-02/20/2024 06:21: Cebu - Magdugo 230 kV Line 1 de-energized at 0619H. (Planned Outage) [WEBSMS] | CVIS
2/20/2024 6:12:41 AM | Luzon Grid-02/20/2024 06:13: Gamu - UPSI Gamu BESS 69kV Line de-energized at 0612H. (Planned Outage) [WEBSMS] | CLUZ
2/20/2024 6:00:59 AM | [NSO Update] Luzon Grid-02/20/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14585MW, PK=10638MW, RR=335MW, NetOpMargin: AM=3612, PM=3277, EVE=2533 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CALACA 2 @180MW, MSLC1 @325MW, ILIJAN A @250MW, ILIJAN B @535MW [WEBSMS] | CLUZ
2/20/2024 5:39:30 AM | [NSO Update] Mindanao Grid-02/20/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3346MW, PK=2197MW, RR=72MW, NetOpMargin: AM=1078, PM=973, EVE=968 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @90MW, AG5 @33MW, AG6 @152MW, AG7 @29MW, PG4 @90MW [WEBSMS] | CMIN
2/20/2024 5:37:25 AM | [NSO Update] Visayas Grid-02/20/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2831MW, PK=2165MW, RR=83MW, NetOpMargin: AM=583, PM=514, EVE=313 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @350MW, PGPP1 @76MW [WEBSMS] | CVIS
2/20/2024 4:16:16 AM | [NSO Update] Mindanao Grid-02/20/2024 04:21: Weather update: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
2/20/2024 4:15:54 AM | [NSO Update] Visayas Grid-02/20/2024 04:16: Weather update: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
2/20/2024 4:13:09 AM | [NSO Update] Luzon Grid-02/20/2024 04:13: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
2/19/2024 11:35:58 PM | Luzon Grid-02/19/2024 23:36: Quezon 115kV Bus 1(Customer Owned) was energized at 2332H. (Unplanned Outage) [WEBSMS] | CLUZ
2/19/2024 10:32:19 PM | Luzon Grid-02/19/2024 22:32: Quezon 115kV Bus 1(Customer Owned) was de-energized at 2226H. (Unplanned Outage) [WEBSMS] | CLUZ
2/19/2024 7:16:05 PM | Visayas Grid-02/19/2024 19:16: Visayas Spot Peak for February 19, 2024, 2185 MW at 1416H. Highest peak is 2458 MW at 1422H on May 17, 2023 [WEBSMS] | CVIS
2/19/2024 5:49:22 PM | [NSO Update] Mindanao Grid-02/19/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3144MW, PK=2199MW, RR=72MW, NetOpMargin: EVE=872 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @33MW, AG6 @152MW, AG7 @29MW, PG4 @90MW [WEBSMS] | CMIN
2/19/2024 5:45:27 PM | [NSO Update] Visayas Grid-02/19/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2488MW, PK=2112MW, RR=83MW, NetOpMargin: EVE=294 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @342MW, PGPP1 @76MW [WEBSMS] | CVIS
2/19/2024 5:43:40 PM | [NSO Update] Luzon Grid-02/19/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13469MW, PK=10426MW, RR=415MW, NetOpMargin: EVE=2628 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CALACA 2 @180MW, ILIJAN A @250MW, ILIJAN B @585MW [WEBSMS] | CLUZ
2/19/2024 5:36:36 PM | Mindanao Grid-02/19/2024 17:41: WMPC DG04 shutdown at 1713H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/19/2024 4:47:11 PM | Mindanao Grid-02/19/2024 16:52: SMC Unit 1 online at 1626H from PMS (Non-GOMP). [WEBSMS] | CMIN
2/19/2024 4:43:12 PM | Mindanao Grid-02/19/2024 16:48: Kibawe-Tacurong 138kV line re-energized at 1633H. From Unplanned Outage. [WEBSMS] | CMIN
2/19/2024 4:35:15 PM | Visayas Grid-02/19/2024 16:35: Magdugo-TVT 230KV line 1 energized at 1628H. (Planned Outage) [WEBSMS] | CVIS
2/19/2024 3:59:34 PM | Mindanao Grid-02/19/2024 16:04: Kibawe-Tacurong 138kV line on emergency shutdown at 1505H per request from D6 TL Manager. Unplanned Outage. [WEBSMS] | CMIN
2/19/2024 1:14:50 PM | Mindanao Grid-02/19/2024 13:19: WMPC DG4 online at 1303H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/19/2024 1:12:13 PM | Mindanao Grid-02/19/2024 13:17: Online at 1303H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/19/2024 12:49:31 PM | [NSO Update] Luzon Grid-02/19/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14531MW, PK=10756MW, RR=435MW, NetOpMargin: PM=3340, EVE=2516 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CALACA 2 @180MW, MASINLOC 1@325MW, ILIJAN A @165MW, ILIJAN B @585MW [WEBSMS] | CLUZ
2/19/2024 12:45:57 PM | [NSO Update] Visayas Grid-02/19/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2589MW, PK=2145MW, RR=85MW, NetOpMargin: PM=359, EVE=245 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @342MW, PGPP1 @76MW [WEBSMS] | CVIS
2/19/2024 12:45:47 PM | [NSO Update] Mindanao Grid-02/19/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3195MW, PK=2290MW, RR=74MW, NetOpMargin: PM=831, EVE=845 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @33MW, AG6 @152MW, AG7 @29MW, PG4 @90MW [WEBSMS] | CMIN
2/19/2024 11:59:51 AM | Mindanao Grid-02/19/2024 12:04: Mt Apo Unit 3 (MA3) with 1.6MW load tripped at 1130H. Cause: For verification. Unplanned Outage. [WEBSMS] | CMIN
2/19/2024 10:59:37 AM | Visayas Grid-02/19/2024 11:00: PGPP1 U1 re-cut in at 1057H (Unplanned Outage) [WEBSMS] | CVIS
2/19/2024 10:27:02 AM | Luzon Grid-02/19/2024 10:27: Lumban-Gumaca 230kV Line 2 tripped/reclosed both side at 1023H (Unplanned Outage) [WEBSMS] | CLUZ
2/19/2024 10:24:00 AM | Visayas Grid-02/19/2024 10:24: PGPP1 U1 tripped at 1019H (Unplanned Outage) [WEBSMS] | CVIS
2/19/2024 6:02:47 AM | [NSO Update] Mindanao Grid-02/19/2024 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3187MW, PK=2124MW, RR=72MW, NetOpMargin: AM=991, PM=880, EVE=919 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @33MW, AG6 @152MW, AG7 @29MW, PG4 @60MW [WEBSMS] | CMIN
2/19/2024 6:01:44 AM | [NSO Update] Visayas Grid-02/19/2024 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2675MW, PK=1974MW, RR=83MW, NetOpMargin: AM=618, PM=437, EVE=309 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @342MW, PGPP1 @76MW [WEBSMS] | CVIS
2/19/2024 5:59:53 AM | [NSO Update] Luzon Grid-02/19/2024 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14867MW, PK=10429MW, RR=428MW, NetOpMargin: AM=4010, PM=3722, EVE=3177 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, ILIJAN A @165MW, ILIJAN B @585MW [WEBSMS] | CLUZ
2/19/2024 4:40:20 AM | [NSO Update] Mindanao Grid-02/19/2024 04:45: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
2/19/2024 4:40:03 AM | [NSO Update] Visayas Grid-02/19/2024 04:40: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
2/19/2024 4:39:47 AM | [NSO Update] Luzon Grid-02/19/2024 04:40: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
2/19/2024 3:04:30 AM | Luzon Grid-02/19/2024 03:04: Quezon-Marilao 230kV line was restored at 0303H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2024 3:03:01 AM | Luzon Grid-02/19/2024 03:03: Marilao 300MVA T02(Customer Owned) was restored at 0300H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2024 2:59:08 AM | Luzon Grid-02/19/2024 02:59: Marilao 300MVA T01(Customer Owned) was restored at 0258H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2024 2:55:55 AM | Luzon Grid-02/19/2024 02:56: Hermosa-Marilao 230kV line was restored at 0253H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2024 12:53:02 AM | Mindanao Grid-02/19/2024 00:58: Baloi - Kauswagan 230kV Line 1 re-energized at 0050H (Planned Outage) [WEBSMS] | CMIN
2/19/2024 12:39:27 AM | Mindanao Grid-02/19/2024 00:44: Butuan - Placer 138kV Line 2 re-energized at 0037H (Planned Outage) [WEBSMS] | CMIN
2/18/2024 10:34:51 PM | Luzon Grid-02/18/2024 22:35: Caparispisan II 80MVA Main Transformer was energized at 2228H. (For 48 hours soaking) [WEBSMS] | CLUZ
2/18/2024 10:13:39 PM | Luzon Grid-02/18/2024 22:14: For info: Commissioning of Tayabas 600MVA T02 New M1 Protection and BFR completed at 2210H. [WEBSMS] | CLUZ
2/18/2024 10:05:33 PM | Luzon Grid-02/18/2024 22:05: Tayabas-Mauban 230kV Line 2 restored at 2204H (Planned Outage) [WEBSMS] | CLUZ
2/18/2024 9:52:28 PM | Luzon Grid-02/18/2024 21:52: Tayabas 600MVA T02 restored at 2150H. Ongoing commissioning of New M1 Protection and BFR (Planned Outage) [WEBSMS] | CLUZ
2/18/2024 9:24:10 PM | Luzon Grid-02/18/2024 21:24: For info: Energization of Caparispisan Phase 2 80MVA transformer as load at 2114H was unsuccessful (6-01CB04PWF tripped after closing). [WEBSMS] | CLUZ
2/18/2024 8:08:11 PM | Visayas Grid-02/18/2024 20:08: Colon-CVC 69kV line energized at 2005H. (Planned Outage) [WEBSMS] | CVIS
2/18/2024 7:52:26 PM | Visayas Grid-02/18/2024 19:52: Colon-Sibonga 69 KV line energized at 1949H. (Planned Outage) [WEBSMS] | CVIS
2/18/2024 7:07:27 PM | Luzon Grid-02/18/2024 19:07: Dona Imelda 300MVA T03 restored at 1907H (Planned Outage) [WEBSMS] | CLUZ
2/18/2024 7:03:14 PM | Mindanao Grid-02/18/2024 19:08: Bunawan - Nabunturan 138kV line re-energized at 1859H (Planned Outage) [WEBSMS] | CMIN
2/18/2024 6:13:53 PM | Mindanao Grid-02/18/2024 18:18: Kibawe - Tacurong 138KV Line re-energized at 1810H (Planned Outage). [WEBSMS] | CMIN
2/18/2024 6:01:30 PM | Mindanao Grid-02/18/2024 18:06: Kauswagan - GNPK 230kV Line 1 re-energized at 1759H (Planned outage). [WEBSMS] | CMIN
2/18/2024 5:51:32 PM | [NSO Update] Mindanao Grid-02/18/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3143MW, PK=2145MW, RR=72MW, NetOpMargin: EVE=926 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @33MW, AG6 @152MW, AG7 @29MW, PG4 @90MW [WEBSMS] | CMIN
2/18/2024 5:50:26 PM | [NSO Update] Visayas Grid-02/18/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2277MW, PK=1836MW, RR=83MW, NetOpMargin: EVE=358 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80MW, LEYTE A @350MW, PGPP1 @76MW [WEBSMS] | CVIS
2/18/2024 5:48:50 PM | [NSO Update] Luzon Grid-02/18/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13578MW, PK=9417MW, RR=287MW, NetOpMargin: EVE=3874 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @325MW, ILIJAN A @250MW, ILIJAN B @585MW [WEBSMS] | CLUZ
2/18/2024 2:13:41 PM | Luzon Grid-02/18/2024 14:14: Bayombong 230kV Bus 1 restored at 1413H (Planned Outage) [WEBSMS] | CLUZ
2/18/2024 1:56:36 PM | Mindanao Grid-02/18/2024 14:01: Kauswagan - GNPK 230kV Line 1 de-energized at 1352H. (Planned Outage). [WEBSMS] | CMIN
2/18/2024 1:28:01 PM | Mindanao Grid-02/18/2024 13:33: Kauswagan SS 230kV Bus 1 re-energized at 1326H (Planned Outage). [WEBSMS] | CMIN
2/18/2024 12:56:07 PM | [NSO Update] Mindanao Grid-02/18/2024 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3187MW, PK=1911MW, RR=74MW, NetOpMargin: PM=1202, EVE=965 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @33MW, AG6 @152MW, AG7 @29MW, PG4 @90MW [WEBSMS] | CMIN
2/18/2024 12:54:27 PM | [NSO Update] Visayas Grid-02/18/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2394MW, PK=1603MW, RR=81MW, NetOpMargin: PM=710, EVE=380 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @350MW, PGPP1 @76MW [WEBSMS] | CVIS
2/18/2024 12:52:46 PM | [NSO Update] Luzon Grid-02/18/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14479MW, PK=8762MW, RR=296MW, NetOpMargin: PM=5422, EVE=3877 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, MSLC1 @325MW, ILIJAN A @250MW, ILIJAN B @585MW [WEBSMS] | CLUZ
2/18/2024 12:45:52 PM | Mindanao Grid-02/18/2024 12:50: Maramag - Pulangi 4 138kV Line 1 energized at 1219H (Planned Outage). [WEBSMS] | CMIN
2/18/2024 12:23:24 PM | Mindanao Grid-02/18/2024 12:28: Pulangi 4 Unit #1 HEPP online at 1218H. Planned Outage. [WEBSMS] | CMIN
2/18/2024 11:58:01 AM | Mindanao Grid-02/18/2024 12:03: Maramag - Kibawe 138kV Line 1 re-energized at 1154H (Planned Outage) [WEBSMS] | CMIN
2/18/2024 9:31:57 AM | Mindanao Grid-02/18/2024 09:36: Kauswagan SS 230kV Bus 1 de-energized at 0923H (Planned Outage). [WEBSMS] | CMIN
2/18/2024 8:25:40 AM | Luzon Grid-02/18/2024 08:26: Olongapo 230kV Bus 1 restored at 0824H (Planned Outage) [WEBSMS] | CLUZ
2/18/2024 8:15:41 AM | Mindanao Grid-02/18/2024 08:20: Maramag - Kibawe 138kV Line 1 de-energized 0810H (Planned Outage). [WEBSMS] | CMIN
2/18/2024 8:06:58 AM | Mindanao Grid-02/18/2024 08:11: Lamsan Biomass Online at 0800H. Planned Outage. [WEBSMS] | CMIN
2/18/2024 7:52:16 AM | Mindanao Grid-02/18/2024 07:57: Lamsan Biomass shutdown at 0700H. Planned Outage. [WEBSMS] | CMIN
2/18/2024 7:48:14 AM | Mindanao Grid-02/18/2024 07:53: Maramag - Pulangi 4 138kV Line 1 de-energized at 0734H (Planned Outage) [WEBSMS] | CMIN
2/18/2024 7:47:45 AM | Mindanao Grid-02/18/2024 07:52: Pulangi 4 U1shutdown at 0734H. Planned Outage. [WEBSMS] | CMIN
2/18/2024 7:38:39 AM | Luzon Grid-02/18/2024 07:39: Dona Imelda 300MVA T03 de-energized at 0738H (Planned Outage) [WEBSMS] | CLUZ
2/18/2024 7:25:42 AM | Luzon Grid-02/18/2024 07:26: Tayabas 600MVA T02 de-energized at 0724H (Planned Outage) [WEBSMS] | CLUZ
2/18/2024 7:19:08 AM | Luzon Grid-02/18/2024 07:19: GMEC 1 online at 0715H (Unplanned Outage) [WEBSMS] | CLUZ
2/18/2024 7:17:05 AM | Luzon Grid-02/18/2024 07:17: Tayabas-Mauban 230kV Line 2 de-energized at 0716H (Planned Outage) [WEBSMS] | CLUZ
2/18/2024 7:06:59 AM | Visayas Grid-02/18/2024 07:07: Colon-Sibonga 69 KV line de-energized at 0706H (Planned Outage) [WEBSMS] | CVIS
2/18/2024 7:05:56 AM | Luzon Grid-02/18/2024 07:06: Bayombong 230kV Bus 1 de-energized at 0704H (Planned Outage) [WEBSMS] | CLUZ
2/18/2024 6:50:32 AM | Mindanao Grid-02/18/2024 06:55: Bunawan - Nabunturan 138kV Line shutdown at 0643H (Planned Outage). [WEBSMS] | CMIN
2/18/2024 6:30:24 AM | Mindanao Grid-02/18/2024 06:35: Baloi-Kauswagan de-energized 230kV Line 1 0622H (Planned Outage). [WEBSMS] | CMIN
2/18/2024 6:02:41 AM | [NSO Update] Luzon Grid-02/18/2024 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14706MW, PK=8529MW, RR=295MW, NetOpMargin: AM=5883, PM=5453, EVE=3819 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, ILIJAN A @250MW, MSLC1 @325MW [WEBSMS] | CLUZ
2/18/2024 5:56:52 AM | Mindanao Grid-02/18/2024 06:01: Kibawe - Tacurong 138KV Line shutdown at 0549H (Planned Outage) [WEBSMS] | CMIN
2/18/2024 5:49:33 AM | [NSO Update] Mindanao Grid-02/18/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3184MW, PK=1756MW, RR=72MW, NetOpMargin: AM=1355, PM=1331, EVE=1178 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @33MW, AG6 @152MW, AG7 @29MW, PG4 @60MW [WEBSMS] | CMIN
2/18/2024 5:38:49 AM | [NSO Update] Visayas Grid-02/18/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2589MW, PK=1695MW, RR=79MW, NetOpMargin: AM=814, PM=685, EVE=242 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80MW, LEYTE A @350MW, PGPP1 @76MW [WEBSMS] | CVIS
2/18/2024 5:36:41 AM | Mindanao Grid-02/18/2024 05:41: Butuan - Placer 138KV Line 2 shutdown at 0531H (Planned Outage) [WEBSMS] | CMIN
2/18/2024 5:10:13 AM | Luzon Grid-02/18/2024 05:10: Olongapo SS 230kV Bus 1 de-energized at 0510H (Planned Outage) [WEBSMS] | CLUZ
2/18/2024 4:22:17 AM | [NSO Update] Luzon Grid-02/18/2024 04:22: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
2/18/2024 4:20:41 AM | [NSO Update] Mindanao Grid-02/18/2024 04:25: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
2/18/2024 4:20:04 AM | [NSO Update] Visayas Grid-02/18/2024 04:20: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
2/18/2024 3:36:33 AM | Mindanao Grid-02/18/2024 03:41: Mt. Apo 3 online at 0319H from PMS (GOMP). [WEBSMS] | CMIN
2/18/2024 12:21:04 AM | Luzon Grid-02/18/2024 00:21: Duhat-Hermosa 230kV Line de-energized at 0021H (Planned Outage) [WEBSMS] | CLUZ
2/18/2024 12:14:52 AM | Luzon Grid-02/18/2024 00:15: Quezon-Duhat 230kV Line de-energized at 0014H (Planned Outage) [WEBSMS] | CLUZ
2/18/2024 12:05:16 AM | Visayas Grid-02/18/2024 00:05: PCPC shutdown at 0001H (Planned Outage) [WEBSMS] | CVIS
2/17/2024 9:34:58 PM | Mindanao Grid-02/17/2024 21:39: Butuan - SS 138KV Bus 1 re-energized at 2132H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 9:26:25 PM | Mindanao Grid-02/17/2024 21:31: Kidapawan - Mt, Apo 3 69kv Line re-energized at 2124H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 9:11:17 PM | Luzon Grid-02/17/2024 21:11: Binan SS 300MVA T02 restored at 2111H (Planned Outage) [WEBSMS] | CLUZ
2/17/2024 8:21:21 PM | Visayas Grid-02/17/2024 20:21: URC U1 cut in at 2018H. (Unplanned Outage) [WEBSMS] | CVIS
2/17/2024 8:19:08 PM | Visayas Grid-02/17/2024 20:19: URC U1 emergency shutdown at 2013H. (Unplanned Outage) [WEBSMS] | CVIS
2/17/2024 7:19:06 PM | Mindanao Grid-02/17/2024 19:24: Baloi - Lugait 138KV Line re-energized/looped at 1917H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 7:08:05 PM | Luzon Grid-02/17/2024 19:08: San Jose 750MVA T05 restored at 1907H (Planned Outage) [WEBSMS] | CLUZ
2/17/2024 6:08:16 PM | [NSO Update] Luzon Grid-02/17/2024 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13057MW, PK=9790MW, RR=396MW, NetOpMargin: EVE=2871 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, ILIJAN A @250MW, MSLC1 @325MW [WEBSMS] | CLUZ
2/17/2024 5:58:44 PM | Mindanao Grid-02/17/2024 18:03: TM1 U1 shutdown at 1732H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
2/17/2024 5:55:45 PM | [NSO Update] Mindanao Grid-02/17/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3143MW, PK=2120MW, RR=70.3MW, NetOpMargin: EVE=953 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @34MW, AG6 @152MW, AG7 @29MW, PG4 @90MW [WEBSMS] | CMIN
2/17/2024 5:48:54 PM | [NSO Update] Visayas Grid-02/17/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2523MW, PK=1995MW, RR=83MW, NetOpMargin: EVE=446 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80MW, LEYTE A @348MW, PGPP1 @76MW [WEBSMS] | CVIS
2/17/2024 5:40:26 PM | Mindanao Grid-02/17/2024 17:45: Bunawan SS 230KV 300MVA Transformer 1 re-energized at 1722H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 5:34:32 PM | Mindanao Grid-02/17/2024 17:39: San Francisco 138KV (50MVA) transformer 1 re-energized at 1708H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 5:25:15 PM | Mindanao Grid-02/17/2024 17:30: Bunawan SS 230kv 300MVA Transformer re-energized/looped at 1722H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 5:19:51 PM | Mindanao Grid-02/17/2024 17:24: San Francisco SS 138KV 50MVA Transformer re-energized at 1708H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 5:09:57 PM | Mindanao Grid-02/17/2024 17:14: Tacurong - Gensan 138KV Line 2 re-energized/looped at 1701H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 4:36:09 PM | Luzon Grid-02/17/2024 16:36: Correction: Binan SS 300MVA T02 de-energized at 1627H (Planned Outage) [WEBSMS] | CLUZ
2/17/2024 4:28:28 PM | Luzon Grid-02/17/2024 16:28: Binan SS 300MVA T03 restored at 1627H (Planned Outage) [WEBSMS] | CLUZ
2/17/2024 4:19:18 PM | Mindanao Grid-02/17/2024 16:24: TM1 U1 Online at 1603H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
2/17/2024 3:55:07 PM | Luzon Grid-02/17/2024 15:55: Tayabas-Mauban 230kV Line 1 restored at 1555H (Planned Outage) [WEBSMS] | CLUZ
2/17/2024 3:28:13 PM | Luzon Grid-02/17/2024 15:28: Binan SS 300MVA T03 restored at 1527H (Planned Outage) [WEBSMS] | CLUZ
2/17/2024 3:14:37 PM | Mindanao Grid-02/17/2024 15:19: Lugait - Opol 138KV line re-energized/looped at 1512H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 3:07:43 PM | Mindanao Grid-02/17/2024 15:12: Lugait - Opol 138KV Line shutdown at 1505H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 3:05:03 PM | Luzon Grid-02/17/2024 15:05: Bayombong SS 230kV Bus 2 restored at 1504H (Planned Outage) [WEBSMS] | CLUZ
2/17/2024 1:10:26 PM | Mindanao Grid-02/17/2024 13:15: PULANGI 4 Unit 3 online at 1303H. From shutdown affected by P&E request. [WEBSMS] | CMIN
2/17/2024 12:39:45 PM | [NSO Update] Mindanao Grid-02/17/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3205MW, PK=2037MW, RR=75MW, NetOpMargin: PM=1093, EVE=1006 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @34MW, AG6 @152MW, AG7 @29MW, PG4 @90MW [WEBSMS] | CMIN
2/17/2024 12:37:55 PM | [NSO Update] Visayas Grid-02/17/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2662MW, PK=1923MW, RR=81MW, NetOpMargin: PM=658, EVE=493 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80MW, LEYTE A @342MW, PGPP1 @76MW [WEBSMS] | CVIS
2/17/2024 12:36:04 PM | [NSO Update] Luzon Grid-02/17/2024 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14014MW, PK=8999MW, RR=400MW, NetOpMargin: PM=4615, EVE=3787 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, ILIJAN A @165MW [WEBSMS] | CLUZ
2/17/2024 11:27:16 AM | Mindanao Grid-02/17/2024 11:32: TM1 U1 declared available at 1030H from PMS (GOMP). [WEBSMS] | CMIN
2/17/2024 10:12:54 AM | Luzon Grid-02/17/2024 10:13: Binan SS 300MVA T03 de-energized at 1011H (Planned Outage) [WEBSMS] | CLUZ
2/17/2024 9:45:03 AM | Mindanao Grid-02/17/2024 09:49: Lugait - Opol 138KV Line re-energized/looped at 0938H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 9:40:54 AM | Luzon Grid-02/17/2024 09:41: Lal-lo-Cagayan North Solar 69kV line 1 & 2 restored at 0940H. (Unplanned Outage) [WEBSMS] | CLUZ
2/17/2024 9:37:32 AM | Luzon Grid-02/17/2024 09:37: Lal-lo-Magapit BESS 69kV line restored at 0936H (Unplanned Outage) [WEBSMS] | CLUZ
2/17/2024 9:25:10 AM | Mindanao Grid-02/17/2024 09:30: PULANGI 4 Unit 3 shutdown at 0902H. Affected by P&E request. [WEBSMS] | CMIN
2/17/2024 9:24:55 AM | Mindanao Grid-02/17/2024 09:29: Baloi - Lugait deenergized at at 0920H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 9:23:23 AM | Mindanao Grid-02/17/2024 09:28: Lugait - Opol 138KV Line shutdown at 0916H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 8:57:14 AM | Mindanao Grid-02/17/2024 09:02: Tacurong - Gensan 138KV Line 2 shutdown at 0851H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 8:55:19 AM | Mindanao Grid-02/17/2024 09:00: Bunawan SS 230KV 300MVA Transformer 1 shutdown at 0836H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 8:02:17 AM | Luzon Grid-02/17/2024 08:02: Bayombong SS 230kV Bus 2 de-energized at 0801H (Planned Outage) [WEBSMS] | CLUZ
2/17/2024 6:54:06 AM | Luzon Grid-02/17/2024 06:54: Tayabas-Mauban 230kV Line 1 de-energized at 0654H (Planned Outage) [WEBSMS] | CLUZ
2/17/2024 6:42:45 AM | Mindanao Grid-02/17/2024 06:47: San Francisco SS 50MVA Transformer ! shutdown at 0636H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 6:19:24 AM | Mindanao Grid-02/17/2024 06:24: Tagoloan - Villanueva 138KV Line 1 re-energized at 0539H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 6:10:00 AM | Luzon Grid-02/17/2024 06:10: Lal-lo-Cagayan North Solar 69kV line 1 & 2 de-energized at 0608H and 0609H, respectively (Unplanned Outage) [WEBSMS] | CLUZ
2/17/2024 6:09:06 AM | Mindanao Grid-02/17/2024 06:14: Butuan SS 138KV Bus 1 shutdown at 0604H (Planned Outage) [WEBSMS] | CMIN
2/17/2024 6:02:56 AM | Luzon Grid-02/17/2024 06:03: Lal-lo-Magapit BESS 69kV line de-energized at 0602H (Unplanned Outage) [WEBSMS] | CLUZ
2/17/2024 5:56:55 AM | [NSO Update] Mindanao Grid-02/17/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3214MW, PK=1923MW, RR=72MW, NetOpMargin: AM=1219, PM=1086, EVE=978 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @34MW, AG6 @152MW, AG7 @29MW, PG4 @90MW [WEBSMS] | CMIN
2/17/2024 5:54:42 AM | [NSO Update] Visayas Grid-02/17/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2519MW, PK=1834MW, RR=83MW, NetOpMargin: AM=602, PM=621, EVE=383 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80MW, LEYTE A @342MW, PGPP1 @76MW [WEBSMS] | CVIS
2/17/2024 5:50:28 AM | [NSO Update] Luzon Grid-02/17/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14109MW, PK=9536MW, RR=393MW, NetOpMargin: AM=4180, PM=3706, EVE=2767 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, ILIJAN A @165MW [WEBSMS] | CLUZ
2/17/2024 5:50:24 AM | Luzon Grid-02/17/2024 05:50: Binan - Southwoods 115kV Line restored at 0550H (Planned Outage) [WEBSMS] | CLUZ
2/17/2024 5:35:00 AM | Luzon Grid-02/17/2024 05:35: GMEC 1 with 130MW load tripped at 0529H. Lowest Frequency dip is 59.65Hz (Unplanned Outage) [WEBSMS] | CLUZ
2/17/2024 5:19:49 AM | Luzon Grid-02/17/2024 05:20: San Jose 750MVA T05 de-energized at 0519H (Planned Outage) [WEBSMS] | CLUZ
2/17/2024 4:58:40 AM | [NSO Update] Mindanao Grid-02/17/2024 05:03: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
2/17/2024 4:58:24 AM | [NSO Update] Visayas Grid-02/17/2024 04:58: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
2/17/2024 4:57:54 AM | [NSO Update] Luzon Grid-02/17/2024 04:58: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
2/17/2024 4:21:34 AM | Mindanao Grid-02/17/2024 04:26: Tagoloan - Villanueva 138kV Line 1 shutdown at 0418H (Planned Outage). [WEBSMS] | CMIN
2/17/2024 3:31:48 AM | Luzon Grid-02/17/2024 03:32: Binan - Southwoods 115kV Line de-energized at 0331H (Planned Outage) [WEBSMS] | CLUZ
2/16/2024 11:44:19 PM | Visayas Grid-02/16/2024 23:44: PEDC U1 cut in at 2343H (Planned Outage) [WEBSMS] | CVIS
2/16/2024 11:35:34 PM | Luzon Grid-02/16/2024 23:35: Binan-San Pedro 115kV Line restored at 2335H (Planned Outage) [WEBSMS] | CLUZ
2/16/2024 10:48:29 PM | Mindanao Grid-02/16/2024 22:53: Mt. Apo U2 Online at 2226H from Forced Outage. Unplanned Outage. [WEBSMS] | CMIN
2/16/2024 10:08:53 PM | Luzon Grid-02/16/2024 22:09: San Jose-Angat 115kV line 3 energized at 2206H at San Jose side (Planned Outage) [WEBSMS] | CLUZ
2/16/2024 9:18:18 PM | Luzon Grid-02/16/2024 21:18: Binan-San Pedro 115kV Line de-energized at 2117H (Planned Outage) [WEBSMS] | CLUZ
2/16/2024 5:59:47 PM | [NSO Update] Mindanao Grid-02/16/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3044MW, PK=2093MW, RR=70.3MW, NetOpMargin: EVE=880 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @34MW, AG6 @152MW, AG7 @29MW, PG4 @90MW [WEBSMS] | CMIN
2/16/2024 5:56:58 PM | [NSO Update] Visayas Grid-02/16/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2466MW, PK=2043MW, RR=83MW, NetOpMargin: EVE=340 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @342MW, PGPP1 @76MW [WEBSMS] | CVIS
2/16/2024 5:53:35 PM | [NSO Update] Luzon Grid-02/16/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13167MW, PK=10135MW, RR=406MW, NetOpMargin: EVE=2626 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CALACA 2 @180MW, GMEC 1 @150MW, ILIJAN A @165MW [WEBSMS] | CLUZ
2/16/2024 5:15:53 PM | Mindanao Grid-02/16/2024 17:20: WMPC DG04 shutdown at 1714H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/16/2024 2:27:08 PM | Luzon Grid-02/16/2024 14:27: Subic 230kV Bus 1 restored at 1418H (Planned Outage) [WEBSMS] | CLUZ
2/16/2024 1:22:11 PM | Luzon Grid-02/16/2024 13:22: Subic SS 230kV Bus 1 de-energized at 1320H (Planned Outage) [WEBSMS] | CLUZ
2/16/2024 1:09:26 PM | Mindanao Grid-02/16/2024 13:14: WMPC DG04 online at 1306H. RPS - System Voltage Requirement [WEBSMS] | CMIN
2/16/2024 12:59:01 PM | [NSO Update] Luzon Grid-02/16/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14302MW, PK=10640MW, RR=428MW, NetOpMargin: PM=3234, EVE=2624 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CALACA 2 @180MW, GMEC 1 @150MW, MASINLOC 1 @325MW, ILIJAN A @250MW [WEBSMS] | CLUZ
2/16/2024 12:55:01 PM | [NSO Update] Mindanao Grid-02/16/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3093MW, PK=2218MW, RR=38MW, NetOpMargin: PM=836, EVE=840 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @34MW, AG6 @152MW, AG7 @29MW, PG4 @90MW [WEBSMS] | CMIN
2/16/2024 12:53:15 PM | [NSO Update] Visayas Grid-02/16/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2563MW, PK=2089MW, RR=87MW, NetOpMargin: PM=388, EVE=352 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @342MW, PGPP1 @76MW [WEBSMS] | CVIS
2/16/2024 12:10:52 PM | Mindanao Grid-02/16/2024 12:15: ASIGA HEPP online at 0716H. Unplanned Outage. [WEBSMS] | CMIN
2/16/2024 11:52:48 AM | Mindanao Grid-02/16/2024 11:57: Corrected: Mt Apo U2 with 40MW gross generation manually out at 1117H due to malfunction of Governor Right hand Valve. Frequency Dipped=59.807Hz. Unplanned Outage. [WEBSMS] | CMIN
2/16/2024 11:51:36 AM | Mindanao Grid-02/16/2024 11:56: Mt Apo U3 with 40MW gross generation manually out at 1117H due to malfunction of Governor Right hand Valve. Frequency Dipped=59.807Hz. Unplanned Outage. [WEBSMS] | CMIN
2/16/2024 10:55:25 AM | Luzon Grid-02/16/2024 10:55: San Lorenzo Module 60 online at 1053H (LNG Commissioning) [WEBSMS] | CLUZ
2/16/2024 10:48:17 AM | Visayas Grid-02/16/2024 10:48: 230KV Cebu - Magdugo line 2 looped @ Cebu side at 1046H. ( Planned Outage ) [WEBSMS] | CVIS
2/16/2024 10:37:45 AM | Visayas Grid-02/16/2024 10:38: 230KV Cebu - Magdugo line 2 energized at 1034H. ( Planned Outage ) [WEBSMS] | CVIS
2/16/2024 9:56:20 AM | Luzon Grid-02/16/2024 09:56: Ilijan GT2-1 online at 0955H (Unplanned Outage) [WEBSMS] | CLUZ
2/16/2024 9:28:25 AM | Luzon Grid-02/16/2024 09:28: Lal-lo-Cagayan North Solar 69kV line 1(CO) restored at 0926H (Unplanned Outage) [WEBSMS] | CLUZ
2/16/2024 8:45:41 AM | Luzon Grid-02/16/2024 08:46: Lal-lo-Cagayan North Solar 69kV line 2(CO) restored at 0842H (Unplanned Outage) [WEBSMS] | CLUZ
2/16/2024 8:38:37 AM | Luzon Grid-02/16/2024 08:38: Lal-lo-Magapit BESS 69kV line restored at 0836H (Unplanned Outage) [WEBSMS] | CLUZ
2/16/2024 8:13:11 AM | Luzon Grid-02/16/2024 08:13: Ilijan GT2-1 (177MW) tripped at 0806H. Lowest system frequency was 59.698Hz. [WEBSMS] | CLUZ
2/16/2024 7:15:14 AM | Mindanao Grid-02/16/2024 07:20: ASIGA HEPP with 6.5MW gross generation tripped at 0650H. Indication: To be determined. Unplanned Outage. [WEBSMS] | CMIN
2/16/2024 6:00:55 AM | Luzon Grid-02/16/2024 06:01: Lal-lo-Magapit BESS 69kV line was de-energized at 0556H. (Unplanned Outage) [WEBSMS] | CLUZ
2/16/2024 5:59:27 AM | Luzon Grid-02/16/2024 05:59: Lal-lo-Cagayan North Solar 69kV line 1(CO) and Lal-lo-Cagayan North Solar 69kV line 2(CO) were de-energized at 0552H and 0554H respectively. (Unplanned Outage) [WEBSMS] | CLUZ
2/16/2024 5:51:07 AM | [NSO Update] Luzon Grid-02/16/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14368MW, PK=10506MW, RR=422MW, NetOpMargin: AM=3440, PM=3034, EVE=2501 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @180MW, GMEC 1 @150MW, ILIJAN A @295MW, ILIJAN B @479MW [WEBSMS] | CLUZ
2/16/2024 5:37:30 AM | [NSO Update] Mindanao Grid-02/16/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3166MW, PK=2105MW, RR=38MW, NetOpMargin: AM=1023, PM=992, EVE=940 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @34MW, AG6 @152MW, AG7 @29MW, PG4 @90MW [WEBSMS] | CMIN
2/16/2024 5:35:22 AM | [NSO Update] Visayas Grid-02/16/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2710MW, PK=2076MW, RR=83MW, NetOpMargin: AM=551, PM=432, EVE=328 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80.5MW, LEYTE A @342MW, PGPP1 @76MW [WEBSMS] | CVIS
2/16/2024 5:32:54 AM | Luzon Grid-02/16/2024 05:33: For info: Ilijan GT1-2 shutdown at 0125H. (Unplanned Outage) [WEBSMS] | CLUZ
2/16/2024 4:42:46 AM | [NSO Update] Mindanao Grid-02/16/2024 04:46: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
2/16/2024 4:42:33 AM | [NSO Update] Visayas Grid-02/16/2024 04:42: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
2/16/2024 4:42:16 AM | [NSO Update] Luzon Grid-02/16/2024 04:42: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
2/16/2024 1:27:04 AM | Luzon Grid-02/16/2024 01:27: Laoag - Pasuquin Solar 115kV Line (Customer Owned) restored at 0123H (Unplanned Outage requested by Pasuquin Solar) [WEBSMS] | CLUZ
2/16/2024 12:08:00 AM | Luzon Grid-02/16/2024 00:08: GNPD Unit 2 shutdown at 0007H. (Planned Outage) [WEBSMS] | CLUZ
2/15/2024 11:44:08 PM | Luzon Grid-02/15/2024 23:44: Ilijan GT2-1 online at 2342H. (Planned Outage) [WEBSMS] | CLUZ
2/15/2024 10:06:47 PM | Luzon Grid-02/15/2024 22:07: San Lorenzo Module 60 shutdown at 2201H (Part of LNG Commissioning) [WEBSMS] | CLUZ
2/15/2024 9:37:05 PM | Visayas Grid-02/15/2024 21:37: Cebu GIS 300 MVA 230/138/13.8 kV TR3 closed loop at 2134H. [WEBSMS] | CVIS
2/15/2024 8:35:08 PM | Luzon Grid-02/15/2024 20:35: Angat HEPP Auxiliary Units Main Transformer(Transformer No. 3) was energized at 2033H.(Planned Outage) [WEBSMS] | CLUZ
2/15/2024 8:27:07 PM | Luzon Grid-02/15/2024 20:27: Angat HEPP 115kV Bus 1 was energized at 2026H. (Planned Outage) [WEBSMS] | CLUZ
2/15/2024 8:22:18 PM | Luzon Grid-02/15/2024 20:22: Correction of line name: San Jose-Angat 115kV line 1 was looped at Angat side at 2003H. (Unplanned Outage) [WEBSMS] | CLUZ
2/15/2024 8:14:17 PM | Luzon Grid-02/15/2024 20:14: San Jose-Angat 115kV line 3 was restored at 2003H. (Unplanned Outage) [WEBSMS] | CLUZ
2/15/2024 7:34:56 PM | Luzon Grid-02/15/2024 19:35: Caparispisan II Main Transformer was attempted to be energized but auto-tripped at 1923H. (On-going commissioning and energization) [WEBSMS] | CLUZ
2/15/2024 7:04:39 PM | Luzon Grid-02/15/2024 19:04: Laoag-Pasuquin Solar 115kV line(Customer Owned) was de-energized at 1902H. (Unplanned Outage requested by Pasuquin Solar) [WEBSMS] | CLUZ
2/15/2024 6:03:45 PM | [NSO Update] Luzon Grid-02/15/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13918MW, PK=10337MW, RR=407MW, NetOpMargin: EVE=3174 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @180MW, ILIJAN A @585MW, ILIJAN B @165MW [WEBSMS] | CLUZ
2/15/2024 5:33:10 PM | [NSO Update] Mindanao Grid-02/15/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3141MW, PK=2161MW, RR=38MW, NetOpMargin: EVE=942 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @33MW, AG6 @152MW, AG7 @29MW, PG4 @135MW [WEBSMS] | CMIN
2/15/2024 5:30:16 PM | [NSO Update] Visayas Grid-02/15/2024 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2468MW, PK=2069MW, RR=82MW, NetOpMargin: EVE=317 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @81MW, LEYTE A @268MW, PGPP1 @76MW [WEBSMS] | CVIS
2/15/2024 4:44:51 PM | Visayas Grid-02/15/2024 16:45: EDC-Mahanagdong A U1 tripped at 1634H. (Unplanned Outage) [WEBSMS] | CVIS
2/15/2024 3:53:10 PM | Visayas Grid-02/15/2024 15:53: Sangi - 2nd Lift 34.5 kV Line energized at 1551H. (Unplanned Outage) [WEBSMS] | CVIS
2/15/2024 3:21:02 PM | Luzon Grid-02/15/2024 15:21: San Lorenzo Module 50 synchronized at 1516H. (Unplanned Outage) [WEBSMS] | CLUZ
2/15/2024 2:16:59 PM | Luzon Grid-02/15/2024 14:17: GMEC Unit 1 synchronized at 1410H. (Unplanned Outage) [WEBSMS] | CLUZ
2/15/2024 1:52:34 PM | Luzon Grid-02/15/2024 13:52: For information: San Lorenzo 50 tripped at 1349H (Unplanned Outage - Ongoing LNG Commissioning) [WEBSMS] | CLUZ
2/15/2024 1:47:38 PM | Luzon Grid-02/15/2024 13:47: For information: San Lorenzo 50 online at 1302H (Unplanned Outage-LNG Commissioning) [WEBSMS] | CLUZ
2/15/2024 12:56:49 PM | [NSO Update] Mindanao Grid-02/15/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3206MW, PK=2250MW, RR=38MW, NetOpMargin: PM=917, EVE=952 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @33MW, AG6 @152MW, AG7 @29MW, PG4 @135MW [WEBSMS] | CMIN
2/15/2024 12:52:52 PM | [NSO Update] Visayas Grid-02/15/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2572MW, PK=2175MW, RR=82MW, NetOpMargin: PM=315, EVE=285 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @81MW, LEYTE A @292MW, PGPP1 @76MW [WEBSMS] | CVIS
2/15/2024 12:46:19 PM | [NSO Update] Luzon Grid-02/15/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14694MW, PK=10838MW, RR=424MW, NetOpMargin: PM=3432, EVE=2913 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @180MW, ILIJAN A @585MW, ILIJAN B @165MW [WEBSMS] | CLUZ
2/15/2024 9:08:00 AM | Mindanao Grid-02/15/2024 09:11: SEDI EEI Unit No.1 online at 0846H. For Generating Unit Capability Test(GUCT). Follow RTD. [WEBSMS] | CMIN
2/15/2024 9:06:32 AM | Luzon Grid-02/15/2024 09:06: MPGC Unit 3 successfully conducted 25% (38MW) Load Rejection Test at 0904H. (On-going commissioning test) [WEBSMS] | CLUZ
2/15/2024 8:47:05 AM | Visayas Grid-02/15/2024 08:47: Sangi-2nd lift 34.5KV T/L de-energized at 0829H. (Unplanned Outage) [WEBSMS] | CVIS
2/15/2024 8:22:35 AM | Luzon Grid-02/15/2024 08:22: Angat HEPP 115kV Bus 1 de-energized at 0820H. (Planned Outage) [WEBSMS] | CLUZ
2/15/2024 7:33:00 AM | Luzon Grid-02/15/2024 07:33: Angat-San Jose 115kV Line 4 restored at 0727H. (Unplanned Outage) [WEBSMS] | CLUZ
2/15/2024 6:53:35 AM | Luzon Grid-02/15/2024 06:53: Laoag SS 300MVA T01 restored at 0653H. (Planned Outage) [WEBSMS] | CLUZ
2/15/2024 5:37:25 AM | [NSO Update] Mindanao Grid-02/15/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3165MW, PK=2147MW, RR=38MW, NetOpMargin: AM=980, PM=958, EVE=1139 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @84MW, AG4 @104MW, AG5 @33MW, AG6 @152MW, AG7 @29MW, PG4 @135MW [WEBSMS] | CMIN
2/15/2024 5:35:28 AM | [NSO Update] Visayas Grid-02/15/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2520MW, PK=2057MW, RR=82MW, NetOpMargin: AM=381, PM=349, EVE=342 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80.5MW, LEYTE A @302MW, PGPP1 @76MW [WEBSMS] | CVIS
2/15/2024 5:33:40 AM | [NSO Update] Luzon Grid-02/15/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14590MW, PK=10236MW, RR=410MW, NetOpMargin: AM=3944, PM=3312, EVE=3116 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @180MW, ILIJAN A @585MW, ILIJAN B @165MW [WEBSMS] | CLUZ
2/15/2024 4:14:12 AM | [NSO Update] Mindanao Grid-02/15/2024 04:18: Weather Update: Easterlies affecting the eastern section of Visayas and Mindanao. Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
2/15/2024 4:13:39 AM | [NSO Update] Visayas Grid-02/15/2024 04:13: Weather Update: Easterlies affecting the eastern section of Visayas and Mindanao. Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
2/15/2024 4:13:14 AM | [NSO Update] Luzon Grid-02/15/2024 04:13: Weather Update: Easterlies affecting the eastern section of Visayas and Mindanao. Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
2/15/2024 4:06:50 AM | Luzon Grid-02/15/2024 04:07: Laoag SS 300MVA T01 de-energized at 0406H (Planned Outage) [WEBSMS] | CLUZ
2/15/2024 1:29:56 AM | Luzon Grid-02/15/2024 01:30: Cayanga Solar Plant 230kV Bus 2 energized at 0128H (Planned Outage) [WEBSMS] | CLUZ
2/15/2024 12:49:09 AM | Mindanao Grid-02/15/2024 00:53: Kidapawan- Mt. Apo 3 69kV Line de-energized at 0034H (Planned Outage). [WEBSMS] | CMIN
2/15/2024 12:18:06 AM | Mindanao Grid-02/15/2024 00:21: Mt. Apo 3 shutdown at 0014H (Planned Outage, GOMP) [WEBSMS] | CMIN
2/15/2024 12:00:54 AM | Luzon Grid-02/15/2024 00:01: Angat-San Jose 115kV Line 4 tripped at 2357H (Unplanned Outage) [WEBSMS] | CLUZ
2/14/2024 10:33:54 PM | Luzon Grid-02/14/2024 22:34: Cayanga Solar Plant 230kV Bus 2 de-energized at 2233H (Planned Outage) [WEBSMS] | CLUZ
2/14/2024 10:29:19 PM | Luzon Grid-02/14/2024 22:29: Cayanga Solar Plant 230kV Bus 1 energized at 2228H (Planned Outage) [WEBSMS] | CLUZ
2/14/2024 10:09:12 PM | Luzon Grid-02/14/2024 22:09: San Lorenzo 50 shutdown at 2207H (Unplanned Outage-LNG Commissioning) [WEBSMS] | CLUZ
2/14/2024 9:26:29 PM | Mindanao Grid-02/14/2024 21:30: SEDI (13MAGDBNK_G01) shutdown at 1819H. End of Capability Test. [WEBSMS] | CMIN
2/14/2024 9:22:13 PM | Visayas Grid-02/14/2024 21:22: Cebu SS 230 KV 300MVA TR3 energized at 2120H for soaking. (Planned Outage) [WEBSMS] | CVIS
2/14/2024 9:21:18 PM | Mindanao Grid-02/14/2024 21:25: WMPC DG10 shutdown at 2114H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/14/2024 6:34:03 PM | Luzon Grid-02/14/2024 18:34: Lal-lo-Cagayan North Solar 69kV line 2(Customer Owned) energized (looped) at Cagayan Solar at 1829H (Unplanned Outage) [WEBSMS] | CLUZ
2/14/2024 6:17:35 PM | Luzon Grid-02/14/2024 18:17: Cayanga Solar Plant 230kV Bus 1 de-energized at 1815H (Planned Outage) [WEBSMS] | CLUZ
2/14/2024 5:59:31 PM | Mindanao Grid-02/14/2024 18:03: Correction: Maco-Therma Marine 138kV L2 energized at 1441H (Planned Outage). P&E Requested shutdown. [WEBSMS] | CMIN
2/14/2024 5:40:08 PM | [NSO Update] Mindanao Grid-02/14/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3171MW, PK=2229MW, RR=72MW, NetOpMargin: EVE=870 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @88MW, AG4 @106MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @144MW [WEBSMS] | CMIN
2/14/2024 5:39:52 PM | Mindanao Grid-02/14/2024 17:43: Agus 6 SS 138kV Bus #1 re-energized at 1724H (Planned Outage). Non-GOMP. P&E Requested activity MSE4P under Schedule 3. [WEBSMS] | CMIN
2/14/2024 5:38:27 PM | [NSO Update] Visayas Grid-02/14/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2523MW, PK=2064MW, RR=87MW, NetOpMargin: EVE=373 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80.5MW, LEYTE A @282MW, PGPP1 @76MW [WEBSMS] | CVIS
2/14/2024 5:38:02 PM | Luzon Grid-02/14/2024 17:38: Tayabas-San Jose 500kV line 2 energized at 1731H (Planned Outage) [WEBSMS] | CLUZ
2/14/2024 5:36:47 PM | [NSO Update] Luzon Grid-02/14/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14026MW, PK=10088MW, RR=407MW, NetOpMargin: EVE=3531 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @180MW, ILIJAN A @585MW, ILIJAN B @165MW [WEBSMS] | CLUZ
2/14/2024 4:11:00 PM | Mindanao Grid-02/14/2024 16:14: WMPC DG03 shutdown at 1609H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/14/2024 1:13:42 PM | Luzon Grid-02/14/2024 13:13: Sta. Rita 30 online at 1310H (Unplanned Outage-LNG Commissioning) [WEBSMS] | CLUZ
2/14/2024 1:11:41 PM | [NSO Update] Mindanao Grid-02/14/2024 13:15: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3222MW, PK=2259MW, RR=74MW, NetOpMargin: PM=889, EVE=933 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @88MW, AG4 @106MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @144MW [WEBSMS] | CMIN
2/14/2024 1:10:03 PM | [NSO Update] Visayas Grid-02/14/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2598MW, PK=2061MW, RR=84MW, NetOpMargin: PM=453, EVE=298 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80.5MW, LEYTE A @260MW, PGPP1 @76MW [WEBSMS] | CVIS
2/14/2024 1:07:01 PM | [NSO Update] Luzon Grid-02/14/2024 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14531MW, PK=10792MW, RR=426MW, NetOpMargin: PM=3313, EVE=3008 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @180MW, ILIJAN A @585MW, ILIJAN B @165MW [WEBSMS] | CLUZ
2/14/2024 1:04:21 PM | Mindanao Grid-02/14/2024 13:08: LIBERTAD POWER online at 1257H (Unplanned Outage) [WEBSMS] | CMIN
2/14/2024 12:16:24 PM | Mindanao Grid-02/14/2024 12:20: LIBERTAD POWER tripped at 1149H. Cause: Turbine Trip. (Unplanned Outage) [WEBSMS] | CMIN
2/14/2024 10:57:27 AM | Mindanao Grid-02/14/2024 11:01: WMPC DG03 online at 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/14/2024 10:44:19 AM | Luzon Grid-02/14/2024 10:44: Lal-lo-Cagayan Solar 69kV line 2(Customer Owned) was energized at Lalo-lo side at 1042H. (Unplanned Outage) [WEBSMS] | CLUZ
2/14/2024 10:35:16 AM | Luzon Grid-02/14/2024 10:35: San Gabriel synchronized at 1027H. (Unplanned Outage - LNG Commissioning) [WEBSMS] | CLUZ
2/14/2024 10:26:51 AM | Mindanao Grid-02/14/2024 10:30: Agus 6 SS PCB 5-02CB24AG6 re-energized at 1019H (Planned Outage). Non-GOMP. MTD-A Request. [WEBSMS] | CMIN
2/14/2024 10:19:58 AM | Luzon Grid-02/14/2024 10:20: Dasmarinas 100MVAR Capacitor Bank 2 was de-energized at 1018H. (Unplanned Outage) [WEBSMS] | CLUZ
2/14/2024 9:12:12 AM | Luzon Grid-02/14/2024 09:12: San Gabriel tripped at 0905H (Unplanned Outage - LNG Commissioning) [WEBSMS] | CLUZ
2/14/2024 9:01:18 AM | Luzon Grid-02/14/2024 09:01: San Gabriel synchronized at 0858H. (Undergoing LNG Commissioning) [WEBSMS] | CLUZ
2/14/2024 8:54:46 AM | Mindanao Grid-02/14/2024 08:58: WMPC DG10 online at 0850H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/14/2024 8:51:07 AM | Mindanao Grid-02/14/2024 08:54: SEDI (13MAGDBNK_G01) online at 0846H. Capability Test. [WEBSMS] | CMIN
2/14/2024 8:39:02 AM | Mindanao Grid-02/14/2024 08:42: Agus 6 SS PCB 5-02CB24AG6 De-energized/shutdown at 0834H (Planned Outage). Non-GOMP. Requested by MTD-A. [WEBSMS] | CMIN
2/14/2024 8:05:38 AM | Mindanao Grid-02/14/2024 08:09: Agus 6 SS 138kV Bus #1 shutdown at 0650H (Planned Outage). Non-GOMP. P&E Request under MSE4P Schedule 3. [WEBSMS] | CMIN
2/14/2024 6:35:43 AM | Luzon Grid-02/14/2024 06:35: Tayabas-San Jose 500kV line 2 was de-energized at 0634H. (Planned Outage) [WEBSMS] | CLUZ
2/14/2024 5:39:56 AM | [NSO Update] Luzon Grid-02/14/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13719MW, PK=10193MW, RR=409MW, NetOpMargin: AM=3116, PM=2438, EVE=2189 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 2 @180MW, ILIJAN A @585MW ILIJAN B @165MW [WEBSMS] | CLUZ
2/14/2024 5:32:40 AM | [NSO Update] Visayas Grid-02/14/2024 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2481MW, PK=1992MW, RR=86MW, NetOpMargin: AM=403, PM=320, EVE=352 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @80.5MW, LEYTE A @302MW, PGPP1 @76MW [WEBSMS] | CVIS
2/14/2024 5:32:37 AM | [NSO Update] Mindanao Grid-02/14/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3243MW, PK=2187MW, RR=72MW, NetOpMargin: AM=983, PM=958, EVE=987 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @88MW, AG4 @106MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @144MW [WEBSMS] | CMIN
2/14/2024 4:14:57 AM | [NSO Update] Mindanao Grid-02/14/2024 04:18: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
2/14/2024 4:14:43 AM | [NSO Update] Visayas Grid-02/14/2024 04:14: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CVIS
2/14/2024 4:14:31 AM | [NSO Update] Luzon Grid-02/14/2024 04:14: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
2/14/2024 3:24:35 AM | Visayas Grid-02/14/2024 03:24: TVI Unit # 2 cut-in to the system at 0322H. ( Planned Outage ) [WEBSMS] | CVIS
2/14/2024 2:12:37 AM | Mindanao Grid-02/14/2024 02:16: Tudaya 1 Unit No. 1 shutdown at 0007H for PMS (GOMP) [WEBSMS] | CMIN
2/14/2024 12:38:46 AM | Visayas Grid-02/14/2024 00:39: Timbaban Hydro back on-line @ 0012H. (Unplanned Outage) [WEBSMS] | CVIS
2/14/2024 12:03:26 AM | Visayas Grid-02/14/2024 00:03: Timbaban Hydro with load of 16.5MW auto tripped @ 0000H. (Unplanned Outage) [WEBSMS] | CVIS
2/13/2024 11:45:08 PM | Luzon Grid-02/13/2024 23:45: San Gabriel shutdown at 2337H (Planned Outage) [WEBSMS] | CLUZ
2/13/2024 11:24:30 PM | Luzon Grid-02/13/2024 23:24: Sta. Rita 30 tripped at 2320H (Unplanned Outage) [WEBSMS] | CLUZ
2/13/2024 11:13:11 PM | Luzon Grid-02/13/2024 23:13: San Lorenzo 50 online at 2308H (Planned Outage) [WEBSMS] | CLUZ
2/13/2024 9:18:49 PM | Mindanao Grid-02/13/2024 21:22: WMPC DG10 shutdown at 2114H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/13/2024 9:07:07 PM | Visayas Grid-02/13/2024 21:07: Cebu SS 138kV Bus 1 energized at 2106H. (Unplanned Outage) [WEBSMS] | CVIS
2/13/2024 6:59:32 PM | Mindanao Grid-02/13/2024 19:03: TM2 U1 Shutdown at 1855H, from MO Dispatched. Follow RTD. [WEBSMS] | CMIN
2/13/2024 6:22:33 PM | Mindanao Grid-02/13/2024 18:26: TM2 U1 Online at 1810H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
2/13/2024 5:54:15 PM | [NSO Update] Mindanao Grid-02/13/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3146MW, PK=2161MW, RR=72MW, NetOpMargin: EVE=913 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @120MW [WEBSMS] | CMIN
2/13/2024 5:52:08 PM | [NSO Update] Visayas Grid-02/13/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2351MW, PK=1988MW, RR=86MW, NetOpMargin: EVE=277 Highest Unit O/L: PEDC 3 @150MW Derated Plant: TGPP @81MW, LEYTE A @275MW, PGPP1 @76MW, [WEBSMS] | CVIS
2/13/2024 5:49:51 PM | [NSO Update] Luzon Grid-02/13/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13255MW, PK=9719MW, RR=401MW, NetOpMargin: EVE=3135 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 2 @180MW, SLTEC 1@85MW, ILIJAN A @450MW, ILIJAN B @300MW [WEBSMS] | CLUZ
2/13/2024 5:37:19 PM | Luzon Grid-02/13/2024 17:37: Tayabas - San Jose 500kV Line 2 energized at 1736H (Planned Outage) [WEBSMS] | CLUZ
2/13/2024 4:43:12 PM | Mindanao Grid-02/13/2024 16:47: Baloi - Agus 6 138kV Line 1 re-energized at 1639H (Planned Outage). [WEBSMS] | CMIN
2/13/2024 4:25:34 PM | Luzon Grid-02/13/2024 16:25: San Lorenzo 50 shutdown at 1622H (Planned Outage) [WEBSMS] | CLUZ
2/13/2024 4:15:44 PM | Mindanao Grid-02/13/2024 16:19: WMPC DG04 shutdown at 1613H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/13/2024 4:07:11 PM | Visayas Grid-02/13/2024 16:07: EDC-UMPP U2 tripped at 1530H (Unplanned Outage) [WEBSMS] | CVIS
2/13/2024 3:46:33 PM | Mindanao Grid-02/13/2024 15:50: AGUS6 Unit 4 online at 1541H. (Unplanned Outage) [WEBSMS] | CMIN
2/13/2024 3:13:38 PM | Luzon Grid-02/13/2024 15:13: San Lorenzo 50 online at 1507H (Planned Outage) [WEBSMS] | CLUZ
2/13/2024 2:38:52 PM | Mindanao Grid-02/13/2024 14:42: ASIGA (ASG) HEP with 7.7MW load tripped at 1421H. Indication: Restricted Earth Fault (Unplanned Outage) [WEBSMS] | CMIN
2/13/2024 2:37:25 PM | Mindanao Grid-02/13/2024 14:41: AGUS6 Unit 4 shutdown at 1424H. Reason: Low forebay elevation. Unplanned Outage. [WEBSMS] | CMIN
2/13/2024 1:40:39 PM | Visayas Grid-02/13/2024 13:40: URC U2 cut in at 1335H. (Unplanned Outage) [WEBSMS] | CVIS
2/13/2024 1:26:25 PM | Visayas Grid-02/13/2024 13:26: SNBP cut in at 1324H. (Unplanned Outage) [WEBSMS] | CVIS
2/13/2024 1:06:43 PM | [NSO Update] Mindanao Grid-02/13/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3194MW, PK=2191MW, RR=74MW, NetOpMargin: PM=929, EVE=913 Highest Unit O/L: GNPK 2, 3, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @120MW [WEBSMS] | CMIN
2/13/2024 1:04:28 PM | [NSO Update] Visayas Grid-02/13/2024 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2531MW, PK=2076MW, RR=88MW, NetOpMargin: PM=367, EVE=272 Highest Unit O/L: PEDC 3 @150MW Derated Plant: TGPP @81MW, LEYTE A @285MW, PGPP1 @76MW [WEBSMS] | CVIS
2/13/2024 1:00:47 PM | [NSO Update] Luzon Grid-02/13/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14360MW, PK=9841MW, RR=420MW, NetOpMargin: PM=4098, EVE=3570 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @180MW, ILIJAN A @450MW, ILIJAN B @275MW [WEBSMS] | CLUZ
2/13/2024 12:43:31 PM | Mindanao Grid-02/13/2024 12:47: Talomo2 HEP Unit No. 3 online at 1048H from PMS (GOMP). [WEBSMS] | CMIN
2/13/2024 12:42:54 PM | Mindanao Grid-02/13/2024 12:46: Talomo2 HEP Unit No. 2 online at 1058H from PMS (GOMP). [WEBSMS] | CMIN
2/13/2024 12:42:24 PM | Mindanao Grid-02/13/2024 12:46: Talomo2 HEP Unit No. 1 online at 1206H from PMS (GOMP). [WEBSMS] | CMIN
2/13/2024 11:58:26 AM | Visayas Grid-02/13/2024 11:58: Maha A U1 tripped at 1152H. (Unplanned Outage) [WEBSMS] | CVIS
2/13/2024 10:57:26 AM | Visayas Grid-02/13/2024 10:57: URC U2 cut out at 1042H. (Unplanned Outage) [WEBSMS] | CVIS
2/13/2024 10:52:23 AM | Mindanao Grid-02/13/2024 10:56: WMPC DG04 online at 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/13/2024 10:48:53 AM | Visayas Grid-02/13/2024 10:49: Cebu SS 138kV Bus 1 de-energized at 1038H. (Unplanned Outage) [WEBSMS] | CVIS
2/13/2024 10:29:12 AM | Visayas Grid-02/13/2024 10:29: CEDC U3 cut in at 1026H. (Planned Outage) [WEBSMS] | CVIS
2/13/2024 10:21:46 AM | Luzon Grid-02/13/2024 10:21: San Jose-Angat 115kV Line 3 de-energized at 1021H. (Planned Outage) [WEBSMS] | CLUZ
2/13/2024 10:19:30 AM | Mindanao Grid-02/13/2024 10:23: SEDI EEI Unit No.3 online at 1016H. For Generating Unit Capability Test(GUCT). Follow RTD. [WEBSMS] | CMIN
2/13/2024 10:15:52 AM | Mindanao Grid-02/13/2024 10:19: Talomo2 HEP Unit No. 1 shutdown at 0905H for PMS (GOMP) [WEBSMS] | CMIN
2/13/2024 10:15:26 AM | Mindanao Grid-02/13/2024 10:19: Talomo2 HEP Units No. 2 & 3 shutdown at 0904H for PMS (GOMP) [WEBSMS] | CMIN
2/13/2024 8:56:44 AM | Luzon Grid-02/13/2024 08:56: Sta. Rita 30 online at 0855H. (On Commissioning) [WEBSMS] | CLUZ
2/13/2024 8:52:56 AM | Mindanao Grid-02/13/2024 08:56: WMPC DG10 online at 0850H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/13/2024 8:16:55 AM | Luzon Grid-02/13/2024 08:17: Mauban-QPPL 230kV Line 1 de-energized at 0816H. (Planned Outage) [WEBSMS] | CLUZ
2/13/2024 6:52:14 AM | Mindanao Grid-02/13/2024 06:56: Baloi - Agus 6 138kV Line 1 de-energized at 0645H (Planned Outage). [WEBSMS] | CMIN
2/13/2024 6:36:23 AM | Luzon Grid-02/13/2024 06:36: Tayabas - San Jose 500kV Line 2 de-energized at 0636H. (Planned Outage) [WEBSMS] | CLUZ
2/13/2024 6:05:56 AM | [NSO Update] Luzon Grid-02/13/2024 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14299MW, PK=9856MW, RR=408MW, NetOpMargin: AM=4035, PM=3593, EVE=2880 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @180MW [WEBSMS] | CLUZ
2/13/2024 5:55:25 AM | [NSO Update] Mindanao Grid-02/13/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3218MW, PK=2067MW, RR=72MW, NetOpMargin: AM=1079, PM=914, EVE=945 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @120MW [WEBSMS] | CMIN
2/13/2024 5:51:30 AM | [NSO Update] Visayas Grid-02/13/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2547MW, PK=1973MW, RR=84MW, NetOpMargin: AM=490, PM=261, EVE=261 Highest Unit O/L: PEDC U3 @150MW Derated Plant: TGPP @81MW, LEYTE A @309MW, PGPP1 @76MW [WEBSMS] | CVIS
2/13/2024 4:39:02 AM | [NSO Update] Mindanao Grid-02/13/2024 04:42: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CMIN
2/13/2024 4:35:46 AM | [NSO Update] Visayas Grid-02/13/2024 04:35: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CVIS
2/13/2024 4:35:24 AM | [NSO Update] Luzon Grid-02/13/2024 04:35: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CLUZ
2/13/2024 12:04:10 AM | Luzon Grid-02/13/2024 00:04: QPPL shutdown at 0000H (Planned Outage) [WEBSMS] | CLUZ
2/12/2024 11:10:56 PM | Mindanao Grid-02/12/2024 23:14: Maramag-Pulangi 138kV L1 re-energized at 2256H. From P&E request under ERC Approved MSRP Stage 1 Schedule II (Planned Outage / Non-GOMP) [WEBSMS] | CMIN
2/12/2024 11:07:51 PM | Luzon Grid-02/12/2024 23:08: Ilijan ST2 online at 2301H (Planned Outage) [WEBSMS] | CLUZ
2/12/2024 10:59:52 PM | Mindanao Grid-02/12/2024 23:03: PULANGI 4 Unit 1 online at 2256H. From shutdown affected by P&E request. [WEBSMS] | CMIN
2/12/2024 10:40:06 PM | Mindanao Grid-02/12/2024 22:43: ASIGA Hydro online at 2226H (Unplanned Outage) [WEBSMS] | CMIN
2/12/2024 10:10:58 PM | Mindanao Grid-02/12/2024 22:14: ASIGA Hydro tripped with 7.8MW load at 2203H. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
2/12/2024 9:22:59 PM | Mindanao Grid-02/12/2024 21:26: WMPC DG10 shutdown at 2114H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/12/2024 8:16:18 PM | Mindanao Grid-02/12/2024 20:20: Maramag SS 138kV Bus # 1 re-energized at 2000H. From P&E request under ERC Approved MSRP Stage 1 Schedule II (Planned Outage / Non-GOMP). [WEBSMS] | CMIN
2/12/2024 7:32:18 PM | Luzon Grid-02/12/2024 19:32: Sta. Rita 30 shutdown at 1929H (On Commissioning) [WEBSMS] | CLUZ
2/12/2024 6:48:15 PM | Mindanao Grid-02/12/2024 18:52: Nabunturan-Masara 138kV Line (CO) re-energized at 1835H. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
2/12/2024 5:40:12 PM | [NSO Update] Luzon Grid-02/12/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13733MW, PK=9383MW, RR=357MW, NetOpMargin: EVE=3993 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @180MW [WEBSMS] | CLUZ
2/12/2024 5:38:16 PM | [NSO Update] Visayas Grid-02/12/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2281MW, PK=1950MW, RR=81MW, NetOpMargin: EVE=250 Highest Unit O/L: PEDC U3 @150MW Derated Plant: TGPP @80.3MW, LEYTE A @318MW, PGPP1 @76MW [WEBSMS] | CVIS
2/12/2024 5:36:51 PM | [NSO Update] Mindanao Grid-02/12/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3151MW, PK=2135MW, RR=72MW, NetOpMargin: EVE=944 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @104MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @95MW [WEBSMS] | CMIN
2/12/2024 4:40:19 PM | Luzon Grid-02/12/2024 16:40: Tayabas-San Jose 500kV line 2 restored at 1638H. (Unplanned Outage) [WEBSMS] | CLUZ
2/12/2024 4:18:46 PM | Visayas Grid-02/12/2024 16:18: Timbaban Hydro cut-in back to the system @1453H. (Unplanned Outage) [WEBSMS] | CVIS
2/12/2024 4:16:51 PM | Luzon Grid-02/12/2024 16:17: San Jose - Tayabas 500kV Line 1 restored at 1615H. (Unplanned Outage) [WEBSMS] | CLUZ
2/12/2024 4:15:00 PM | Mindanao Grid-02/12/2024 16:18: WMPC DG04 shutdown at 1613H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/12/2024 3:45:10 PM | Mindanao Grid-02/12/2024 15:48: WMPC DG08 declared available at 1540H. From forced outage. [WEBSMS] | CMIN
2/12/2024 3:21:27 PM | Mindanao Grid-02/12/2024 15:25: GNPK Unit 3 online at 1519H. From Reserve Shutdown. [WEBSMS] | CMIN
2/12/2024 3:13:07 PM | Mindanao Grid-02/12/2024 15:16: MINERGY 2 (WARTSILA) shutdown at 1508H. From SO Dispatch. [WEBSMS] | CMIN
2/12/2024 2:54:20 PM | Mindanao Grid-02/12/2024 14:58: MINERGY 2 (WARTSILA) online at 1432H. SO Dispatch. [WEBSMS] | CMIN
2/12/2024 2:52:35 PM | Mindanao Grid-02/12/2024 14:56: WMPC DG06 online at 1432H. SO Dispatch. [WEBSMS] | CMIN
2/12/2024 2:05:57 PM | Visayas Grid-02/12/2024 14:06: Timbaban Hydro auto tripped @1401H [WEBSMS] | CVIS
2/12/2024 1:45:15 PM | Visayas Grid-02/12/2024 13:45: SNBP cut in at 1307H. (Unplanned Outage) [WEBSMS] | CVIS
2/12/2024 1:29:19 PM | Luzon Grid-02/12/2024 13:29: Kalayaan 4 shutdown at 1328H. (Unplanned Outage) [WEBSMS] | CLUZ
2/12/2024 12:56:11 PM | [NSO Update] Luzon Grid-02/12/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14619MW, PK=9956MW, RR=379MW, NetOpMargin: PM=4284, EVE=3835 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @180MW [WEBSMS] | CLUZ
2/12/2024 12:55:30 PM | Mindanao Grid-02/12/2024 12:59: Baloi-Agus 2 138kV L1 successfully restored at 1232H. From Unplanned Outage. [WEBSMS] | CMIN
2/12/2024 12:52:59 PM | [NSO Update] Visayas Grid-02/12/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2401MW, PK=2000MW, RR=85MW, NetOpMargin: PM=316, EVE=251 Highest Unit O/L: PEDC U3 @150MW Derated Plant: TGPP @81MW, LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
2/12/2024 12:49:26 PM | [NSO Update] Mindanao Grid-02/12/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3217MW, PK=2129MW, RR=75MW, NetOpMargin: PM=1013, EVE=992 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @104MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @95MW [WEBSMS] | CMIN
2/12/2024 12:30:05 PM | Luzon Grid-02/12/2024 12:30: Tayabas-San Jose 500kV line 2 de-energized at 1229H. (Unplanned Outage) [WEBSMS] | CLUZ
2/12/2024 11:26:13 AM | Mindanao Grid-02/12/2024 11:30: WMPC DG04 online at 1100H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/12/2024 11:17:09 AM | Mindanao Grid-02/12/2024 11:20: AGUS 4 Unit 3 online at 1113H. From plant-initiated shutdown (testing of its computer area network bus communication). [WEBSMS] | CMIN
2/12/2024 11:13:18 AM | Mindanao Grid-02/12/2024 11:17: AGUS 4 Unit 3 shutdown at 1102H. Plant-initiated shutdown to facilitate testing of its computer area network bus communication which required shutdown of the unit. [WEBSMS] | CMIN
2/12/2024 10:53:57 AM | Mindanao Grid-02/12/2024 10:57: WMPC DG08 declared not available at 1040H. Reason: Module Fault Alarm. [WEBSMS] | CMIN
2/12/2024 10:04:46 AM | Luzon Grid-02/12/2024 10:04: Sta. Rita Module 40 on-line at 1002H (On Commissioning) [WEBSMS] | CLUZ
2/12/2024 9:41:00 AM | Mindanao Grid-02/12/2024 09:44: Maco-Therma Marine 1 138KV L2 de-energized at 0852H. P&E request. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
2/12/2024 9:38:15 AM | Mindanao Grid-02/12/2024 09:42: shutdown at 0852H Maco-Therma Marine 1 138KV L2 de-energized at 0852H. P&E request. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
2/12/2024 8:54:10 AM | Mindanao Grid-02/12/2024 08:57: WMPC DG10 online at 0850H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/12/2024 8:33:09 AM | Mindanao Grid-02/12/2024 08:36: Nabunturan-Masara 138kV Line (CO) de-energized at 0738H per request from Apex Mining management. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
2/12/2024 8:15:02 AM | Luzon Grid-02/12/2024 08:15: Sta. Rita Module 20 on-line at 0808H (On Commissioning) [WEBSMS] | CLUZ
2/12/2024 7:42:32 AM | Luzon Grid-02/12/2024 07:42: SCPC 1 online at 0740H. (Unplanned Outage) [WEBSMS] | CLUZ
2/12/2024 6:58:17 AM | Mindanao Grid-02/12/2024 07:02: Maramag SS 138kV Bus # 1 de-energized at 0621H. P&E request under ERC Approved MSRP Stage 1 Schedule II. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
2/12/2024 6:47:35 AM | Mindanao Grid-02/12/2024 06:51: Maramag-Pulangi 138kV L1 de-energized at 0601H. P&E request under ERC Approved MSRP Stage 1 Schedule II. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
2/12/2024 6:20:46 AM | Luzon Grid-02/12/2024 06:20: San Jose - Tayabas 500kV Line 1tripped at 0619H. (Unplanned Outage) [WEBSMS] | CLUZ
2/12/2024 6:10:26 AM | Mindanao Grid-02/12/2024 06:14: PULANGI 4 Unit 1 shutdown at 0601H. Affected by P&E request. [WEBSMS] | CMIN
2/12/2024 5:54:29 AM | [NSO Update] Mindanao Grid-02/12/2024 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3315MW, PK=2028MW, RR=72MW, NetOpMargin: AM=1215, PM=1138, EVE=1159 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @124MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
2/12/2024 5:52:14 AM | [NSO Update] Visayas Grid-02/12/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2481MW, PK=1997MW, RR=83MW, NetOpMargin: AM=402, PM=276, EVE=287 Highest Unit O/L: PEDC U3 @150MW Derated Plant: TGPP @81MW, LEYTE A @309MW, PGPP1 @76MW [WEBSMS] | CVIS
2/12/2024 5:49:02 AM | [NSO Update] Luzon Grid-02/12/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14249MW, PK=9756MW, RR=373MW, NetOpMargin: AM=4120, PM=3664, EVE=3441 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @179MW [WEBSMS] | CLUZ
2/12/2024 4:53:37 AM | Mindanao Grid-02/12/2024 04:57: Butuan-Placer 138kV Line 2 energized at 0451H (Planned Outage) [WEBSMS] | CMIN
2/12/2024 4:18:36 AM | [NSO Update] Mindanao Grid-02/12/2024 04:22: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CMIN
2/12/2024 4:17:46 AM | [NSO Update] Visayas Grid-02/12/2024 04:17: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CVIS
2/12/2024 4:17:07 AM | [NSO Update] Luzon Grid-02/12/2024 04:17: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
2/12/2024 3:56:21 AM | Visayas Grid-02/12/2024 03:56: KSPC Unit no. 1 cut-in to the system at 0352H. (Unplanned Outage) [WEBSMS] | CVIS
2/12/2024 2:33:19 AM | Mindanao Grid-02/12/2024 02:37: TM1 Unit #1 shutdown at 0011H for PMS (GOMP). [WEBSMS] | CMIN
2/12/2024 12:22:32 AM | Visayas Grid-02/12/2024 00:22: Sogongon PGPP 2 U2 cut-in to the system at 0016H.(Unplanned Outage) [WEBSMS] | CVIS
2/11/2024 11:24:51 PM | Luzon Grid-02/11/2024 23:25: San Jose - Tayabas 500kV Line 1 tripped/reclosed at 2321H (Unplanned Outage) [WEBSMS] | CLUZ
2/11/2024 10:20:17 PM | Luzon Grid-02/11/2024 22:20: For info: Sta. Rita Module 20 shutdown at 2137H (On Commissioning) [WEBSMS] | CLUZ
2/11/2024 9:37:53 PM | Luzon Grid-02/11/2024 21:38: One Subic Power 55MVA T02 restored at 2128H (Planned Outage) [WEBSMS] | CLUZ
2/11/2024 9:01:27 PM | Visayas Grid-02/11/2024 21:01: Magdugo SS 300 MVA 230/138/13.8 kV TR2 energized at 2046H. (Planned Outage) [WEBSMS] | CVIS
2/11/2024 8:58:22 PM | Luzon Grid-02/11/2024 20:58: San Roque Unit 1 (95MW) tripped at 2052H. Lowest system frequency is 59.80Hz. [WEBSMS] | CLUZ
2/11/2024 7:35:46 PM | Luzon Grid-02/11/2024 19:35: Sta. Rita 40 shutdown at 1933H (On Commissioning) [WEBSMS] | CLUZ
2/11/2024 6:30:32 PM | Visayas Grid-02/11/2024 18:30: Sogongon PGPP U#2 with load of 20MW tripped @1826H. ( Unplanned Outage ) [WEBSMS] | CVIS
2/11/2024 5:49:17 PM | Luzon Grid-02/11/2024 17:49: Dasmarinas-Ilijan 500kV Line restored at 1748H (Planned Outage) [WEBSMS] | CLUZ
2/11/2024 5:47:12 PM | [NSO Update] Mindanao Grid-02/11/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3275MW, PK=1911MW, RR=72MW, NetOpMargin: EVE=1292 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @124MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
2/11/2024 5:45:18 PM | [NSO Update] Visayas Grid-02/11/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2228MW, PK=1759MW, RR=79MW, NetOpMargin: EVE=390 Highest Unit O/L: PEDC U3 @150MW Derated Plant: TGPP @80.3MW, LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
2/11/2024 5:43:43 PM | [NSO Update] Luzon Grid-02/11/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13775MW, PK=8609MW, RR=327MW, NetOpMargin: EVE=4839 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @179MW [WEBSMS] | CLUZ
2/11/2024 5:33:21 PM | Mindanao Grid-02/11/2024 17:37: Tacurong SS 138kV Power Transformer No. 3 re-energized at 1726H (Planned Outage). [WEBSMS] | CMIN
2/11/2024 5:04:38 PM | Mindanao Grid-02/11/2024 17:08: Butuan SS 138kV Bus No. 2 re-energized at 1657H (Planned Outage) [WEBSMS] | CMIN
2/11/2024 5:02:44 PM | Mindanao Grid-02/11/2024 17:06: Zamboanga SS 138kV Bus No. 1 re-energized at 1655H (Planned Outage) [WEBSMS] | CMIN
2/11/2024 4:58:34 PM | Luzon Grid-02/11/2024 16:58: Correction: Mexico 100MVA Mobile Transformer restored at 1655H (Planned Outage) [WEBSMS] | CLUZ
2/11/2024 4:56:54 PM | Luzon Grid-02/11/2024 16:57: Mexico 100MVA Mobile Transformer restored at 1555H (Planned Outage) [WEBSMS] | CLUZ
2/11/2024 4:17:45 PM | Mindanao Grid-02/11/2024 16:21: AGUS4 U3 online at 1602H from PMS(Non-GOMP). [WEBSMS] | CMIN
2/11/2024 3:38:28 PM | Luzon Grid-02/11/2024 15:38: Makban Plant B- Makban Plant C 230kV Tie Line restored at 1535H (Unplanned Outage) [WEBSMS] | CLUZ
2/11/2024 3:31:40 PM | Mindanao Grid-02/11/2024 15:35: Agus 2 - Baloi 138kV Line 1 tripped 1522H (Unplanned Outage). [WEBSMS] | CMIN
2/11/2024 3:18:04 PM | Mindanao Grid-02/11/2024 15:21: Correction: Zamboanga SS 50MVA Power Transformer No. 1 energized without load at 1502H (Planned Outage). [WEBSMS] | CMIN
2/11/2024 3:10:21 PM | Mindanao Grid-02/11/2024 15:14: Lake Mainit HEP online at 1437H. (Unplanned Outage) [WEBSMS] | CMIN
2/11/2024 3:04:15 PM | Mindanao Grid-02/11/2024 15:08: Zamboanga SS 50MVA Power Transformer No. 1 de-energized without load at 1502H (Planned Outage). [WEBSMS] | CMIN
2/11/2024 2:26:39 PM | Mindanao Grid-02/11/2024 14:30: ASIGA (ASG) HEP online at 1401H. (Unplanned Outage) [WEBSMS] | CMIN
2/11/2024 2:10:08 PM | Mindanao Grid-02/11/2024 14:13: ASIGA (ASG) HEP with 8MW load tripped at 1338H. Cause: For verification (Unplanned Outage) [WEBSMS] | CMIN
2/11/2024 2:09:26 PM | Mindanao Grid-02/11/2024 14:13: Lake Mainit HEP with 20.8MW load tripped at 1338H. Cause: For verification (Unplanned Outage) [WEBSMS] | CMIN
2/11/2024 1:05:37 PM | Mindanao Grid-02/11/2024 13:09: Butuan SS 138kV Bus No. 2 de-energized at 1302H (Planned Outage). [WEBSMS] | CMIN
2/11/2024 12:55:08 PM | [NSO Update] Luzon Grid-02/11/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14487MW, PK=7929MW, RR=320MW, NetOpMargin: PM=6239, EVE=4695 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @179MW [WEBSMS] | CLUZ
2/11/2024 12:52:21 PM | [NSO Update] Visayas Grid-02/11/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2201MW, PK=1586MW, RR=77MW, NetOpMargin: PM=538, EVE=323 Highest Unit O/L: PEDC 3 @150MW Derated Plant: TGPP @80.3MW, LEYTE A @306MW, PGPP1 @76MW [WEBSMS] | CVIS
2/11/2024 12:49:31 PM | [NSO Update] Mindanao Grid-02/11/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3303MW, PK=1658MW, RR=74MW, NetOpMargin: PM=1572, EVE=1316 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @104MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
2/11/2024 10:42:54 AM | Mindanao Grid-02/11/2024 10:46: Corrected: Tacurong SS 138kV Power Transformer No. 3 de-energized at 0759H (Planned Outage) [WEBSMS] | CMIN
2/11/2024 9:53:59 AM | Luzon Grid-02/11/2024 09:54: Makban Plant B- Makban Plant C 230kV Tie Line de-energized at 0952H (Unplanned Outage) [WEBSMS] | CLUZ
2/11/2024 9:16:30 AM | Mindanao Grid-02/11/2024 09:20: Zamboanga SS 50MVA Power Transformer No. 1 de-energized without load at 0912H (Planned Outage) [WEBSMS] | CMIN
2/11/2024 9:14:02 AM | Luzon Grid-02/11/2024 09:14: Sta Rita Module 20 online at 0903H (Planned Outage) [WEBSMS] | CLUZ
2/11/2024 8:38:21 AM | Luzon Grid-02/11/2024 08:38: One Subic Power 55MVA T02 de-energized at 0837H (Planned Outage) [WEBSMS] | CLUZ
2/11/2024 8:13:37 AM | Mindanao Grid-02/11/2024 08:17: Zamboanga SS 138kV Bus No. 1 de-energized at 0809H (Planned Outage) [WEBSMS] | CMIN
2/11/2024 8:00:12 AM | Mindanao Grid-02/11/2024 08:03: Tacurong SS 138kV Power Transformer No. 3 de-energized at 0745H (Planned Outage). [WEBSMS] | CMIN
2/11/2024 7:51:13 AM | Mindanao Grid-02/11/2024 07:54: Butuan-Placer 138kV Line 2 de-energized at 0557H. (Planned Outage). [WEBSMS] | CMIN
2/11/2024 7:11:36 AM | Luzon Grid-02/11/2024 07:11: Mexico 100MVA Mobile Transformer de-energized at 0711H (Planned Outage) [WEBSMS] | CLUZ
2/11/2024 6:40:15 AM | Luzon Grid-02/11/2024 06:40: Dasmarinas-Ilijan 500kV Line de-energized at 0640H (Planned Outage) [WEBSMS] | CLUZ
2/11/2024 6:34:26 AM | Visayas Grid-02/11/2024 06:34: Magdugo SS 300 MVA 230/138/13.8 kV TR2 de-energized at 0632H. (Planned Outage) [WEBSMS] | CVIS
2/11/2024 6:03:06 AM | [NSO Update] Mindanao Grid-02/11/2024 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3295MW, PK=1584MW, RR=72MW, NetOpMargin: AM=1638, PM=1525, EVE=1212 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @104MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
2/11/2024 6:01:55 AM | [NSO Update] Visayas Grid-02/11/2024 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2204MW, PK=1572MW, RR=79MW, NetOpMargin: AM=553, PM=516, EVE=259 Highest Unit O/L: PEDC 3 @150MW Derated Plant: TGPP @81MW, LEYTE A @318MW, PGPP1 @76MW [WEBSMS] | CVIS
2/11/2024 6:00:47 AM | [NSO Update] Luzon Grid-02/11/2024 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14688MW, PK=7739MW, RR=295MW, NetOpMargin: AM=6654, PM=5808, EVE=4491 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @179MW [WEBSMS] | CLUZ
2/11/2024 5:12:40 AM | [NSO Update] Mindanao Grid-02/11/2024 05:16: Weather Update: Northeast Monsoon affecting Luzon. [WEBSMS] | CMIN
2/11/2024 5:12:23 AM | [NSO Update] Visayas Grid-02/11/2024 05:12: Weather Update: Northeast Monsoon affecting Luzon. [WEBSMS] | CVIS
2/11/2024 5:12:07 AM | [NSO Update] Luzon Grid-02/11/2024 05:12: Weather Update: Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
2/11/2024 3:20:37 AM | Luzon Grid-02/11/2024 03:20: Binan-Balibago 115kV line was restored at 0318H (Planned Outage) [WEBSMS] | CLUZ
2/11/2024 12:47:56 AM | Luzon Grid-02/11/2024 00:48: Balsik-San Marcelino 230kV Line 2 was restored at 0035H (Planned Outage). Commissioning of Balsik SS PCB 8-02CB24BIK completed at 0041H. [WEBSMS] | CLUZ
2/10/2024 11:09:42 PM | Luzon Grid-02/10/2024 23:09: Binan-Balibago 115kV line was de-energized at 2306H. (Planned Outage) [WEBSMS] | CLUZ
2/10/2024 10:55:17 PM | Luzon Grid-02/10/2024 22:55: One Subic Power 55MVA T01 (8XF01OSP) was energized at 2252H. (Planned Outage) [WEBSMS] | CLUZ
2/10/2024 7:49:33 PM | Luzon Grid-02/10/2024 19:49: Dasmarinas 300MVA T02 was restored at 1949H. (Unplanned Outage) [WEBSMS] | CLUZ
2/10/2024 7:00:45 PM | Mindanao Grid-02/10/2024 19:04: Bislig SS 138kV 50MVA Power Transformer # 1 re-energized at 1829H after the conduct of annual PMS. From Planned Outage / GOMP. [WEBSMS] | CMIN
2/10/2024 6:47:05 PM | Mindanao Grid-02/10/2024 18:50: Baloi-Agus 5 138KV line re-energized at 1815H. From P&E request under MSRP Stage 1 Schedule III (Planned Outage / Non-GOMP). [WEBSMS] | CMIN
2/10/2024 6:40:51 PM | Luzon Grid-02/10/2024 18:40: Dasmarinas 300MVA T02 was de-energized at 1839H. (Unplanned Outage) [WEBSMS] | CLUZ
2/10/2024 6:35:28 PM | Luzon Grid-02/10/2024 18:35: Sta Rita Module 20 shutdown at 1832H. (On-going LNG Commissioning) [WEBSMS] | CLUZ
2/10/2024 6:28:31 PM | Luzon Grid-02/10/2024 18:28: Bolo-Cayanga 230kV line 2(Customer Owned and Maintained) was looped at Cayanga side at 1827H. (Unplanned Outage) [WEBSMS] | CLUZ
2/10/2024 6:05:52 PM | Luzon Grid-02/10/2024 18:05: San Jose 750MVA T04 was restored at 1804H. (Planned Outage) [WEBSMS] | CLUZ
2/10/2024 5:59:34 PM | Luzon Grid-02/10/2024 17:59: Balsik 230kV Bus 1 was energized at 1758H. (Planned Outage) [WEBSMS] | CLUZ
2/10/2024 5:59:22 PM | [NSO Update] Mindanao Grid-02/10/2024 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3251MW, PK=2006MW, RR=70.3MW, NetOpMargin: EVE=1174 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @104MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
2/10/2024 5:55:26 PM | [NSO Update] Visayas Grid-02/10/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2263MW, PK=1903MW, RR=79MW, NetOpMargin: EVE=281 Highest Unit O/L: PEDC U3 @150MW Derated Plant: TGPP @80.3MW, LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
2/10/2024 5:51:47 PM | [NSO Update] Luzon Grid-02/10/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13943MW, PK=8823MW, RR=346MW, NetOpMargin: EVE=4774 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW [WEBSMS] | CLUZ
2/10/2024 5:29:58 PM | Mindanao Grid-02/10/2024 17:33: The new SKU SS 138kV 100MVA Power Transformer # 2 successfully energized without load at 1635H. [WEBSMS] | CMIN
2/10/2024 5:03:22 PM | Luzon Grid-02/10/2024 17:03: Dasmarinas 300MVA T02 was restored at 1700H. (Planned Outage) [WEBSMS] | CLUZ
2/10/2024 4:38:01 PM | Luzon Grid-02/10/2024 16:38: Labrador 230kV Bus 1 was energized at 1637H. (Planned Outage) [WEBSMS] | CLUZ
2/10/2024 12:56:02 PM | Visayas Grid-02/10/2024 12:56: Calongcalong - Century Peak 69 kV Line energized at 1254H (Unplanned Outage) [WEBSMS] | CVIS
2/10/2024 12:47:18 PM | [NSO Update] Mindanao Grid-02/10/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3313MW, PK=1930MW, RR=75MW, NetOpMargin: PM=1307, EVE=1237 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @104MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
2/10/2024 12:44:50 PM | [NSO Update] Visayas Grid-02/10/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2394MW, PK=1841MW, RR=81MW, NetOpMargin: PM=472, EVE=289 Highest Unit O/L: PEDC U3 @150MW Derated Plant: TGPP @80.3MW, LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
2/10/2024 12:43:30 PM | [NSO Update] Luzon Grid-02/10/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14426MW, PK=8878MW, RR=338MW, NetOpMargin: PM=5211, EVE=4327 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW [WEBSMS] | CLUZ
2/10/2024 12:25:22 PM | Visayas Grid-02/10/2024 12:25: Calongcalong - Century Peak 69 kV Line tripped at 1214H (Unplanned Outage) [WEBSMS] | CVIS
2/10/2024 10:30:02 AM | Visayas Grid-02/10/2024 10:30: LGPP U3 shutdown at 1025H (Unplanned Outage) [WEBSMS] | CVIS
2/10/2024 10:02:13 AM | Luzon Grid-02/10/2024 10:02: Balsik-San Marcelino 230kV Line 2 de-energized at 1001H (Planned Outage) [WEBSMS] | CLUZ
2/10/2024 9:14:02 AM | Luzon Grid-02/10/2024 09:14: Balsik SS 230kV Bus 1 de-energized at 0913H (Planned Outage) [WEBSMS] | CLUZ
2/10/2024 8:36:03 AM | Luzon Grid-02/10/2024 08:36: Sta. Rita 10 online at 0829H (Planned Outage) [WEBSMS] | CLUZ
2/10/2024 8:25:39 AM | Luzon Grid-02/10/2024 08:25: One Subic Power 55MVA T01 (8XF01OSP) de-energized at 0820H (Planned Outage) [WEBSMS] | CLUZ
2/10/2024 8:03:49 AM | Mindanao Grid-02/10/2024 08:07: AGUS 4 Unit 3 shutdown at 0801H (PMS, Non-GOMP). [WEBSMS] | CMIN
2/10/2024 7:44:26 AM | Luzon Grid-02/10/2024 07:44: Labrador SS 230kV Bus 1 de-energized at 0744H (Planned Outage) [WEBSMS] | CLUZ
2/10/2024 7:23:00 AM | Mindanao Grid-02/10/2024 07:26: Bislig SS 138kV 50MVA Power Transformer # 1 de-energized at 0709H for annual PMS. Planned Outage / GOMP. [WEBSMS] | CMIN
2/10/2024 7:08:01 AM | Luzon Grid-02/10/2024 07:08: San Jose SS 750MVA T04 de-energized at 0707H (Planned Outage) [WEBSMS] | CLUZ
2/10/2024 6:57:49 AM | Luzon Grid-02/10/2024 06:57: Dasmarinas SS 300MVA T02 de-energized at 0657H (Planned Outage) [WEBSMS] | CLUZ
2/10/2024 6:50:56 AM | Mindanao Grid-02/10/2024 06:54: Baloi-Agus 5 138KV line de-energized at 0633H. P&E request under MSRP Stage 1 Schedule III. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
2/10/2024 5:47:09 AM | [NSO Update] Mindanao Grid-02/10/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3321MW, PK=1764MW, RR=72MW, NetOpMargin: AM=1485, PM=1286, EVE=1222 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @104MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
2/10/2024 5:45:51 AM | [NSO Update] Visayas Grid-02/10/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2470MW, PK=1852MW, RR=79MW, NetOpMargin: AM=539, PM=329, EVE=254 Highest Unit O/L: PEDC 3 @150MW Derated Plant: PCPC @30MW, LEYTE A @313MW, PGPP1 @76MW [WEBSMS] | CVIS
2/10/2024 5:43:45 AM | [NSO Update] Luzon Grid-02/10/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14783MW, PK=9128MW, RR=347MW, NetOpMargin: AM=5308, PM=5483, EVE=4391 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW [WEBSMS] | CLUZ
2/10/2024 5:07:42 AM | Mindanao Grid-02/10/2024 05:11: Villanueva SS PCB 7-05CB08VLN re-energized at 0503H (Planned Outage). Non-GOMP. No line involved. [WEBSMS] | CMIN
2/10/2024 4:56:16 AM | Mindanao Grid-02/10/2024 04:59: Villanueva SS PCB 7-05CB08VLN de-energized at 0441H (Planned Outage) to conduct hotspot correction. No line involve. [WEBSMS] | CMIN
2/10/2024 4:47:00 AM | [NSO Update] Mindanao Grid-02/10/2024 04:50: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
2/10/2024 4:46:44 AM | [NSO Update] Visayas Grid-02/10/2024 04:46: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
2/10/2024 4:46:31 AM | [NSO Update] Luzon Grid-02/10/2024 04:46: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
2/9/2024 11:40:01 PM | Mindanao Grid-02/09/2024 23:43: STEAG Unit 1 online at 2317H (Unplanned Outage) [WEBSMS] | CMIN
2/9/2024 10:15:26 PM | Mindanao Grid-02/09/2024 22:19: Asiga Hydro (ASG) online at 2024H. (Unplanned Outage). [WEBSMS] | CMIN
2/9/2024 10:14:41 PM | Mindanao Grid-02/09/2024 22:18: APC Lake Mainit Hydro online at 2045H. (Unplanned Outage). [WEBSMS] | CMIN
2/9/2024 8:11:17 PM | Luzon Grid-02/09/2024 20:11: MPGC Unit 3 online at 2007H after the Load Rejection Test. (On-going Commissioning Test) [WEBSMS] | CLUZ
2/9/2024 8:11:06 PM | Mindanao Grid-02/09/2024 20:14: APC Lake Mainit HEP with 20.8MW tripped at 2003H. Indication: Power Signal Fault (Unplanned Outage) No FLV. [WEBSMS] | CMIN
2/9/2024 8:09:17 PM | Luzon Grid-02/09/2024 20:09: MPGC Unit 3 successfully conducted 100% Load Rejection Test(150MW) at 2003H. The lowest Luzon system frequency was only at 59.76Hz during the LRT. (On-going Commissiong Test) [WEBSMS] | CLUZ
2/9/2024 8:04:35 PM | Mindanao Grid-02/09/2024 20:08: ASIGA (ASG) HEP with 8MW load tripped at 1950H. Indication: Restricted Earth Fault. (Unplanned Outage). [WEBSMS] | CMIN
2/9/2024 8:01:33 PM | Luzon Grid-02/09/2024 20:01: Bolo-Cayanga 230kV line 2(Customer Owned and Maintained Line) was unlooped at Cayanga side at 1958H. (Unplanned Outage) [WEBSMS] | CLUZ
2/9/2024 7:35:47 PM | Visayas Grid-02/09/2024 19:35: Magdugo - TVI 230 kV Line 2 energized at 1924H. (Planned Outage) [WEBSMS] | CVIS
2/9/2024 7:24:50 PM | Mindanao Grid-02/09/2024 19:28: WMPC DG10 shutdown at 1917H, from MO Dispatched. Follow RTD. [WEBSMS] | CMIN
2/9/2024 7:20:01 PM | Luzon Grid-02/09/2024 19:20: Sta Rita Module 10 shutdown at 1915H. (On-going LNG Commissioning) [WEBSMS] | CLUZ
2/9/2024 7:13:39 PM | Luzon Grid-02/09/2024 19:13: Ilijan PCB 9-02CB08ILJ was closed at 1844H. (Customer Owned - Normalization of Block B Unit Transformers) [WEBSMS] | CLUZ
2/9/2024 6:40:43 PM | Luzon Grid-02/09/2024 18:40: Ilijan Block B Unit Transformers were energized upon closing of PCB 9-02CB24ILJ at 1837H. [WEBSMS] | CLUZ
2/9/2024 6:40:09 PM | Mindanao Grid-02/09/2024 18:43: WMPC DG10 Online at 1820H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
2/9/2024 6:18:59 PM | Luzon Grid-02/09/2024 18:19: Ilijan PCBs 9-02CB24ILJ and 9-02CB08ILJ were opened at 1812H and 1813H respectively to facilitate the normalization of Block B Unit Transformers. [WEBSMS] | CLUZ
2/9/2024 5:46:15 PM | [NSO Update] Mindanao Grid-02/09/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3170MW, PK=1985MW, RR=70MW, NetOpMargin: EVE=1115 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
2/9/2024 5:42:13 PM | [NSO Update] Visayas Grid-02/09/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2387MW, PK=2020MW, RR=79MW, NetOpMargin: EVE=288 Highest Unit O/L: PEDC U3 @150MW Derated Plant: PCPC @30MW, LEYTE A @313MW, PGPP1 @76MW [WEBSMS] | CVIS
2/9/2024 5:39:32 PM | [NSO Update] Luzon Grid-02/09/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13815MW, PK=9495MW, RR=324MW, NetOpMargin: EVE=3396 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/9/2024 5:09:44 PM | Luzon Grid-02/09/2024 17:09: Correction: Bolo-Cayanga 230kV line 1(Customer Owned and Maintained line) was looped at Cayanga Substation side at 1701H. (Unplanned Outage requested by Cayanga Solar) [WEBSMS] | CLUZ
2/9/2024 5:02:52 PM | Luzon Grid-02/09/2024 17:02: Bolo-Cayanga 230kV line 1 was restored at 1701H. (Planned Outage) [WEBSMS] | CLUZ
2/9/2024 4:59:57 PM | Luzon Grid-02/09/2024 17:00: Bantay PCB 6-01CB24BAN was energized at 1658H. (Planned Outage) [WEBSMS] | CLUZ
2/9/2024 4:41:32 PM | Luzon Grid-02/09/2024 16:41: Nagsaag SS PCB 9Z-03CB24NGS was energized at 1640H. (Planned Outage) [WEBSMS] | CLUZ
2/9/2024 4:14:53 PM | Luzon Grid-02/09/2024 16:14: Calaca PCB 8-05CB04CLC was energized at 1613H. (Unplanned Outage) [WEBSMS] | CLUZ
2/9/2024 3:32:00 PM | Mindanao Grid-02/09/2024 15:35: Sultan Kudarat SS Bus #2 re-energized at 1529H (Planned Outage). Non-GOMP. P&E Request. [WEBSMS] | CMIN
2/9/2024 2:57:26 PM | Luzon Grid-02/09/2024 14:57: Calaca PCB 8-05CB04CLC was de-energized at 1456H. (Unplanned Outage) [WEBSMS] | CLUZ
2/9/2024 2:27:09 PM | Luzon Grid-02/09/2024 14:27: Laoag 300MVA T02 restored at 1426H (Unplanned Outage) [WEBSMS] | CLUZ
2/9/2024 1:39:29 PM | Mindanao Grid-02/09/2024 13:43: WMPC DG10 shutdown at 1336H, from MO Dispatched. Follow RTD. [WEBSMS] | CMIN
2/9/2024 1:16:17 PM | Mindanao Grid-02/09/2024 13:19: WMPC DG10 Online at 1313H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
2/9/2024 12:50:40 PM | [NSO Update] Luzon Grid-02/09/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14838MW, PK=9188MW, RR=328MW, NetOpMargin: PM=5322, EVE=4099 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/9/2024 12:35:17 PM | [NSO Update] Mindanao Grid-02/09/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3222MW, PK=1998MW, RR=75MW, NetOpMargin: PM=1149, EVE=1083 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
2/9/2024 12:31:26 PM | [NSO Update] Visayas Grid-02/09/2024 12:31: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2392MW, PK=1944MW, RR=80MW, NetOpMargin: PM=368, EVE=251 Highest Unit O/L: PEDC U3 @150MW Derated Plant: PCPC @30MW, LEYTE A @313MW, PGPP1 @76MW [WEBSMS] | CVIS
2/9/2024 12:06:35 PM | Luzon Grid-02/09/2024 12:06: Balsik SS PCB 9Z-02CB04BIK restored at 1206H (Planned Outage) [WEBSMS] | CLUZ
2/9/2024 12:02:41 PM | Luzon Grid-02/09/2024 12:02: Laoag 300MVA TO2 energized on high side at 1159H (Unplanned Outage/For Soaking) [WEBSMS] | CLUZ
2/9/2024 9:07:09 AM | Luzon Grid-02/09/2024 09:07: Balsik SS PCB 9Z-02CB04BIK de-energized at 0906H (Planned Outage) [WEBSMS] | CLUZ
2/9/2024 8:37:25 AM | Mindanao Grid-02/09/2024 08:41: Sultan Kudarat SS Bus #2 shutdown at 0803H (Planned Outage). P & E Request. [WEBSMS] | CMIN
2/9/2024 7:16:47 AM | Luzon Grid-02/09/2024 07:16: Nagsaag SS PCB 9Z-03CB24NGS de-energized at 0709H (Planned Outage) [WEBSMS] | CLUZ
2/9/2024 5:47:30 AM | [NSO Update] Luzon Grid-02/09/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14878MW, PK=8975MW, RR=335MW, NetOpMargin: AM=5569, PM=4785, EVE=3838 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/9/2024 5:46:30 AM | [NSO Update] Mindanao Grid-02/09/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3228MW, PK=1895MW, RR=72MW, NetOpMargin: AM=1261, PM=1094, EVE=996 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
2/9/2024 5:45:17 AM | [NSO Update] Visayas Grid-02/09/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2352MW, PK=1844MW, RR=79MW, NetOpMargin: AM=429, PM=302, EVE=279 Highest Unit O/L: PEDC 3 @150MW Derated Plant: PCPC @30MW, LEYTE A @313MW, PGPP1 @76MW [WEBSMS] | CVIS
2/9/2024 4:45:45 AM | Visayas Grid-02/09/2024 04:45: Magdugo - TVI 230 kV Line 1 de-energized at 0444H. (Planned Outage) [WEBSMS] | CVIS
2/9/2024 4:29:31 AM | [NSO Update] Mindanao Grid-02/09/2024 04:33: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
2/9/2024 4:28:19 AM | [NSO Update] Visayas Grid-02/09/2024 04:28: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
2/9/2024 4:28:02 AM | [NSO Update] Luzon Grid-02/09/2024 04:28: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
2/9/2024 4:06:43 AM | Mindanao Grid-02/09/2024 04:10: Baloi SS 138KV Bus 2 re-energized at 0400H (Planned Outage) [WEBSMS] | CMIN
2/8/2024 11:55:57 PM | Visayas Grid-02/08/2024 23:55: Cebu SS 138 kV Bus 1 energized at 2348H. (Planned Outage) [WEBSMS] | CVIS
2/8/2024 11:07:43 PM | Mindanao Grid-02/08/2024 23:11: Sultan Kudarat SS 138KV Bus 1 re-energized at 2303H. (Planned Outage) [WEBSMS] | CMIN
2/8/2024 10:15:57 PM | Luzon Grid-02/08/2024 22:15: San Jose PCB 8-05CB08SJO restored at 2215H. (Unplanned Outage) [WEBSMS] | CLUZ
2/8/2024 9:37:24 PM | Mindanao Grid-02/08/2024 21:41: Baloi SS 138KV Bus 2 deenergized at 2129H. Planned Outage. [WEBSMS] | CMIN
2/8/2024 9:15:19 PM | Mindanao Grid-02/08/2024 21:18: WMPC DG10 shutdown at 2114H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/8/2024 5:48:56 PM | [NSO Update] Mindanao Grid-02/08/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3152MW, PK=2056MW, RR=72MW, NetOpMargin: EVE=1024 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
2/8/2024 5:44:36 PM | [NSO Update] Luzon Grid-02/08/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13866MW, PK=10330MW, RR=403MW, NetOpMargin: EVE=3133 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @177MW, ILIJAN A@450MW [WEBSMS] | CLUZ
2/8/2024 5:35:14 PM | [NSO Update] Visayas Grid-02/08/2024 17:35: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2427MW, PK=2087MW, RR=79MW, NetOpMargin: EVE=260 Highest Unit O/L: PEDC 3 @150MW Derated Plant: PCPC@70MW, LEYTE A @315MW, PGPP1@76MW [WEBSMS] | CVIS
2/8/2024 4:15:36 PM | Mindanao Grid-02/08/2024 16:19: WMPC DG06 shutdown at 1613H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/8/2024 4:06:42 PM | Visayas Grid-02/08/2024 16:06: KSPC U1 cut out at 1602H with 15MW load involved due to possible boiler tube leak. (Unplanned Outage) [WEBSMS] | CVIS
2/8/2024 12:53:19 PM | [NSO Update] Luzon Grid-02/08/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14894MW, PK=10556MW, RR=412MW, NetOpMargin: PM=3926, EVE=3293 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @177MW, ILIJAN A@450MW, [WEBSMS] | CLUZ
2/8/2024 12:39:10 PM | [NSO Update] Visayas Grid-02/08/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2479MW, PK=2117MW, RR=82MW, NetOpMargin: PM=280, EVE=250 Highest Unit O/L: PEDC 3 @150MW Derated Plant: PCPC@70MW, LEYTE A @318MW, PGPP1@76MW, KSPC 1@75MW [WEBSMS] | CVIS
2/8/2024 12:36:26 PM | [NSO Update] Mindanao Grid-02/08/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3205MW, PK=2130MW, RR=75MW, NetOpMargin: PM=1000, EVE=1041 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
2/8/2024 11:21:25 AM | Mindanao Grid-02/08/2024 11:25: Bislig - Nabunturan 138KV Line auto tripped and auto reclosed at 105955H and 105958H respectively. (Unplanned Outage) [WEBSMS] | CMIN
2/8/2024 10:52:02 AM | Mindanao Grid-02/08/2024 10:55: WMPC DG06 online at 1050H. RPS - System voltage requirement. [WEBSMS] | CMIN
2/8/2024 10:39:40 AM | Mindanao Grid-02/08/2024 10:43: SUPREME POWER MATI online at 1011H (Unplanned Outage) [WEBSMS] | CMIN
2/8/2024 10:38:55 AM | Mindanao Grid-02/08/2024 10:42: SUPREME POWER MATI tripped with 3.2MW load at 1006H (Unplanned Outage). Freq dipped at 60.00Hz. Indication: TE 622 charged air temp charged air cooler (CAC) high shutdown. [WEBSMS] | CMIN
2/8/2024 9:10:09 AM | Mindanao Grid-02/08/2024 09:13: WMPC DG10 online at 0850H. RPS - System voltage requirement. [WEBSMS] | CMIN
2/8/2024 8:08:05 AM | Luzon Grid-02/08/2024 08:08: Bantay PCB 6-01CB24BAN was de-energized at 0803H. (Planned Outage) [WEBSMS] | CLUZ
2/8/2024 8:04:22 AM | Mindanao Grid-02/08/2024 08:08: Sultan Kudarat SS 138KV Bus 1 deenergized at 0802H (Planned Outage) [WEBSMS] | CMIN
2/8/2024 5:57:41 AM | [NSO Update] Mindanao Grid-02/08/2024 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3216MW, PK=2056MW, RR=72MW, NetOpMargin: AM=1088, PM=959, EVE=1063 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
2/8/2024 5:55:28 AM | [NSO Update] Visayas Grid-02/08/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2351MW, PK=2016MW, RR=79MW, NetOpMargin: AM=256, PM=205, EVE=185 Highest Unit O/L: PEDC 3 @150MW Derated Plant: PCPC @65MW, LEYTE A @318MW, PGPP1 @76MW [WEBSMS] | CVIS
2/8/2024 5:51:02 AM | [NSO Update] Luzon Grid-02/08/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15161MW, PK=10303MW, RR=404MW, NetOpMargin: AM=4454, PM=4097, EVE=3635 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/8/2024 4:23:41 AM | [NSO Update] Mindanao Grid-02/08/2024 04:27: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
2/8/2024 4:23:25 AM | [NSO Update] Visayas Grid-02/08/2024 04:23: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
2/8/2024 4:23:01 AM | [NSO Update] Luzon Grid-02/08/2024 04:22: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
2/8/2024 2:26:42 AM | Luzon Grid-02/08/2024 02:26: San Jose PCB 8-05CB08SJO emergency shutdown at 0213H due to air leak (Unplanned Outage) [WEBSMS] | CLUZ
2/7/2024 11:40:43 PM | Mindanao Grid-02/07/2024 23:44: Libertad Power online at 2238H. Unplanned Outage. [WEBSMS] | CMIN
2/7/2024 10:07:08 PM | Luzon Grid-02/07/2024 22:07: Laoag 300MVA TO2 de-energized at 2207H to conduct inspection and testing due to the transformer�s unusual sound after the earthquake (Unplanned Outage) [WEBSMS] | CLUZ
2/7/2024 9:47:54 PM | Mindanao Grid-02/07/2024 21:51: Libertad Power with 6MW tripped at 2033H. Indication: Earth fault. Unplanned Outage. [WEBSMS] | CMIN
2/7/2024 9:20:02 PM | Mindanao Grid-02/07/2024 21:23: WMPC DG10 shutdown at 2114H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
2/7/2024 8:11:07 PM | Luzon Grid-02/07/2024 20:11: MPGC Unit 3 online at 2009H (Planned Outage-On Commissioning Test) [WEBSMS] | CLUZ
2/7/2024 8:07:23 PM | Luzon Grid-02/07/2024 20:07: MPGC Unit 3 successfully conducted 75% (112.5MW) Load Rejection Test at 2004H. (On-going commissioning test) [WEBSMS] | CLUZ
2/7/2024 7:13:05 PM | Mindanao Grid-02/07/2024 19:16: WMPC DG06 Shutdown at 1904H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
2/7/2024 7:02:42 PM | Mindanao Grid-02/07/2024 19:06: WMPC DG06 Online at 1821H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
2/7/2024 5:49:39 PM | [NSO Update] Luzon Grid-02/07/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13724MW, PK=10231MW, RR=362MW, NetOpMargin: EVE=3131 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @177MW, GMEC 2 @240MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/7/2024 5:42:56 PM | [NSO Update] Mindanao Grid-02/07/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3205MW, PK=2070MW, RR=72MW, NetOpMargin: EVE=1063 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @155MW, AG7 @30MW, PG4 @200MW [WEBSMS] | CMIN
2/7/2024 5:37:27 PM | [NSO Update] Visayas Grid-02/07/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2418MW, PK=2025MW, RR=84MW, NetOpMargin: EVE=309 Highest Unit O/L: PEDC U3 @150MW Derated Plant: LEYTE A @318MW, PGPP1 @76MW [WEBSMS] | CVIS
2/7/2024 5:32:26 PM | Mindanao Grid-02/07/2024 17:36: Toril SS 230kV 300MVA Power Transformer No.2 energized at 1728H (Planned Outage/Non GOMP) [WEBSMS] | CMIN
2/7/2024 4:28:31 PM | Mindanao Grid-02/07/2024 16:32: WMPC DG06 shutdown at 1614H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
2/7/2024 3:32:03 PM | Mindanao Grid-02/07/2024 15:35: WMPC DG06 Online at 1525H, from Forced Outage. RPS-System Voltage Requirement. [WEBSMS] | CMIN
2/7/2024 3:28:49 PM | Mindanao Grid-02/07/2024 15:32: Update: WMPC DG06 with 8.5MW gross generation tripped at 1517H. Indication: HT Low Pressure Stop. RPS-System Voltage Requirement. Unplanned Outage. [WEBSMS] | CMIN
2/7/2024 3:26:50 PM | Mindanao Grid-02/07/2024 15:30: WMPC DG06 with 8.5MW gross generation tripped at 1517H. RPS-System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
2/7/2024 1:12:40 PM | Luzon Grid-02/07/2024 13:12: Currimao-Paguludan 69kV line(Customer Owned) was restored at 1311H. (Planned Outage) [WEBSMS] | CLUZ
2/7/2024 12:59:46 PM | [NSO Update] Luzon Grid-02/07/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14843MW, PK=10486MW, RR=387MW, NetOpMargin: PM=3970, EVE=3383 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @177MW, GMEC 2 @240MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/7/2024 12:48:13 PM | Mindanao Grid-02/07/2024 12:52: Butuan- Placer 138kV Line 1 auto-tripped and auto-reclosed 1218H at Placer SS side only. (Unplanned outage) [WEBSMS] | CMIN
2/7/2024 12:40:52 PM | [NSO Update] Mindanao Grid-02/07/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3266MW, PK=2118MW, RR=75MW, NetOpMargin: PM=1073, EVE=1126 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @165MW, AG7 @30MW, PG4 @200MW [WEBSMS] | CMIN
2/7/2024 12:40:50 PM | [NSO Update] Visayas Grid-02/07/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2524MW, PK=2078MW, RR=88MW, NetOpMargin: PM=359, EVE=272 Highest Unit O/L: PEDC U3 @150MW Derated Plant: LEYTE A @318MW, PGPP1 @76MW [WEBSMS] | CVIS
2/7/2024 12:07:13 PM | Luzon Grid-02/07/2024 12:07: Bantay-Currimao 115kV line and Currimao-Laoag 115kV line were restored at 1203H and 1204H respectively. (Planned Outage) [WEBSMS] | CLUZ
2/7/2024 12:02:45 PM | Visayas Grid-02/07/2024 12:02: SEPALCO SPP with load of 30.8MW tripped at 1135H, Energized back at 1154H. (Unplanned outage) [WEBSMS] | CVIS
2/7/2024 11:11:00 AM | Mindanao Grid-02/07/2024 11:14: Updated: Toril SS 230kV 300MVA Power Transformer No.2 de-energized at 0841H (Planned Outage/Non GOMP) [WEBSMS] | CMIN
2/7/2024 11:09:51 AM | Mindanao Grid-02/07/2024 11:13: WMPC DG06 online at 1049H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/7/2024 8:51:28 AM | Mindanao Grid-02/07/2024 08:55: WMPC DG10 online at 0848H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/7/2024 8:48:51 AM | Mindanao Grid-02/07/2024 08:52: Toril SS 230 300MVA Power Transformer @shutdown at 0841H (Planned Outage) [WEBSMS] | CMIN
2/7/2024 8:37:13 AM | Luzon Grid-02/07/2024 08:37: Laoag-Currimao 115kV line and Currimao-Bantay 115kV line were de-energized at 0833H and 0834H respectively. (Planned Outage) [WEBSMS] | CLUZ
2/7/2024 7:43:11 AM | Luzon Grid-02/07/2024 07:43: Currimao-Paguludan 69kV line(Customer Owned) was de-energized at 0742H. (Planned Outage) [WEBSMS] | CLUZ
2/7/2024 5:37:07 AM | [NSO Update] Mindanao Grid-02/07/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3230MW, PK=2069MW, RR=72MW, NetOpMargin: AM=1090, PM=891, EVE=935 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @165MW, AG7 @30MW, PG4 @150MW [WEBSMS] | CMIN
2/7/2024 5:35:49 AM | [NSO Update] Visayas Grid-02/07/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2464MW, PK=1985MW, RR=85MW, NetOpMargin: AM=394, PM=275, EVE=251 Highest Unit O/L: PEDC U3 @150MW Derated Plant: LEYTE A @318MW, PGPP1 @76MW [WEBSMS] | CVIS
2/7/2024 5:34:13 AM | [NSO Update] Luzon Grid-02/07/2024 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14767MW, PK=10230MW, RR=382MW, NetOpMargin: AM=4154, PM=4007, EVE=3353 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, GMEC 2 @240MW, MSLC1 @325MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/7/2024 4:13:34 AM | [NSO Update] Luzon Grid-02/07/2024 04:13: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
2/7/2024 4:12:28 AM | [NSO Update] Mindanao Grid-02/07/2024 04:16: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
2/7/2024 4:12:11 AM | [NSO Update] Visayas Grid-02/07/2024 04:12: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
2/7/2024 12:38:49 AM | Mindanao Grid-02/07/2024 00:42: Update: Pulangi IV Unit 3 with 69.46MW load tripped at 2316H. Indication: Residual Over current (Y). No ALD, frequency dip to 59.493Hz. Online at 0028H (Unplanned Outage) [WEBSMS] | CMIN
2/7/2024 12:24:20 AM | Visayas Grid-02/07/2024 00:24: THVI U1 cut out at 0023H (Planned Outage) [WEBSMS] | CVIS
2/6/2024 11:25:12 PM | Mindanao Grid-02/06/2024 23:29: Pulangi IV Unit 3 with 69.46MW load tripped at 2316H. Indication: For investigation. No ALD, frequency dip to 59.493Hz (Unplanned Outage) [WEBSMS] | CMIN
2/6/2024 9:48:21 PM | Mindanao Grid-02/06/2024 21:52: Agus 6 Unit 1 online at 2141H from extended GOMP maintenance. (Unplanned Outage) [WEBSMS] | CMIN
2/6/2024 9:14:45 PM | Mindanao Grid-02/06/2024 21:18: WMPC DG10 shutdown at 2114H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/6/2024 8:12:58 PM | Luzon Grid-02/06/2024 20:13: MPGC Unit 3 online at 2011H from Load Rejection Test(LRT). (On-going commissioning test) [WEBSMS] | CLUZ
2/6/2024 8:07:59 PM | Luzon Grid-02/06/2024 20:08: MPGC Unit 3 successfully conducted 50% Load Rejection Test(75MW) at 2005H. (On-going commissioning test) [WEBSMS] | CLUZ
2/6/2024 6:19:08 PM | Mindanao Grid-02/06/2024 18:23: Lake Mainit HEP online at 1806H. (Unplanned Outage) [WEBSMS] | CMIN
2/6/2024 6:11:33 PM | Mindanao Grid-02/06/2024 18:15: Pulangi IV Unit 3 online at 1810H from Forced outage. (Unplanned Outage) [WEBSMS] | CMIN
2/6/2024 5:55:36 PM | Mindanao Grid-02/06/2024 17:59: Lake Mainit HEP with 21MW tripped at 1751H. Indication: Excitation Voltage Trip. (Unplanned Outage) [WEBSMS] | CMIN
2/6/2024 5:35:46 PM | [NSO Update] Mindanao Grid-02/06/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3136MW, PK=2075MW, RR=72MW, NetOpMargin: EVE=989 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @130MW [WEBSMS] | CMIN
2/6/2024 5:33:58 PM | [NSO Update] Visayas Grid-02/06/2024 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2372MW, PK=1949MW, RR=82MW, NetOpMargin: EVE=342 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE A @318MW, PGPP1 @76MW [WEBSMS] | CVIS
2/6/2024 5:31:45 PM | [NSO Update] Luzon Grid-02/06/2024 17:31: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13803MW, PK=10195MW, RR=403MW, NetOpMargin: EVE=3205 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, MSLC2 @280MW, MSLC3 @325MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/6/2024 4:15:17 PM | Mindanao Grid-02/06/2024 16:19: WMPC DG06 shutdown at 1615H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/6/2024 3:33:51 PM | Mindanao Grid-02/06/2024 15:37: Agus 6 SS 69KV Bus 1 reenergized at 1530H. Planned Outage. [WEBSMS] | CMIN
2/6/2024 12:42:15 PM | [NSO Update] Mindanao Grid-02/06/2024 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3188MW, PK=2133MW, RR=75MW, NetOpMargin: PM=981, EVE=1022 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @130MW [WEBSMS] | CMIN
2/6/2024 12:39:59 PM | [NSO Update] Visayas Grid-02/06/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2547MW, PK=2079MW, RR=87MW, NetOpMargin: PM=381, EVE=351 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: Leyte A @ 318MW, PGPP1 @ 76MW [WEBSMS] | CVIS
2/6/2024 12:37:36 PM | [NSO Update] Luzon Grid-02/06/2024 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14691MW, PK=10770MW, RR=423MW, NetOpMargin: PM=3498, EVE=2979 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 177MW, GMEC 2 @ 240MW, Masinloc 3 @ 325MW, SLTEC 1 @ 117MW, SLTEC 2 @ 115MW, Ilijan A @ 450MW [WEBSMS] | CLUZ
2/6/2024 10:51:08 AM | Mindanao Grid-02/06/2024 10:54: WMPC DG06 online at 1048H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
2/6/2024 8:51:11 AM | Mindanao Grid-02/06/2024 08:55: WMPC DG10 online at 0849H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
2/6/2024 8:47:05 AM | Mindanao Grid-02/06/2024 08:50: Agus 6 SS 69KV Bus 1 deenergized at 0833H. Planned Outage. [WEBSMS] | CMIN
2/6/2024 7:09:27 AM | Mindanao Grid-02/06/2024 07:13: ASIGA (ASG) HEP with 8MW load tripped at 0649H. Indication: Restricted Earth Fault. (Unplanned Outage). [WEBSMS] | CMIN
2/6/2024 5:48:43 AM | [NSO Update] Luzon Grid-02/06/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14886MW, PK=10590MW, RR=422MW, NetOpMargin: AM=3874, PM=3344, EVE=2777 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC2 @177MW, GMEC 2 @240MW, ILIJAN A @ 450MW [WEBSMS] | CLUZ
2/6/2024 5:31:25 AM | [NSO Update] Visayas Grid-02/06/2024 05:31: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2519MW, PK=2081MW, RR=85MW, NetOpMargin: AM=353, PM=518, EVE=338 Highest Unit O/L: THVI 1@169MW Derated Plant: LEYTE A @318MW, PGPP1 @76MW [WEBSMS] | CVIS
2/6/2024 5:25:31 AM | [NSO Update] Mindanao Grid-02/06/2024 05:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3195MW, PK=2124MW, RR=72MW, NetOpMargin: AM=998, PM=942, EVE=921 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @130MW [WEBSMS] | CMIN
2/6/2024 4:03:20 AM | [NSO Update] Luzon Grid-02/06/2024 04:03: Weather Advisory: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
2/6/2024 4:03:16 AM | [NSO Update] Visayas Grid-02/06/2024 04:03: Weather Advisory: Easterlies affecting the eastern section of the country. [WEBSMS] | CVIS
2/6/2024 4:03:14 AM | [NSO Update] Mindanao Grid-02/06/2024 04:07: Weather Advisory: Easterlies affecting the eastern section of the country. [WEBSMS] | CMIN
2/5/2024 11:56:01 PM | Visayas Grid-02/05/2024 23:56: Magdugo SS 230 KV bus 1 energized at 2355H (Planned Outage) [WEBSMS] | CVIS
2/5/2024 9:15:24 PM | Mindanao Grid-02/05/2024 21:19: WMPC DG10 shutdown at 2114H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/5/2024 5:41:20 PM | [NSO Update] Luzon Grid-02/05/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13817MW, PK=10530MW, RR=374MW, NetOpMargin: EVE=2914 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 177MW, Ilijan A @ 450MW [WEBSMS] | CLUZ
2/5/2024 5:41:10 PM | [NSO Update] Visayas Grid-02/05/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2490MW, PK=2119MW, RR=85MW, NetOpMargin: EVE=286 Highest Unit O/L: THVI 1@169MW Derated Plant: Leyte A @ 316MW, PGPP1 @ 76MW [WEBSMS] | CVIS
2/5/2024 5:41:05 PM | [NSO Update] Mindanao Grid-02/05/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3166MW, PK=2064MW, RR=70MW, NetOpMargin: EVE=1031 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @130MW [WEBSMS] | CMIN
2/5/2024 5:03:29 PM | Mindanao Grid-02/05/2024 17:07: STEAG U1 with 100MW gross generation on Emergency Shutdown at 1650H due to Boiler Fouling. Follow RTD and Ramp rate. Unplanned Outage. [WEBSMS] | CMIN
2/5/2024 4:56:09 PM | Luzon Grid-02/05/2024 16:56: For info: Angat-San Jose 115kV Line 1 was unloop at 1439H due to tripping of Angat Main transformer B due to differential protection alarm. [WEBSMS] | CLUZ
2/5/2024 4:18:56 PM | Mindanao Grid-02/05/2024 16:22: WMPC DG08 shutdown at 1614H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/5/2024 3:48:15 PM | Visayas Grid-02/05/2024 15:48: Cebu GIS 300 MVA 230/138/13.8 kV TR1 energized at 1546H (Planned Outage) [WEBSMS] | CVIS
2/5/2024 3:44:39 PM | Visayas Grid-02/05/2024 15:44: Sangi - 2nd Lift 34.5 kV Line energized at 1543H (Planned Outage) [WEBSMS] | CVIS
2/5/2024 3:28:37 PM | Luzon Grid-02/05/2024 15:28: Angat-San Jose 115kV Line 1 which tripped at 1439H at Angat side restored at 1511H (Unplanned Outage) [WEBSMS] | CLUZ
2/5/2024 3:14:57 PM | Mindanao Grid-02/05/2024 15:18: Lake Mainit HEPP (AGC) Online at 1441H. Unplanned Outage. [WEBSMS] | CMIN
2/5/2024 2:45:30 PM | Mindanao Grid-02/05/2024 14:49: Lake Mainit HEPP (AGC) with 14.4MW gross generation tripped at 1432H. Frequency=59.8Hz. Indication: Differential Current. Unplanned Outage. [WEBSMS] | CMIN
2/5/2024 1:25:01 PM | Mindanao Grid-02/05/2024 13:28: Lake Mainit HEPP (AGC) Online at 1115H. Unplanned Outage. [WEBSMS] | CMIN
2/5/2024 12:47:15 PM | [NSO Update] Luzon Grid-02/05/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14867MW, PK=10882MW, RR=377MW, NetOpMargin: PM=3608, EVE=3146 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 177MW, SLTEC 1 @ 117MW, SLTEC 2 @ 120MW, Ilijan A @ 450MW [WEBSMS] | CLUZ
2/5/2024 12:45:39 PM | [NSO Update] Mindanao Grid-02/05/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3331MW, PK=2050MW, RR=75MW, NetOpMargin: PM=1206, EVE=1199 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @130MW [WEBSMS] | CMIN
2/5/2024 12:44:45 PM | [NSO Update] Visayas Grid-02/05/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2633MW, PK=2147MW, RR=87MW, NetOpMargin: PM=399, EVE=298 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: Leyte A @ 315MW, PGPP1 @ 76MW [WEBSMS] | CVIS
2/5/2024 11:13:53 AM | Mindanao Grid-02/05/2024 11:17: Lake Mainit HEPP (AGC) with 14.4MW gross generation tripped at 1101H. Frequency=60.0Hz. Indication: Buchholz Relay Trip. Unplanned Outage. [WEBSMS] | CMIN
2/5/2024 10:54:25 AM | Mindanao Grid-02/05/2024 10:58: WMPC DG08 online at 1052H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
2/5/2024 10:51:48 AM | Luzon Grid-02/05/2024 10:51: Pagbilao EHV PCB 8-05CB08PGB restored at 1051H. (Unplanned Outage) [WEBSMS] | CLUZ
2/5/2024 10:05:25 AM | Luzon Grid-02/05/2024 10:05: Pagbilao EHV PCB 8-05CB08PGB tripped at 0959H. (Unplanned Outage) [WEBSMS] | CLUZ
2/5/2024 8:52:48 AM | Mindanao Grid-02/05/2024 08:56: WMPC DG10 online at 0849H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
2/5/2024 8:42:28 AM | Visayas Grid-02/05/2024 08:42: Cebu GIS 300MVA TR1 de-energized at 0838HH (Planned Outage) [WEBSMS] | CVIS
2/5/2024 8:13:42 AM | Mindanao Grid-02/05/2024 08:17: Lake Mainit HEPP (AGC) Online at 0805H. Unplanned Outage. [WEBSMS] | CMIN
2/5/2024 8:02:43 AM | Visayas Grid-02/05/2024 08:02: Sangi-2nd lift 34.5KV T/L de-energized at 0756H (Planned Outage) [WEBSMS] | CVIS
2/5/2024 6:45:59 AM | Luzon Grid-02/05/2024 06:46: SCPC Unit 1 with 99MW tripped at 0643H. Lowest system frequency was 59.736Hz. (Unplanned Outage) [WEBSMS] | CLUZ
2/5/2024 6:37:30 AM | Mindanao Grid-02/05/2024 06:41: Corrected: Lake Mainit HEPP (AGC) with 14.4MW gross generation tripped at 0621H. Frequency Dipped=59.7724Hz. Indication: 86GZ Generator Master Trip Relay. Unplanned Outage. [WEBSMS] | CMIN
2/5/2024 6:35:45 AM | Luzon Grid-02/05/2024 06:35: Quezon-Marilao 230kV line restored at 0634H. (Planned Outage) [WEBSMS] | CLUZ
2/5/2024 6:33:23 AM | Luzon Grid-02/05/2024 06:33: Marilao 300MVA T02 restored at 0632H. (Unplanned Outage) [WEBSMS] | CLUZ
2/5/2024 6:31:33 AM | Mindanao Grid-02/05/2024 06:35: Lake Mainit HEPP (AGC) Tripped at 0621H. Indication: 86GZ Generator Master Trip Relay. Unplanned Outage. [WEBSMS] | CMIN
2/5/2024 6:06:40 AM | [NSO Update] Mindanao Grid-02/05/2024 06:10: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3339MW, PK=1915MW, RR=72MW, NetOpMargin: AM=1352, PM=1145, EVE=1095 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @130MW [WEBSMS] | CMIN
2/5/2024 6:04:06 AM | [NSO Update] Visayas Grid-02/05/2024 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2703MW, PK=2080MW, RR=84MW, NetOpMargin: AM=538, PM=387, EVE=307 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
2/5/2024 5:59:28 AM | [NSO Update] Luzon Grid-02/05/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15097MW, PK=10113MW, RR=3785MW, NetOpMargin: AM=4614, PM=4367, EVE=3785 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, ILIJAN A @450MW, SLTEC 1 @117MW [WEBSMS] | CLUZ
2/5/2024 5:30:26 AM | Visayas Grid-02/05/2024 05:30: 230KV Dumanjug-Magdugo Line 2 de-energized at 0529H (Planned Outage) [WEBSMS] | CVIS
2/5/2024 4:48:05 AM | Luzon Grid-02/05/2024 04:48: Bacman 3 online at 0443H (Unplanned Outage) [WEBSMS] | CLUZ
2/5/2024 4:25:18 AM | [NSO Update] Luzon Grid-02/05/2024 04:25: Weather Update: Easterlies affecting the eastern section of the country. Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
2/5/2024 4:21:51 AM | [NSO Update] Mindanao Grid-02/05/2024 04:25: Weather Update: Easterlies affecting the eastern section of the country. Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CMIN
2/5/2024 4:20:39 AM | [NSO Update] Visayas Grid-02/05/2024 04:20: Weather Update: Easterlies affecting the eastern section of the country. Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CVIS
2/5/2024 12:10:28 AM | Luzon Grid-02/05/2024 00:10: Quezon-Marilao 230kV line was de-energized at 0010H. (Planned Outage) [WEBSMS] | CLUZ
2/5/2024 12:04:31 AM | Luzon Grid-02/05/2024 00:04: Marilao 300MVA T02 was de-energized at 0003H. (Unplanned Outage) [WEBSMS] | CLUZ
2/4/2024 10:26:52 PM | Luzon Grid-02/04/2024 22:27: Lal-lo-Cagayan North Solar 69kV line 2 was de-energized at 2224H. (Unplanned Outage) [WEBSMS] | CLUZ
2/4/2024 6:57:40 PM | Mindanao Grid-02/04/2024 19:01: ASIGA (ASG) HEP with 8MW load tripped at 1848H. Indication: Restricted Earth Fault. (Unplanned Outage). [WEBSMS] | CMIN
2/4/2024 6:37:27 PM | [NSO Update] Mindanao Grid-02/04/2024 18:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3266MW, PK=1915MW, RR=72MW, NetOpMargin: EVE=1278 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @130MW [WEBSMS] | CMIN
2/4/2024 6:30:15 PM | [NSO Update] Visayas Grid-02/04/2024 18:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2328MW, PK=1858MW, RR=77MW, NetOpMargin: EVE=393 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @76MW [WEBSMS] | CVIS
2/4/2024 6:17:23 PM | [NSO Update] Luzon Grid-02/04/2024 18:17: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13680MW, PK=9546MW, RR=313MW, NetOpMargin: EVE=3821 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, GMEC 2 @260MW, MSLC3 @300MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/4/2024 6:08:10 PM | Mindanao Grid-02/04/2024 18:11: Lamsan Biomass online at 1800H. Affected by shutdown of Sultan Kudarat SS 69kV BUS for P & E related activities. (Planned Outage) [WEBSMS] | CMIN
2/4/2024 5:46:38 PM | Luzon Grid-02/04/2024 17:46: Laoag-Pasuquin Solar 115kV Line (CO) restored at 1746H (Planned Outage) [WEBSMS] | CLUZ
2/4/2024 5:44:07 PM | Visayas Grid-02/04/2024 17:44: Calongcalong-DaanLungsod 138 KV Line 2 energized at 1639H (Planned Outage) [WEBSMS] | CVIS
2/4/2024 5:40:58 PM | Mindanao Grid-02/04/2024 17:44: Manolo Fortich-Maramag 138kV Line 1 re-energized at 1730H. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
2/4/2024 5:27:58 PM | Luzon Grid-02/04/2024 17:28: MPGC 3 online at 1726H (On Commissioning Test) [WEBSMS] | CLUZ
2/4/2024 4:22:50 PM | Luzon Grid-02/04/2024 16:22: SBMA-Olongapo 230kV Line restored at 1622H (Planned Outage) [WEBSMS] | CLUZ
2/4/2024 4:05:24 PM | Luzon Grid-02/04/2024 16:05: Dasmarinas-Tayabas 500kV Line restored at 1601H (Planned Outage) [WEBSMS] | CLUZ
2/4/2024 4:03:39 PM | Luzon Grid-02/04/2024 16:03: MPGC 3 load reject @ 38 MW at 1600H (On Commissioning Test) [WEBSMS] | CLUZ
2/4/2024 3:21:13 PM | Luzon Grid-02/04/2024 15:21: Olongapo SS 230kV Bus 1 restored at 1520H (Planned Outage) [WEBSMS] | CLUZ
2/4/2024 2:44:16 PM | Mindanao Grid-02/04/2024 14:48: GNPK Unit 3 declared available at 1439H from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
2/4/2024 1:00:15 PM | Luzon Grid-02/04/2024 13:00: Correction: Sta. Rita 40 online at 1213H. (Planned Outage) [WEBSMS] | CLUZ
2/4/2024 1:00:07 PM | [NSO Update] Luzon Grid-02/04/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14246MW, PK=8503MW, RR=296MW, NetOpMargin: PM=5447, EVE=3931 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, GMEC 2 @240MW, MSLC3 @320MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/4/2024 12:58:13 PM | [NSO Update] Mindanao Grid-02/04/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3302MW, PK=1797MW, RR=74MW, NetOpMargin: PM=1430, EVE=1183 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @130MW [WEBSMS] | CMIN
2/4/2024 12:56:47 PM | [NSO Update] Visayas Grid-02/04/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2432MW, PK=1687MW, RR=80MW, NetOpMargin: PM=665, EVE=371 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @76MW [WEBSMS] | CVIS
2/4/2024 12:16:43 PM | Luzon Grid-02/04/2024 12:16: Sta. Rita 40 online at 0013H. (Planned Outage) [WEBSMS] | CLUZ
2/4/2024 10:04:48 AM | Luzon Grid-02/04/2024 10:04: MPGC Unit 3 online at 1003H. (Testing and Commissioning) [WEBSMS] | CLUZ
2/4/2024 8:21:06 AM | Visayas Grid-02/04/2024 08:21: Daang-lungsod SS 138KV Bus 2 de-energized at 0811H.(Planned Outage) [WEBSMS] | CVIS
2/4/2024 8:18:22 AM | Visayas Grid-02/04/2024 08:18: Cebu SS 300MVA TR2 de-energized at 0812H. (Planned Outage) [WEBSMS] | CVIS
2/4/2024 8:03:56 AM | Mindanao Grid-02/04/2024 08:07: Lamsan Biomass shutdown at 0800H (Planned Outage) [WEBSMS] | CMIN
2/4/2024 7:23:08 AM | Mindanao Grid-02/04/2024 07:26: Manolo Fortich-Maramag 138kV Line 1 de-energized at 0610H to facilitate preparation for commissioning / energization of 7-09CB24MRM and its associated DSs & CTs. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
2/4/2024 7:18:58 AM | Visayas Grid-02/04/2024 07:19: Calongcalong-DaanLungsod 138 KV Line 2 de-energized at 0705H (Planned Outage) [WEBSMS] | CVIS
2/4/2024 6:38:37 AM | Luzon Grid-02/04/2024 06:38: SBMA-Olongapo 230kV Line de-energized at 0638H. (Planned Outage) [WEBSMS] | CLUZ
2/4/2024 6:24:22 AM | Luzon Grid-02/04/2024 06:24: Olongapo SS 230kV Bus 1 de-energized at 0623H. (Planned Outage) [WEBSMS] | CLUZ
2/4/2024 6:23:45 AM | Luzon Grid-02/04/2024 06:23: Dasmarinas-Tayabas 500kV Line de-energized at 0623H. (Planned Outage) [WEBSMS] | CLUZ
2/4/2024 6:08:20 AM | Luzon Grid-02/04/2024 06:08: Laoag-Pasuquin Solar 115kV Line (CO) de-energized at 0607H. (Planned Outage) [WEBSMS] | CLUZ
2/4/2024 5:34:28 AM | [NSO Update] Luzon Grid-02/04/2024 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14492MW, PK=8636MW, RR=295MW, NetOpMargin: AM=5561, PM=5707, EVE=4474 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @177MW, GMEC 2 @240MW, MASINLOC 3 @320MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/4/2024 5:29:09 AM | [NSO Update] Mindanao Grid-02/04/2024 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3313MW, PK=1670MW, RR=72MW, NetOpMargin: AM=1571, PM=1523, EVE=1297 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @120MW [WEBSMS] | CMIN
2/4/2024 5:29:06 AM | [NSO Update] Visayas Grid-02/04/2024 05:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2557MW, PK=1699MW, RR=79MW, NetOpMargin: AM=779, PM=798, EVE=490 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
2/4/2024 4:04:17 AM | [NSO Update] Mindanao Grid-02/04/2024 04:08: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the eastern section of Visayas and Mindanao. [WEBSMS] | CMIN
2/4/2024 4:03:59 AM | [NSO Update] Visayas Grid-02/04/2024 04:04: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the eastern section of Visayas and Mindanao. [WEBSMS] | CVIS
2/4/2024 4:03:45 AM | [NSO Update] Luzon Grid-02/04/2024 04:03: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the eastern section of Visayas and Mindanao. [WEBSMS] | CLUZ
2/4/2024 12:57:03 AM | Mindanao Grid-02/04/2024 01:00: Corrected: Sibulan HEPP (A,B and Tudaya1) online at 2226H. Unplanned Outage. [WEBSMS] | CMIN
2/4/2024 12:54:12 AM | Luzon Grid-02/04/2024 00:54: Sta. Rita Module 40 shutdown at 0040H (Planned Outage) [WEBSMS] | CLUZ
2/4/2024 12:52:04 AM | Mindanao Grid-02/04/2024 00:55: Sibulan HEPP (A,B and Tudaya1) online at 1043H. Unplanned Outage. [WEBSMS] | CMIN
2/4/2024 12:23:19 AM | Mindanao Grid-02/04/2024 00:27: Naga Mindanao SS 138kV Bus #1 Online at 0954H (Planned Outage). Non-GOMP. [WEBSMS] | CMIN
2/4/2024 12:14:59 AM | Luzon Grid-02/04/2024 00:15: Kalayaan Unit 3 (134MW) tripped as pump at 0007H. Highest system frequency reached 60.376Hz. [WEBSMS] | CLUZ
2/3/2024 11:17:17 PM | Luzon Grid-02/03/2024 23:17: Correction: SBMA-Subic Solar Power 230 kV Line restored at 2248H (Planned Outage) [WEBSMS] | CLUZ
2/3/2024 10:49:09 PM | Luzon Grid-02/03/2024 22:49: SBMA SS 230kV Bus 1 restored at 2248H (Planned Outage) [WEBSMS] | CLUZ
2/3/2024 10:01:58 PM | Mindanao Grid-02/03/2024 22:05: Villanueva SS 300MVA Transformer #2 energized/loop at 2158H from emergency shutdown due to hotspot correction. (Unplanned Outage). [WEBSMS] | CMIN
2/3/2024 9:47:35 PM | Luzon Grid-02/03/2024 21:47: San Jose 300MVA T02 restored at 2145H, San Jose 300MVA T03 unlopped at 2147H (Planned Outage) [WEBSMS] | CLUZ
2/3/2024 9:39:18 PM | Mindanao Grid-02/03/2024 21:43: Sibulan HEPP (Sibulan A,B and Tudaya1) with total gross generation of 44.15MW tripped at 2103H. Frequency dipped=59.699Hz. Indication: To be determined. Unplanned Outage. [WEBSMS] | CMIN
2/3/2024 9:10:41 PM | Mindanao Grid-02/03/2024 21:14: Emergency shutdown of Villanueva SS 300MVA Transformer #2 at 2056H due to hotspot correction(Temp. of 335 Deg. Cent.) (Unplanned Outage) [WEBSMS] | CMIN
2/3/2024 9:04:49 PM | Luzon Grid-02/03/2024 21:04: SBMA SS 230kV Bus 1 restored at 2104H (Planned Outage) [WEBSMS] | CLUZ
2/3/2024 5:51:37 PM | [NSO Update] Luzon Grid-02/03/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13816MW, PK=9670MW, RR=365MW, NetOpMargin: EVE=3781 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @177MW, MASINLOC 3 @320MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/3/2024 5:44:46 PM | [NSO Update] Visayas Grid-02/03/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2385MW, PK=1985MW, RR=85MW, NetOpMargin: EVE=315 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
2/3/2024 5:42:09 PM | [NSO Update] Mindanao Grid-02/03/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3256MW, PK=2135MW, RR=70MW, NetOpMargin: EVE=1051 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @120MW [WEBSMS] | CMIN
2/3/2024 5:41:38 PM | Visayas Grid-02/03/2024 17:41: Calongcalong-DaanLungsod 138 KV Line 1 energized at 1739H (Planned Outage) [WEBSMS] | CVIS
2/3/2024 5:02:43 PM | Mindanao Grid-02/03/2024 17:06: Agus 6 SS 138kV Bus #2 online/energized at 1657H (Planned Outage). Non-GOMP. [WEBSMS] | CMIN
2/3/2024 4:09:56 PM | Mindanao Grid-02/03/2024 16:13: Naga Mindanao SS Power Transformer #1 Online at 1558H (Planned Outage). Non-GOMP. [WEBSMS] | CMIN
2/3/2024 4:06:19 PM | Mindanao Grid-02/03/2024 16:10: Villanueva SS Power Transformer #1 Online at 1554H (Planned Outage). GOMP. [WEBSMS] | CMIN
2/3/2024 3:17:35 PM | Mindanao Grid-02/03/2024 15:21: WMPC DG10 shutdown at 1514H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/3/2024 12:59:55 PM | [NSO Update] Luzon Grid-02/03/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14630MW, PK=9464MW, RR=377MW, NetOpMargin: PM=4788, EVE=3752 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @177MW, GMEC 2 @150MW, MASINLOC 3 @320MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/3/2024 12:58:14 PM | [NSO Update] Visayas Grid-02/03/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2502MW, PK=1890MW, RR=90MW, NetOpMargin: PM=522, EVE=392 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
2/3/2024 12:56:53 PM | [NSO Update] Mindanao Grid-02/03/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3320MW, PK=1999MW, RR=75MW, NetOpMargin: PM=1246, EVE=1134 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @120MW [WEBSMS] | CMIN
2/3/2024 11:28:40 AM | Visayas Grid-02/03/2024 11:28: Timbaban Hydro cut in at 0830H. (Unplanned Outage) [WEBSMS] | CVIS
2/3/2024 11:24:47 AM | Visayas Grid-02/03/2024 11:24: Timbaban Hydro cut in at 0830H. (Unplanned Outage) [WEBSMS] | CVIS
2/3/2024 9:53:39 AM | Mindanao Grid-02/03/2024 09:57: WMPC DG10 online at 0949H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/3/2024 9:53:23 AM | [NSO Update] Luzon Grid-02/03/2024 09:53: MO-initiated Market Intervention is issued today, 03 February 2024, for Luzon, Visayas, & Mindanao Grid for interval 0925H due to Power Flow Divergent. Market resumption on interval 0930H [WEBSMS] | CLUZ
2/3/2024 9:53:13 AM | [NSO Update] Visayas Grid-02/03/2024 09:53: MO-initiated Market Intervention is issued today, 03 February 2024, for Luzon, Visayas, & Mindanao Grid for interval 0925H due to Power Flow Divergent. Market resumption on interval 0930H [WEBSMS] | CVIS
2/3/2024 9:52:57 AM | [NSO Update] Mindanao Grid-02/03/2024 09:56: MO-initiated Market Intervention is issued today, 03 February 2024, for Luzon, Visayas, & Mindanao Grid for interval 0925H due to Power Flow Divergent. Market resumption on interval 0930H [WEBSMS] | CMIN
2/3/2024 9:50:02 AM | Mindanao Grid-02/03/2024 09:53: Agus 6 SS 138kV Bus #2 shutdown at 0824H (Planned Outage). Non-GOMP. [WEBSMS] | CMIN
2/3/2024 9:10:20 AM | Mindanao Grid-02/03/2024 09:14: shutdown of PCB 7-03CB04PLA at 0904H. Non-GOMP. (Planned Outage). MTD-B Request. [WEBSMS] | CMIN
2/3/2024 9:02:48 AM | Mindanao Grid-02/03/2024 09:06: Villanueva SS Power Transformer #1 Shutdown. PMS. GOMP. (Planned Outage) [WEBSMS] | CMIN
2/3/2024 8:50:26 AM | Visayas Grid-02/03/2024 08:50: Daanlungsod-Calongcalong 138kV Line 2 restored at 0848H. (Unplanned Outage) [WEBSMS] | CVIS
2/3/2024 8:17:25 AM | Visayas Grid-02/03/2024 08:17: Timbaban Hydro tripped at 0800H. (Unplanned Outage) [WEBSMS] | CVIS
2/3/2024 8:03:45 AM | Visayas Grid-02/03/2024 08:03: Daanlungsod-Calongcalong 138kV Line 2 tripped at 0759H. (Unplanned Outage) [WEBSMS] | CVIS
2/3/2024 6:37:25 AM | Visayas Grid-02/03/2024 06:37: Daanlungsod-Calongcalong 138kV Line 1 de-energized at 0634H. (Planned Outage) [WEBSMS] | CVIS
2/3/2024 6:27:09 AM | Luzon Grid-02/03/2024 06:27: San Jose 300MVA T02 de-energized at 0622H, San Jose T03 looped at 0619H (Planned Outage) [WEBSMS] | CLUZ
2/3/2024 6:21:01 AM | Mindanao Grid-02/03/2024 06:24: Nagamin SS 138KV Bus #1 shutdown at 0610H. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
2/3/2024 6:04:10 AM | [NSO Update] Mindanao Grid-02/03/2024 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3325MW, PK=1856MW, RR=72MW, NetOpMargin: AM=1397, PM=1279, EVE=1186 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @120MW [WEBSMS] | CMIN
2/3/2024 5:59:25 AM | [NSO Update] Visayas Grid-02/03/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2460MW, PK=1810MW, RR=87MW, NetOpMargin: AM=562, PM=500, EVE=408 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
2/3/2024 5:55:54 AM | [NSO Update] Luzon Grid-02/03/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14505MW, PK=9271MW, RR=373MW, NetOpMargin: AM=4862, PM=4585, EVE=3674 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @177MW, GMEC 2 @130MW, MASINLOC 3 @320MW, ILIJAN A @450MW, [WEBSMS] | CLUZ
2/3/2024 5:36:17 AM | Luzon Grid-02/03/2024 05:36: BCCPP-Lamao 230kV Line 2 restored at 0536H (Planned Outage) [WEBSMS] | CLUZ
2/3/2024 4:17:43 AM | [NSO Update] Luzon Grid-02/03/2024 04:17: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Trough of the Low Pressure Area (LPA) affecting Southern Mindanao. [WEBSMS] | CLUZ
2/3/2024 4:16:36 AM | [NSO Update] Mindanao Grid-02/03/2024 04:20: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Trough of the Low Pressure Area (LPA) affecting Southern Mindanao. [WEBSMS] | CMIN
2/3/2024 4:14:13 AM | [NSO Update] Visayas Grid-02/03/2024 04:14: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Trough of the Low Pressure Area (LPA) affecting Southern Mindanao. [WEBSMS] | CVIS
2/3/2024 3:29:16 AM | Luzon Grid-02/03/2024 03:29: GMEC Unit 2 online at 0327H (Unplanned Outage) [WEBSMS] | CLUZ
2/3/2024 3:13:58 AM | Luzon Grid-02/03/2024 03:14: Dona Imelda 300MVA T02 restored at 0312H (Planned Outage) [WEBSMS] | CLUZ
2/3/2024 2:21:42 AM | Mindanao Grid-02/03/2024 02:25: Nagamin SS Power Transformer # 3 / SVC successfully re-energized at 0157H. From P&E shutdown request (Planned Outage / Non-GOMP). [WEBSMS] | CMIN
2/3/2024 12:37:03 AM | Mindanao Grid-02/03/2024 00:40: Nagamin SS Power Transformer # 3 / SVC de-energized at 0006H. P&E request. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
2/3/2024 12:11:38 AM | Luzon Grid-02/03/2024 00:11: BCCPP-Lamao 230kV Line 2 de-energized at 0011H (Planned Outage) [WEBSMS] | CLUZ
2/3/2024 12:08:09 AM | Mindanao Grid-02/03/2024 00:11: Minergy Coal Unit 2 reserved shutdown at 0002H. [WEBSMS] | CMIN
2/2/2024 11:28:28 PM | Luzon Grid-02/02/2024 23:28: San Lorenzo Module 50 shutdown at 2326H (Planned Outage) [WEBSMS] | CLUZ
2/2/2024 10:15:40 PM | Luzon Grid-02/02/2024 22:15: Dona Imelda 300MVA T02 de-energized at 2214H (Planned Outage) [WEBSMS] | CLUZ
2/2/2024 9:15:15 PM | Mindanao Grid-02/02/2024 21:18: WMPC DG10 shutdown at 2114H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/2/2024 6:49:57 PM | Mindanao Grid-02/02/2024 18:53: ASIGA (ASG) HEP Tripped at 1845H with 8MW load. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
2/2/2024 6:00:16 PM | [NSO Update] Mindanao Grid-02/02/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3257MW, PK=2028MW, RR=70.3MW, NetOpMargin: EVE=1159 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @120MW [WEBSMS] | CMIN
2/2/2024 5:58:17 PM | [NSO Update] Visayas Grid-02/02/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2398MW, PK=2024MW, RR=85MW, NetOpMargin: EVE=289 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE A @309MW, PGPP1 @76MW [WEBSMS] | CVIS
2/2/2024 5:55:20 PM | [NSO Update] Luzon Grid-02/02/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13946MW, PK=9910MW, RR=373MW, NetOpMargin: EVE=3663 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @177MW, MASINLOC 3 @320MW, SLTEC 2 @112MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/2/2024 5:36:12 PM | Mindanao Grid-02/02/2024 17:39: Agus 6 SS 138kV Bus # 1 re-energized at 1715H. From P&E request (Planned Outage / Non-GOMP). [WEBSMS] | CMIN
2/2/2024 5:01:25 PM | Visayas Grid-02/02/2024 17:01: Carcon-Sangi 34.5kV Line 3 energized at 1655H. (Planned Outage) [WEBSMS] | CVIS
2/2/2024 4:15:18 PM | Mindanao Grid-02/02/2024 16:19: WMPC DG08 shutdown at 1614H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/2/2024 12:42:22 PM | [NSO Update] Luzon Grid-02/02/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14832MW, PK=10012MW, RR=386MW, NetOpMargin: PM=4435, EVE=3869 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @177MW, MASINLOC 3 @320MW, SLTEC 2 @112MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/2/2024 12:39:52 PM | [NSO Update] Visayas Grid-02/02/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2578MW, PK=2039MW, RR=89MW, NetOpMargin: PM=450, EVE=304 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE A @307MW, PGPP1 @76MW [WEBSMS] | CVIS
2/2/2024 12:36:48 PM | [NSO Update] Mindanao Grid-02/02/2024 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3326MW, PK=2038MW, RR=75MW, NetOpMargin: PM=1213, EVE=1181 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @135MW [WEBSMS] | CMIN
2/2/2024 12:09:25 PM | Visayas Grid-02/02/2024 12:09: Lapu-Lapu SS 69kV Feeder 4 de-energized at 1201H. (Planned Outage) [WEBSMS] | CVIS
2/2/2024 11:24:30 AM | Mindanao Grid-02/02/2024 11:28: Nagamin SS 138KV 50MVA Power Transformer # 2 re-energized at 1051H after the "hotspot" correction. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
2/2/2024 10:54:36 AM | Mindanao Grid-02/02/2024 10:58: WMPC DG08 online at 1052H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/2/2024 9:45:32 AM | Mindanao Grid-02/02/2024 09:49: Agus 6 SS 138kV Bus # 1 de-energized at 0848H. P&E request. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
2/2/2024 9:30:43 AM | Visayas Grid-02/02/2024 09:30: Carcon-Sangi 34.5kV Line 3 de-energized at 0923H. (Planned Outage) [WEBSMS] | CVIS
2/2/2024 9:09:30 AM | Mindanao Grid-02/02/2024 09:13: WMPC DG10 online at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/2/2024 8:29:08 AM | Mindanao Grid-02/02/2024 08:32: Nagamin SS 138KV 50MVA Power Transformer # 2 de-energized at 0810H to facilitate "hotspot" correction at 5Z-DS05(7Z-XFO2NAA) Phase A facing CVT. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
2/2/2024 7:09:52 AM | Mindanao Grid-02/02/2024 07:13: Update; Libertad Power (LPE) tripped with 6.0MW load at 0629H. Indication: Earth Fault. restored at 0640H. (Unplanned Outage) [WEBSMS] | CMIN
2/2/2024 6:37:22 AM | Mindanao Grid-02/02/2024 06:41: LIBERTAD POWER with 6MW load tripped at 0629H. Indication: For further investigation. (Unplanned Outage) [WEBSMS] | CMIN
2/2/2024 6:17:18 AM | Visayas Grid-02/02/2024 06:17: Cebu SS 138kV Bus 1 de-energized at 0616H. (Planned Outage) [WEBSMS] | CVIS
2/2/2024 5:46:49 AM | [NSO Update] Luzon Grid-02/02/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14918MW, PK=10110MW, RR=385MW, NetOpMargin: AM=4423, PM=4721, EVE=4122 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @177MW, MASINLOC 3 @320MW, SLTEC 2 @112MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/2/2024 5:33:10 AM | [NSO Update] Visayas Grid-02/02/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2621MW, PK=2033MW, RR=87MW, NetOpMargin: AM=501, PM=435, EVE=345 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: LEYTE A @314MW, PGPP1 @76MW [WEBSMS] | CVIS
2/2/2024 5:28:24 AM | [NSO Update] Mindanao Grid-02/02/2024 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3315MW, PK=1906MW, RR=72MW, NetOpMargin: AM=1337, PM=1124, EVE=1122 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @32.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @120MW [WEBSMS] | CMIN
2/2/2024 4:02:46 AM | [NSO Update] Luzon Grid-02/02/2024 04:02: Weather Advisory: Northeast Monsoon affecting Luzon. Trough of the Low Pressure Area (LPA) affecting Mindanao. [WEBSMS] | CLUZ
2/2/2024 4:02:43 AM | [NSO Update] Visayas Grid-02/02/2024 04:02: Weather Advisory: Northeast Monsoon affecting Luzon. Trough of the Low Pressure Area (LPA) affecting Mindanao. [WEBSMS] | CVIS
2/2/2024 4:02:40 AM | [NSO Update] Mindanao Grid-02/02/2024 04:06: Weather Advisory: Northeast Monsoon affecting Luzon. Trough of the Low Pressure Area (LPA) affecting Mindanao. [WEBSMS] | CMIN
2/2/2024 2:02:31 AM | Mindanao Grid-02/02/2024 02:06: Maramag SS 138KV Bus 1 re-energized at 0157H (Unplanned Outage) [WEBSMS] | CMIN
2/2/2024 12:51:29 AM | Mindanao Grid-02/02/2024 00:55: Baloi - Aurora 138KV Line 1 autotripped at 003034H and autoreclosed at 003035H. (Unplanned Outage) [WEBSMS] | CMIN
2/1/2024 11:31:13 PM | Mindanao Grid-02/01/2024 23:34: Maramag SS 138KV Bus 1 manually out/emergency shutdown at 2310H. Unplanned Outage. [WEBSMS] | CMIN
2/1/2024 11:21:53 PM | Mindanao Grid-02/01/2024 23:25: Pulangi U3 with 60MW gross generation tripped at 2249H. Frequency dipped=59.626HZ. Indication: Back-up Protection Electrical Emergency Shutdown. Unplanned Outage. [WEBSMS] | CMIN
2/1/2024 9:15:29 PM | Mindanao Grid-02/01/2024 21:19: WMPC DG10 shutdown at 2113H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/1/2024 7:42:18 PM | Luzon Grid-02/01/2024 19:42: (Resending with correct line name): Lal-lo-Cagayan North Solar 69kV line 2 was restored at 1849H. (Unplanned Outage) [WEBSMS] | CLUZ
2/1/2024 6:53:49 PM | Luzon Grid-02/01/2024 18:53: Lal-lo-Cagayan North Solar 69kV line was restored at 1849H. (Unplanned Outage) [WEBSMS] | CLUZ
2/1/2024 5:54:44 PM | [NSO Update] Mindanao Grid-02/01/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3193MW, PK=1987MW, RR=70MW, NetOpMargin: EVE=1136 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @107MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @120MW [WEBSMS] | CMIN
2/1/2024 5:51:35 PM | [NSO Update] Visayas Grid-02/01/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2472MW, PK=1976MW, RR=85MW, NetOpMargin: EVE=411 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: Leyte A @ 309MW, PGPP1 @ 76MW [WEBSMS] | CVIS
2/1/2024 5:44:10 PM | [NSO Update] Luzon Grid-02/01/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13925MW, PK=9843MW, RR=376MW, NetOpMargin: EVE=3706 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 177MW, SLTEC 1 @ 119MW, SLTEC 2 @ 110MW, Ilijan A @ 450MW [WEBSMS] | CLUZ
2/1/2024 4:39:56 PM | Mindanao Grid-02/01/2024 16:43: Energized GNPK - Kauswagan 230KV Line 3 at 1630H (Planned Outage) [WEBSMS] | CMIN
2/1/2024 4:39:38 PM | Mindanao Grid-02/01/2024 16:43: WMPC DG07 shutdown at 1614H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/1/2024 2:29:37 PM | Visayas Grid-02/01/2024 14:29: CEDC Unit # 1tripped with 45MW load at 1411H.( Unplanned Outage) [WEBSMS] | CVIS
2/1/2024 12:55:39 PM | [NSO Update] Mindanao Grid-02/01/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3224MW, PK=2006MW, RR=75MW, NetOpMargin: PM=1143, EVE=1101 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @107MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @100MW [WEBSMS] | CMIN
2/1/2024 12:54:42 PM | [NSO Update] Visayas Grid-02/01/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2560MW, PK=1997MW, RR=89MW, NetOpMargin: PM=474, EVE=380 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: Leyte A @ 309MW, PGPP1 @ 76MW [WEBSMS] | CVIS
2/1/2024 12:53:17 PM | [NSO Update] Luzon Grid-02/01/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14808MW, PK=10130MW, RR=391MW, NetOpMargin: PM=4287, EVE=3813 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 177MW, Masinloc 2 @ 340MW, SLTEC 1 @ 119MW, SLTEC 2 @ 110MW, Ilijan A @ 450MW [WEBSMS] | CLUZ
2/1/2024 10:51:45 AM | Mindanao Grid-02/01/2024 10:55: WMPC DG07 online at 1048H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/1/2024 10:42:13 AM | Visayas Grid-02/01/2024 10:42: Carcon - Sangi 34.5 kV Line 2 de-energized at 1039H. (Planned Outage) [WEBSMS] | CVIS
2/1/2024 9:55:16 AM | Mindanao Grid-02/01/2024 09:58: WMPC DG10 online at 0902H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
2/1/2024 9:24:21 AM | Mindanao Grid-02/01/2024 09:28: GNPK - Kauswagan 230KV Line 3 shutdown at 0917H (Planned Outage) [WEBSMS] | CMIN
2/1/2024 5:36:22 AM | [NSO Update] Luzon Grid-02/01/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14820MW, PK=9974MW, RR=391MW, NetOpMargin: AM=4455, PM=4166, EVE=3627 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @177MW, MASINLOC 3 @280MW, SLTEC 2 @110MW, ILIJAN A @450MW [WEBSMS] | CLUZ
2/1/2024 5:33:47 AM | [NSO Update] Visayas Grid-02/01/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2605MW, PK=2038MW, RR=87MW, NetOpMargin: AM=481, PM=315, EVE=283 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: LEYTE A @302MW, PGPP1 @76MW [WEBSMS] | CVIS
2/1/2024 5:32:19 AM | [NSO Update] Mindanao Grid-02/01/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3224MW, PK=1852MW, RR=72MW, NetOpMargin: AM=1299, PM=998, EVE=1015 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @107MW, AG5 @34MW, AG6 @149MW, AG7 @30MW, PG4 @100MW [WEBSMS] | CMIN
2/1/2024 5:13:47 AM | Luzon Grid-02/01/2024 05:13: Quezon (Balintawak) 300MVA T02 restored at 0504H. (Planned Outage) [WEBSMS] | CLUZ
2/1/2024 5:12:41 AM | Luzon Grid-02/01/2024 05:12: SBMA SS 230kV Bus 1 de-energized at 0508H. (Planned Outage) [WEBSMS] | CLUZ
2/1/2024 5:11:32 AM | Luzon Grid-02/01/2024 05:11: SBMA-Subic Solar Power 230kV Line de-energized at 0506H. (Planned Outage) [WEBSMS] | CLUZ
2/1/2024 4:02:51 AM | [NSO Update] Luzon Grid-02/01/2024 04:02: Weather Advisory: Northeast Monsoon affecting Luzon. Trough of the Low Pressure Area (LPA) affecting Mindanao. [WEBSMS] | CLUZ
2/1/2024 4:02:26 AM | [NSO Update] Visayas Grid-02/01/2024 04:02: Weather Advisory: Northeast Monsoon affecting Luzon. Trough of the Low Pressure Area (LPA) affecting Mindanao. [WEBSMS] | CVIS
2/1/2024 4:02:22 AM | [NSO Update] Mindanao Grid-02/01/2024 04:06: Weather Advisory: Northeast Monsoon affecting Luzon. Trough of the Low Pressure Area (LPA) affecting Mindanao. [WEBSMS] | CMIN
2/1/2024 12:48:39 AM | Luzon Grid-02/01/2024 00:48: Quezon (Balintawak) 300MVA T02 de-energized at 0039H (Planned Outage) [WEBSMS] | CLUZ
2/1/2024 12:10:48 AM | Visayas Grid-02/01/2024 00:11: PEDC U1 cut-out at 0006H. (Planned Outage) [WEBSMS] | CVIS
1/31/2024 11:29:46 PM | Luzon Grid-01/31/2024 23:30: Naga - Tiwi C 230kV Line 1 fully commissioned at 2328H. (End of commissioning) [WEBSMS] | CLUZ
1/31/2024 10:54:25 PM | Luzon Grid-01/31/2024 22:54: Naga - Tiwi C 230kV Line 1 energized and looped at 2254H. (On-going commissioning) [WEBSMS] | CLUZ
1/31/2024 12:53:28 PM | [NSO Update] Luzon Grid-01/31/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14427MW, PK=9854MW, RR=385MW, NetOpMargin: PM=4188, EVE=3651 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 177MW, Masinloc 3 @ 300MW, SCPC 2 @ 145MW, SLTEC 1 @ 119MW, SLTEC 2 @ 98MW, Ilijan A @ 200MW [WEBSMS] | CLUZ
1/31/2024 12:50:55 PM | [NSO Update] Mindanao Grid-01/31/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3183MW, PK=1953MW, RR=71MW, NetOpMargin: PM=1159, EVE=1104 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @157MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
1/31/2024 12:50:53 PM | Luzon Grid-01/31/2024 12:51: Ilijan ST1 online at 1249H (Unplanned Outage) [WEBSMS] | CLUZ
1/31/2024 12:49:55 PM | [NSO Update] Visayas Grid-01/31/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2581MW, PK=2024MW, RR=89MW, NetOpMargin: PM=468, EVE=337 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: Leyte A @ 302MW, PGPP1 @ 76MW, PEDC 1 @ 50MW [WEBSMS] | CVIS
1/31/2024 12:23:04 PM | Luzon Grid-01/31/2024 12:23: Ilijan ST1 (178MW) tripped at 1213H. Lowest system frequency is 59.455Hz. [WEBSMS] | CLUZ
1/31/2024 11:32:27 AM | Mindanao Grid-01/31/2024 11:36: Matanao-Kidapawan 138kV L2 energized at 1018H. From Planned Outage/Non-GOMP. [WEBSMS] | CMIN
1/31/2024 9:51:35 AM | Visayas Grid-01/31/2024 09:51: PEDC U2 online at 0948H. (Planned Outage) [WEBSMS] | CVIS
1/31/2024 9:49:21 AM | Visayas Grid-01/31/2024 09:49: Carcon - Sangi 34.5 kV Line 1 de-energized at 0946H. (Planned Outage) [WEBSMS] | CVIS
1/31/2024 8:53:12 AM | Mindanao Grid-01/31/2024 08:57: WMPC DG10 Online at 0850H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/31/2024 8:38:54 AM | Mindanao Grid-01/31/2024 08:42: Matanao-Kidapawan 138kV L2 deenergized at 0828H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
1/31/2024 8:10:10 AM | Mindanao Grid-01/31/2024 08:14: Culaman - SMC MCFPP 230kV L1 deenergized at 0754H. Planned Outage/Non-GOMP. (Customer, SMC, requested shutdown). [WEBSMS] | CMIN
1/31/2024 7:33:28 AM | Mindanao Grid-01/31/2024 07:37: Baloi-Agus 4 138kV L1 deenergized at 0714H. Planned Outage/Non-GOMP. (P & E Request Shutdown). [WEBSMS] | CMIN
1/31/2024 6:53:47 AM | Luzon Grid-01/31/2024 06:54: Hermosa-Calaguiman 69kV Line restored at 0649H (Planned Outage) [WEBSMS] | CLUZ
1/31/2024 6:13:30 AM | Luzon Grid-01/31/2024 06:13: Hermosa-BCCPP 230kV Line 1 de-energized at 0613H (Planned Outage) [WEBSMS] | CLUZ
1/31/2024 6:08:59 AM | Mindanao Grid-01/31/2024 06:12: New Bataan Hydro with 1.5MW load tripped at 0452H due to clogged trash rack of de-sander. (Unplanned Outage) [WEBSMS] | CMIN
1/31/2024 5:48:18 AM | Luzon Grid-01/31/2024 05:48: Hermosa-Calaguiman 69kV Line de-energized at 0547H (Planned Outage) [WEBSMS] | CLUZ
1/31/2024 5:45:32 AM | [NSO Update] Luzon Grid-01/31/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14686MW, PK=9741MW, RR=380MW, NetOpMargin: AM=4566, PM=4660, EVE=3954 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, MSLC2 @335MW, SLTEC 1 @119MW, SLTEC 2 @110MW, Ilijan A @450MW [WEBSMS] | CLUZ
1/31/2024 5:41:43 AM | [NSO Update] Visayas Grid-01/31/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2456MW, PK=1983MW, RR=86MW, NetOpMargin: AM=387, PM=436, EVE=290 Highest Unit O/L: THVI 1 @169MW Derated Plant: LEYTE A @302MW, PGPP1 @76MW [WEBSMS] | CVIS
1/31/2024 5:38:59 AM | [NSO Update] Mindanao Grid-01/31/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3196MW, PK=2018MW, RR=70MW, NetOpMargin: AM=1109, PM=1114, EVE=1055 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @60MW, AG2 @86MW, AG4 @106MW, AG5 @34MW, AG6 @157MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
1/31/2024 5:20:41 AM | Luzon Grid-01/31/2024 05:20: San Lorenzo 60 online at 0505H (Planned Outage) [WEBSMS] | CLUZ
1/31/2024 4:46:03 AM | [NSO Update] Mindanao Grid-01/31/2024 04:49: Weather Update: Northeast Monsoon affecting Luzon and Visayas. Trough of a Low Pressure Area (LPA) affecting Mindanao. [WEBSMS] | CMIN
1/31/2024 4:45:45 AM | [NSO Update] Visayas Grid-01/31/2024 04:45: Weather Update: Northeast Monsoon affecting Luzon and Visayas. Trough of a Low Pressure Area (LPA) affecting Mindanao. [WEBSMS] | CVIS
1/31/2024 4:45:28 AM | [NSO Update] Luzon Grid-01/31/2024 04:45: Weather Update: Northeast Monsoon affecting Luzon and Visayas. Trough of a Low Pressure Area (LPA) affecting Mindanao. [WEBSMS] | CLUZ
1/31/2024 4:19:58 AM | Luzon Grid-01/31/2024 04:20: San Jose-Camarin 115kV Line restored at 0419H (Planned Outage) [WEBSMS] | CLUZ
1/31/2024 3:17:02 AM | Luzon Grid-01/31/2024 03:16: San Lorenzo Module 60 shutdown at 0314H (Planned Outage) [WEBSMS] | CLUZ
1/31/2024 2:05:39 AM | Luzon Grid-01/31/2024 02:05: San Lorenzo Module 60 on-line at 0159H (Planned Outage) [WEBSMS] | CLUZ
1/31/2024 1:16:43 AM | Luzon Grid-01/31/2024 01:16: Calamba 300MVA T01 de-energized at 1311H (Planned Outage) [WEBSMS] | CLUZ
1/31/2024 12:22:26 AM | Mindanao Grid-01/31/2024 00:26: Tudaya 2 Unit 2 online at 2358H (Unplanned Outage) [WEBSMS] | CMIN
1/31/2024 12:21:17 AM | Mindanao Grid-01/31/2024 00:25: Update: Tudaya 2 Unit 1 online at 2339H (Unplanned Outage) [WEBSMS] | CMIN
1/31/2024 12:18:50 AM | Mindanao Grid-01/31/2024 00:22: Tudaya 2 Unit 1 online at 1139H. (Unplanned Outage) [WEBSMS] | CMIN
1/30/2024 11:10:19 PM | Luzon Grid-01/30/2024 23:10: San Jose-Camarin 115kV Line de-energized at 2310H (Planned Outage) [WEBSMS] | CLUZ
1/30/2024 9:20:30 PM | Mindanao Grid-01/30/2024 21:24: WMPC DG05 shutdown at 2114H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
1/30/2024 9:16:00 PM | Luzon Grid-01/30/2024 21:16: SCPC 2 online at 2112H (Planned Outage) [WEBSMS] | CLUZ
1/30/2024 7:40:31 PM | Luzon Grid-01/30/2024 19:40: Hermosa-BCCPP 230kV Line 2 restored at 1940H (Planned Outage) [WEBSMS] | CLUZ
1/30/2024 7:25:13 PM | Luzon Grid-01/30/2024 19:25: Binga HEPP 230kV Overhead Line 1 restored at 1924H (Planned Outage) [WEBSMS] | CLUZ
1/30/2024 7:07:48 PM | Mindanao Grid-01/30/2024 19:11: TUDAYA 2 Unit 1 and 2 on emergency shutdown for a switchgear inspection - total load of 6.2MW at 1847H. (Unplanned Outage) [WEBSMS] | CMIN
1/30/2024 6:09:24 PM | Mindanao Grid-01/30/2024 18:13: PULANGI 4 Unit 1online at 1741H. (Unplanned Outage) [WEBSMS] | CMIN
1/30/2024 6:04:37 PM | Mindanao Grid-01/30/2024 18:08: AGUS 2 Unit 3 online at 1755H from FO. (Unplanned Outage) [WEBSMS] | CMIN
1/30/2024 6:03:53 PM | [NSO Update] Mindanao Grid-01/30/2024 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3047MW, PK=1990MW, RR=72.3MW, NetOpMargin: EVE=985 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @56MW, AG2 @48MW, AG4 @97MW, AG5 @31MW, AG6 @142MW, AG7 @27MW, PG4 @80MW [WEBSMS] | CMIN
1/30/2024 5:58:21 PM | [NSO Update] Visayas Grid-01/30/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2338MW, PK=1938MW, RR=86MW, NetOpMargin: EVE=315 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: Leyte A @ 298MW, PGPP1 @ 76MW, PEDC U1 @ 50MW [WEBSMS] | CVIS
1/30/2024 5:47:45 PM | [NSO Update] Luzon Grid-01/30/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13218MW, PK=9453MW, RR=260MW, NetOpMargin: EVE=3504 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 177MW, Masinloc 2 @ 335MW, SLTEC 1 @ 119MW, Ilijan A @ 450MW [WEBSMS] | CLUZ
1/30/2024 5:31:38 PM | Mindanao Grid-01/30/2024 17:35: Villanueva- Maramag 230 kV L1 (8LI1VLN-MRM) restored from the emergency shutdown at 1721H, while Villanueva 230 kV, 300 MVA, Power transformer T2 (8FX02VLN) energized back at 1718H. [WEBSMS] | CMIN
1/30/2024 5:29:21 PM | Mindanao Grid-01/30/2024 17:33: WMPC DG04 shutdown at 1613H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
1/30/2024 5:27:00 PM | Mindanao Grid-01/30/2024 17:30: WMPC DG04 online at 1445H. (Unplanned Outage) [WEBSMS] | CMIN
1/30/2024 4:42:21 PM | Visayas Grid-01/30/2024 16:42: Sangi-2nd Lift 34.5 KV line energized at 1638H (Planned Outage) [WEBSMS] | CVIS
1/30/2024 4:04:33 PM | Luzon Grid-01/30/2024 16:04: Binga HEPP 230kV Overhead Line 2 restored at 1602H (Planned Outage) [WEBSMS] | CLUZ
1/30/2024 3:57:51 PM | Mindanao Grid-01/30/2024 16:01: Emergency shutdown of Villanueva- Maramag 230 kV L1 at 1537H (8LI1VLN-MRM) to conduct hotspot correction at linetrap ph-B terminal facing Villanueva 230 kV switchyard. Also, Villanueva 230 kV, 300 MVA,Power transformer T2 (8FX02VLN) was isolated since PCB 08-04CB08VLN is not operational (for replacement.) [WEBSMS] | CMIN
1/30/2024 2:52:31 PM | Mindanao Grid-01/30/2024 14:56: WMPC online at 1445H. (Unplanned Outage) [WEBSMS] | CMIN
1/30/2024 2:49:56 PM | Mindanao Grid-01/30/2024 14:53: WMPC DG04 -online as RPS with 8.5MW load on emergency shutdown at 1435H. Reason: Engine Stop - Emergency stop button alarm. (Unplanned Outage). [WEBSMS] | CMIN
1/30/2024 2:30:31 PM | Mindanao Grid-01/30/2024 14:34: Zamboanga - WMPC 138KV Line 2 restored at 1428H (Planned Outage) [WEBSMS] | CMIN
1/30/2024 1:48:28 PM | Mindanao Grid-01/30/2024 13:52: ASIGA (ASG) HEP Tripped at 1333H with 8MW load. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
1/30/2024 12:48:32 PM | [NSO Update] Luzon Grid-01/30/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14201MW, PK=9630MW, RR=281MW, NetOpMargin: PM=4290, EVE=3699 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 177MW, Masinloc 2 @ 335MW, SLTEC 1 @ 119MW, Ilijan A @ 450MW [WEBSMS] | CLUZ
1/30/2024 12:39:46 PM | [NSO Update] Mindanao Grid-01/30/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3041MW, PK=2003MW, RR=72MW, NetOpMargin: PM=965, EVE=939 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @56MW, AG2 @48MW, AG4 @97MW, AG5 @31MW, AG6 @142MW, AG7 @27MW, PG4 @80MW [WEBSMS] | CMIN
1/30/2024 12:38:11 PM | [NSO Update] Visayas Grid-01/30/2024 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2558MW, PK=2030MW, RR=89MW, NetOpMargin: PM=439, EVE=305 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TGPP @ 113MW, Leyte A @ 298MW, PGPP1 @ 76MW, PEDC U1 @ 50MW [WEBSMS] | CVIS
1/30/2024 10:58:45 AM | Mindanao Grid-01/30/2024 11:02: WMPC DG04 Online at 1052H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/30/2024 10:56:08 AM | Visayas Grid-01/30/2024 10:56: PGPP1U1 recut in at 1040H (Unplanned Outage) [WEBSMS] | CVIS
1/30/2024 9:11:52 AM | Visayas Grid-01/30/2024 09:12: PGPP1 U1 tripped at 0902H. (Unplanned Outage) [WEBSMS] | CVIS
1/30/2024 9:11:15 AM | Mindanao Grid-01/30/2024 09:15: AGUS 7 Unit 1 HEP online at 0902H (Unplanned Outage). [WEBSMS] | CMIN
1/30/2024 9:08:05 AM | Mindanao Grid-01/30/2024 09:11: WMPC DG05 Online at 0850H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/30/2024 8:41:45 AM | Luzon Grid-01/30/2024 08:41: Binga HEPP 230kV Overhead Line 1 & 2 de-energized at 0836H & 0837H, respectively (Planned Outage) [WEBSMS] | CLUZ
1/30/2024 7:25:03 AM | Visayas Grid-01/30/2024 07:25: Sangi-2nd Lift 34.5 KV line de-energized at 0717H (Planned Outage) [WEBSMS] | CVIS
1/30/2024 6:25:14 AM | Mindanao Grid-01/30/2024 06:29: AGUS 7 Unit 1 with 14.0MW load tripped at 0611H. Indication: 86 Supervisory alarm / Gov. maximum differential pressure and Excitation alarm. (Unplanned Outage) [WEBSMS] | CMIN
1/30/2024 6:17:29 AM | Luzon Grid-01/30/2024 06:17: Hermosa-BCCPP 230kV Line 2 de-energized at 0616H (Planned Outage) [WEBSMS] | CLUZ
1/30/2024 5:36:45 AM | [NSO Update] Luzon Grid-01/30/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14135MW, PK=9222MW, RR=403MW, NetOpMargin: AM=4510, PM=4341, EVE=3685 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @177MW, MASINLOC 3 @280MW, ILIJAN A @450MW, [WEBSMS] | CLUZ
1/30/2024 5:35:26 AM | Mindanao Grid-01/30/2024 05:39: Agus 2 Unit 3 with 30MW load tripped at 0528H. Indication: Generator Ground Fault & Generator Over Current. Lowest Frequency dip: 59.7034Hz. (unplanned outage) [WEBSMS] | CMIN
1/30/2024 5:33:09 AM | [NSO Update] Visayas Grid-01/30/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2536MW, PK=1916MW, RR=87MW, NetOpMargin: AM=533, PM=278, EVE=250 Highest Unit O/L: THVI 1@169MW Derated Plant: TGPP @113MW, LEYTE A @298MW, PGPP1 @76MW, PEDC U1@50MW [WEBSMS] | CVIS
1/30/2024 5:30:15 AM | [NSO Update] Mindanao Grid-01/30/2024 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3122MW, PK=2044MW, RR=70MW, NetOpMargin: AM=1008, PM=917, EVE=901 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @34.5MW, MA2 @50MW, AG1 @56MW, AG2 @78MW, AG4 @97MW, AG5 @31MW, AG6 @142MW, AG7 @27MW, PG4 @120MW [WEBSMS] | CMIN
1/30/2024 5:11:19 AM | Mindanao Grid-01/30/2024 05:15: Zamboanga-WMPC 138KV L2 de-energized at 0500H. Planned Outage (OO07AD)/Non-GOMP. Shutdown requested by WMPC management (Annual SS servicing of 80MVA T2). [WEBSMS] | CMIN
1/30/2024 4:02:29 AM | [NSO Update] Luzon Grid-01/30/2024 04:02: Weather Advisory: Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
1/30/2024 4:02:25 AM | [NSO Update] Visayas Grid-01/30/2024 04:02: Weather Advisory: Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
1/30/2024 4:02:12 AM | [NSO Update] Mindanao Grid-01/30/2024 04:06: Weather Advisory: Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
1/29/2024 11:51:10 PM | Luzon Grid-01/29/2024 23:51: SLTEC 2 online at 2349H. (Planned Outage) [WEBSMS] | CLUZ
1/29/2024 10:27:22 PM | Mindanao Grid-01/29/2024 22:31: Agus 4 Unit 3 online at 2225H from Forced outage. (Unplanned Outage) [WEBSMS] | CMIN
1/29/2024 9:21:27 PM | Mindanao Grid-01/29/2024 21:25: Update: Agus 4 Unit 3 with 34.7MW load tripped at 2025H. Indication: 86E, Excitation System Trip. Lowest Frequency at 59.6991Hz. (Unplanned Outage) [WEBSMS] | CMIN
1/29/2024 9:15:08 PM | Mindanao Grid-01/29/2024 21:19: WMPC DG09 shutdown at 2114H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/29/2024 8:29:39 PM | Mindanao Grid-01/29/2024 20:33: Agus 4 Unit 3 with 34.7MW load tripped at 2025H. Details: to follow. Lowest Frequency at 59.6991Hz. (Unplanned Outage) [WEBSMS] | CMIN
1/29/2024 5:38:48 PM | [NSO Update] Visayas Grid-01/29/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2321MW, PK=1921MW, RR=86MW, NetOpMargin: EVE=315 Highest Unit O/L: THVI 1@169MW Derated Plant: TGPP @113MW, LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
1/29/2024 5:38:24 PM | [NSO Update] Luzon Grid-01/29/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13471MW, PK=9209MW, RR=350MW, NetOpMargin: EVE=3912 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @177MW, ILIJAN A @450MW [WEBSMS] | CLUZ
1/29/2024 5:37:48 PM | [NSO Update] Mindanao Grid-01/29/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3023MW, PK=1962MW, RR=72MW, NetOpMargin: EVE=988 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @97MW, AG5 @31MW, AG6 @125MW, AG7 @27MW, PG4 @60MW [WEBSMS] | CMIN
1/29/2024 5:08:45 PM | Luzon Grid-01/29/2024 17:08: Bay-Calamba 230kV Line 2 restored at 1708H. (Unplanned Outage) [WEBSMS] | CLUZ
1/29/2024 4:56:36 PM | Mindanao Grid-01/29/2024 17:00: Zamboanga-WMPC 138KV L1 energized at 1642H. From Planned Outage (OO07AD)/Non-GOMP. Shutdown requested by WMPC management (Annual SS servicing of 80MVA T1). [WEBSMS] | CMIN
1/29/2024 4:14:23 PM | Mindanao Grid-01/29/2024 16:18: WMPC DG07 shutdown at 1613H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/29/2024 3:12:13 PM | Mindanao Grid-01/29/2024 15:16: Pulangi 4 U1 manually shutdown at 1508H due to Low Water Elevation. Follow RTD. (Unplanned Outage) [WEBSMS] | CMIN
1/29/2024 1:18:11 PM | Luzon Grid-01/29/2024 13:18: Bay-Calamba 230kV Line 2 emergency shutdown at 1317H (Unplanned Outage) [WEBSMS] | CLUZ
1/29/2024 1:12:47 PM | [NSO Update] Mindanao Grid-01/29/2024 13:16: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3037MW, PK=2239MW, RR=0MW, NetOpMargin: PM=727, EVE=731 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @97MW, AG5 @31MW, AG6 @125MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/29/2024 12:58:57 PM | [NSO Update] Visayas Grid-01/29/2024 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2454MW, PK=2114MW, RR=90MW, NetOpMargin: PM=250, EVE=259 Highest Unit O/L: THVI 1@169MW Derated Plant: TGPP @113MW, LEYTE A @305MW, PGPP1 @76MW [WEBSMS] | CVIS
1/29/2024 12:54:55 PM | [NSO Update] Luzon Grid-01/29/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14110MW, PK=9497MW, RR=371MW, NetOpMargin: PM=4242, EVE=3633 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, ILIJAN A @450MW [WEBSMS] | CLUZ
1/29/2024 12:03:50 PM | Luzon Grid-01/29/2024 12:04: Muntinlupa 300MVA T04 restored at 1203H (Planned Outage) [WEBSMS] | CLUZ
1/29/2024 12:00:25 PM | Luzon Grid-01/29/2024 12:00: Nagsaag-Binga 230kV Line 1 restored at 1200H (Unplanned Outage) [WEBSMS] | CLUZ
1/29/2024 11:57:55 AM | Luzon Grid-01/29/2024 11:58: Nagsaag-Binga 230kV Line 1 tripped at 1154H (Unplanned Outage) [WEBSMS] | CLUZ
1/29/2024 11:49:28 AM | Mindanao Grid-01/29/2024 11:53: WMPC DG07 Online at 1050H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/29/2024 9:17:28 AM | Luzon Grid-01/29/2024 09:17: Naga-Tiwi Plant A 230kV Line de-energized at 0915H (Planned Outage) [WEBSMS] | CLUZ
1/29/2024 8:54:16 AM | Mindanao Grid-01/29/2024 08:58: WMPC DG09 Online at 0850H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/29/2024 7:56:09 AM | Mindanao Grid-01/29/2024 08:00: Baloi SS 138KV Bus # 2 energized at 0748H. From Planned Outage / N-GOMP. (P&E shutdown request). [WEBSMS] | CMIN
1/29/2024 6:06:45 AM | [NSO Update] Luzon Grid-01/29/2024 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14249MW, PK=9153MW, RR=374MW, NetOpMargin: AM=4722, PM=4111, EVE=3601 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, SLTEC 1 @119MW [WEBSMS] | CLUZ
1/29/2024 5:44:24 AM | [NSO Update] Visayas Grid-01/29/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2392MW, PK=1855MW, RR=88MW, NetOpMargin: AM=449, PM=221, EVE=169 Highest Unit O/L: THVI 1@169MW Derated Plant: TGPP @113MW, LEYTE A @305MW, PGPP1 @76MW [WEBSMS] | CVIS
1/29/2024 5:40:52 AM | [NSO Update] Mindanao Grid-01/29/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3080MW, PK=1904MW, RR=70MW, NetOpMargin: AM=1106, PM=1017, EVE=1068 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @97MW, AG5 @31MW, AG6 @146MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/29/2024 5:36:37 AM | Mindanao Grid-01/29/2024 05:40: Zamboanga-WMPC 138KV L1 de-energized at 0503H per request from WMPC management (Annual SS servicing of 80MVA T1). OO07AD / non-GOMP [WEBSMS] | CMIN
1/29/2024 4:13:12 AM | [NSO Update] Mindanao Grid-01/29/2024 04:17: Weather Update: Northeast Monsoon affecting the country. [WEBSMS] | CMIN
1/29/2024 4:12:54 AM | [NSO Update] Visayas Grid-01/29/2024 04:13: Weather Update: Northeast Monsoon affecting the country. [WEBSMS] | CVIS
1/29/2024 4:12:33 AM | [NSO Update] Luzon Grid-01/29/2024 04:12: Weather Update: Northeast Monsoon affecting the country. [WEBSMS] | CLUZ
1/29/2024 3:10:26 AM | Luzon Grid-01/29/2024 03:10: Daraga-Tiwi Plant A 230kV Line commissioned at 0308H (End of Commissioning) [WEBSMS] | CLUZ
1/29/2024 2:34:58 AM | Luzon Grid-01/29/2024 02:35: Daraga-Tiwi Plant A 230kV Line looped at 0233H (On Commisisoning) [WEBSMS] | CLUZ
1/29/2024 2:15:45 AM | Luzon Grid-01/29/2024 02:15: Daraga-Tiwi Plant A 230kV Line energized at Daraga side at 0213H (On Commissioning) [WEBSMS] | CLUZ
1/29/2024 12:07:20 AM | Mindanao Grid-01/29/2024 00:11: Baloi SS 138KV Bus # 2 de-energized at 2306H. P&E shutdown request. Planned Outage / N-GOMP. [WEBSMS] | CMIN
1/29/2024 12:05:06 AM | Visayas Grid-01/29/2024 00:05: PEDC U2 shutdown at 0000H (Planned Outage) [WEBSMS] | CVIS
1/28/2024 7:25:03 PM | Luzon Grid-01/28/2024 19:25: Dasmarinas-Ilijan 500kV Line restored at 1924H (Planned Outage) [WEBSMS] | CLUZ
1/28/2024 7:14:19 PM | Visayas Grid-01/28/2024 19:14: Pajo Load-end 13.8 kV Feeder restored at 1911H (Unplanned Outage) [WEBSMS] | CVIS
1/28/2024 6:46:13 PM | Visayas Grid-01/28/2024 18:46: Palo Load-end 13.8 kV Feeder tripped at 1833H (Unplanned Outage) [WEBSMS] | CVIS
1/28/2024 6:12:33 PM | Visayas Grid-01/28/2024 18:12: Quiot SS 100 MVA TR2 energized at 1809H (Planned Outage) [WEBSMS] | CVIS
1/28/2024 5:37:58 PM | [NSO Update] Mindanao Grid-01/28/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3060MW, PK=1872MW, RR=70MW, NetOpMargin: EVE=1117 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @97MW, AG5 @31MW, AG6 @125MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/28/2024 5:37:48 PM | [NSO Update] Visayas Grid-01/28/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2320MW, PK=1792MW, RR=85MW, NetOpMargin: EVE=443 Highest Unit O/L: THVI 1@ 169MW Derated Plant: TGPP @113MW, LEYTE A @283MW, PGPP1 @76MW, PEDC 1@50MW, PEDC 2@ 50MW [WEBSMS] | CVIS
1/28/2024 5:37:36 PM | [NSO Update] Luzon Grid-01/28/2024 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13410MW, PK=7991MW, RR=271MW, NetOpMargin: EVE=5148 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @177MW [WEBSMS] | CLUZ
1/28/2024 3:28:12 PM | Mindanao Grid-01/28/2024 15:32: Matanao SS 138KV 100MVA Power Transformer # 1 re-energized at 1510H. From Planned Outage / GOMP. [WEBSMS] | CMIN
1/28/2024 1:37:42 PM | Luzon Grid-01/28/2024 13:37: Labrador SS 230kV Bus 1 restored at 1337H. (Planned Outage) [WEBSMS] | CLUZ
1/28/2024 12:34:33 PM | [NSO Update] Luzon Grid-01/28/2024 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14284MW, PK=7627MW, RR=278MW, NetOpMargin: PM=6379, EVE=5026 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @ 177MW [WEBSMS] | CLUZ
1/28/2024 12:31:48 PM | [NSO Update] Visayas Grid-01/28/2024 12:31: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2423MW, PK=1548MW, RR=85MW, NetOpMargin: PM=790, EVE=469 Highest Unit O/L: THVI 1 @169MW Derated Plant: TGPP @113MW, LEYTE A @325MW, PGPP1 @76MW [WEBSMS] | CVIS
1/28/2024 12:31:42 PM | [NSO Update] Mindanao Grid-01/28/2024 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3109MW, PK=1590MW, RR=70MW, NetOpMargin: PM=1449, EVE=1215 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @97MW, AG5 @31MW, AG6 @125MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/28/2024 11:35:34 AM | Luzon Grid-01/28/2024 11:35: San Rafael-Cabanatuan 230kV Line restored at 1135H. (Planned Outage) [WEBSMS] | CLUZ
1/28/2024 9:32:16 AM | Mindanao Grid-01/28/2024 09:36: Matanao SS 138KV Power Transformer # 1 de-energized at 0831H for hotspot correction. Planned Outage / GOMP. [WEBSMS] | CMIN
1/28/2024 8:52:00 AM | Luzon Grid-01/28/2024 08:52: Labrador SS 230kV Bus 1 de-energized at 0831H. (Planned Outage) [WEBSMS] | CLUZ
1/28/2024 8:42:51 AM | Luzon Grid-01/28/2024 08:42: San Rafael-Cabanatuan 230kV Line de-energized at 0842H. (Planned Outage) [WEBSMS] | CLUZ
1/28/2024 6:20:38 AM | Luzon Grid-01/28/2024 06:20: Dasmarinas-Ilijan 500kV Line de-energized at 0619H. (Planned Outage) [WEBSMS] | CLUZ
1/28/2024 5:54:51 AM | [NSO Update] Visayas Grid-01/28/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2395MW, PK=1531MW, RR=77MW, NetOpMargin: AM=787, PM=594, EVE=353 Highest Unit O/L: THVI 1 @169MW Derated Plant: TGPP @113MW, LEYTE A @325MW, PGPP1 @76MW [WEBSMS] | CVIS
1/28/2024 5:53:03 AM | [NSO Update] Luzon Grid-01/28/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14497MW, PK=7648MW, RR=284MW, NetOpMargin: AM=6565, PM=5728, EVE=4472 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, SLTEC 1 @120MW [WEBSMS] | CLUZ
1/28/2024 5:51:09 AM | [NSO Update] Mindanao Grid-01/28/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3126MW, PK=1636MW, RR=70MW, NetOpMargin: AM=1420, PM=1312, EVE=1080 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @97MW, AG5 @31MW, AG6 @125MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/28/2024 5:36:24 AM | Visayas Grid-01/28/2024 05:36: Quiot SS 100 MVA TR2 de-energized at 0535H (Planned Outage) [WEBSMS] | CVIS
1/28/2024 4:19:16 AM | [NSO Update] Mindanao Grid-01/28/2024 04:23: Weather Update: Northeast Monsoon affecting the country. [WEBSMS] | CMIN
1/28/2024 4:18:57 AM | [NSO Update] Visayas Grid-01/28/2024 04:19: Weather Update: Northeast Monsoon affecting the country. [WEBSMS] | CVIS
1/28/2024 4:18:36 AM | [NSO Update] Luzon Grid-01/28/2024 04:18: Weather Update: Northeast Monsoon affecting the country. [WEBSMS] | CLUZ
1/28/2024 12:20:21 AM | Mindanao Grid-01/28/2024 00:24: GN Power Unit #1 shutdown at 0018H, for reserved shutdown. [WEBSMS] | CMIN
1/27/2024 11:12:30 PM | Luzon Grid-01/27/2024 23:12: Ilijan 500kV Bus 2 restored at 2312H (Planned Outage) [WEBSMS] | CLUZ
1/27/2024 8:01:04 PM | Luzon Grid-01/27/2024 20:01: BCCPP-Lamao 230kV Line 1 restored at 2001H (Planned Outage) [WEBSMS] | CLUZ
1/27/2024 7:33:36 PM | Luzon Grid-01/27/2024 19:33: San Jose SS 115kV Bus 2 restored at 1932H (Planned Outage) [WEBSMS] | CLUZ
1/27/2024 7:25:57 PM | Luzon Grid-01/27/2024 19:26: San Jose-Angat 115kV Line 3 energized at 1924H (Planned Outage) [WEBSMS] | CLUZ
1/27/2024 6:29:28 PM | Mindanao Grid-01/27/2024 18:33: AGUS 6 Unit 2 online at 1818H (Planned Outage Non-GOMP) [WEBSMS] | CMIN
1/27/2024 5:52:02 PM | Mindanao Grid-01/27/2024 17:55: APC Lake Mainit Hydro online at 1747H. (Unplanned Outage). [WEBSMS] | CMIN
1/27/2024 5:36:53 PM | Mindanao Grid-01/27/2024 17:40: Asiga Hydro (ASG) online at 1721H. (Unplanned Outage). [WEBSMS] | CMIN
1/27/2024 5:31:48 PM | Luzon Grid-01/27/2024 17:31: San Jose-San Rafael 230kV Line restored at 1731H (Planned Outage) [WEBSMS] | CLUZ
1/27/2024 5:30:09 PM | [NSO Update] Mindanao Grid-01/27/2024 17:33: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3044MW, PK=1980MW, RR=72MW, NetOpMargin: EVE=992 Highest Unit O/L: GNPK 1,2 &4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @97MW, AG5 @31MW, AG6 @115MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/27/2024 5:28:22 PM | [NSO Update] Visayas Grid-01/27/2024 17:28: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2260MW, PK=1811MW, RR=90MW, NetOpMargin: EVE=360 Highest Unit O/L: THVI 1 @169MW Derated Plant: TGPP @113MW, LEYTE A @260MW, PGPP1 @76MW [WEBSMS] | CVIS
1/27/2024 5:27:15 PM | [NSO Update] Luzon Grid-01/27/2024 17:27: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13089MW, PK=8429MW, RR=347MW, NetOpMargin: EVE=4313 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, MSLC1 @340MW, SLTEC 1 @120MW [WEBSMS] | CLUZ
1/27/2024 4:01:32 PM | Luzon Grid-01/27/2024 16:01: Limay-PAVI Green ORS 69kV Line restored at 1600H (Unplanned Outage) [WEBSMS] | CLUZ
1/27/2024 3:48:38 PM | [NSO Update] Visayas Grid-01/27/2024 15:48: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1546H with power going to Visayas [WEBSMS] | CVIS
1/27/2024 3:48:14 PM | [NSO Update] Mindanao Grid-01/27/2024 15:52: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1546H with power going to Visayas [WEBSMS] | CMIN
1/27/2024 3:43:56 PM | Mindanao Grid-01/27/2024 15:47: Manolo 2 Unit 2 online at 1524H. (Planned Outage Non-GOMP) [WEBSMS] | CMIN
1/27/2024 3:38:40 PM | [NSO Update] Mindanao Grid-01/27/2024 15:42: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1536H from reverse power direction [WEBSMS] | CMIN
1/27/2024 3:38:12 PM | [NSO Update] Visayas Grid-01/27/2024 15:38: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1536H from reverse power direction [WEBSMS] | CVIS
1/27/2024 3:18:12 PM | Mindanao Grid-01/27/2024 15:22: WMPC DG10 shutdown at 1513H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/27/2024 12:56:53 PM | [NSO Update] Mindanao Grid-01/27/2024 13:00: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1251H with power going to Mindanao. [WEBSMS] | CMIN
1/27/2024 12:56:23 PM | [NSO Update] Visayas Grid-01/27/2024 12:56: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1251H with power going to Mindanao. [WEBSMS] | CVIS
1/27/2024 12:54:53 PM | [NSO Update] Mindanao Grid-01/27/2024 12:58: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1215H from forward power direction. [WEBSMS] | CMIN
1/27/2024 12:54:30 PM | [NSO Update] Visayas Grid-01/27/2024 12:54: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1215H from forward power direction. [WEBSMS] | CVIS
1/27/2024 12:50:30 PM | [NSO Update] Mindanao Grid-01/27/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3202MW, PK=1959MW, RR=72MW, NetOpMargin: PM=1171, EVE=955 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @97MW, AG5 @31MW, AG6 @115MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/27/2024 12:48:33 PM | [NSO Update] Visayas Grid-01/27/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2562MW, PK=1785MW, RR=85MW, NetOpMargin: PM=692, EVE=340 Highest Unit O/L: THVI 1 @169MW Derated Plant: TGPP @113MW, LEYTE A @295MW, PGPP1 @76MW, PEDC 1 @50MW, PEDC 2 @50MW [WEBSMS] | CVIS
1/27/2024 12:39:34 PM | [NSO Update] Luzon Grid-01/27/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13791MW, PK=8662MW, RR=351MW, NetOpMargin: PM=4777, EVE=3959 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @177MW, MSLC1 @340MW, SLTEC 1 @120MW [WEBSMS] | CLUZ
1/27/2024 12:06:05 PM | Mindanao Grid-01/27/2024 12:09: Asiga Hydro (ASG) shutdown at 1201H. (Unplanned Outage, affected by ANECO emergency shutdown) [WEBSMS] | CMIN
1/27/2024 12:04:27 PM | Mindanao Grid-01/27/2024 12:08: APC Lake Mainit Hydro shutdown at 1145H. (Unplanned Outage, affected by ANECO emergency shutdown) [WEBSMS] | CMIN
1/27/2024 10:19:28 AM | Luzon Grid-01/27/2024 10:19: San Jose SS 115kV Bus 2 de-energized at 1018H. (Planned Outage) [WEBSMS] | CLUZ
1/27/2024 10:02:30 AM | Mindanao Grid-01/27/2024 10:06: SPC Mati online at 1001H. MO dispatched. [WEBSMS] | CMIN
1/27/2024 9:54:57 AM | Mindanao Grid-01/27/2024 09:58: WMPC DG10 Online at 0950H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/27/2024 7:54:29 AM | Luzon Grid-01/27/2024 07:54: San Jose-Angat 115kV Line 3 de-energized at 0748H. (Planned Outage) [WEBSMS] | CLUZ
1/27/2024 7:27:57 AM | Mindanao Grid-01/27/2024 07:31: Manolo 2 Unit 2 shutdown at 0723H. (Planned Outage Non-GOMP) [WEBSMS] | CMIN
1/27/2024 7:15:20 AM | Luzon Grid-01/27/2024 07:15: Daraga-Tiwi Plant A 230kV Line de-energized at 0714H. (Planned Outage) [WEBSMS] | CLUZ
1/27/2024 7:11:24 AM | Luzon Grid-01/27/2024 07:11: San Jose-San Rafael 230kV Line de-energized at 0710H. (Planned Outage) [WEBSMS] | CLUZ
1/27/2024 6:40:09 AM | Luzon Grid-01/27/2024 06:40: BCCPP-Lamao 230kV Line 1 de-energized at 0639H. (Planned Outage) [WEBSMS] | CLUZ
1/27/2024 6:10:29 AM | Luzon Grid-01/27/2024 06:10: Ilijan PP SS 500KV Bus 2 de-energized at 0610H. (Planned Outage) [WEBSMS] | CLUZ
1/27/2024 5:58:41 AM | [NSO Update] Mindanao Grid-01/27/2024 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3109MW, PK=1813MW, RR=70MW, NetOpMargin: AM=1226, PM=1158, EVE=1095 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @97MW, AG5 @31MW, AG6 @115MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/27/2024 5:57:42 AM | [NSO Update] Visayas Grid-01/27/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2320MW, PK=1747MW, RR=81MW, NetOpMargin: AM=492, PM=461, EVE=341 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TGPP @ 113MW, Leyte A @ 295MW, PGPP1 @ 76MW, PEDC U1 @ 50MW, PEDC U2 @ 50MW [WEBSMS] | CVIS
1/27/2024 5:56:17 AM | [NSO Update] Luzon Grid-01/27/2024 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13885MW, PK=8539MW, RR=334MW, NetOpMargin: AM=5013, PM=4678, EVE=3811 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 177MW, Masinloc 1 @ 340MW, SLTEC 1 @ 120MW [WEBSMS] | CLUZ
1/27/2024 4:43:18 AM | Visayas Grid-01/27/2024 04:43: Magdugo-TVT 230 KV L2 de-energized at 0429H (Planned Outage) [WEBSMS] | CVIS
1/27/2024 4:18:35 AM | [NSO Update] Mindanao Grid-01/27/2024 04:22: Weather Update: Northeast Monsoon affecting the country. [WEBSMS] | CMIN
1/27/2024 4:18:16 AM | [NSO Update] Visayas Grid-01/27/2024 04:18: Weather Update: Northeast Monsoon affecting the country. [WEBSMS] | CVIS
1/27/2024 4:17:03 AM | [NSO Update] Luzon Grid-01/27/2024 04:17: Weather Update: Northeast Monsoon affecting the country. [WEBSMS] | CLUZ
1/27/2024 3:20:41 AM | Luzon Grid-01/27/2024 03:20: Pagbilao 3 online at 0310H (Planned Outage) [WEBSMS] | CLUZ
1/27/2024 3:14:12 AM | Luzon Grid-01/27/2024 03:14: online at 0310H (Planned Outage) [WEBSMS] | CLUZ
1/26/2024 11:22:00 PM | Visayas Grid-01/26/2024 23:22: TVI U2 tripped at 2316H w/a load of 56MW. Unit scheduled for maint at 2400H. (Unplanned Outage) [WEBSMS] | CVIS
1/26/2024 10:15:18 PM | Luzon Grid-01/26/2024 22:15: Kalayaan Unit 4 (-163MW) tripped as pump at 2209H. The highest Luzon system frequency reached 60.630Hz (Unplanned Outage) [WEBSMS] | CLUZ
1/26/2024 9:59:49 PM | Mindanao Grid-01/26/2024 22:03: Villanueva-Maramag 230kV L2 re-energized at 2129H. From NPD-MSO shutdown request (Planned Outage / N-GOMP). [WEBSMS] | CMIN
1/26/2024 9:23:04 PM | Luzon Grid-01/26/2024 21:23: Hermosa 230kV Bus 1 restored at 2122H (Unplanned Outage) [WEBSMS] | CLUZ
1/26/2024 9:14:23 PM | Mindanao Grid-01/26/2024 21:18: WMPC DG10 shutdown at 2114H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/26/2024 9:05:16 PM | Mindanao Grid-01/26/2024 21:09: ASIGA HEP with 8MW tripped at 2100H. Cause: Restricted Earth fault.(Unplanned Outage) [WEBSMS] | CMIN
1/26/2024 5:56:55 PM | [NSO Update] Mindanao Grid-01/26/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3051MW, PK=2033MW, RR=72.3MW, NetOpMargin: EVE=945 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @97MW, AG5 @31MW, AG6 @115MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/26/2024 5:55:57 PM | [NSO Update] Visayas Grid-01/26/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2412MW, PK=1932MW, RR=85MW, NetOpMargin: EVE=395 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 113.6MW, Leyte A @ 285MW, PGPP1 @ 76MW, PEDC U1 @ 50MW, PEDC U2 @ 50MW [WEBSMS] | CVIS
1/26/2024 5:53:58 PM | [NSO Update] Luzon Grid-01/26/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12642MW, PK=8995MW, RR=350MW, NetOpMargin: EVE=3297 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 340MW, SLTEC 1 @ 119MW [WEBSMS] | CLUZ
1/26/2024 5:17:53 PM | Mindanao Grid-01/26/2024 17:21: Manolo 2 Unit 1 online at 1609H (Planned Outage) [WEBSMS] | CMIN
1/26/2024 5:09:31 PM | Mindanao Grid-01/26/2024 17:13: ASIGA HEP with 8MW tripped at 1703H. Cause: Restricted Earth fault.(Unplanned Outage) [WEBSMS] | CMIN
1/26/2024 4:57:59 PM | Mindanao Grid-01/26/2024 17:01: ASIGA HEP online at 1652H from FO isolated from tripping of ANECO 69kV Line. [WEBSMS] | CMIN
1/26/2024 4:48:53 PM | Mindanao Grid-01/26/2024 16:52: Agusan Lake Mainit Hydro online at 1643H. (Unplanned Outage) [WEBSMS] | CMIN
1/26/2024 4:15:23 PM | Mindanao Grid-01/26/2024 16:19: WMPC DG04 shutdown at 1614H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/26/2024 3:11:05 PM | Luzon Grid-01/26/2024 15:11: Hermosa 230kV Bus 1 de-energized at 1508H (Unplanned Outage) [WEBSMS] | CLUZ
1/26/2024 3:08:40 PM | Mindanao Grid-01/26/2024 15:12: ASIGA HEP with 8MW tripped at 1441H. Cause: restricted earth fault. (Unplanned Outage) [WEBSMS] | CMIN
1/26/2024 3:05:01 PM | Mindanao Grid-01/26/2024 15:08: Agusan Lake Mainit Hydro with 20MW load tripped at 1456H. Affected by the Forced outage of ANECO 69kV Line. (Unplanned Outage). No FLV. [WEBSMS] | CMIN
1/26/2024 2:47:06 PM | [NSO Update] Mindanao Grid-01/26/2024 14:50: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1445H with power going to Visayas. [WEBSMS] | CMIN
1/26/2024 2:46:50 PM | [NSO Update] Visayas Grid-01/26/2024 14:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1445H with power going to Visayas. [WEBSMS] | CVIS
1/26/2024 2:35:47 PM | [NSO Update] Visayas Grid-01/26/2024 14:35: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1433H from reverse power direction. [WEBSMS] | CVIS
1/26/2024 2:34:58 PM | [NSO Update] Mindanao Grid-01/26/2024 14:38: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1433H from reverse power direction. [WEBSMS] | CMIN
1/26/2024 12:49:48 PM | [NSO Update] Mindanao Grid-01/26/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3155MW, PK=2233MW, RR=70MW, NetOpMargin: PM=852, EVE=830 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @97MW, AG5 @31MW, AG6 @115MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/26/2024 12:45:32 PM | [NSO Update] Visayas Grid-01/26/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2573MW, PK=2001MW, RR=85MW, NetOpMargin: PM=487, EVE=351 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @ 252MW, PGPP1 @ 76MW, PEDC U1 @ 50MW, PEDC U2 @ 50MW [WEBSMS] | CVIS
1/26/2024 12:42:36 PM | [NSO Update] Luzon Grid-01/26/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13814MW, PK=9393MW, RR=371MW, NetOpMargin: PM=4049, EVE=3292 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW [WEBSMS] | CLUZ
1/26/2024 12:11:52 PM | [NSO Update] Visayas Grid-01/26/2024 12:11: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1210H with power going to Mindanao. [WEBSMS] | CVIS
1/26/2024 12:11:31 PM | [NSO Update] Mindanao Grid-01/26/2024 12:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1210H with power going to Mindanao. [WEBSMS] | CMIN
1/26/2024 12:03:20 PM | [NSO Update] Mindanao Grid-01/26/2024 12:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1158H from forward power direction. [WEBSMS] | CMIN
1/26/2024 12:03:16 PM | [NSO Update] Visayas Grid-01/26/2024 12:03: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1158H from forward power direction. [WEBSMS] | CVIS
1/26/2024 11:22:50 AM | Mindanao Grid-01/26/2024 11:26: ASIGA Hydro tripped with 4MW load at 1115H. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
1/26/2024 11:16:03 AM | Mindanao Grid-01/26/2024 11:19: WMPC DG04 Online at 1113H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/26/2024 9:49:36 AM | Luzon Grid-01/26/2024 09:49: Balsik SS PCB 9Z-01CB24BIK open at 0948H (Planned Outage) [WEBSMS] | CLUZ
1/26/2024 8:57:01 AM | Mindanao Grid-01/26/2024 09:00: WMPC DG10 Online at 0852H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/26/2024 8:46:23 AM | Visayas Grid-01/26/2024 08:46: Gahit-Barotac 230KV Line 2 declared on normal operation at 0838H, Test & Comissioning completed. [WEBSMS] | CVIS
1/26/2024 8:32:50 AM | Mindanao Grid-01/26/2024 08:36: Manolo 2 Unit 2 online at 0815H. (Unplanned Outage) [WEBSMS] | CMIN
1/26/2024 8:29:31 AM | Mindanao Grid-01/26/2024 08:33: Manolo 2 Unit 2 with 4.3MW load trip at 0810H. (Unplanned Outage) [WEBSMS] | CMIN
1/26/2024 7:12:33 AM | Mindanao Grid-01/26/2024 07:16: Villanueva-Maramag 230kV L2 de-energized at 0636H per request from NPD-MSO. Planned Outage / N-GOMP. [WEBSMS] | CMIN
1/26/2024 7:12:03 AM | Mindanao Grid-01/26/2024 07:15: Manolo 2 Unit 1 shutdown at 0707H. (Planned Outage Non-GOMP) [WEBSMS] | CMIN
1/26/2024 6:42:56 AM | Luzon Grid-01/26/2024 06:42: Amadeo 300MVA T02(Customer Owned) restored at 0639H (Planned Outage) [WEBSMS] | CLUZ
1/26/2024 6:14:16 AM | Visayas Grid-01/26/2024 06:14: New 230KV Gahit-Barotac Line 2 energized looping @0605H. [WEBSMS] | CVIS
1/26/2024 5:54:52 AM | [NSO Update] Luzon Grid-01/26/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13782MW, PK=9339MW, RR=374MW, NetOpMargin: AM=4069, PM=3287, EVE=2629 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @250MW [WEBSMS] | CLUZ
1/26/2024 5:50:05 AM | [NSO Update] Mindanao Grid-01/26/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3115MW, PK=2069MW, RR=70MW, NetOpMargin: AM=976, PM=664, EVE=657 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @56MW, AG2 @76MW, AG4 @97MW, AG5 @31MW, AG6 @115MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/26/2024 5:46:43 AM | [NSO Update] Visayas Grid-01/26/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2651MW, PK=1985MW, RR=81MW, NetOpMargin: AM=585, PM=352, EVE=356 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @295MW, PGPP1 @76MW [WEBSMS] | CVIS
1/26/2024 5:21:03 AM | Visayas Grid-01/26/2024 05:21: New 230KV Gahit-Barotac Line 2 energized @0513H. [WEBSMS] | CVIS
1/26/2024 4:49:53 AM | [NSO Update] Mindanao Grid-01/26/2024 04:53: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CMIN
1/26/2024 4:49:35 AM | [NSO Update] Visayas Grid-01/26/2024 04:49: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CVIS
1/26/2024 4:49:20 AM | [NSO Update] Luzon Grid-01/26/2024 04:49: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
1/26/2024 3:15:43 AM | Luzon Grid-01/26/2024 03:15: Kalayaan Unit 4 (-159MW) tripped as pump at 0309H. The highest Luzon system frequency reached 60.44Hz. (Unplanned Outage) [WEBSMS] | CLUZ
1/26/2024 1:24:29 AM | Luzon Grid-01/26/2024 01:24: Kalayaan Unit 4 online as pump at 0121H. (From an unplanned outage) [WEBSMS] | CLUZ
1/26/2024 1:03:30 AM | Luzon Grid-01/26/2024 01:03: Amadeo 300MVA T02(Customer Owned) was de-energized at 0051H. (Planned Outage) [WEBSMS] | CLUZ
1/25/2024 9:43:31 PM | Mindanao Grid-01/25/2024 21:47: WMPC DG10 shutdown at 2114H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/25/2024 9:05:53 PM | Mindanao Grid-01/25/2024 21:09: Villanueva - Maramag 230kV L1 energized at 2102H (Planned Outage). [WEBSMS] | CMIN
1/25/2024 8:27:52 PM | Luzon Grid-01/25/2024 20:27: Hermosa PCB 8-02CB04HER was energized at 2021H after SF6 gas refilling at 8-02CT05HER phase A. (Unplanned Outage) [WEBSMS] | CLUZ
1/25/2024 7:46:57 PM | Luzon Grid-01/25/2024 19:46: Hermosa-BCCPP 230kV line 3 was restored at 1946H. (Planned Outage) [WEBSMS] | CLUZ
1/25/2024 5:58:35 PM | [NSO Update] Mindanao Grid-01/25/2024 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3025MW, PK=2209MW, RR=72.3MW, NetOpMargin: EVE=744 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @77MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/25/2024 5:57:33 PM | [NSO Update] Visayas Grid-01/25/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2480MW, PK=2139MW, RR=87MW, NetOpMargin: EVE=254 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 288MW, PGPP1 @ 76MW, PEDC U1 @ 50MW, PEDC U2 @ 50MW [WEBSMS] | CVIS
1/25/2024 5:54:50 PM | [NSO Update] Luzon Grid-01/25/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12840MW, PK=9467MW, RR=390MW, NetOpMargin: EVE=2983 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 340MW, SLTEC 1 @ 119MW [WEBSMS] | CLUZ
1/25/2024 4:18:16 PM | Mindanao Grid-01/25/2024 16:22: WMPC DG04 shutdown at 1614H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/25/2024 4:10:31 PM | Luzon Grid-01/25/2024 16:10: Lal-lo-NAREDCO 69kV line 2 auto-tripped at 1600H. (Unplanned Outage) [WEBSMS] | CLUZ
1/25/2024 3:22:42 PM | [NSO Update] Mindanao Grid-01/25/2024 15:26: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1522H with power going to Visayas. [WEBSMS] | CMIN
1/25/2024 3:22:24 PM | [NSO Update] Visayas Grid-01/25/2024 15:22: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1522H with power going to Visayas. [WEBSMS] | CVIS
1/25/2024 3:21:48 PM | Luzon Grid-01/25/2024 15:21: Hermosa PCB 8-02CB04HER was de-energized at 1520H. (To facilitate SF6 gas refilling. - Unplanned Outage) [WEBSMS] | CLUZ
1/25/2024 3:21:27 PM | Mindanao Grid-01/25/2024 15:25: GN Power Kauswagan Unit #1 online at 1515H from reserved shutdown. Follow RTD. [WEBSMS] | CMIN
1/25/2024 2:59:36 PM | Luzon Grid-01/25/2024 14:59: For info: The commissioning and energization of Cagayan North Solar Power Plant as Load(Lal-lo-NAREDCO 69kV line 2) was completed at 1450H. [WEBSMS] | CLUZ
1/25/2024 2:40:45 PM | [NSO Update] Visayas Grid-01/25/2024 14:40: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1439H from forward power direction. [WEBSMS] | CVIS
1/25/2024 2:40:23 PM | [NSO Update] Mindanao Grid-01/25/2024 14:44: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1439H from forward power direction. [WEBSMS] | CMIN
1/25/2024 2:29:24 PM | Luzon Grid-01/25/2024 14:29: Dasmarinas-TMC II (Ternate) 115kV Line energized at 1427H (Planned Outage) [WEBSMS] | CLUZ
1/25/2024 1:43:47 PM | Luzon Grid-01/25/2024 13:43: Tiwi C SS 230kV Bus 2 restored at 1341H (Planned Outage) [WEBSMS] | CLUZ
1/25/2024 12:39:26 PM | [NSO Update] Luzon Grid-01/25/2024 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13750MW, PK=10011MW, RR=411MW, NetOpMargin: PM=3328, EVE=2839 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLTEC 1 @118MW, ILIJAN A @600MW [WEBSMS] | CLUZ
1/25/2024 12:34:28 PM | [NSO Update] Visayas Grid-01/25/2024 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2740MW, PK=2215MW, RR=90MW, NetOpMargin: PM=435, EVE=327 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @107.5MW, LEYTE A @293MW, PGPP1 @76MW [WEBSMS] | CVIS
1/25/2024 12:31:30 PM | [NSO Update] Mindanao Grid-01/25/2024 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3089MW, PK=2232MW, RR=72MW, NetOpMargin: PM=785, EVE=803 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @77MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/25/2024 10:55:29 AM | Mindanao Grid-01/25/2024 10:59: WMPC DG04 Online at 1050H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/25/2024 9:15:01 AM | Luzon Grid-01/25/2024 09:15: Tiwi C SS 230kV Bus 2 de-energized at 0914H (Planned Outage) [WEBSMS] | CLUZ
1/25/2024 9:09:43 AM | Luzon Grid-01/25/2024 09:09: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0907H (Planned Outage) [WEBSMS] | CLUZ
1/25/2024 9:07:12 AM | Mindanao Grid-01/25/2024 09:10: WMPC DG10 Online at 0856H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/25/2024 8:59:36 AM | Mindanao Grid-01/25/2024 09:03: Agus 5 - Aurora 138kv line restored 0820H. (Unplanned outage). [WEBSMS] | CMIN
1/25/2024 7:24:09 AM | Luzon Grid-01/25/2024 07:24: Limay-PAVI Green ORS 69kV Line restored at 0722H (Planned Outage) [WEBSMS] | CLUZ
1/25/2024 6:23:47 AM | Luzon Grid-01/25/2024 06:23: Limay-PAVI Green ORS 69kV Line de-energized at 0619H (Planned Outage) [WEBSMS] | CLUZ
1/25/2024 6:15:33 AM | Mindanao Grid-01/25/2024 06:19: Villanueva-Maramag 230kV L1 de-energized 0609H. (Planed outage) [WEBSMS] | CMIN
1/25/2024 6:06:49 AM | Luzon Grid-01/25/2024 06:06: Hermosa-BCCPP 230kV Line 3 de-energized at 0605H (Planned Outage) [WEBSMS] | CLUZ
1/25/2024 5:49:45 AM | [NSO Update] Luzon Grid-01/25/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13785MW, PK=9499MW, RR=405MW, NetOpMargin: AM=3881, PM=2739, EVE=2427 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @340MW, SLTEC 1 @118MW [WEBSMS] | CLUZ
1/25/2024 5:44:59 AM | [NSO Update] Mindanao Grid-01/25/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3096MW, PK=2185MW, RR=70MW, NetOpMargin: AM=840, PM=724, EVE=752 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @77MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/25/2024 5:43:52 AM | [NSO Update] Visayas Grid-01/25/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2583MW, PK=2120MW, RR=87MW, NetOpMargin: AM=376, PM=221, EVE=204 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @107.5MW, LEYTE A @295MW, PGPP1 @76MW [WEBSMS] | CVIS
1/25/2024 4:54:12 AM | [NSO Update] Mindanao Grid-01/25/2024 04:57: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CMIN
1/25/2024 4:53:57 AM | [NSO Update] Visayas Grid-01/25/2024 04:53: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CVIS
1/25/2024 4:53:39 AM | [NSO Update] Luzon Grid-01/25/2024 04:53: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CLUZ
1/25/2024 2:25:51 AM | Luzon Grid-01/25/2024 02:25: Tiwi A-Tiwi C 230kV Tie Line 1 & Line 2 restored at 0223H and 0225H, respectively. (Planned Outage) [WEBSMS] | CLUZ
1/25/2024 1:59:21 AM | Mindanao Grid-01/25/2024 02:03: Agus 5 U1 Online at 0156H. Unplanned Outage. [WEBSMS] | CMIN
1/25/2024 1:21:02 AM | Mindanao Grid-01/25/2024 01:25: Baloi - Tagoloan 138KV Line 1 autotripped and autoreclosed at 0053H (Unplanned Outage) [WEBSMS] | CMIN
1/25/2024 1:12:29 AM | Luzon Grid-01/25/2024 01:12: Ilijan Block B transformer de-energized at 0111H (Planned Outage) [WEBSMS] | CLUZ
1/25/2024 12:58:51 AM | Mindanao Grid-01/25/2024 01:02: Agus 5 U2 Online at 0046H. Unplanned Outage. [WEBSMS] | CMIN
1/25/2024 12:56:34 AM | Mindanao Grid-01/25/2024 01:00: At 0001H, Agus 5 - Aurora138kV line tripped while Baloi-Agus 5 138kV line PCB tripped at Agus 5 SS side only, resulted to the isolation of Agus 5 HEP U1 and U2. Unplanned Outage. [WEBSMS] | CMIN
1/25/2024 12:19:57 AM | Mindanao Grid-01/25/2024 00:24: Agus 5 - Aurora 138KV line tripped at 0001H (Unplanned Outage) [WEBSMS] | CMIN
1/24/2024 11:54:21 PM | Luzon Grid-01/24/2024 23:54: Ilijan GT2-1 shutdown at 2353H (Planned Outage) [WEBSMS] | CLUZ
1/24/2024 11:48:57 PM | Luzon Grid-01/24/2024 23:49: Kalayaan 4 as pump (-160MW) tripped at 2346H. Highest Frequency is 60.53Hz (Unplanned Outage) [WEBSMS] | CLUZ
1/24/2024 11:45:29 PM | Luzon Grid-01/24/2024 23:45: Ilijan ST2 shutdown at 2342H (Planned Outage) [WEBSMS] | CLUZ
1/24/2024 9:47:11 PM | Mindanao Grid-01/24/2024 21:51: WMPC DG04 shutdown at 2114H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/24/2024 7:58:48 PM | Visayas Grid-01/24/2024 19:59: CEDC U1 cut in at 1957H (Unplanned Outage) [WEBSMS] | CVIS
1/24/2024 5:53:46 PM | [NSO Update] Mindanao Grid-01/24/2024 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3022MW, PK=2183MW, RR=70MW, NetOpMargin: EVE=769 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @77MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/24/2024 5:51:03 PM | [NSO Update] Visayas Grid-01/24/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2547MW, PK=2169MW, RR=84MW, NetOpMargin: EVE=294 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 290MW, PGPP1 @ 68MW [WEBSMS] | CVIS
1/24/2024 5:49:12 PM | [NSO Update] Luzon Grid-01/24/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13161MW, PK=9855MW, RR=394MW, NetOpMargin: EVE=2912 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 340MW, SLTEC 1 @ 118MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
1/24/2024 5:44:08 PM | Mindanao Grid-01/24/2024 17:48: Agus 1 U1 Online at 1659H, from Forced Outage. Follow RTD. [WEBSMS] | CMIN
1/24/2024 4:21:45 PM | Visayas Grid-01/24/2024 16:22: PGPP 1 U3 cut in at 1619H (Unplanned Outage) [WEBSMS] | CVIS
1/24/2024 4:16:51 PM | Mindanao Grid-01/24/2024 16:20: WMPC DG06 shutdown at 1614H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/24/2024 2:41:44 PM | Luzon Grid-01/24/2024 14:42: Tayabas PCB 9-03CB24TAY restored at 1439H (Unplanned Outage) [WEBSMS] | CLUZ
1/24/2024 12:50:17 PM | [NSO Update] Mindanao Grid-01/24/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3074MW, PK=2291MW, RR=71MW, NetOpMargin: PM=712, EVE=739 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @77MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/24/2024 12:49:11 PM | [NSO Update] Visayas Grid-01/24/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2628MW, PK=2281MW, RR=87MW, NetOpMargin: PM=260, EVE=251 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @285MW, PGPP1 @38MW [WEBSMS] | CVIS
1/24/2024 12:47:23 PM | [NSO Update] Luzon Grid-01/24/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13724MW, PK=10275MW, RR=408MW, NetOpMargin: PM=3042, EVE=2765 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @280MW, MSLC3 @315MW, SLTEC 1 @118MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/24/2024 10:53:52 AM | Mindanao Grid-01/24/2024 10:57: WMPC DG06 Online at 1051H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/24/2024 8:57:50 AM | Mindanao Grid-01/24/2024 09:01: WMPC DG04 Online at 0851H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/24/2024 8:31:50 AM | Luzon Grid-01/24/2024 08:32: Tiwi A-Tiwi C 230kV Tie Line 1 & Line 2 de-energized at 0829H and 0832H, respectively. (Planned Outage) [WEBSMS] | CLUZ
1/24/2024 5:47:18 AM | [NSO Update] Luzon Grid-01/24/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13754MW, PK=10034MW, RR=404MW, NetOpMargin: AM=3316, PM=3558, EVE=3324 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @280MW, MASINLOC 3 @315MW, SLTEC 1 @118MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/24/2024 5:47:08 AM | Luzon Grid-01/24/2024 05:47: BCCPP 230kV Bus 1 was energized at 0546H. (Planned Outage) [WEBSMS] | CLUZ
1/24/2024 5:34:54 AM | [NSO Update] Mindanao Grid-01/24/2024 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3094MW, PK=2081MW, RR=70MW, NetOpMargin: AM=943, PM=829, EVE=769 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @77MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @27MW, PG4 @90MW [WEBSMS] | CMIN
1/24/2024 5:34:49 AM | [NSO Update] Visayas Grid-01/24/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2618MW, PK=2105MW, RR=85MW, NetOpMargin: AM=427, PM=416, EVE=304 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @293MW, PGPP1 @38MW [WEBSMS] | CVIS
1/24/2024 4:19:43 AM | Luzon Grid-01/24/2024 04:19: SBMA-Subic Solar Power 230kV line energized at 0419H (Planned Outage) [WEBSMS] | CLUZ
1/24/2024 4:08:27 AM | [NSO Update] Luzon Grid-01/24/2024 04:08: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
1/24/2024 4:08:22 AM | [NSO Update] Mindanao Grid-01/24/2024 04:12: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
1/24/2024 4:08:01 AM | [NSO Update] Visayas Grid-01/24/2024 04:08: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CVIS
1/23/2024 11:44:58 PM | Visayas Grid-01/23/2024 23:45: CEDC unit #1 cut-out at 2330H, due to DE Super Heater Isolation Valve leak. (Unplanned Outage) [WEBSMS] | CVIS
1/23/2024 10:38:11 PM | Luzon Grid-01/23/2024 22:38: BCCPP 230kV Bus 1 was de-energized at 2237H. (Planned Outage) [WEBSMS] | CLUZ
1/23/2024 9:15:57 PM | Mindanao Grid-01/23/2024 21:19: WMPC DG10 shutdown at 2114H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/23/2024 6:41:38 PM | Luzon Grid-01/23/2024 18:41: SBMA-Subic Solar Power 230kV line was de-energized at 1839H. (Planned Outage) [WEBSMS] | CLUZ
1/23/2024 5:56:22 PM | Luzon Grid-01/23/2024 17:56: Lamao-Alas-asin 230kV line 2 was restored at 1754H. (Planned Outage) [WEBSMS] | CLUZ
1/23/2024 5:41:08 PM | [NSO Update] Mindanao Grid-01/23/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3152MW, PK=2192MW, RR=72MW, NetOpMargin: EVE=887 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @33MW, MA2 @50MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/23/2024 5:40:58 PM | [NSO Update] Visayas Grid-01/23/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2498MW, PK=2176MW, RR=88MW, NetOpMargin: EVE=234 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @285MW, PGPP1 @38MW [WEBSMS] | CVIS
1/23/2024 5:40:44 PM | [NSO Update] Luzon Grid-01/23/2024 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13146MW, PK=10182MW, RR=390MW, NetOpMargin: EVE=2574 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @175MW, MASINLOC 3 @310MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/23/2024 5:24:54 PM | Mindanao Grid-01/23/2024 17:28: Agus 6 SY-Agus 6 HEP 69kV L1 energized at 1617H. After MTD-A ride on activities, HVE testing completed. (Planned Outage Requested by Generators). [WEBSMS] | CMIN
1/23/2024 4:50:27 PM | Mindanao Grid-01/23/2024 16:54: Culaman - SMC MCFPP 230kV L1 energized at 1559H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
1/23/2024 4:17:06 PM | Mindanao Grid-01/23/2024 16:21: WMPC DG04 shutdown at 1614H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/23/2024 1:24:23 PM | Mindanao Grid-01/23/2024 13:28: Agus 6 SY 69kV Bus 1 energized at 1218H after clearance from MTD-A. (Unplanned Outage). [WEBSMS] | CMIN
1/23/2024 1:19:09 PM | Mindanao Grid-01/23/2024 13:23: Agus 6 SY 69kV Bus 1 tripped at 1151H. No indications as per SEOD. (Unplanned Outage). [WEBSMS] | CMIN
1/23/2024 12:46:42 PM | [NSO Update] Mindanao Grid-01/23/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3144MW, PK=2228MW, RR=71MW, NetOpMargin: PM=844, EVE=885 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @33MW, MA2 @50MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @120MW [WEBSMS] | CMIN
1/23/2024 12:45:35 PM | [NSO Update] Visayas Grid-01/23/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2583MW, PK=2203MW, RR=89MW, NetOpMargin: PM=291, EVE=227 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 284MW, PGPP1 @ 38MW [WEBSMS] | CVIS
1/23/2024 12:44:16 PM | [NSO Update] Luzon Grid-01/23/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13904MW, PK=10342MW, RR=404MW, NetOpMargin: PM=3159, EVE=2696 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 280MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
1/23/2024 12:00:48 PM | Mindanao Grid-01/23/2024 12:04: Culaman - SMC MCFPP 230kV L1 deenergized at 0957H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
1/23/2024 11:43:09 AM | Mindanao Grid-01/23/2024 11:47: Agus 6 SY-Agus 6 HEP 69kV L1 deenergized at 1023H. Planned Outage Requested by Generators. [WEBSMS] | CMIN
1/23/2024 11:10:36 AM | Mindanao Grid-01/23/2024 11:14: WMPC DG04 Online at 1052H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/23/2024 10:45:39 AM | Mindanao Grid-01/23/2024 10:49: Culaman - SMC MCFPP 230kV L1 deenergized at 0957H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
1/23/2024 9:00:13 AM | Luzon Grid-01/23/2024 09:00: Calaca - Binan 230kV Line restored at 0859H (Unplanned Outage) [WEBSMS] | CLUZ
1/23/2024 8:51:43 AM | Mindanao Grid-01/23/2024 08:55: WMPC DG10 Online at 0849H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/23/2024 6:45:45 AM | Luzon Grid-01/23/2024 06:45: Lamao-Alas-asin 230kV Line 2 de-energized at 0642H (Planned Outage) [WEBSMS] | CLUZ
1/23/2024 5:39:17 AM | [NSO Update] Mindanao Grid-01/23/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3208MW, PK=2088MW, RR=70MW, NetOpMargin: AM=1049, PM=961, EVE=847 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @33MW, MA2 @50MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/23/2024 5:37:45 AM | [NSO Update] Visayas Grid-01/23/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2565MW, PK=2070MW, RR=86MW, NetOpMargin: AM=408, PM=416, EVE=258 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @284MW, PGPP1 @38MW [WEBSMS] | CVIS
1/23/2024 5:35:34 AM | [NSO Update] Luzon Grid-01/23/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13837MW, PK=9978MW, RR=397MW, NetOpMargin: AM=3462, PM=3349, EVE=3063 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/23/2024 4:49:41 AM | [NSO Update] Mindanao Grid-01/23/2024 04:53: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
1/23/2024 4:49:26 AM | [NSO Update] Visayas Grid-01/23/2024 04:49: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
1/23/2024 4:48:59 AM | [NSO Update] Luzon Grid-01/23/2024 04:49: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
1/22/2024 11:37:28 PM | Mindanao Grid-01/22/2024 23:41: WMPC DG04 Shutdown at 2144H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/22/2024 11:17:53 PM | Visayas Grid-01/22/2024 23:18: PEDC unit #3 cut-in to the system at 2314H, initial load 15MW. (Unplanned Outage) [WEBSMS] | CVIS
1/22/2024 11:01:03 PM | Luzon Grid-01/22/2024 23:01: Sta. Rita 30 on-line at 2257H (Unplanned Outage) [WEBSMS] | CLUZ
1/22/2024 9:51:04 PM | Mindanao Grid-01/22/2024 21:55: Nagamin - Zamboanga 138KV Line 1 successfully looped at 2146H (Planned Outage) [WEBSMS] | CMIN
1/22/2024 9:03:40 PM | Visayas Grid-01/22/2024 21:03: 230KV Cebu-Magdugo energized @2102H. (Unplanned Outage) [WEBSMS] | CVIS
1/22/2024 8:02:22 PM | Luzon Grid-01/22/2024 20:02: Calaca - Binan 230kV Line tripped at 2001H. (Unplanned Outage) [WEBSMS] | CLUZ
1/22/2024 7:42:20 PM | Mindanao Grid-01/22/2024 19:46: Zamboanga SS 138KV Bus 2 re-energized at 1939H (Unplanned Outage) [WEBSMS] | CMIN
1/22/2024 6:09:55 PM | [NSO Update] Mindanao Grid-01/22/2024 18:13: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3176MW, PK=2204MW, RR=72MW, NetOpMargin: EVE=900 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46MW, MA2 @34MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/22/2024 6:07:54 PM | [NSO Update] Visayas Grid-01/22/2024 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2414MW, PK=2125MW, RR=82MW, NetOpMargin: EVE=207 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @285MW, PGPP1 @17MW [WEBSMS] | CVIS
1/22/2024 6:05:55 PM | [NSO Update] Luzon Grid-01/22/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13245MW, PK=10071MW, RR=397MW, NetOpMargin: EVE=2777 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW [WEBSMS] | CLUZ
1/22/2024 6:04:04 PM | Luzon Grid-01/22/2024 18:04: Lamao-Alas-asin 230kV line 1 restored at 1802H. (Planned Outage) [WEBSMS] | CLUZ
1/22/2024 5:37:01 PM | Visayas Grid-01/22/2024 17:37: Cebu-Magdugo 230KV Line 1 auto tripped @1734H. (Unplanned Outage) [WEBSMS] | CVIS
1/22/2024 5:34:41 PM | Luzon Grid-01/22/2024 17:34: Sta. Rita 30 with 163MW tripped at 1733H. Lowest system frequency is 59.681Hz. (Unplanned Outage) [WEBSMS] | CLUZ
1/22/2024 4:49:07 PM | Mindanao Grid-01/22/2024 16:53: Baloi - Agus 4 138KV Line 1 re-energized at 1645H (Planned Outage) [WEBSMS] | CMIN
1/22/2024 4:23:00 PM | Luzon Grid-01/22/2024 16:23: Tayabas PCB 9-03CB24TAY de-energized at 1621H. (Unplanned Outage) [WEBSMS] | CLUZ
1/22/2024 4:14:44 PM | Mindanao Grid-01/22/2024 16:18: Zamboanga SS 138KV Bus 2 deenergized at 1610H. Unplanned Outage. [WEBSMS] | CMIN
1/22/2024 2:31:41 PM | Visayas Grid-01/22/2024 14:31: TGPP U#3 cut-in at 1416H. (Unplanned Outage) [WEBSMS] | CVIS
1/22/2024 1:37:21 PM | Visayas Grid-01/22/2024 13:37: LGPP U3 tripped at 1333H (Unplanned Outage) [WEBSMS] | CVIS
1/22/2024 12:54:54 PM | [NSO Update] Mindanao Grid-01/22/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3233MW, PK=2148MW, RR=72MW, NetOpMargin: PM=1013, EVE=1018 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46MW, MA2 @34MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/22/2024 12:52:53 PM | [NSO Update] Visayas Grid-01/22/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2507MW, PK=2219MW, RR=90MW, NetOpMargin: PM=199, EVE=216 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 285MW, [WEBSMS] | CVIS
1/22/2024 12:51:01 PM | Visayas Grid-01/22/2024 12:51: PGPP1 U1 online at 1249H (Unplanned Outage) [WEBSMS] | CVIS
1/22/2024 12:48:55 PM | [NSO Update] Luzon Grid-01/22/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14372MW, PK=10350MW, RR=410MW, NetOpMargin: PM=3612, EVE=3034 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 330MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/22/2024 12:15:12 PM | Visayas Grid-01/22/2024 12:15: NNBP online at 1202H (Unplanned Outage) [WEBSMS] | CVIS
1/22/2024 12:13:52 PM | Visayas Grid-01/22/2024 12:14: PGPP1 U1 tripped at 1212H (Unplanned Outage) [WEBSMS] | CVIS
1/22/2024 11:11:53 AM | Mindanao Grid-01/22/2024 11:15: WMPC DG04 Online at 1050H. RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/22/2024 11:11:21 AM | Visayas Grid-01/22/2024 11:11: PGPP1 U1 online at 1109H (Unplanned Outage) [WEBSMS] | CVIS
1/22/2024 10:24:54 AM | Visayas Grid-01/22/2024 10:25: PGPP1 U1 tripped at 1022H (Unplanned Outage) [WEBSMS] | CVIS
1/22/2024 9:52:36 AM | Mindanao Grid-01/22/2024 09:56: Baloi - Agus 4 138KV Line 1 deenergized at 0945H (Planned Outage) [WEBSMS] | CMIN
1/22/2024 9:36:33 AM | Mindanao Grid-01/22/2024 09:40: Mt Apo U3 online at 0928H. (Unplanned Outage) [WEBSMS] | CMIN
1/22/2024 6:43:37 AM | Luzon Grid-01/22/2024 06:43: Lamao-Alas-asin 230kV line 1 was de-energized at 0642H. (Planned Outage) [WEBSMS] | CLUZ
1/22/2024 6:42:59 AM | Visayas Grid-01/22/2024 06:43: HPC U2 shutdown at 0629H. (Planned Outage) [WEBSMS] | CVIS
1/22/2024 5:50:00 AM | [NSO Update] Mindanao Grid-01/22/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3370MW, PK=2240MW, RR=32MW, NetOpMargin: AM=1098, PM=901, EVE=875 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46MW, MA2 @34MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/22/2024 5:45:24 AM | [NSO Update] Visayas Grid-01/22/2024 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2557MW, PK=2087MW, RR=88MW, NetOpMargin: AM=382, PM=260, EVE=266 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @283MW, PGPP1 @38MW [WEBSMS] | CVIS
1/22/2024 5:41:07 AM | [NSO Update] Luzon Grid-01/22/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14374MW, PK=10381MW, RR=402MW, NetOpMargin: AM=3591, PM=3441, EVE=3163 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/22/2024 5:08:26 AM | Mindanao Grid-01/22/2024 05:12: Mt. Apo Unit 3 with 2.5MW load tripped at 0501H. Reason: For further investigation. (Unplanned Outage) [WEBSMS] | CMIN
1/22/2024 4:32:39 AM | Visayas Grid-01/22/2024 04:32: PGPP1 Unit #1 cut-in 0259H. (Unplanned Outage) [WEBSMS] | CVIS
1/22/2024 4:12:48 AM | [NSO Update] Luzon Grid-01/22/2024 04:13: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
1/22/2024 4:10:32 AM | [NSO Update] Visayas Grid-01/22/2024 04:10: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CVIS
1/22/2024 4:09:25 AM | [NSO Update] Mindanao Grid-01/22/2024 04:13: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
1/22/2024 3:04:07 AM | Mindanao Grid-01/22/2024 03:08: MALITA BESS Declared available for AS/RR at 0300H. [WEBSMS] | CMIN
1/22/2024 1:48:49 AM | Mindanao Grid-01/22/2024 01:52: Culaman-UPSI BESS 69KV line energized at 0110H. Planned Outage /Non-GOMP. P & E Requested shutdown. [WEBSMS] | CMIN
1/22/2024 1:30:48 AM | Mindanao Grid-01/22/2024 01:34: Culaman SS 230kV 50MVA Power Transformer T1 energized at 0043H. Planned Outage /Non-GOMP. P&E Requested shutdown. [WEBSMS] | CMIN
1/21/2024 8:18:14 PM | Visayas Grid-01/21/2024 20:18: PGPP2 Nasulo cut-in to the system at 2004H. (Unplanned Outage) [WEBSMS] | CVIS
1/21/2024 7:14:02 PM | Visayas Grid-01/21/2024 19:14: Amlan-Nasuji 138KV Line 1 energized at 1912H.(Unplanned Outage) [WEBSMS] | CVIS
1/21/2024 6:39:24 PM | Mindanao Grid-01/21/2024 18:43: WMPC DG07 with 8.5MW load, running as RPS tripped at 1814H. Indication: For further investigation. (Unplanned Outage) [WEBSMS] | CMIN
1/21/2024 5:51:25 PM | [NSO Update] Mindanao Grid-01/21/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3176MW, PK=1988MW, RR=34MW, NetOpMargin: EVE=1154 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46MW, MA2 @34MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/21/2024 5:46:28 PM | [NSO Update] Visayas Grid-01/21/2024 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2340MW, PK=1951MW, RR=80MW, NetOpMargin: EVE=309 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @284MW [WEBSMS] | CVIS
1/21/2024 5:38:48 PM | [NSO Update] Luzon Grid-01/21/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13562MW, PK=9137MW, RR=311MW, NetOpMargin: EVE=4114 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/21/2024 4:59:48 PM | Luzon Grid-01/21/2024 16:59: Pagbilao PP 230kV Bus 1 restored at 1658H (Planned Outage) [WEBSMS] | CLUZ
1/21/2024 4:47:57 PM | Luzon Grid-01/21/2024 16:48: Concepcion 230kV Bus 1 restored at 1647H (Planned Outage) [WEBSMS] | CLUZ
1/21/2024 4:26:01 PM | Mindanao Grid-01/21/2024 16:29: Tagoloan-San Martin ECAC (SME) 138kV L energized at 1611H. From Planned Outage. Affected by Shutdown of Tagoloan SS 138kV Bus 1. (Customers owned and maintained line, CEPALCO) [WEBSMS] | CMIN
1/21/2024 3:58:12 PM | Luzon Grid-01/21/2024 15:58: Sta. Rita SS 230kV Busbar 1 restored at 1557H (Planned Outage) [WEBSMS] | CLUZ
1/21/2024 3:32:26 PM | Visayas Grid-01/21/2024 15:32: Amlan-Nasuji 138KV Line 1 tripped at 1503H, load transfer to line 2. (Unplanned Outage) [WEBSMS] | CVIS
1/21/2024 3:20:55 PM | Visayas Grid-01/21/2024 15:21: PGPP2 Nasulo(40.MW) auto-tripped at 1504H.(Unplanned Outage) [WEBSMS] | CVIS
1/21/2024 2:54:02 PM | Mindanao Grid-01/21/2024 14:57: Tacurong SS 138kV, 50 MVA Power Transformer No.2 energized at 1447H from Planned Outage/GOMP. [WEBSMS] | CMIN
1/21/2024 2:28:18 PM | Luzon Grid-01/21/2024 14:28: Calaca-Binan 230kV line restored at 1425H (Unplanned Outage) [WEBSMS] | CLUZ
1/21/2024 1:34:01 PM | Mindanao Grid-01/21/2024 13:37: Kibawe Solar (KSO) online at 1324H (Unplanned Outage). [WEBSMS] | CMIN
1/21/2024 1:30:29 PM | Mindanao Grid-01/21/2024 13:34: Kibawe-Agus 2 138kV L1 tripped at 1227H. Ind: L3E, 41.3kms. Reenergized at 1245H. Unplanned Outage). (The line is energized w/o load, from Kibawe up to Twr. #103 for anti-pilferage purposes only). [WEBSMS] | CMIN
1/21/2024 1:19:25 PM | Mindanao Grid-01/21/2024 13:23: Kibawe Solar (KSO) with 4.87MW load tripped at 1227H (Unplanned Outage). [WEBSMS] | CMIN
1/21/2024 1:00:50 PM | [NSO Update] Mindanao Grid-01/21/2024 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3220MW, PK=1776MW, RR=33MW, NetOpMargin: PM=1411, EVE=1236 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46MW, MA2 @34MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/21/2024 12:58:47 PM | [NSO Update] Visayas Grid-01/21/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2576MW, PK=1822MW, RR=77MW, NetOpMargin: PM=676, EVE=217 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @275MW [WEBSMS] | CVIS
1/21/2024 12:56:52 PM | [NSO Update] Luzon Grid-01/21/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14506MW, PK=8676MW, RR=315MW, NetOpMargin: PM=5515, EVE=4062 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/21/2024 12:22:38 PM | Mindanao Grid-01/21/2024 12:26: Tacurong SS 138kV Power Transformer No.2 deenergized at 1216H (Planned Outage/GOMP). [WEBSMS] | CMIN
1/21/2024 10:01:07 AM | Mindanao Grid-01/21/2024 10:05: Tacurong SS 138kV Power Transformer No.4 energized at 0957H from Planned Outage/GOMP. [WEBSMS] | CMIN
1/21/2024 9:53:31 AM | Luzon Grid-01/21/2024 09:53: For Info: The auto-tripping for Calaca-Binan 230kV line at 0903H was due to the cut OHGW at structure 20. [WEBSMS] | CLUZ
1/21/2024 9:52:17 AM | Mindanao Grid-01/21/2024 09:56: WMPC DG07 online at 0949H, RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/21/2024 9:46:10 AM | Mindanao Grid-01/21/2024 09:50: Tagoloan-Manolo Fortich 138kV L2 energized at 0940H from Planned Outage/ Non-GOMP. [WEBSMS] | CMIN
1/21/2024 9:39:21 AM | Mindanao Grid-01/21/2024 09:43: Tagoloan SS 138kV Bus 1 energized back at 0936H from Planned Outage/Non-GOMP. [WEBSMS] | CMIN
1/21/2024 9:06:56 AM | Luzon Grid-01/21/2024 09:07: Calaca-Binan 230kV line auto-tripped at 0903H. (Unplanned Outage) [WEBSMS] | CLUZ
1/21/2024 8:19:33 AM | Mindanao Grid-01/21/2024 08:23: Nagamin-Zamboanga 138kV L1 deenergized at 0735H (Planned Outage). P & E requested shutdown. [WEBSMS] | CMIN
1/21/2024 8:13:02 AM | Mindanao Grid-01/21/2024 08:16: Tacurong SS 138kV Power Transformer No.4 deenergized at 0708H (Planned Outage/GOMP). [WEBSMS] | CMIN
1/21/2024 8:07:53 AM | Luzon Grid-01/21/2024 08:08: Concepcion 230kV Bus 1 was de-energized at 0807H. (Planned Outage) [WEBSMS] | CLUZ
1/21/2024 8:04:35 AM | Mindanao Grid-01/21/2024 08:08: Tagoloan SS 138kV Bus 1 deenergized at 0636H (Planned Outage/Non-GOMP). P & E requested shutdown. [WEBSMS] | CMIN
1/21/2024 7:57:11 AM | Mindanao Grid-01/21/2024 08:01: Tagoloan-Manolo Fortich 138kV L2 deenergized at 0632H (Planned Outage). Affected by Shutdown of Tagoloan SS 138kV Bus 1. [WEBSMS] | CMIN
1/21/2024 7:39:26 AM | Mindanao Grid-01/21/2024 07:43: Tagoloan-San Martin ECAC (SME) 138kV L deenergized at 0628H. (Planned Outage). Affected by Shutdown of Tagoloan SS 138kV Bus 1. (Customers owned and maintained line, CEPALCO) [WEBSMS] | CMIN
1/21/2024 7:14:23 AM | Mindanao Grid-01/21/2024 07:18: LAMSAN (LSK) online at 0705H (Planned Outage) [WEBSMS] | CMIN
1/21/2024 7:12:01 AM | Mindanao Grid-01/21/2024 07:15: Update: WMPC DG10 online at 0650H, RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/21/2024 7:09:16 AM | Mindanao Grid-01/21/2024 07:13: WMPC DG10 shutdown at 0650H, RPS- System Voltage Requirement. [WEBSMS] | CMIN
1/21/2024 5:51:40 AM | Luzon Grid-01/21/2024 05:51: Muntinlupa SS 300MVA T04 de-energized at 0547H (Planned Outage) [WEBSMS] | CLUZ
1/21/2024 5:36:05 AM | [NSO Update] Mindanao Grid-01/21/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3235MW, PK=1671MW, RR=32MW, NetOpMargin: AM=1532, PM=1461, EVE=1218 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46MW, MA2 @34MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/21/2024 5:36:02 AM | [NSO Update] Visayas Grid-01/21/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2562MW, PK=1725MW, RR=77MW, NetOpMargin: AM=761, PM=669, EVE=252 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @288MW [WEBSMS] | CVIS
1/21/2024 5:35:58 AM | [NSO Update] Luzon Grid-01/21/2024 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14560MW, PK=8072MW, RR=315MW, NetOpMargin: AM=6174, PM=5906, EVE=4408 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @330MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/21/2024 4:08:49 AM | [NSO Update] Luzon Grid-01/21/2024 04:08: Weather Advisory: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
1/21/2024 4:08:46 AM | [NSO Update] Visayas Grid-01/21/2024 04:08: Weather Advisory: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
1/21/2024 4:08:38 AM | [NSO Update] Mindanao Grid-01/21/2024 04:12: Weather Advisory: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
1/21/2024 1:09:25 AM | Mindanao Grid-01/21/2024 01:13: Culaman SS 230kV 50MVA Power Transformer T2 re-energized at 0049H. From Planned Outage /Non-GOMP (P&E request). [WEBSMS] | CMIN
1/20/2024 11:17:36 PM | Luzon Grid-01/20/2024 23:17: Las Pinas(Zapote) 300MVA T03 restored at 2316H (Planned Outage) [WEBSMS] | CLUZ
1/20/2024 9:38:15 PM | Luzon Grid-01/20/2024 21:38: SBPL online at 2135H (Unplanned Outage) [WEBSMS] | CLUZ
1/20/2024 9:35:07 PM | Mindanao Grid-01/20/2024 21:39: Peak Power SOCCSARGEN Shutdown at 1911H, from MO Dispatched. Follow RTD. [WEBSMS] | CMIN
1/20/2024 9:33:46 PM | Mindanao Grid-01/20/2024 21:37: Peak Power SOCCSARGEN Online at 1852H, MO Dispatched. Follow RTD. [WEBSMS] | CMIN
1/20/2024 9:31:35 PM | Mindanao Grid-01/20/2024 21:35: Peak Power San Frans Shutdown at 1917H, from MO Dispatched. Follow RTD. [WEBSMS] | CMIN
1/20/2024 9:29:04 PM | Mindanao Grid-01/20/2024 21:32: Peak Power San Frans Online at 1856H, MO Dispatched. Follow RTD. [WEBSMS] | CMIN
1/20/2024 9:26:46 PM | Mindanao Grid-01/20/2024 21:30: WMPC DG10 shutdown at 1947H, from MO Dispatched. Follow RTD. [WEBSMS] | CMIN
1/20/2024 9:25:05 PM | Mindanao Grid-01/20/2024 21:29: WMPC DG10 Online at 1858H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
1/20/2024 9:20:23 PM | Mindanao Grid-01/20/2024 21:24: TM2 U2 Shutdown at 1935H, from MO Dispatched. Follow RTD. [WEBSMS] | CMIN
1/20/2024 9:19:03 PM | Mindanao Grid-01/20/2024 21:22: TM2 U2 Online at 1919H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
1/20/2024 9:06:24 PM | Mindanao Grid-01/20/2024 21:10: WMPC DG04 with 7.5MW gross generation tripped at 2054H. Indication: HT Low Pressure Stop. Unplanned Outage. [WEBSMS] | CMIN
1/20/2024 8:50:58 PM | Mindanao Grid-01/20/2024 20:54: TM2 U2 shutdown at 1856H from DENR emission test. Follow RTD. (Security Limit schedule) [WEBSMS] | CMIN
1/20/2024 8:42:16 PM | Visayas Grid-01/20/2024 20:42: Cebu GIS 300 MVA 230/138/13.8 kV TR2 energized at 2011H, stability testing done at 2040H [WEBSMS] | CVIS
1/20/2024 8:12:51 PM | Visayas Grid-01/20/2024 20:12: Cebu GIS 300 MVA 230/138/13.8 kV TR2 energized at 2011H, for stability testing [WEBSMS] | CVIS
1/20/2024 7:52:51 PM | Mindanao Grid-01/20/2024 19:56: Pulangi 4 U3 online at 1926H. Unplanned Outage. [WEBSMS] | CMIN
1/20/2024 7:06:54 PM | Mindanao Grid-01/20/2024 19:10: Pulangi 4 U3 with 60MW gross generation tripped at 1840H. (Indication: To follow), with its lowest frequency of 59.108 Hz causing ALD of about 47.92 MW. (Unplanned Outage) [WEBSMS] | CMIN
1/20/2024 6:07:41 PM | Mindanao Grid-01/20/2024 18:11: Tagoloan-Villanueva 138kV L1 re-energized at 1741H. From Planned Outage / GOMP. [WEBSMS] | CMIN
1/20/2024 6:02:13 PM | Mindanao Grid-01/20/2024 18:06: Baloi-Agus 5 138KV line re-energized at 1727H. From Planned Outage /Non-GOMP (P&E request). [WEBSMS] | CMIN
1/20/2024 5:56:30 PM | [NSO Update] Mindanao Grid-01/20/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3160MW, PK=2054MW, RR=34MW, NetOpMargin: EVE=1072 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46MW, MA2 @34MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @27MW, PG4 @180MW [WEBSMS] | CMIN
1/20/2024 5:54:43 PM | [NSO Update] Visayas Grid-01/20/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2385MW, PK=2058MW, RR=85MW, NetOpMargin: EVE=242 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @295MW [WEBSMS] | CVIS
1/20/2024 5:48:10 PM | [NSO Update] Luzon Grid-01/20/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13024MW, PK=9323MW, RR=350MW, NetOpMargin: EVE=3351 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @330MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/20/2024 3:35:25 PM | Visayas Grid-01/20/2024 15:35: Magdugo - Daanlungsod 138 KV Line re-energized at 1534H. (Planned Outage) [WEBSMS] | CVIS
1/20/2024 3:20:45 PM | Luzon Grid-01/20/2024 15:20: Pagbilao PP 230kV Bus 1 de-energized at 1520H (Planned Outage) [WEBSMS] | CLUZ
1/20/2024 3:14:44 PM | Mindanao Grid-01/20/2024 15:18: WMPC DG10 shutdown at 1513H, RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/20/2024 3:09:52 PM | Luzon Grid-01/20/2024 15:10: Pagbilao EHV-Pagbilao Plant 230kV Line 1 restored at 1509H (Planned Outage) [WEBSMS] | CLUZ
1/20/2024 2:33:24 PM | Luzon Grid-01/20/2024 14:33: Concepcion SS 230kV Bus 2 restored at 1432H (Planned Outage) [WEBSMS] | CLUZ
1/20/2024 1:13:17 PM | [NSO Update] Mindanao Grid-01/20/2024 13:17: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3211MW, PK=2030MW, RR=34MW, NetOpMargin: PM=1147, EVE=1026 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46MW, MA2 @34MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @27MW, PG4 @180MW [WEBSMS] | CMIN
1/20/2024 1:11:55 PM | [NSO Update] Visayas Grid-01/20/2024 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2562MW, PK=1965MW, RR=81MW, NetOpMargin: PM=516, EVE=227 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @286MW [WEBSMS] | CVIS
1/20/2024 1:10:09 PM | [NSO Update] Luzon Grid-01/20/2024 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13324MW, PK=9336MW, RR=364MW, NetOpMargin: PM=3624, EVE=2559 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/20/2024 9:52:00 AM | Mindanao Grid-01/20/2024 09:55: WMPC DG10 online at 0950H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/20/2024 9:13:24 AM | Mindanao Grid-01/20/2024 09:17: TM2 U2 online at 0901H to facilitate scheduled DENR emission test. Follow RTD. (With security limit schedule) [WEBSMS] | CMIN
1/20/2024 8:50:38 AM | Mindanao Grid-01/20/2024 08:54: Baloi-Agus 5 138KV line de-energized at 0836H. P&E request. Planned Outage /Non-GOMP. [WEBSMS] | CMIN
1/20/2024 8:29:12 AM | Mindanao Grid-01/20/2024 08:33: shutdown at 0808H Culaman SS 230kV 50MVA Power Transformer T1 de-energized at 0808H. P&E request. Planned Outage /Non-GOMP. [WEBSMS] | CMIN
1/20/2024 8:09:33 AM | Luzon Grid-01/20/2024 08:09: Concepcion SS 230kV Bus 2 de-energized at 0809H. (Planned Outage) [WEBSMS] | CLUZ
1/20/2024 7:40:23 AM | Mindanao Grid-01/20/2024 07:44: Culaman SS 230kV 50MVA Power Transformer T2 de-energized at 0716H. P&E request. Planned Outage /Non-GOMP. [WEBSMS] | CMIN
1/20/2024 7:19:08 AM | Visayas Grid-01/20/2024 07:19: Magdugo-DaanLungsod 138 KV Line de-energized at 0716H. (Planned Outage) [WEBSMS] | CVIS
1/20/2024 6:48:05 AM | Mindanao Grid-01/20/2024 06:51: Tagoloan-Villanueva 138kV L1 de-energized at 0630H for line maintenance. Planned Outage / GOMP. [WEBSMS] | CMIN
1/20/2024 6:18:29 AM | Luzon Grid-01/20/2024 06:18: Pagbilao EHV-Pagbilao Plant 230kV Line 1 de-energized at 0618H. (Planned Outage) [WEBSMS] | CLUZ
1/20/2024 6:00:34 AM | [NSO Update] Visayas Grid-01/20/2024 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2599MW, PK=1920MW, RR=79MW, NetOpMargin: AM=600, PM=736, EVE=196 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 295MW [WEBSMS] | CVIS
1/20/2024 5:43:52 AM | [NSO Update] Mindanao Grid-01/20/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3221MW, PK=1910MW, RR=32MW, NetOpMargin: AM=1278, PM=1122, EVE=986 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46MW, MA2 @34MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @27MW, PG4 @180MW [WEBSMS] | CMIN
1/20/2024 5:39:08 AM | [NSO Update] Luzon Grid-01/20/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13259MW, PK=9202MW, RR=361MW, NetOpMargin: AM=3695, PM=3774, EVE=2791 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 330MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/20/2024 5:23:50 AM | Mindanao Grid-01/20/2024 05:27: Malita BESS shutdown at 0501H affected by P&E requested shutdown at Culaman SS. Ride-on maintenance activities to be conducted also by SBPI Malita BESS. [WEBSMS] | CMIN
1/20/2024 5:09:56 AM | Luzon Grid-01/20/2024 05:10: Sta. Rita SS 230kV Busbar 1 de-energized at 0509H (Planned Outage) [WEBSMS] | CLUZ
1/20/2024 4:10:06 AM | [NSO Update] Mindanao Grid-01/20/2024 04:13: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
1/20/2024 4:09:51 AM | [NSO Update] Visayas Grid-01/20/2024 04:09: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
1/20/2024 4:09:30 AM | [NSO Update] Luzon Grid-01/20/2024 04:09: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
1/20/2024 1:22:42 AM | Luzon Grid-01/20/2024 01:22: SBPL tripped with a load of 183MW at 0117H, the lowest frequency recorded is 59.399hz, no ALD (Unplanned Outage) [WEBSMS] | CLUZ
1/20/2024 12:27:23 AM | Visayas Grid-01/20/2024 00:27: Cebu - Magdugo 230 kV Line 1 energized at 2251H from Magdugo SS, closed loop in Cebu SS at 0024H [WEBSMS] | CVIS
1/19/2024 11:41:42 PM | Luzon Grid-01/19/2024 23:41: San Lorenzo Module 60 shutdown at 2339H (Planned Outage) [WEBSMS] | CLUZ
1/19/2024 10:54:50 PM | Visayas Grid-01/19/2024 22:54: Cebu - Magdugo 230 kV Line 1 energized at 2251H from Magdugo SS [WEBSMS] | CVIS
1/19/2024 9:14:43 PM | Mindanao Grid-01/19/2024 21:18: WMPC DG10 shutdown at 2113H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/19/2024 7:00:12 PM | Mindanao Grid-01/19/2024 19:04: Libertad Power online at 1845H (Unplanned Outage). [WEBSMS] | CMIN
1/19/2024 6:59:02 PM | Mindanao Grid-01/19/2024 19:02: TM2 U1 shutdown at 1856H from DENR emission testing. [WEBSMS] | CMIN
1/19/2024 6:02:31 PM | Luzon Grid-01/19/2024 18:02: SBPL online at 1800H (Planned Outage) [WEBSMS] | CLUZ
1/19/2024 6:00:19 PM | [NSO Update] Mindanao Grid-01/19/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3172MW, PK=2090MW, RR=72.4MW, NetOpMargin: EVE=1009 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46MW, MA2 @34MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @27MW, PG4 @180MW [WEBSMS] | CMIN
1/19/2024 5:55:36 PM | [NSO Update] Visayas Grid-01/19/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2545MW, PK=2161MW, RR=86MW, NetOpMargin: EVE=298 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 81.2MW, Leyte A @ 296MW [WEBSMS] | CVIS
1/19/2024 5:49:32 PM | [NSO Update] Luzon Grid-01/19/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12706MW, PK=9816MW, RR=300MW, NetOpMargin: EVE=2590 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 330MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/19/2024 4:47:45 PM | Luzon Grid-01/19/2024 16:47: Pagbilao EHV SS 1000MVA T03 restored at 1647H (Planned Outage) [WEBSMS] | CLUZ
1/19/2024 4:11:18 PM | Mindanao Grid-01/19/2024 16:15: WMPC DG03 shutdown at 1609H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/19/2024 3:58:12 PM | Mindanao Grid-01/19/2024 16:02: Agus 5 - Aurora 138kV line re-energized at 1555H (Planned Outage) [WEBSMS] | CMIN
1/19/2024 1:35:43 PM | Mindanao Grid-01/19/2024 13:39: Zamboanga SS 138kV 50MVA Power Transformer T1 energized at 1330H. (Planned outage) [WEBSMS] | CMIN
1/19/2024 12:45:56 PM | [NSO Update] Mindanao Grid-01/19/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3215MW, PK=2029MW, RR=71MW, NetOpMargin: PM=1115, EVE=1075 Highest Unit O/L: GNPK 2 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46MW, MA2 @34MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @27MW, PG4 @180MW [WEBSMS] | CMIN
1/19/2024 12:44:21 PM | [NSO Update] Visayas Grid-01/19/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2504MW, PK=2093MW, RR=90MW, NetOpMargin: PM=320, EVE=273 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 81.2MW, Leyte A @ 275MW [WEBSMS] | CVIS
1/19/2024 12:42:13 PM | [NSO Update] Luzon Grid-01/19/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13632MW, PK=10088MW, RR=321MW, NetOpMargin: PM=3223, EVE=2467 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 330MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/19/2024 11:46:14 AM | Visayas Grid-01/19/2024 11:46: Maha A U3 tripped at 1142H, L=30MW. (Unplanned Outage) [WEBSMS] | CVIS
1/19/2024 11:44:38 AM | Visayas Grid-01/19/2024 11:44: Dumanjug-Colon 138 KV Line 1 restored at 1140H. (Unplanned Outage) [WEBSMS] | CVIS
1/19/2024 11:24:17 AM | Luzon Grid-01/19/2024 11:24: Laoag - Balaoi Wind 115kV Line (CO) restored at 1123H. (Unplanned Outage) [WEBSMS] | CLUZ
1/19/2024 11:08:05 AM | Visayas Grid-01/19/2024 11:08: Dumanjug-Colon 138 KV Line 1 tripped at 1043H. (Unplanned Outage) [WEBSMS] | CVIS
1/19/2024 10:52:27 AM | Mindanao Grid-01/19/2024 10:56: WMPC DG03 online at 1050H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/19/2024 10:13:40 AM | Luzon Grid-01/19/2024 10:13: San Lorenzo 60 online at 1009H. (Unplanned Outage) [WEBSMS] | CLUZ
1/19/2024 9:03:25 AM | Mindanao Grid-01/19/2024 09:07: TM2 U1 online at 0901H for DENR emission test. [WEBSMS] | CMIN
1/19/2024 9:00:34 AM | Mindanao Grid-01/19/2024 09:04: WMPC DG10 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/19/2024 8:09:42 AM | Luzon Grid-01/19/2024 08:09: Laoag - Balaoi Wind 115kV Line (CO) de-energized at 0806H. (Unplanned Outage) [WEBSMS] | CLUZ
1/19/2024 8:04:32 AM | Mindanao Grid-01/19/2024 08:08: Agus 5 - Aurora 138kV line shutdown at 0801H (Planned Outage). [WEBSMS] | CMIN
1/19/2024 6:22:29 AM | Luzon Grid-01/19/2024 06:22: Pagbilao EHV SS 1000MVA T03 de-energized at 0621H. (Planned Outage) [WEBSMS] | CLUZ
1/19/2024 6:14:32 AM | [NSO Update] Visayas Grid-01/19/2024 06:14: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2589MW, PK=2063MW, RR=86MW, NetOpMargin: AM=440, PM=231, EVE=194 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @81.2MW, LEYTE A @283MW [WEBSMS] | CVIS
1/19/2024 6:00:27 AM | [NSO Update] Luzon Grid-01/19/2024 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12962MW, PK=9794MW, RR=324MW, NetOpMargin: AM=2844, PM=2689, EVE=2334 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @330MW, ILIJAN B@ 295MW [WEBSMS] | CLUZ
1/19/2024 5:37:27 AM | [NSO Update] Mindanao Grid-01/19/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3219MW, PK=1957MW, RR=70MW, NetOpMargin: AM=1191, PM=1147, EVE=1154 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @46MW, MA2 @34MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @27MW, PG4 @180MW [WEBSMS] | CMIN
1/19/2024 5:28:29 AM | Mindanao Grid-01/19/2024 05:32: Zamboanga SS 138kV 50MVA Power Transformer T1 de-energized at 0508H. P&E request under MSUP Stage 1, Schedule 4. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
1/19/2024 4:25:56 AM | [NSO Update] Luzon Grid-01/19/2024 04:26: Weather Advisory: Shear line affecting the eastern section of Visayas and Mindanao. Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
1/19/2024 4:24:03 AM | [NSO Update] Visayas Grid-01/19/2024 04:24: Weather Advisory: Shear line affecting the eastern section of Visayas and Mindanao. Northeast Monsoon affecting Luzon. [WEBSMS] | CVIS
1/19/2024 4:23:59 AM | [NSO Update] Mindanao Grid-01/19/2024 04:27: Weather Advisory: Shear line affecting the eastern section of Visayas and Mindanao. Northeast Monsoon affecting Luzon. [WEBSMS] | CMIN
1/19/2024 2:07:35 AM | Mindanao Grid-01/19/2024 02:11: Bunawan-Toril 230kV L1 auto-tripped & auto-reclosed at 0118H. Unplanned Outage. [WEBSMS] | CMIN
1/18/2024 10:45:38 PM | Luzon Grid-01/18/2024 22:45: Angat-San Jose 115kV Line 4 restored at 2244H (Unplanned Outage) [WEBSMS] | CLUZ
1/18/2024 9:43:20 PM | Luzon Grid-01/18/2024 21:43: Angat-San Jose 115kV Line 4 tripped at 2139H (Unplanned Outage) [WEBSMS] | CLUZ
1/18/2024 9:18:25 PM | Mindanao Grid-01/18/2024 21:22: WMPC DG10 shutdown at 2113H. RPS-System Voltage Requirement [WEBSMS] | CMIN
1/18/2024 9:11:57 PM | Luzon Grid-01/18/2024 21:12: San Lorenzo 60 shutdown at 2110H (Unplanned Outage) [WEBSMS] | CLUZ
1/18/2024 7:17:50 PM | Luzon Grid-01/18/2024 19:17: San Gabriel online at 1915H (Unplanned Outage) [WEBSMS] | CLUZ
1/18/2024 5:43:58 PM | [NSO Update] Luzon Grid-01/18/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12612MW, PK=9629MW, RR=300MW, NetOpMargin: EVE=2683 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @330MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/18/2024 5:36:34 PM | [NSO Update] Visayas Grid-01/18/2024 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2409MW, PK=2053MW, RR=85MW, NetOpMargin: EVE=271 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @275MW [WEBSMS] | CVIS
1/18/2024 5:35:40 PM | [NSO Update] Mindanao Grid-01/18/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3225MW, PK=1967MW, RR=72MW, NetOpMargin: EVE=1186 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46.5MW, MA2 @35.5MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/18/2024 5:05:21 PM | Luzon Grid-01/18/2024 17:05: For info: San Lorenzo-Sta Rita 230kV Busses were unlopped at 1659H while Batangas 300MVA T04 and T05 were paralleled at 1702H. (Preparation for the synchronization of San Gabriel) [WEBSMS] | CLUZ
1/18/2024 4:10:52 PM | Mindanao Grid-01/18/2024 16:14: WMPC DG03 shutdown at 1608H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/18/2024 12:49:19 PM | [NSO Update] Mindanao Grid-01/18/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3258MW, PK=2019MW, RR=72MW, NetOpMargin: PM=1167, EVE=1198 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46.5MW, MA2 @35.5MW, AG1 @35MW, AG2 @98MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/18/2024 12:47:53 PM | [NSO Update] Visayas Grid-01/18/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2556MW, PK=2121MW, RR=86MW, NetOpMargin: PM=350, EVE=271 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @275MW [WEBSMS] | CVIS
1/18/2024 12:44:43 PM | [NSO Update] Luzon Grid-01/18/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13262MW, PK=9774MW, RR=318MW, NetOpMargin: PM=3170, EVE=2592 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/18/2024 11:19:58 AM | Mindanao Grid-01/18/2024 11:23: WMPC DG03 online at 1050H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/18/2024 9:24:49 AM | Luzon Grid-01/18/2024 09:24: Batangas 300MVA T04 /T05 split and Sta. Rita and San Lorenzo Bus 1 & 2 loop at 0919H and 0920 respectively (Unplanned Outage) [WEBSMS] | CLUZ
1/18/2024 9:02:26 AM | Mindanao Grid-01/18/2024 09:06: WMPC DG10 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/18/2024 8:47:33 AM | Mindanao Grid-01/18/2024 08:51: Tudaya 2 Unit 1 with 5.2MW gross generation tripped at 0825H. Indication: Nitrogen Pressure Low. Unplanned Outage. [WEBSMS] | CMIN
1/18/2024 7:01:25 AM | Luzon Grid-01/18/2024 07:01: San Gabriel shutdown at 0657H (Unplanned Outage) [WEBSMS] | CLUZ
1/18/2024 5:55:45 AM | [NSO Update] Luzon Grid-01/18/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13756MW, PK=9779MW, RR=324MW, NetOpMargin: AM=3653, PM=3310, EVE=2735 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/18/2024 5:51:01 AM | [NSO Update] Visayas Grid-01/18/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2492MW, PK=2004MW, RR=83MW, NetOpMargin: AM=405, PM=337, EVE=234 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @291MW [WEBSMS] | CVIS
1/18/2024 5:48:48 AM | [NSO Update] Mindanao Grid-01/18/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3306MW, PK=2001MW, RR=70MW, NetOpMargin: AM=1234, PM=1127, EVE=1128 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46.5MW, MA2 @35.5MW, AG1 @35MW, AG2 @118MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/18/2024 4:23:19 AM | [NSO Update] Mindanao Grid-01/18/2024 04:27: Weather Update: Shear line affecting the eastern section of Mindanao. Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
1/18/2024 4:23:07 AM | [NSO Update] Visayas Grid-01/18/2024 04:23: Weather Update: Shear line affecting the eastern section of Mindanao. Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
1/18/2024 4:22:51 AM | [NSO Update] Luzon Grid-01/18/2024 04:22: Weather Update: Shear line affecting the eastern section of Mindanao. Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
1/17/2024 9:17:27 PM | Mindanao Grid-01/17/2024 21:21: WMPC DG10 shutdown at 2114H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/17/2024 7:42:14 PM | Luzon Grid-01/17/2024 19:42: Malaya-Ingrid 230kV Line 2 (CO) restored at 1941H (Planned Outage) [WEBSMS] | CLUZ
1/17/2024 7:23:47 PM | [NSO Update] Visayas Grid-01/17/2024 19:23: SO-initiated Market Intervention for Visayas has been lifted today at 1907H. Market operations will resume starting interval 1915H. [WEBSMS] | CVIS
1/17/2024 7:02:45 PM | [NSO Update] Visayas Grid-01/17/2024 19:02: SO initiated Market Intervention for Visayas is issued today at 1848H starting interval 1850H due to overloading of Cebu-Negros submarine cable. [WEBSMS] | CVIS
1/17/2024 6:50:25 PM | Visayas Grid-01/17/2024 18:50: Implemented manual load dropping at Negros and Panay Sub-Grid at 1848H due to overloading of Amlan - Samboan 138 kV Line affected by the tripping of PEDC U3 at 1844H [WEBSMS] | CVIS
1/17/2024 6:11:54 PM | [NSO Update] Mindanao Grid-01/17/2024 18:15: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2982MW, PK=2056MW, RR=72.4MW, NetOpMargin: EVE=854 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35.5MW, AG1 @35MW, AG2 @118MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/17/2024 6:05:02 PM | [NSO Update] Visayas Grid-01/17/2024 18:05: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2527MW, PK=2008MW, RR=82MW, NetOpMargin: EVE=437 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @321MW [WEBSMS] | CVIS
1/17/2024 5:56:29 PM | [NSO Update] Luzon Grid-01/17/2024 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12928MW, PK=9440MW, RR=300MW, NetOpMargin: EVE=3188 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/17/2024 4:18:24 PM | Mindanao Grid-01/17/2024 16:22: WMPC DG07 shutdown at 1614H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/17/2024 12:47:43 PM | [NSO Update] Luzon Grid-01/17/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13891MW, PK=9991MW, RR=321MW, NetOpMargin: PM=3579, EVE=3091 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/17/2024 12:45:13 PM | [NSO Update] Mindanao Grid-01/17/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3312MW, PK=2120MW, RR=72MW, NetOpMargin: PM=1119, EVE=1117 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35.5MW, AG1 @35MW, AG2 @118MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/17/2024 12:44:04 PM | [NSO Update] Visayas Grid-01/17/2024 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2579MW, PK=2009MW, RR=90MW, NetOpMargin: PM=480, EVE=380 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @325MW [WEBSMS] | CVIS
1/17/2024 11:49:48 AM | Mindanao Grid-01/17/2024 11:53: WMPC DG03 declared unavailable at 1122H. Failed to start as RPS. Reason: Generator Reverse Power. (Unplanned Outage) [WEBSMS] | CMIN
1/17/2024 11:42:59 AM | Mindanao Grid-01/17/2024 11:46: WMPC DG07 online at 1131H as RPS replacement for WMPC DG03. [WEBSMS] | CMIN
1/17/2024 10:36:54 AM | Mindanao Grid-01/17/2024 10:40: TSI Unit 1 and 2 change setting at 1016H from APC ON/ Free Governor-OFF to APC OFF/ Free Governor-ON. AS-CR replacement for TMI 1 unit 1. [WEBSMS] | CMIN
1/17/2024 9:55:12 AM | Mindanao Grid-01/17/2024 09:59: TMI Unit 1 (AS-CR provider) declared unavailable at 0930H due to HVAC problem. (Unplanned Outage) [WEBSMS] | CMIN
1/17/2024 9:44:24 AM | [NSO Update] Mindanao Grid-01/17/2024 09:48: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0939H with power going to Visayas [WEBSMS] | CMIN
1/17/2024 9:43:55 AM | [NSO Update] Visayas Grid-01/17/2024 09:43: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0939H with power going to Visayas [WEBSMS] | CVIS
1/17/2024 9:16:04 AM | [NSO Update] Mindanao Grid-01/17/2024 09:19: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0907H from forward power direction [WEBSMS] | CMIN
1/17/2024 9:15:02 AM | [NSO Update] Visayas Grid-01/17/2024 09:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0907H from forward power direction [WEBSMS] | CVIS
1/17/2024 8:56:01 AM | Mindanao Grid-01/17/2024 08:59: WMPC DG10 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/17/2024 7:06:37 AM | Luzon Grid-01/17/2024 07:06: Pagbilao EHV SS 1000MVA T02 de-energized at 0701H (Planned Outage) [WEBSMS] | CLUZ
1/17/2024 5:51:27 AM | [NSO Update] Mindanao Grid-01/17/2024 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3323MW, PK=1996MW, RR=70MW, NetOpMargin: AM=1257, PM=970, EVE=1027 Highest Unit O/L: GNPK 2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35.5MW, AG1 @35MW, AG2 @118MW, AG4 @98MW, AG5 @31MW, AG6 @114MW, AG7 @28MW, PG4 @180MW [WEBSMS] | CMIN
1/17/2024 5:50:02 AM | [NSO Update] Visayas Grid-01/17/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2566MW, PK=2025MW, RR=86MW, NetOpMargin: AM=454, PM=280, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @325MW [WEBSMS] | CVIS
1/17/2024 5:44:17 AM | [NSO Update] Luzon Grid-01/17/2024 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14006MW, PK=9779MW, RR=324MW, NetOpMargin: AM=3903, PM=3343, EVE=2953 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/17/2024 4:45:15 AM | [NSO Update] Mindanao Grid-01/17/2024 04:49: Weather Update: Shear line affecting the eastern section of Mindanao. Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
1/17/2024 4:45:00 AM | [NSO Update] Visayas Grid-01/17/2024 04:45: Weather Update: Shear line affecting the eastern section of Mindanao. Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
1/17/2024 4:44:36 AM | [NSO Update] Luzon Grid-01/17/2024 04:44: Weather Update: Shear line affecting the eastern section of Mindanao. Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
1/17/2024 4:28:28 AM | Mindanao Grid-01/17/2024 04:32: Corrected: GNPK Unit 1 with 34MW tripped at 0342H during ramping down to zero for Reserved Shutdown (Unplanned Outage) [WEBSMS] | CMIN
1/17/2024 4:03:42 AM | Mindanao Grid-01/17/2024 04:08: GNPK Unit 4 with 34MW tripped at 0342H during ramping down to zero for Reserved Shutdown (Unplanned Outage) [WEBSMS] | CMIN
1/16/2024 10:10:16 PM | Luzon Grid-01/16/2024 22:10: Muntinlupa 300MVA T04 restored at 2210H (Unplanned Outage) [WEBSMS] | CLUZ
1/16/2024 9:14:48 PM | Mindanao Grid-01/16/2024 21:19: WMPC DG10 shutdown at 2113H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/16/2024 9:01:12 PM | Mindanao Grid-01/16/2024 21:05: Mt Apo Unit 3 online at 2058H from Forced outage. (Unplanned Outage) [WEBSMS] | CMIN
1/16/2024 6:11:46 PM | Luzon Grid-01/16/2024 18:12: Pagbilao EHV 1000MVA T01 restored at 1811H (Planned Outage) [WEBSMS] | CLUZ
1/16/2024 5:55:38 PM | [NSO Update] Mindanao Grid-01/16/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3092MW, PK=2012MW, RR=72.4MW, NetOpMargin: EVE=1008 Highest Unit O/L: GNPK 1, 2 & 4 Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35.5MW, AG1 @27MW, AG2 @114MW, AG4 @94MW, AG5 @29MW, AG6 @114MW, AG7 @26MW, PG4 @100MW [WEBSMS] | CMIN
1/16/2024 5:53:25 PM | [NSO Update] Visayas Grid-01/16/2024 17:53: Visayas Grid-01/16/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2481MW, PK=2031MW, RR=84MW, NetOpMargin: EVE=366 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 117.5MW, Leyte A @ 312MW, PGPP1 @ 38MW [WEBSMS] | CVIS
1/16/2024 5:52:15 PM | [NSO Update] Visayas Grid-01/16/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2481MW, PK=2031MW, RR=84MW, NetOpMargin: EVE=366 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 117.5MW, Leyte A @ 312MW, PGPP1 @ 75MW [WEBSMS] | CVIS
1/16/2024 5:50:55 PM | [NSO Update] Luzon Grid-01/16/2024 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12876MW, PK=9652MW, RR=300MW, NetOpMargin: EVE=2924 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 330MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/16/2024 5:07:47 PM | Mindanao Grid-01/16/2024 17:12: Nasipit SS 138KV Bus 2 re-energized at 1705H (Planned Outage) [WEBSMS] | CMIN
1/16/2024 5:02:27 PM | Luzon Grid-01/16/2024 17:02: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1700H (Planned Outage) [WEBSMS] | CLUZ
1/16/2024 4:32:04 PM | Luzon Grid-01/16/2024 16:32: Naga-Tiwi A 230kV Line restored at 1627H (Unplanned Outage) [WEBSMS] | CLUZ
1/16/2024 4:14:39 PM | Mindanao Grid-01/16/2024 16:18: WMPC DG04 shutdown at 1614H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/16/2024 4:01:40 PM | Mindanao Grid-01/16/2024 16:05: Alamada HEPP tripped at 1426H due to forced outage of COTELCO (Unplanned Outage). [WEBSMS] | CMIN
1/16/2024 2:48:24 PM | Luzon Grid-01/16/2024 14:48: Naga-Tiwi A 230kV Line de-energized at 1441H (Unplanned Outage) [WEBSMS] | CLUZ
1/16/2024 2:42:04 PM | Mindanao Grid-01/16/2024 14:46: Agus 2 Unit 1 online at 1440H. (Planned Outage) [WEBSMS] | CMIN
1/16/2024 12:34:23 PM | [NSO Update] Luzon Grid-01/16/2024 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13783MW, PK=10067MW, RR=321MW, NetOpMargin: PM=3396, EVE=2744 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/16/2024 12:25:58 PM | [NSO Update] Visayas Grid-01/16/2024 12:26: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2663MW, PK=2022MW, RR=87MW, NetOpMargin: PM=554, EVE=440 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @38MW [WEBSMS] | CVIS
1/16/2024 12:25:04 PM | [NSO Update] Mindanao Grid-01/16/2024 12:29: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3121MW, PK=1976MW, RR=72MW, NetOpMargin: PM=1072, EVE=1058 Highest Unit O/L: GNPK 1,2 &4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35.5MW, AG1 @27MW, AG2 @94MW, AG4 @94MW, AG5 @29MW, AG6 @114MW, AG7 @26MW, PG4 @100MW [WEBSMS] | CMIN
1/16/2024 12:02:22 PM | Mindanao Grid-01/16/2024 12:06: TMI 1 declared available for CR at at 1201H. [WEBSMS] | CMIN
1/16/2024 10:52:58 AM | Mindanao Grid-01/16/2024 10:57: WMPC DG04 online at 1050H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/16/2024 9:23:21 AM | Luzon Grid-01/16/2024 09:23: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0921H (Planned Outage) [WEBSMS] | CLUZ
1/16/2024 9:09:38 AM | Mindanao Grid-01/16/2024 09:13: AGUS 6 Unit 2 shutdown at 0902H. (Planned Outage - Non-GOMP) [WEBSMS] | CMIN
1/16/2024 9:07:09 AM | Mindanao Grid-01/16/2024 09:11: AGUS 6 Unit 1 shutdown at 0901H. (Planned Outage - GOMP) [WEBSMS] | CMIN
1/16/2024 9:02:13 AM | Mindanao Grid-01/16/2024 09:06: WMPC DG10 online at 0901H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/16/2024 8:33:07 AM | Visayas Grid-01/16/2024 08:33: Mandaue SS 138KV Bus 2 de-energized at 0809H. (Planned Outage) [WEBSMS] | CVIS
1/16/2024 7:00:18 AM | Luzon Grid-01/16/2024 07:00: Pagbilao EHV SS 1000MVA T01 de-energized at 0659H (Planned Outage) [WEBSMS] | CLUZ
1/16/2024 6:37:16 AM | Luzon Grid-01/16/2024 06:37: Muntinlupa 300MVA T04 de-energized at 0637H (Unplanned Outage) [WEBSMS] | CLUZ
1/16/2024 5:50:00 AM | Mindanao Grid-01/16/2024 05:54: Libertad Power online at 0545H (Unplanned Outage). [WEBSMS] | CMIN
1/16/2024 5:45:37 AM | [NSO Update] Mindanao Grid-01/16/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3122MW, PK=2019MW, RR=70MW, NetOpMargin: AM=1032, PM=688, EVE=785 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35.5MW, AG1 @27MW, AG2 @94MW, AG4 @94MW, AG5 @29MW, AG6 @114MW, AG7 @26MW, PG4 @100MW [WEBSMS] | CMIN
1/16/2024 5:43:06 AM | [NSO Update] Visayas Grid-01/16/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2552MW, PK=2031MW, RR=82MW, NetOpMargin: AM=439, PM=318, EVE=233 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @38MW [WEBSMS] | CVIS
1/16/2024 5:40:58 AM | [NSO Update] Luzon Grid-01/16/2024 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13609MW, PK=9915MW, RR=324MW, NetOpMargin: AM=3371, PM=2974, EVE=2540 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/16/2024 4:49:57 AM | Mindanao Grid-01/16/2024 04:54: LIBERTAD POWER tripped with 6MW load at 0409H. Indication: For further investigation. (Unplanned Outage) [WEBSMS] | CMIN
1/16/2024 4:36:42 AM | [NSO Update] Mindanao Grid-01/16/2024 04:40: Weather Update: Shear line affecting the northern and eastern sections of Mindanao. Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
1/16/2024 4:36:23 AM | [NSO Update] Visayas Grid-01/16/2024 04:36: Weather Update: Shear line affecting the northern and eastern sections of Mindanao. Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
1/16/2024 4:35:58 AM | [NSO Update] Luzon Grid-01/16/2024 04:36: Weather Update: Shear line affecting the northern and eastern sections of Mindanao. Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
1/16/2024 3:07:15 AM | Luzon Grid-01/16/2024 03:07: Sta. Rita Module 30 online at 0303H (Unplanned Outage) [WEBSMS] | CLUZ
1/16/2024 12:04:54 AM | Mindanao Grid-01/16/2024 00:09: TSI Unit 1 and 2 change setting at 0001H from APC ON/ Free Governor-OFF to APC OFF/ Free Governor-ON. AS-CR replacement for TMI 1 unit 1. [WEBSMS] | CMIN
1/16/2024 12:02:18 AM | Mindanao Grid-01/16/2024 00:06: TMI 1 declared un-available for CR at at 0001H. AS/CR served by TSI Unit 1 and 2. [WEBSMS] | CMIN
1/15/2024 11:26:40 PM | Mindanao Grid-01/15/2024 23:30: LIBERTAD POWER tripped with 6MW load at 2320H. Indication: For further investigation. (Unplanned Outage) [WEBSMS] | CMIN
1/15/2024 10:32:31 PM | Mindanao Grid-01/15/2024 22:36: WMPC DG10 shutdown at 2113H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/15/2024 10:03:33 PM | Mindanao Grid-01/15/2024 22:07: Agus 2-Kibawe 138kV L2 auto-tripped at 2101H. Unplanned Outage. (The line is energized up to str# 33 only, to prevent pilferage). [WEBSMS] | CMIN
1/15/2024 9:39:43 PM | Visayas Grid-01/15/2024 21:40: Bacolod-Gahit 230 KV L2 energized in Bacolod SS side at 2132H. (Planned Outage) [WEBSMS] | CVIS
1/15/2024 7:59:14 PM | Mindanao Grid-01/15/2024 20:03: Culaman SS Power Transformer No.1, 50MVA (Brand New), successfully energized (without load) at 1826H. As per approved ERFP-24-01-05. (P & E requested energization). [WEBSMS] | CMIN
1/15/2024 7:35:35 PM | Mindanao Grid-01/15/2024 19:39: Davao -Bunawan 138 kV L1 auto-tripped and auto-reclosed at 1916H. (Unplanned outage) [WEBSMS] | CMIN
1/15/2024 5:57:11 PM | [NSO Update] Mindanao Grid-01/15/2024 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3111MW, PK=2082MW, RR=72MW, NetOpMargin: EVE=956 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35MW, AG1 @35MW, AG2 @74MW, AG4 @94MW, AG5 @30MW, AG6 @131MW, AG7 @27MW, PG4 @120MW [WEBSMS] | CMIN
1/15/2024 5:48:10 PM | [NSO Update] Visayas Grid-01/15/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2566MW, PK=2076MW, RR=90MW, NetOpMargin: EVE=400 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @324MW, PGPP1 @38MW [WEBSMS] | CVIS
1/15/2024 5:44:49 PM | [NSO Update] Luzon Grid-01/15/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12840MW, PK=9878MW, RR=390MW, NetOpMargin: EVE=2572 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/15/2024 4:16:53 PM | Mindanao Grid-01/15/2024 16:21: WMPC DG04 shutdown at 1615H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/15/2024 2:23:27 PM | Visayas Grid-01/15/2024 14:23: Cebu-Mandaue 138 KV L2/Mandaue SS 100 MVA TR2 started loading at 1333H/1414H after 24 hrs soaking. (Planned Outage) [WEBSMS] | CVIS
1/15/2024 2:19:22 PM | Visayas Grid-01/15/2024 14:19: PEDC U3 re cut in at 1417H. (Unplanned Outage) [WEBSMS] | CVIS
1/15/2024 12:55:46 PM | [NSO Update] Mindanao Grid-01/15/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3160MW, PK=2227MW, RR=72MW, NetOpMargin: PM=860, EVE=905 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35MW, AG1 @35MW, AG2 @74MW, AG4 @94MW, AG5 @30MW, AG6 @139MW, AG7 @27MW, PG4 @120MW [WEBSMS] | CMIN
1/15/2024 12:54:51 PM | [NSO Update] Visayas Grid-01/15/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2605MW, PK=2113MW, RR=89MW, NetOpMargin: PM=404, EVE=289 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 324MW, PGPP1 @ 38MW [WEBSMS] | CVIS
1/15/2024 12:53:33 PM | [NSO Update] Luzon Grid-01/15/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13734MW, PK=10207MW, RR=411MW, NetOpMargin: PM=3116, EVE=2572 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
1/15/2024 12:04:43 PM | Mindanao Grid-01/15/2024 12:08: TSI Unit 1 and 2 change setting at 1201H from APC OFF/ Free Governor-ON to APC ON/ Free Governor-OFF. AS-CR back to TMI 1 unit 1. [WEBSMS] | CMIN
1/15/2024 12:02:25 PM | Mindanao Grid-01/15/2024 12:06: TMI 1 declared available for CR at at 1201H. [WEBSMS] | CMIN
1/15/2024 12:00:39 PM | Mindanao Grid-01/15/2024 12:04: WMPC DG10 online at 1056H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/15/2024 11:01:35 AM | Visayas Grid-01/15/2024 11:02: PEDC U3 tripped at 1057H, load involved 112MW. system normal. (Unplanned Outage) [WEBSMS] | CVIS
1/15/2024 10:32:10 AM | Mindanao Grid-01/15/2024 10:36: Supreme Power Mati online at 1015H (Unplanned Outage). [WEBSMS] | CMIN
1/15/2024 10:28:25 AM | Mindanao Grid-01/15/2024 10:32: SPC Mati with 2.8MW load tripped at 1011H. Indication: for further investigation. (Unplanned Outage). [WEBSMS] | CMIN
1/15/2024 10:25:30 AM | Mindanao Grid-01/15/2024 10:29: Supreme Power Mati online at 1009H (Unplanned Outage). [WEBSMS] | CMIN
1/15/2024 10:16:12 AM | Mindanao Grid-01/15/2024 10:20: SPC Mati with 3MW load tripped at 1006H. Indication: Over Voltage Trip.(Unplanned Outage). [WEBSMS] | CMIN
1/15/2024 8:57:07 AM | Mindanao Grid-01/15/2024 09:01: WMPC DG10 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/15/2024 5:39:11 AM | [NSO Update] Luzon Grid-01/15/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13667MW, PK=9884MW, RR=408MW, NetOpMargin: AM=3375, PM=2731, EVE=2315 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/15/2024 5:36:46 AM | [NSO Update] Visayas Grid-01/15/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2597MW, PK=2068MW, RR=88MW, NetOpMargin: AM=441, PM=387, EVE=257 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @324MW, PGPP1 @38MW [WEBSMS] | CVIS
1/15/2024 5:36:29 AM | [NSO Update] Mindanao Grid-01/15/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3166MW, PK=2159MW, RR=70MW, NetOpMargin: AM=937, PM=741, EVE=783 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35MW, AG1 @35MW, AG2 @74MW, AG4 @94MW, AG5 @30MW, AG6 @139MW, AG7 @27MW, PG4 @120MW [WEBSMS] | CMIN
1/15/2024 4:14:01 AM | [NSO Update] Luzon Grid-01/15/2024 04:14: Weather Advisory: Shear line affecting the eastern sections of Visayas and Mindanao. Northeast Monsoon affecting Luzon and the rest of Visayas. [WEBSMS] | CLUZ
1/15/2024 4:13:46 AM | [NSO Update] Visayas Grid-01/15/2024 04:14: Weather Advisory: Shear line affecting the eastern sections of Visayas and Mindanao. Northeast Monsoon affecting Luzon and the rest of Visayas. [WEBSMS] | CVIS
1/15/2024 4:13:13 AM | [NSO Update] Mindanao Grid-01/15/2024 04:17: Weather Advisory: Shear line affecting the eastern sections of Visayas and Mindanao. Northeast Monsoon affecting Luzon and the rest of Visayas. [WEBSMS] | CMIN
1/15/2024 12:55:05 AM | Mindanao Grid-01/15/2024 00:59: Marbel Euro Hydro with 0.3MW shutdown at 2113H affected by the NIA intake gate shutdown. (Unplanned Outage) [WEBSMS] | CMIN
1/14/2024 11:35:43 PM | Visayas Grid-01/14/2024 23:36: Sibonga Load End SS 13.8KV energized back @2330H. (Unplanned Outage) [WEBSMS] | CVIS
1/14/2024 11:15:39 PM | Visayas Grid-01/14/2024 23:16: Sibonga Load End SS 13.8KV emergency open @2310H. (Unplanned Outage) [WEBSMS] | CVIS
1/14/2024 11:00:48 PM | Mindanao Grid-01/14/2024 23:05: Update: Agus 1 Unit 1 with 21MW load tripped at 2033H. Lowest Frequency at 59.7068Hz. Cause: Initial info: Thrust Bearing high temp. (Unplanned Outage). [WEBSMS] | CMIN
1/14/2024 9:54:42 PM | Luzon Grid-01/14/2024 21:55: Sta. Rita 40 online at 2132H (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 9:14:32 PM | Luzon Grid-01/14/2024 21:14: Batangas Transformer no. 4 and no. 5 on parallel configuration at 2108H (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 9:12:39 PM | Luzon Grid-01/14/2024 21:13: Sta. Rita and San Lorenzo Bus 1 and Bus 2 unloop at 2104H (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 9:12:06 PM | Visayas Grid-01/14/2024 21:12: Mandaue SS 100 MVA TR2 energized at 2110H w/o load for 24 hrs soaking. (Planned Outage) [WEBSMS] | CVIS
1/14/2024 9:07:17 PM | Visayas Grid-01/14/2024 21:07: Cebu-Mandaue 138 KV L2 energized at 2102H w/o load, for 24 hrs soaking. (Planned Outage) [WEBSMS] | CVIS
1/14/2024 8:49:12 PM | Mindanao Grid-01/14/2024 20:53: Agus 1 Unit 1 with 21MW load tripped at 2033H. Lowest Frequency at 59.7068Hz. Details to follow (Unplanned Outage). [WEBSMS] | CMIN
1/14/2024 7:46:04 PM | Mindanao Grid-01/14/2024 19:50: WMPC DG10 shutdown at 1944H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/14/2024 7:12:16 PM | Luzon Grid-01/14/2024 19:12: Pagbilao PP SS 230kV Bus 2 restored at 1910H (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 6:52:57 PM | Mindanao Grid-01/14/2024 18:57: Baloi SS 50MVA Transformer 1 re-energized at 1831H (Planned Outage) [WEBSMS] | CMIN
1/14/2024 6:48:03 PM | Luzon Grid-01/14/2024 18:48: Sta. Rita-San Lorenzo 230kV Bus 1 loop at 1846H (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 6:45:23 PM | Luzon Grid-01/14/2024 18:45: Sta. Rita SS 230kV Busbar 1 restored at 1845H (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 6:22:31 PM | Luzon Grid-01/14/2024 18:22: San Jose 300MVA T03 restored at 1821H (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 6:13:20 PM | Luzon Grid-01/14/2024 18:13: Calaca-Binan 230kV line restored at 1813H (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 6:01:59 PM | Luzon Grid-01/14/2024 18:02: Mexico-Hermosa 230kV line 2 restored at 1801H (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 6:01:00 PM | Mindanao Grid-01/14/2024 18:05: Davao SS 138KV/150MVA Transformer # 3 reenergized at 1755H. Planned Outage. [WEBSMS] | CMIN
1/14/2024 6:00:38 PM | Luzon Grid-01/14/2024 18:01: Binan-Calamba 230kV line 1 restored at 1759H (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 5:57:45 PM | Mindanao Grid-01/14/2024 18:01: Nagamin SVC re-energized at 1749H (Planned Outage) [WEBSMS] | CMIN
1/14/2024 5:56:49 PM | Mindanao Grid-01/14/2024 18:01: Nagamin SS 138KV Bus 2 re-energized at 1746H (Planned Outage) [WEBSMS] | CMIN
1/14/2024 5:38:45 PM | [NSO Update] Mindanao Grid-01/14/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3130MW, PK=1950MW, RR=72MW, NetOpMargin: EVE=1108 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35MW, AG1 @54MW, AG2 @94MW, AG4 @94MW, AG5 @30MW, AG6 @137MW, AG7 @27MW, PG4 @120MW [WEBSMS] | CMIN
1/14/2024 5:38:33 PM | [NSO Update] Visayas Grid-01/14/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2310MW, PK=1752MW, RR=85MW, NetOpMargin: EVE=473 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @320MW, PGPP1 @38MW [WEBSMS] | CVIS
1/14/2024 5:38:15 PM | [NSO Update] Luzon Grid-01/14/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12578MW, PK=8708MW, RR=300MW, NetOpMargin: EVE=3569 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @175MW, MASINLOC1 @215MW, ILIJAN B @295MW, [WEBSMS] | CLUZ
1/14/2024 4:59:10 PM | Visayas Grid-01/14/2024 16:59: Col-Nay 69kV Line energized at 1659H. (Planned Outage) [WEBSMS] | CVIS
1/14/2024 4:56:08 PM | Visayas Grid-01/14/2024 16:56: Colon SS 100MVA TR 2 energized at 1654H. (Planned Outage) [WEBSMS] | CVIS
1/14/2024 1:37:19 PM | [NSO Update] Mindanao Grid-01/14/2024 13:41: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1336H with power going to Visayas. [WEBSMS] | CMIN
1/14/2024 1:36:57 PM | [NSO Update] Visayas Grid-01/14/2024 13:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1336H with power going to Visayas. [WEBSMS] | CVIS
1/14/2024 1:26:49 PM | Visayas Grid-01/14/2024 13:27: Dumanjug SS 230kV HVDC Converter Pole 2 energized at 1325H. (Unplanned Outage) [WEBSMS] | CVIS
1/14/2024 1:07:51 PM | Mindanao Grid-01/14/2024 13:12: SPC Mati with 3MW load tripped at 1231H due to reverse power indication.(Unplanned Outage). [WEBSMS] | CMIN
1/14/2024 12:55:52 PM | [NSO Update] Luzon Grid-01/14/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13369MW, PK=8147MW, RR=321MW, NetOpMargin: PM=4902, EVE=3717 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/14/2024 12:54:17 PM | [NSO Update] Visayas Grid-01/14/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2335MW, PK=1574MW, RR=78MW, NetOpMargin: PM=683, EVE=394 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 320MW, PGPP1 @ 38MW [WEBSMS] | CVIS
1/14/2024 12:50:17 PM | [NSO Update] Mindanao Grid-01/14/2024 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3231MW, PK=1891MW, RR=72MW, NetOpMargin: PM=1268, EVE=1021 Highest Unit O/L: GNPK 1, 2 & 4 Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35MW, AG1 @54MW, AG2 @94MW, AG4 @94MW, AG5 @30MW, AG6 @137MW, AG7 @27MW, PG4 @120MW [WEBSMS] | CMIN
1/14/2024 12:37:57 PM | [NSO Update] Mindanao Grid-01/14/2024 12:42: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was auto-blocked at 1231H with power going to Visayas. [WEBSMS] | CMIN
1/14/2024 12:37:23 PM | [NSO Update] Visayas Grid-01/14/2024 12:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was auto-blocked at 1231H with power going to Visayas. [WEBSMS] | CVIS
1/14/2024 12:15:53 PM | Mindanao Grid-01/14/2024 12:20: TSI Unit 1 and 2 change setting at 1201H from APC OFF/ Free Governor-ON to APC ON/ Free Governor-OFF. AS-CR back to TMI 1 unit 1. [WEBSMS] | CMIN
1/14/2024 12:05:36 PM | Visayas Grid-01/14/2024 12:06: Colon -Magdugo 138KV Line 1 energized at 1203H. (Planned Outage) [WEBSMS] | CVIS
1/14/2024 10:13:46 AM | Mindanao Grid-01/14/2024 10:17: Villanueva SS 138KV Bus 1 re-energized at 0712H (Planned Outage) [WEBSMS] | CMIN
1/14/2024 10:10:47 AM | Mindanao Grid-01/14/2024 10:15: Zamboanga SS 138KV Bus 2 re-energized at 0841H (Planned Outage) [WEBSMS] | CMIN
1/14/2024 8:49:02 AM | Mindanao Grid-01/14/2024 08:53: Nagamin SS 138KV Bus 2 deenergized at 0812H (Planned Outage) [WEBSMS] | CMIN
1/14/2024 8:47:38 AM | Mindanao Grid-01/14/2024 08:51: Nagamin SVC shutdown at 0811H (Planned Outage) [WEBSMS] | CMIN
1/14/2024 8:00:45 AM | Mindanao Grid-01/14/2024 08:04: Baloi SS 138KV/50mva Transformer #1 shutdown at 0740H (Planned Outage) [WEBSMS] | CMIN
1/14/2024 7:58:59 AM | Mindanao Grid-01/14/2024 08:03: Baloi - Agus 6 69KV Tie line deenergized at 0725H (Planned Outage) [WEBSMS] | CMIN
1/14/2024 7:56:54 AM | Mindanao Grid-01/14/2024 08:01: 5CB04(7XF03BLO) opened at at 0723H (Planned Outage) [WEBSMS] | CMIN
1/14/2024 7:48:48 AM | Mindanao Grid-01/14/2024 07:53: WMPC DG10 online at 0715H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/14/2024 7:45:39 AM | Mindanao Grid-01/14/2024 07:49: Baloi SS 138KV 50MVA transformer #1 shutdown at 0740H (Planned Outage) [WEBSMS] | CMIN
1/14/2024 7:39:44 AM | Visayas Grid-01/14/2024 07:40: Dumanjug SS 230kV HVDC Converter Pole 2 de-energized at 0735H. (Unplanned Outage) [WEBSMS] | CVIS
1/14/2024 7:28:22 AM | Mindanao Grid-01/14/2024 07:32: Villanueva SS 138KV Bus 1 re-energized at 0712H (Planned Outage) [WEBSMS] | CMIN
1/14/2024 7:04:07 AM | Luzon Grid-01/14/2024 07:04: Mexico-Hermosa 230kV line 2 was de-energized at 0703H. (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 6:48:00 AM | Luzon Grid-01/14/2024 06:48: San Jose 300MVA T03 was de-energized at 0647H. (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 6:40:23 AM | Mindanao Grid-01/14/2024 06:44: Tudaya 2 unit 1 with 1.97MW load shutdown at 0333H due to damaged Power Supply Cable for Forebay sump pump. Online at 0539H. (Unplanned Outage) [WEBSMS] | CMIN
1/14/2024 6:27:55 AM | Visayas Grid-01/14/2024 06:28: Colon SS 100MVA TR 2 de-energized at 0623H. (Planned Outage) [WEBSMS] | CVIS
1/14/2024 6:23:37 AM | Luzon Grid-01/14/2024 06:24: Calaca-Binan 230kV line was de-energized at 0623H. (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 6:20:42 AM | Luzon Grid-01/14/2024 06:21: Binan-Calamba 230kV line 1 was de-energized at 0619H. (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 6:19:31 AM | Mindanao Grid-01/14/2024 06:23: Davao SS 150MVA Transformer # 3 de-energized at 0610H (Planned Outage) [WEBSMS] | CMIN
1/14/2024 6:18:56 AM | Visayas Grid-01/14/2024 06:19: Col-Nay 69kV Line de-energized at 0617H. (Planned Outage) [WEBSMS] | CVIS
1/14/2024 5:39:48 AM | [NSO Update] Luzon Grid-01/14/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13584MW, PK=8106MW, RR=324MW, NetOpMargin: AM=5154, PM=4623, EVE=2999 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @150MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/14/2024 5:37:25 AM | [NSO Update] Visayas Grid-01/14/2024 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2457MW, PK=1606MW, RR=77MW, NetOpMargin: AM=774, PM=642, EVE=370 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @324MW, PGPP1 @38MW [WEBSMS] | CVIS
1/14/2024 5:36:21 AM | Mindanao Grid-01/14/2024 05:40: Zamboanga SS 138kV Bus 2 de-energized 0534H (Planned Outage). [WEBSMS] | CMIN
1/14/2024 5:35:04 AM | Visayas Grid-01/14/2024 05:35: Colon-Veco-Aya 69KV feeder de-energized at 0531H. (Planned Outage) [WEBSMS] | CVIS
1/14/2024 5:31:41 AM | [NSO Update] Mindanao Grid-01/14/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3197MW, PK=1739MW, RR=70MW, NetOpMargin: AM=1388, PM=1192, EVE=939 Highest Unit O/L: GNPK 1,2&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35MW, AG1 @54MW, AG2 @94MW, AG4 @94MW, AG5 @30MW, AG6 @137MW, AG7 @27MW, PG4 @120MW [WEBSMS] | CMIN
1/14/2024 5:17:55 AM | Visayas Grid-01/14/2024 05:18: Colon -Madugo 138KV Line 1 de-energized at 0510H. (Planned Outage) [WEBSMS] | CVIS
1/14/2024 4:09:48 AM | [NSO Update] Luzon Grid-01/14/2024 04:10: Weather Update: Shear line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon and the rest of Visayas. [WEBSMS] | CLUZ
1/14/2024 4:09:32 AM | Luzon Grid-01/14/2024 04:09: SCPC U2 shutdown at 0405H (Planned Outage) [WEBSMS] | CLUZ
1/14/2024 4:09:32 AM | Mindanao Grid-01/14/2024 04:13: Villanueva SS 138kV Bus 1 de-energized 0405H. Planned outage. [WEBSMS] | CMIN
1/14/2024 4:04:16 AM | [NSO Update] Mindanao Grid-01/14/2024 04:08: Weather Update: Shear line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon and the rest of Visayas. [WEBSMS] | CMIN
1/14/2024 4:04:08 AM | [NSO Update] Visayas Grid-01/14/2024 04:04: Weather Update: Shear line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon and the rest of Visayas. [WEBSMS] | CVIS
1/13/2024 8:51:42 PM | Luzon Grid-01/13/2024 20:52: Masinloc 1 online at 2051H. (Unplanned Outage) [WEBSMS] | CLUZ
1/13/2024 8:15:27 PM | Mindanao Grid-01/13/2024 20:19: TMI 1 declared un-available for CR at at 2001H. AS/CR served by TSI Unit 1 and 2. [WEBSMS] | CMIN
1/13/2024 8:11:38 PM | Mindanao Grid-01/13/2024 20:15: TSI Unit 1 and 2 change setting at 2001H from APC ON/ Free Governor-OFF to APC OFF/ Free Governor-ON. AS-CR replacement for TMI 1 unit 1. [WEBSMS] | CMIN
1/13/2024 7:50:35 PM | Luzon Grid-01/13/2024 19:50: Masinloc 1 tripped with 50MW at 1949H. Lowest system is 59.9Hz. (Unplanned Outage) [WEBSMS] | CLUZ
1/13/2024 7:36:08 PM | Luzon Grid-01/13/2024 19:36: Masinloc 1 online at 1934H. (Unplanned Outage) [WEBSMS] | CLUZ
1/13/2024 6:48:06 PM | Luzon Grid-01/13/2024 18:48: Hermosa-Mexico 230kV line 1 restored at 1847H. (Planned Outage) [WEBSMS] | CLUZ
1/13/2024 5:50:18 PM | Visayas Grid-01/13/2024 17:50: Cebu-Compostela 138kV Line 1 energized at 1746H (Planned Outage) [WEBSMS] | CVIS
1/13/2024 5:31:52 PM | [NSO Update] Mindanao Grid-01/13/2024 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3157MW, PK=2208MW, RR=72MW, NetOpMargin: EVE=876 Highest Unit O/L: GNPK 1, 2 & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35MW, AG1 @54MW, AG2 @94MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @120MW [WEBSMS] | CMIN
1/13/2024 5:29:55 PM | [NSO Update] Luzon Grid-01/13/2024 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12488MW, PK=9232MW, RR=390MW, NetOpMargin: EVE=2867 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @135MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/13/2024 5:29:25 PM | [NSO Update] Visayas Grid-01/13/2024 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2262MW, PK=1918MW, RR=85MW, NetOpMargin: EVE=260 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @324MW, PGPP1 @38MW [WEBSMS] | CVIS
1/13/2024 4:35:51 PM | Mindanao Grid-01/13/2024 16:40: Zamboanga SS 50MVA Power Transformer 2 energized 1634H. Planned outage [WEBSMS] | CMIN
1/13/2024 4:01:44 PM | Luzon Grid-01/13/2024 16:02: Pagbilao PP SS 230kV Bus 2 de-energized at 1555H. (Planned Outage) [WEBSMS] | CLUZ
1/13/2024 3:49:31 PM | Luzon Grid-01/13/2024 15:49: Pagbilao EHV-Pagbilao Plant 230kV Line 2 restored at 1549H. (Planned Outage) [WEBSMS] | CLUZ
1/13/2024 3:15:48 PM | Mindanao Grid-01/13/2024 15:20: WMPC DG10 shutdown at 1513H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/13/2024 2:29:53 PM | Mindanao Grid-01/13/2024 14:34: AGUS 6 Unit 3 online at 1417H. PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
1/13/2024 2:16:04 PM | Mindanao Grid-01/13/2024 14:20: WMPC DG04 shutdown at 1414H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/13/2024 1:59:43 PM | Mindanao Grid-01/13/2024 14:03: NagaMin-Zamboanga 138kV T/L 2 energized at 1322H (Planned Outage) [WEBSMS] | CMIN
1/13/2024 1:48:46 PM | Mindanao Grid-01/13/2024 13:52: Zamboanga SS 50MVA Power Transformer 2 de-energized 1344H. Planned outage. [WEBSMS] | CMIN
1/13/2024 1:34:55 PM | Mindanao Grid-01/13/2024 13:39: NagaMin SS 7XF03NAA (SVC) energized at 1322H. Planned outage. [WEBSMS] | CMIN
1/13/2024 1:32:33 PM | Mindanao Grid-01/13/2024 13:36: Matanao-Kidapawan 138kV line 2 autotripped and autoreclosed 1312H. [WEBSMS] | CMIN
1/13/2024 1:18:00 PM | [NSO Update] Visayas Grid-01/13/2024 13:18: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2341MW, PK=1856MW, RR=81MW, NetOpMargin: PM=404, EVE=269 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @324MW, PGPP1 @38MW [WEBSMS] | CVIS
1/13/2024 1:11:11 PM | Mindanao Grid-01/13/2024 13:15: Supreme Power Mati online at 1308H (Unplanned Outage). [WEBSMS] | CMIN
1/13/2024 1:08:40 PM | Mindanao Grid-01/13/2024 13:12: SUPREME POWER Mati tripped with 3MW load at 1239H. Cause: affected by the line tripping of Pintatagan-Mati 69kv STL. (Unplanned Outage) [WEBSMS] | CMIN
1/13/2024 1:03:41 PM | [NSO Update] Mindanao Grid-01/13/2024 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3212MW, PK=2112MW, RR=72MW, NetOpMargin: PM=1027, EVE=891 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35MW, AG1 @54MW, AG2 @94MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @120MW [WEBSMS] | CMIN
1/13/2024 12:51:27 PM | [NSO Update] Luzon Grid-01/13/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13442MW, PK=9446MW, RR=399MW, NetOpMargin: PM=3597, EVE=2803 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @140MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/13/2024 12:41:53 PM | Mindanao Grid-01/13/2024 12:46: Supreme Power Mati online at 1236H. (Unplanned Outage) [WEBSMS] | CMIN
1/13/2024 12:39:36 PM | Mindanao Grid-01/13/2024 12:43: SUPREME POWER Mati tripped with 3MW load at 1228H. Cause: For further investigation. (Unplanned Outage) [WEBSMS] | CMIN
1/13/2024 12:18:39 PM | Mindanao Grid-01/13/2024 12:22: TSI Unit 1 and 2 change setting at 1201H from APC OFF/ Free Governor-ON to APC ON/ Free Governor-OFF. AS-CR back to TMI 1. [WEBSMS] | CMIN
1/13/2024 12:04:40 PM | Mindanao Grid-01/13/2024 12:08: TMI 1 declared available for CR at at 1201H. [WEBSMS] | CMIN
1/13/2024 9:47:56 AM | Mindanao Grid-01/13/2024 09:52: AGUS 6 Unit 2 online at 0944H. (Unplanned Outage) [WEBSMS] | CMIN
1/13/2024 9:13:42 AM | Mindanao Grid-01/13/2024 09:17: AGUS 6 Unit 3 shutdown with 38.08MW load at 0906H. PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
1/13/2024 9:06:32 AM | Mindanao Grid-01/13/2024 09:10: AGUS 6 unit 2 tripped with 16.4MW load at 0854H. Cause: for further investigation (Unplanned Outage). [WEBSMS] | CMIN
1/13/2024 7:45:59 AM | Luzon Grid-01/13/2024 07:46: Masinloc Unit 1 shutdown at 0736H. (Unplanned Outage) [WEBSMS] | CLUZ
1/13/2024 7:35:03 AM | Mindanao Grid-01/13/2024 07:39: Villanueva SS 138 kV Bus 2 energized at 0731H. Planned outage [WEBSMS] | CMIN
1/13/2024 7:34:39 AM | Luzon Grid-01/13/2024 07:35: For info: Batangas 300MVA T04 and T05 was unparalleled on the 69kV side at 0728H. San Lorenzo-Sta Rita 230kV Bus 2 was looped at 0729H. [WEBSMS] | CLUZ
1/13/2024 7:05:34 AM | Luzon Grid-01/13/2024 07:05: Hermosa-Mexico 230kV line 1 was de-energized at 0705H. (Planned Outage) [WEBSMS] | CLUZ
1/13/2024 6:36:18 AM | Visayas Grid-01/13/2024 06:36: Cebu-Compostela 138kV Line 1 de-energized at 0633H (Planned Outage) [WEBSMS] | CVIS
1/13/2024 6:34:05 AM | Mindanao Grid-01/13/2024 06:38: STEAG Unit 2 online at 0631H. (Unplanned Outage) [WEBSMS] | CMIN
1/13/2024 6:04:40 AM | Luzon Grid-01/13/2024 06:05: Pagbilao EHV-Pagbilao Plant 230kV Line 2 de-energized at 0604H (Planned Outage) [WEBSMS] | CLUZ
1/13/2024 6:03:16 AM | [NSO Update] Luzon Grid-01/13/2024 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13943MW, PK=9519MW, RR=374MW, NetOpMargin: AM=4050, PM=3711, EVE=2910 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, SLPGC 1 @135MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/13/2024 5:44:29 AM | [NSO Update] Mindanao Grid-01/13/2024 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3211MW, PK=2023MW, RR=70MW, NetOpMargin: AM=1117, PM=825, EVE=722 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35MW, AG1 @54MW, AG2 @94MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @120MW [WEBSMS] | CMIN
1/13/2024 5:42:54 AM | [NSO Update] Visayas Grid-01/13/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2399MW, PK=1857MW, RR=80MW, NetOpMargin: AM=462, PM=319, EVE=251 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @324MW, PGPP1 @38MW [WEBSMS] | CVIS
1/13/2024 5:10:27 AM | Visayas Grid-01/13/2024 05:10: PEDC U3 cut-out at 0504H, due to furnace temp. too low, load 11MW. (Unplanned Outage) [WEBSMS] | CVIS
1/13/2024 4:38:35 AM | Mindanao Grid-01/13/2024 04:42: Villanueva SS 138 kV Bus 2 (7BS02VLN) de-energized at 0423H (P.O/ Non-GOMP. To conduct PMS / hotspot correction of all HVES at bus 2 side at bays 3, 4, 5 & 6. namely; 7Z-06DS07VLN,7Z-05DS07VLN, 7Z-04DS07VLN, 7Z-03DS07VLN, 7Z-05CT09VLN7Z-04CT09VLN. [WEBSMS] | CMIN
1/13/2024 4:16:14 AM | [NSO Update] Mindanao Grid-01/13/2024 04:20: Weather Advisory: Shear line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon and the rest of Visayas. [WEBSMS] | CMIN
1/13/2024 4:15:59 AM | [NSO Update] Visayas Grid-01/13/2024 04:16: Weather Advisory: Shear line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon and the rest of Visayas. [WEBSMS] | CVIS
1/13/2024 4:15:44 AM | [NSO Update] Luzon Grid-01/13/2024 04:16: Weather Advisory: Shear line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon and the rest of Visayas. [WEBSMS] | CLUZ
1/13/2024 3:44:12 AM | Luzon Grid-01/13/2024 03:44: Quezon SS 300MVA T01 restored at 0343H (Planned Outage) [WEBSMS] | CLUZ
1/13/2024 2:13:16 AM | Visayas Grid-01/13/2024 02:13: PEDC U3 cut-in to the system at 0159H, initial load 14MW. [WEBSMS] | CVIS
1/13/2024 12:58:54 AM | Mindanao Grid-01/13/2024 01:03: Nagamin-Zamboanga 138kV Line 2 (7LI2NAA-ZAM) de-energized at 0053H (P.O/Non-GOMP,) to facilitate the termination and interconnection of new BF(7Z-01CB08NAA) to existing line protections M1 and M2 of 7LI2NAA-ZAM. [WEBSMS] | CMIN
1/13/2024 12:40:27 AM | Luzon Grid-01/13/2024 00:40: Quezon SS 300MVA T01 de-energized at 0034H (Planned Outage) [WEBSMS] | CLUZ
1/13/2024 12:25:24 AM | Mindanao Grid-01/13/2024 00:29: NagaMin SS 7XF03NAA (SVC) and NagaMin 138 kV Bus 2 (7BS02NAA) de-energized at 0009H & 0012H, respectively ( P.O/Non-GOMP). This is to facilitate the tapping of drop conductors from 7BS02NAA to the new 7-01DS07NAA. [WEBSMS] | CMIN
1/13/2024 12:23:29 AM | Luzon Grid-01/13/2024 00:23: Malaya-Ingrid 230kV Line 2 (CO de-energized at 0018H (Planned Outage) [WEBSMS] | CLUZ
1/13/2024 12:03:38 AM | Mindanao Grid-01/13/2024 00:07: WMPC DG04 online at 0001H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/13/2024 12:02:58 AM | Mindanao Grid-01/13/2024 00:07: WMPC DG10 online at 0000H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/12/2024 11:54:16 PM | Luzon Grid-01/12/2024 23:54: Sta. Rita Module 40 shutdown at 2353H (Planned Outage) [WEBSMS] | CLUZ
1/12/2024 10:25:50 PM | Luzon Grid-01/12/2024 22:26: Limay - PAVI Green ORS 69kV L restored at 2225H (Planned Outage) [WEBSMS] | CLUZ
1/12/2024 9:20:11 PM | Mindanao Grid-01/12/2024 21:24: WMPC DG10 shutdown at 2119H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/12/2024 7:08:33 PM | Luzon Grid-01/12/2024 19:08: Limay-PAVI Green ORS 69kV Line de-energized at 1906H (Planned Outage) [WEBSMS] | CLUZ
1/12/2024 5:56:06 PM | Mindanao Grid-01/12/2024 18:00: SPC Mati with 3MW load tripped at 1746H due to reverse power indication.(Unplanned Outage). [WEBSMS] | CMIN
1/12/2024 5:41:12 PM | [NSO Update] Luzon Grid-01/12/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13138MW, PK=9706MW, RR=412MW, NetOpMargin: EVE=3020 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @135MW, SLPGC 2 @120MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/12/2024 5:41:04 PM | [NSO Update] Visayas Grid-01/12/2024 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2374MW, PK=2090MW, RR=90MW, NetOpMargin: EVE=194 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @327MW, PGPP1 @38MW [WEBSMS] | CVIS
1/12/2024 5:40:53 PM | [NSO Update] Mindanao Grid-01/12/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3080MW, PK=2211MW, RR=72MW, NetOpMargin: EVE=796 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35MW, AG1 @54MW, AG2 @94MW, AG4 @94MW, AG5 @29MW, AG6 @163MW, AG7 @26MW, PG4 @120MW [WEBSMS] | CMIN
1/12/2024 5:00:07 PM | Visayas Grid-01/12/2024 17:00: Daanlungsod SS 138 kV Bus 2 energized at 1637H (Planned Outage) [WEBSMS] | CVIS
1/12/2024 4:22:20 PM | Mindanao Grid-01/12/2024 16:26: SPC Mati with 3MW load tripped at 1610H due to reverse power indication.(Unplanned Outage). [WEBSMS] | CMIN
1/12/2024 4:19:51 PM | Mindanao Grid-01/12/2024 16:24: Culaman SS 230kV Bus 2 energized at 1559H. Planned Outage. [WEBSMS] | CMIN
1/12/2024 4:15:34 PM | Mindanao Grid-01/12/2024 16:19: WMPC DG04 shutdown at 1614H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/12/2024 4:03:24 PM | Visayas Grid-01/12/2024 16:03: 138KV Cebu Bus 2 energized @1558H.(Unplanned Outage) [WEBSMS] | CVIS
1/12/2024 3:03:51 PM | [NSO Update] Visayas Grid-01/12/2024 15:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1502H with power going to Visayas. [WEBSMS] | CVIS
1/12/2024 3:03:18 PM | [NSO Update] Mindanao Grid-01/12/2024 15:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1502H with power going to Visayas. [WEBSMS] | CMIN
1/12/2024 2:55:42 PM | [NSO Update] Visayas Grid-01/12/2024 14:56: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1452H from reverse power direction. [WEBSMS] | CVIS
1/12/2024 2:54:59 PM | [NSO Update] Mindanao Grid-01/12/2024 14:59: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1452H from reverse power direction. [WEBSMS] | CMIN
1/12/2024 2:25:57 PM | Visayas Grid-01/12/2024 14:26: 138KV Cebu Bus 2 Emergency de-energized @1420H.(Unplanned Outage) [WEBSMS] | CVIS
1/12/2024 2:18:18 PM | Mindanao Grid-01/12/2024 14:22: Update: ASIGA Unit 2 with 4MW tripped at 1116H. Cause DE bearing Axial thrust pad temp alarm & trip. Online back at 1134H. [WEBSMS] | CMIN
1/12/2024 1:16:26 PM | Mindanao Grid-01/12/2024 13:20: ASIGA Unit 2 with 4MW tripped at 1116H. Cause for investigation. Online back at 1134H. (Unplanned Outage) [WEBSMS] | CMIN
1/12/2024 12:58:43 PM | [NSO Update] Mindanao Grid-01/12/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3137MW, PK=2282MW, RR=72MW, NetOpMargin: PM=783, EVE=785 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35MW, AG1 @54MW, AG2 @94MW, AG4 @94MW, AG5 @29MW, AG6 @163MW, AG7 @26MW, PG4 @120MW [WEBSMS] | CMIN
1/12/2024 12:57:16 PM | [NSO Update] Visayas Grid-01/12/2024 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2621MW, PK=2206MW, RR=92MW, NetOpMargin: PM=324, EVE=186 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @315MW, PGPP1 @38MW [WEBSMS] | CVIS
1/12/2024 12:55:36 PM | [NSO Update] Luzon Grid-01/12/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14035MW, PK=10180MW, RR=430MW, NetOpMargin: PM=3425, EVE=2811 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @135MW, SLPGC 2 @120MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/12/2024 12:43:19 PM | [NSO Update] Mindanao Grid-01/12/2024 12:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1241H with power going to Mindanao. [WEBSMS] | CMIN
1/12/2024 12:42:57 PM | [NSO Update] Visayas Grid-01/12/2024 12:43: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1241H with power going to Mindanao. [WEBSMS] | CVIS
1/12/2024 12:36:23 PM | [NSO Update] Mindanao Grid-01/12/2024 12:40: undefined at 1231H Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1231H from forward power direction. [WEBSMS] | CMIN
1/12/2024 12:35:51 PM | [NSO Update] Visayas Grid-01/12/2024 12:36: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1231H from forward power direction. [WEBSMS] | CVIS
1/12/2024 11:26:45 AM | Mindanao Grid-01/12/2024 11:30: Agus 6 HEP 69kV L4 energized at 1040H. Planned Outage. (Requested by Agus 6 HEP for the PMS of their Unit-4). [WEBSMS] | CMIN
1/12/2024 11:19:15 AM | Mindanao Grid-01/12/2024 11:23: WMPC DG04 online at 1051H . RPS-System Voltage Requirement [WEBSMS] | CMIN
1/12/2024 10:54:31 AM | Mindanao Grid-01/12/2024 10:58: Agus 6 Unit 4 online at 1049H. (Planned Outage) [WEBSMS] | CMIN
1/12/2024 8:32:45 AM | Visayas Grid-01/12/2024 08:33: Daanlungsod SS 138 kV Bus 2 de-energized at 0823H (Planned Outage) [WEBSMS] | CVIS
1/12/2024 5:53:58 AM | [NSO Update] Mindanao Grid-01/12/2024 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3190MW, PK=2332MW, RR=70MW, NetOpMargin: AM=788, PM=784, EVE=764 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46MW, MA2 @35MW, AG1 @54MW, AG2 @94MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @120MW [WEBSMS] | CMIN
1/12/2024 5:52:16 AM | [NSO Update] Visayas Grid-01/12/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2565MW, PK=2122MW, RR=88MW, NetOpMargin: AM=354, PM=263, EVE=246 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 319MW, PGPP1 @ 38MW [WEBSMS] | CVIS
1/12/2024 5:51:00 AM | [NSO Update] Luzon Grid-01/12/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13918MW, PK=10063MW, RR=422MW, NetOpMargin: AM=3433, PM=2773, EVE=2443 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, SLPGC 1 @ 135MW, SLPGC 2 @ 120MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/12/2024 4:16:58 AM | [NSO Update] Luzon Grid-01/12/2024 04:17: Weather Update: Shear line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CLUZ
1/12/2024 4:16:46 AM | [NSO Update] Mindanao Grid-01/12/2024 04:20: Weather Update: Shear line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CMIN
1/12/2024 4:16:28 AM | [NSO Update] Visayas Grid-01/12/2024 04:16: Weather Update: Shear line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CVIS
1/11/2024 9:18:41 PM | Mindanao Grid-01/11/2024 21:22: WMPC DG05 shutdown at 2113H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/11/2024 9:06:19 PM | Mindanao Grid-01/11/2024 21:10: TSI Unit 1 and 2 change setting at 2101H from APC ON/ Free Governor-OFF to APC OFF/ Free Governor-ON. AS-CR replacement for TMI 1 unit 1. [WEBSMS] | CMIN
1/11/2024 7:49:39 PM | Luzon Grid-01/11/2024 19:49: Sual Unit 1 online at 1949H (Unplanned Outage) [WEBSMS] | CLUZ
1/11/2024 7:15:17 PM | Mindanao Grid-01/11/2024 19:19: WMPC DG01 cut-out at 1907H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/11/2024 6:37:19 PM | Mindanao Grid-01/11/2024 18:41: Peak Power San Francisco U2 cut-in at 1834H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/11/2024 6:25:42 PM | Mindanao Grid-01/11/2024 18:29: Peak Power San Francisco U2 cut-out at 1823H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/11/2024 6:18:24 PM | Mindanao Grid-01/11/2024 18:22: Peak Power San Francisco U2 cut-in at 1814H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/11/2024 6:10:28 PM | Mindanao Grid-01/11/2024 18:14: WMPC DG01 Online at 1805H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/11/2024 5:44:53 PM | [NSO Update] Mindanao Grid-01/11/2024 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3059MW, PK=2277MW, RR=72.4MW, NetOpMargin: EVE=710 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @35MW, AG1 @54MW, AG2 @94MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @120MW [WEBSMS] | CMIN
1/11/2024 5:44:01 PM | [NSO Update] Visayas Grid-01/11/2024 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2459MW, PK=2193MW, RR=93MW, NetOpMargin: EVE=173 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 310MW, PGPP1 @ 38MW [WEBSMS] | CVIS
1/11/2024 5:42:35 PM | [NSO Update] Luzon Grid-01/11/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12511MW, PK=10221MW, RR=390MW, NetOpMargin: EVE=1900 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, SLPGC 1 @ 135MW, SLPGC 2 @ 120MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/11/2024 5:17:40 PM | Mindanao Grid-01/11/2024 17:21: Mt. Apo Unit #3 synchronized back at 1649H, from forced outage. Follow RTD. [WEBSMS] | CMIN
1/11/2024 4:41:16 PM | Luzon Grid-01/11/2024 16:41: Limay - BCCPP 230kV Line 2 restored at 1640H (Planned Outage) [WEBSMS] | CLUZ
1/11/2024 4:40:23 PM | Mindanao Grid-01/11/2024 16:44: WMPC DG01 cut out at 1633H. End of MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/11/2024 2:42:26 PM | Luzon Grid-01/11/2024 14:42: Dasmarinas - TMC II (Ternate) 115kV Line restored at 1439H (Planned Outage) [WEBSMS] | CLUZ
1/11/2024 1:33:38 PM | [NSO Update] Visayas Grid-01/11/2024 13:33: Lala - Dumanjug 350kV HVDC (Mindanao - Visayas) was de-blocked at 1332H with power going to Visayas. [WEBSMS] | CVIS
1/11/2024 1:32:57 PM | [NSO Update] Mindanao Grid-01/11/2024 13:37: Lala - Dumanjug 350kV HVDC (Mindanao - Visayas) was de-blocked at 1332H with power going to Visayas. [WEBSMS] | CMIN
1/11/2024 1:25:19 PM | [NSO Update] Mindanao Grid-01/11/2024 13:29: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1322H from reverse power direction. [WEBSMS] | CMIN
1/11/2024 1:25:05 PM | [NSO Update] Visayas Grid-01/11/2024 13:25: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1322H from reverse power direction. [WEBSMS] | CVIS
1/11/2024 12:59:49 PM | [NSO Update] Luzon Grid-01/11/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13278MW, PK=10692MW, RR=411MW, NetOpMargin: PM=2175, EVE=1712 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 3 @280MW, SLPGC 1 @135MW, SLPGC 2 @120MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/11/2024 12:56:30 PM | [NSO Update] Mindanao Grid-01/11/2024 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3090MW, PK=2361MW, RR=72MW, NetOpMargin: PM=657, EVE=638 Highest Unit O/L: GNPK 1,2 & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @35MW, AG1 @54MW, AG2 @94MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @90MW [WEBSMS] | CMIN
1/11/2024 12:50:53 PM | [NSO Update] Mindanao Grid-01/11/2024 12:55: Lala - Dumanjug 350kV HVDC (Mindanao - Visayas) was de-blocked at 1237H with power going to Mindanao. [WEBSMS] | CMIN
1/11/2024 12:49:18 PM | [NSO Update] Visayas Grid-01/11/2024 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2616MW, PK=2277MW, RR=90MW, NetOpMargin: PM=250, EVE=251 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @310MW, PGPP1 @38MW [WEBSMS] | CVIS
1/11/2024 12:46:43 PM | [NSO Update] Luzon Grid-01/11/2024 12:46: Lala - Dumanjug 350kV HVDC (Mindanao - Visayas) was de-blocked at 1237H with power going to Mindanao. [WEBSMS] | CLUZ
1/11/2024 12:45:52 PM | [NSO Update] Visayas Grid-01/11/2024 12:46: Lala - Dumanjug 350kV HVDC (Mindanao - Visayas) was de-blocked at 1237H with power going to Mindanao. [WEBSMS] | CVIS
1/11/2024 12:41:47 PM | [NSO Update] Luzon Grid-01/11/2024 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13278MW, PK=10692MW, RR=411MW, NetOpMargin: PM=2175, EVE=1712 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 2 @280MW, SLPGC 1 @135MW, SLPGC 2 @120MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/11/2024 12:33:48 PM | [NSO Update] Mindanao Grid-01/11/2024 12:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1227H from forward power direction. [WEBSMS] | CMIN
1/11/2024 12:32:52 PM | [NSO Update] Visayas Grid-01/11/2024 12:33: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1227H from forward power direction. [WEBSMS] | CVIS
1/11/2024 11:57:45 AM | Luzon Grid-01/11/2024 11:58: Sual 1 tripped with 233MW load at 1155H. Lowest system frequency was 59.426Hz. (Unplanned Outage) [WEBSMS] | CLUZ
1/11/2024 10:53:10 AM | Mindanao Grid-01/11/2024 10:57: WMPC DG01 online at 0850H . RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/11/2024 9:21:47 AM | Mindanao Grid-01/11/2024 09:25: TSI Unit 1 and 2 change setting at 0901H from APC OFF/ Free Governor-ON to APC ON/ Free Governor-OFF. AS-CR back to TMI 1. [WEBSMS] | CMIN
1/11/2024 9:11:01 AM | Luzon Grid-01/11/2024 09:11: Dasmarinas - TMC II (Ternate) 115kV Line de-energized at 0910H. (Planned Outage) [WEBSMS] | CLUZ
1/11/2024 9:08:09 AM | Mindanao Grid-01/11/2024 09:12: TMI 1 declared available for CR at at 0901H. [WEBSMS] | CMIN
1/11/2024 8:54:20 AM | Mindanao Grid-01/11/2024 08:58: WMPC DG05 online at 0850H . RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/11/2024 8:38:29 AM | Mindanao Grid-01/11/2024 08:42: Culaman SS 230kV Bus 2 de-energized 0833H. Planned outage [WEBSMS] | CMIN
1/11/2024 6:12:41 AM | Luzon Grid-01/11/2024 06:12: Limay - BCCPP 230kV Line 2 de-energized at 0611H. (Planned Outage) [WEBSMS] | CLUZ
1/11/2024 5:35:36 AM | [NSO Update] Luzon Grid-01/11/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13873MW, PK=10774MW, RR=414MW, NetOpMargin: AM=2685, PM=2554, EVE=2041 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC2 @280MW, SLPGC 1 @135MW, SLPGC 2 @120MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/11/2024 5:33:34 AM | [NSO Update] Visayas Grid-01/11/2024 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2512MW, PK=2203MW, RR=86MW, NetOpMargin: AM=224, PM=232, EVE=250 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @305MW, PGPP1 @76MW [WEBSMS] | CVIS
1/11/2024 5:31:48 AM | [NSO Update] Mindanao Grid-01/11/2024 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3114MW, PK=2285MW, RR=70MW, NetOpMargin: AM=759, PM=708, EVE=716 Highest Unit O/L: GNPK 1,2 & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @35MW, AG1 @54MW, AG2 @94MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @120MW [WEBSMS] | CMIN
1/11/2024 5:22:54 AM | Luzon Grid-01/11/2024 05:23: Sta. Rita SS 230kV Busbar 1 de-energized at 0519H (Planned Outage) [WEBSMS] | CLUZ
1/11/2024 4:10:39 AM | [NSO Update] Luzon Grid-01/11/2024 04:10: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Shear line affecting the eastern section of Southern Luzon. [WEBSMS] | CLUZ
1/11/2024 4:10:22 AM | [NSO Update] Visayas Grid-01/11/2024 04:10: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Shear line affecting the eastern section of Southern Luzon. [WEBSMS] | CVIS
1/11/2024 4:10:13 AM | [NSO Update] Mindanao Grid-01/11/2024 04:14: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Shear line affecting the eastern section of Southern Luzon. [WEBSMS] | CMIN
1/11/2024 2:52:54 AM | Luzon Grid-01/11/2024 02:53: Limay-PAVI Green ORS 69kV Line restored at 0252H (Planned Outage) [WEBSMS] | CLUZ
1/11/2024 2:24:25 AM | Luzon Grid-01/11/2024 02:24: San Jose PCB 8-05CB08SJO restored at 0224H (Unplanned Outage) [WEBSMS] | CLUZ
1/11/2024 12:05:10 AM | Mindanao Grid-01/11/2024 00:09: TMI Unit 1 (AS-CR provider) declared unavailable at 0001H due to HVAC problem. (Unplanned Outage) [WEBSMS] | CMIN
1/10/2024 11:45:52 PM | Luzon Grid-01/10/2024 23:46: Sta. Rita module 30 shutdown at 2343H (Unplanned Outage) [WEBSMS] | CLUZ
1/10/2024 11:10:09 PM | Luzon Grid-01/10/2024 23:10: Kalayaan Unit 4 tripped as pump at 2303H. The highest frequency is 60.32Hz (Unplanned Outage)t [WEBSMS] | CLUZ
1/10/2024 9:38:32 PM | Mindanao Grid-01/10/2024 21:42: ASIGA HEPP online at 2003H. (Unplanned Outage) [WEBSMS] | CMIN
1/10/2024 9:16:37 PM | Mindanao Grid-01/10/2024 21:20: WMPC DG10 cut out at 2114H. End of RPS. [WEBSMS] | CMIN
1/10/2024 7:53:40 PM | Mindanao Grid-01/10/2024 19:57: ASIGA HEPP with 8MW gross generation tripped at 1939H. Indication: Restricted Earth Fault (REF). Unplanned Outage. [WEBSMS] | CMIN
1/10/2024 7:47:44 PM | Mindanao Grid-01/10/2024 19:51: Correction: NagaMin-Zamboanga 138 kV L2 was isolated during the tripping of NagaMin SS Power Transformer T2 (50MVA) at 1703H since 7-01CB08NAA was opened/de-energized last Nov. 5, 2023, to facilitate the replacement of 7-01DS09NAA [WEBSMS] | CMIN
1/10/2024 7:27:00 PM | Mindanao Grid-01/10/2024 19:31: WMPC DG07 shutdown at 1922H. From MOT raise. [WEBSMS] | CMIN
1/10/2024 7:26:44 PM | Mindanao Grid-01/10/2024 19:30: Correction: NagaMin-Zamboanga 138 kV L2 was de-energized during the tripping of NagaMin SS Power Transformer T2 (50MVA) at 1703H since 7-01CB08NAA was opened/de-energized last Nov. 5, 2023, to facilitate the replacement of 7-01DS09NAA [WEBSMS] [WEBSMS] | CMIN
1/10/2024 7:24:00 PM | Mindanao Grid-01/10/2024 19:28: NagaMin-Zamboanga 138 kV L2 was de-energized during the tripping of NagaMin SS Power Transformer T2 (50MVA) at 1703H since 7-01CB08NAA was opened/energized last Nov. 5, 2023, to facilitate the replacement of 7-01DS09NAA [WEBSMS] | CMIN
1/10/2024 7:20:48 PM | Luzon Grid-01/10/2024 19:21: Limay-PAVI Green ORS 69kV Line de-energized at 1918H (Planned Outage) [WEBSMS] | CLUZ
1/10/2024 6:57:56 PM | Luzon Grid-01/10/2024 18:58: San Jose PCB 8-05CB08SJO de-energized at 1849H (Unplanned Outage) [WEBSMS] | CLUZ
1/10/2024 6:56:33 PM | Luzon Grid-01/10/2024 18:56: Limay-BCCPP 230kV Line 1 restored at 1840H (Planned Outage) [WEBSMS] | CLUZ
1/10/2024 5:56:16 PM | Mindanao Grid-01/10/2024 18:00: Nagamin SS Transformer No. 2 tripped at 1703H. (Unplanned Outage) [WEBSMS] | CMIN
1/10/2024 5:44:08 PM | [NSO Update] Mindanao Grid-01/10/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3055MW, PK=2218MW, RR=72MW, NetOpMargin: EVE=765 Highest Unit O/L: GNPK 1,2 & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @35MW, AG1 @54MW, AG2 @85MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @130MW [WEBSMS] | CMIN
1/10/2024 5:43:47 PM | [NSO Update] Visayas Grid-01/10/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2593MW, PK=2282MW, RR=91MW, NetOpMargin: EVE=221 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @282MW, PGPP1 @76MW [WEBSMS] | CVIS
1/10/2024 5:42:33 PM | [NSO Update] Luzon Grid-01/10/2024 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13315MW, PK=10802MW, RR=390MW, NetOpMargin: EVE=2123 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC2 @280MW, SLPGC 1 @135MW, SLPGC 2 @120MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/10/2024 4:45:32 PM | Mindanao Grid-01/10/2024 16:49: WMPC DG07 shutdown at 1637H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/10/2024 3:22:34 PM | Luzon Grid-01/10/2024 15:22: San Jose PCB 8-08CB04SJO restored at 1519H (Unplanned Outage) [WEBSMS] | CLUZ
1/10/2024 2:46:05 PM | Mindanao Grid-01/10/2024 14:50: WMPC DG01 shutdown at 1430H due to Lube oil leak. (Unplanned Outage) [WEBSMS] | CMIN
1/10/2024 2:10:34 PM | Mindanao Grid-01/10/2024 14:14: Nabunturan-Masara 138kV L energized at 1336H. Planned Outage. (Customers, AMCI, request shutdown). [WEBSMS] | CMIN
1/10/2024 2:02:23 PM | Mindanao Grid-01/10/2024 14:06: Peak Power San Francisco online at 1359H. MO dispatch. [WEBSMS] | CMIN
1/10/2024 1:35:48 PM | Mindanao Grid-01/10/2024 13:39: WMPC DG01 online at 1333H. MOT raised. [WEBSMS] | CMIN
1/10/2024 1:11:52 PM | Mindanao Grid-01/10/2024 13:15: Pulangi IV unit 3 online at 1301H. (Unplanned Outage) [WEBSMS] | CMIN
1/10/2024 12:53:15 PM | [NSO Update] Luzon Grid-01/10/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14355MW, PK=10957MW, RR=411MW, NetOpMargin: PM=2987, EVE=2412 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 300MW, Masinloc 3 @ 280MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/10/2024 12:44:03 PM | [NSO Update] Mindanao Grid-01/10/2024 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3054MW, PK=2266MW, RR=72MW, NetOpMargin: PM=715, EVE=707 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @35MW, AG1 @54MW, AG2 @85MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @90MW [WEBSMS] | CMIN
1/10/2024 12:41:04 PM | [NSO Update] Visayas Grid-01/10/2024 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2579MW, PK=2252MW, RR=91MW, NetOpMargin: PM=236, EVE=268 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 300MW, PGPP1 @ 76MW [WEBSMS] | CVIS
1/10/2024 11:00:49 AM | Mindanao Grid-01/10/2024 11:04: Correction: WMPC DG07 online at 1055H . RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/10/2024 10:59:20 AM | Mindanao Grid-01/10/2024 11:03: WMPC DG10 online at 1055H . RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/10/2024 10:33:26 AM | Mindanao Grid-01/10/2024 10:37: Agus 2 Unit 3 online at 1031H for ANCILLARY TEST : ANCILLARY RESERVE TEST(Planned Outage) [WEBSMS] | CMIN
1/10/2024 10:32:09 AM | Mindanao Grid-01/10/2024 10:36: Agus 2 Unit 3 shutdown at 1018H for ANCILLARY TEST : ANCILLARY RESERVE TEST (Planned Outage). [WEBSMS] | CMIN
1/10/2024 9:32:18 AM | Mindanao Grid-01/10/2024 09:36: Bislig -Nabunturan 138 kV Line auto-tripped at 0912H and successfully reclosed both sides. [WEBSMS] | CMIN
1/10/2024 8:56:25 AM | Mindanao Grid-01/10/2024 09:00: WMPC DG10 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/10/2024 7:55:40 AM | Mindanao Grid-01/10/2024 07:59: Nabunturan-Masara 138kV L deenergized at 0742H. Planned Outage. (Customers, AMCI, request shutdown). [WEBSMS] | CMIN
1/10/2024 6:08:14 AM | Luzon Grid-01/10/2024 06:08: Limay-BCCPP 230kV Line 1 de-energized at 0605H (Planned Outage) [WEBSMS] | CLUZ
1/10/2024 5:59:26 AM | [NSO Update] Mindanao Grid-01/10/2024 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3107MW, PK=2251MW, RR=70MW, NetOpMargin: AM=785, PM=702, EVE=705 Highest Unit O/L: GNPK 1, 2 & 4 Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @35MW, AG1 @54MW, AG2 @110MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @90MW [WEBSMS] | CMIN
1/10/2024 5:57:01 AM | [NSO Update] Visayas Grid-01/10/2024 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2542MW, PK=2160MW, RR=88MW, NetOpMargin: AM=294, PM=310, EVE=261 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 315MW, PGPP1 @ 76MW [WEBSMS] | CVIS
1/10/2024 5:54:28 AM | [NSO Update] Luzon Grid-01/10/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14195MW, PK=10755MW, RR=414MW, NetOpMargin: AM=3027, PM=2965, EVE=2740 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 300MW, Masinloc 3 @ 280MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/10/2024 4:22:14 AM | [NSO Update] Luzon Grid-01/10/2024 04:22: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
1/10/2024 4:16:43 AM | [NSO Update] Visayas Grid-01/10/2024 04:16: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
1/10/2024 4:15:45 AM | [NSO Update] Mindanao Grid-01/10/2024 04:19: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
1/10/2024 1:40:33 AM | Mindanao Grid-01/10/2024 01:44: TMI Unit 1 (AS-CR provider) declared unavailable at 1230H due to High Temp. No replacement CR. (Unplanned Outage) [WEBSMS] | CMIN
1/9/2024 10:21:57 PM | Luzon Grid-01/09/2024 22:22: San Marcelino Solar Power Plant 170MVA T02(Customer Owned) was energized at 2218H. (Planned Outage) [WEBSMS] | CLUZ
1/9/2024 9:37:19 PM | Mindanao Grid-01/09/2024 21:41: WMPC DG03 shutdown at 1612H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/9/2024 9:35:12 PM | Mindanao Grid-01/09/2024 21:39: WMPC DG10 shutdown at 2130H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/9/2024 9:19:47 PM | Mindanao Grid-01/09/2024 21:23: Peak Power San Francisco U2 cut-out at 2117H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/9/2024 9:12:28 PM | Mindanao Grid-01/09/2024 21:16: Peak Power San Francisco U2 cut-in at 2102H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/9/2024 8:57:36 PM | Mindanao Grid-01/09/2024 21:01: WMPC DG03 cut-out at 2037H. [WEBSMS] | CMIN
1/9/2024 8:55:40 PM | Mindanao Grid-01/09/2024 20:59: Peak Power San Francisco U2 cut-out at 2027H. [WEBSMS] | CMIN
1/9/2024 8:35:42 PM | Mindanao Grid-01/09/2024 20:39: Minergy ME2 (WARTSILA) cut-out at 2032H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/9/2024 8:26:57 PM | Mindanao Grid-01/09/2024 20:31: Minergy ME2 (WARTSILA) Online at 2001H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/9/2024 8:18:27 PM | Mindanao Grid-01/09/2024 20:22: Peak Power San Francisco U2 cut-in for MOT raise at 1951H. [WEBSMS] | CMIN
1/9/2024 8:06:23 PM | Mindanao Grid-01/09/2024 20:10: WMPC DG03 cut-in for MOT raise at 1951H. [WEBSMS] | CMIN
1/9/2024 7:21:38 PM | Mindanao Grid-01/09/2024 19:25: Peak Power San Francisco U2 shutdown at 1818H. MO dispatch / Follow RTD. [WEBSMS] | CMIN
1/9/2024 7:20:31 PM | Mindanao Grid-01/09/2024 19:24: Peak Power San Francisco U1 shutdown at 1907H. MO dispatch / Follow RTD. [WEBSMS] | CMIN
1/9/2024 7:11:17 PM | Luzon Grid-01/09/2024 19:11: San Marcelino Solar Power Plant 170MVA T02 (Customer Owned) was de-energized at 1907H. (Planned Outage) [WEBSMS] | CLUZ
1/9/2024 7:05:55 PM | Mindanao Grid-01/09/2024 19:10: TSI Unit 1 and 2 change setting at 1901H from APC ON/ Free Governor-OFF to APC OFF/ Free Governor-ON. AS-CR replacement for TMI 1 unit 1. [WEBSMS] | CMIN
1/9/2024 6:14:36 PM | Mindanao Grid-01/09/2024 18:18: Peak Power San Frans U1 Online at 1727H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/9/2024 6:13:17 PM | Mindanao Grid-01/09/2024 18:17: Peak Power San Frans U2 Online at 1804H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/9/2024 5:48:23 PM | [NSO Update] Luzon Grid-01/09/2024 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13372MW, PK=10626MW, RR=390MW, NetOpMargin: EVE=2356 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 290MW, Masinloc 3 @ 220MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/9/2024 5:47:19 PM | [NSO Update] Visayas Grid-01/09/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2591MW, PK=2239MW, RR=92MW, NetOpMargin: EVE=260 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 307MW, PGPP1 @ 76MW [WEBSMS] | CVIS
1/9/2024 5:46:06 PM | [NSO Update] Mindanao Grid-01/09/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3008MW, PK=2227MW, RR=72.4MW, NetOpMargin: EVE=708 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @35MW, AG1 @54MW, AG2 @80MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @90MW [WEBSMS] | CMIN
1/9/2024 5:29:23 PM | [NSO Update] Mindanao Grid-01/09/2024 17:33: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1727H with power going to Visayas. [WEBSMS] | CMIN
1/9/2024 5:28:48 PM | [NSO Update] Visayas Grid-01/09/2024 17:29: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1727H with power going to Visayas. [WEBSMS] | CVIS
1/9/2024 4:45:27 PM | Mindanao Grid-01/09/2024 16:49: FDC (FMP) Unit #1 cut-in at 1639H from unplanned outage. [WEBSMS] | CMIN
1/9/2024 4:05:27 PM | [NSO Update] Mindanao Grid-01/09/2024 16:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1604H from reverse power direction. [WEBSMS] | CMIN
1/9/2024 4:04:58 PM | [NSO Update] Visayas Grid-01/09/2024 16:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1604H from reverse power direction. [WEBSMS] | CVIS
1/9/2024 3:48:51 PM | Mindanao Grid-01/09/2024 15:52: Agus2 U2 with 45.47MW gross generation tripped at 0930H. Indication: Activation of Generator Lock-out Relay. Unplanned Outage. [WEBSMS] | CMIN
1/9/2024 1:21:26 PM | [NSO Update] Luzon Grid-01/09/2024 13:21: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14159MW, PK=10557MW, RR=411MW, NetOpMargin: PM=3190, EVE=2802 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @250MW, MSLC3 @220MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/9/2024 1:16:00 PM | [NSO Update] Mindanao Grid-01/09/2024 13:20: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2988MW, PK=2294MW, RR=72MW, NetOpMargin: PM=622, EVE=589 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @35MW, AG1 @54MW, AG2 @80MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @90MW [WEBSMS] | CMIN
1/9/2024 1:12:29 PM | [NSO Update] Visayas Grid-01/09/2024 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2742MW, PK=2265MW, RR=94MW, NetOpMargin: PM=383, EVE=274 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
1/9/2024 12:23:44 PM | [NSO Update] Mindanao Grid-01/09/2024 12:27: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1216H with power going to Mindanao. [WEBSMS] | CMIN
1/9/2024 12:22:58 PM | [NSO Update] Visayas Grid-01/09/2024 12:23: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1216H with power going to Mindanao. [WEBSMS] | CVIS
1/9/2024 12:10:00 PM | [NSO Update] Mindanao Grid-01/09/2024 12:14: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1204H from forward power direction. [WEBSMS] | CMIN
1/9/2024 12:09:27 PM | [NSO Update] Visayas Grid-01/09/2024 12:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1204H from forward power direction. [WEBSMS] | CVIS
1/9/2024 12:08:34 PM | [NSO Update] Visayas Grid-01/09/2024 12:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1204H from forward power direction. [WEBSMS] | CVIS
1/9/2024 11:09:29 AM | Mindanao Grid-01/09/2024 11:13: WMPC DG03 online at 1050H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/9/2024 10:59:49 AM | Luzon Grid-01/09/2024 11:00: Tiwi C SS 230kV Bus 2 restored at 1056H (Planned Outage) [WEBSMS] | CLUZ
1/9/2024 10:51:51 AM | Mindanao Grid-01/09/2024 10:55: TM2 Unit 2 cut-out as DR at 1038H. Call Time: 1031H. [WEBSMS] | CMIN
1/9/2024 10:45:05 AM | Mindanao Grid-01/09/2024 10:49: TM2 Unit 2 synchronized at 0954H. Utilized 37.5MW as Dispatchable Reserve. Call Time: 0940H. [WEBSMS] | CMIN
1/9/2024 9:07:28 AM | Mindanao Grid-01/09/2024 09:11: WMPC DG10 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/9/2024 8:51:41 AM | Mindanao Grid-01/09/2024 08:55: SMC Unit 1 shutdown at 0814H for PMS (Non-GOMP). (Unplanned Outage) [WEBSMS] | CMIN
1/9/2024 8:40:03 AM | Visayas Grid-01/09/2024 08:40: CEDC U2 cut in 0835H. (Unplanned Outage) [WEBSMS] | CVIS
1/9/2024 8:37:06 AM | Luzon Grid-01/09/2024 08:37: Tiwi C SS 230kV Bus 2 de-energized at 0833H (Planned Outage) [WEBSMS] | CLUZ
1/9/2024 8:19:58 AM | Mindanao Grid-01/09/2024 08:24: TMI 1 declared available for CR at at 0801H. [WEBSMS] | CMIN
1/9/2024 5:50:38 AM | [NSO Update] Luzon Grid-01/09/2024 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14086MW, PK=10616MW, RR=414MW, NetOpMargin: AM=3056, PM=2861, EVE=2431 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @220MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/9/2024 5:45:51 AM | [NSO Update] Mindanao Grid-01/09/2024 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2997MW, PK=2271MW, RR=70MW, NetOpMargin: AM=656, PM=640, EVE=548 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @35MW, AG1 @54MW, AG2 @80MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @90MW [WEBSMS] | CMIN
1/9/2024 5:39:15 AM | [NSO Update] Visayas Grid-01/09/2024 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2639MW, PK=2256MW, RR=90MW, NetOpMargin: AM=293, PM=252, EVE=275 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @320MW, PGPP1 @76MW [WEBSMS] | CVIS
1/9/2024 4:56:07 AM | Mindanao Grid-01/09/2024 05:00: WMPC DG10 shutdown at 0443H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/9/2024 4:55:30 AM | [NSO Update] Mindanao Grid-01/09/2024 04:59: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
1/9/2024 4:55:14 AM | [NSO Update] Visayas Grid-01/09/2024 04:55: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CVIS
1/9/2024 4:54:55 AM | [NSO Update] Luzon Grid-01/09/2024 04:54: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
1/9/2024 4:50:42 AM | Visayas Grid-01/09/2024 04:50: KSPC U1 online at 0448H (Unplanned Outage) [WEBSMS] | CVIS
1/9/2024 4:20:03 AM | Mindanao Grid-01/09/2024 04:24: Nagamin - Zamboanga 138KV Line 1 re-energized at 0416H (Unplanned Outage) [WEBSMS] | CMIN
1/9/2024 1:53:27 AM | Mindanao Grid-01/09/2024 01:57: Nagamin - Zamboanga 138KV LIne 1 manually out at 0149H (Unplanned Outage) [WEBSMS] | CMIN
1/9/2024 1:06:31 AM | Luzon Grid-01/09/2024 01:06: Masinloc Unit 1 online at 0105H. (Unplanned Outage) [WEBSMS] | CLUZ
1/8/2024 11:24:58 PM | Luzon Grid-01/08/2024 23:25: Anda synchronized at 2320H. (Planned Outage) [WEBSMS] | CLUZ
1/8/2024 10:32:38 PM | Luzon Grid-01/08/2024 22:32: San Marcelino Solar Power Plant 170MVA T01 was energized at 2229H. (Planned Outage) [WEBSMS] | CLUZ
1/8/2024 7:05:27 PM | Luzon Grid-01/08/2024 19:05: San Marcelino Solar Power Plant 170MVA T01 was de-energized at 1903H. (Planned Outage) [WEBSMS] | CLUZ
1/8/2024 6:08:53 PM | Mindanao Grid-01/08/2024 18:12: Mt. Apo U3 with 2.7MW gross generation tripped at 1750H. Indication: Activation of Generator Lock-out Relay. Unplanned Outage. [WEBSMS] | CMIN
1/8/2024 6:00:20 PM | [NSO Update] Visayas Grid-01/08/2024 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2545MW, PK=2278MW, RR=89MW, NetOpMargin: EVE=178 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
1/8/2024 5:59:59 PM | [NSO Update] Mindanao Grid-01/08/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2987MW, PK=2188MW, RR=72MW, NetOpMargin: EVE=727 Highest Unit O/L: GNPK 1, 2, and 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @54MW, AG2 @80MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @50MW [WEBSMS] | CMIN
1/8/2024 5:52:15 PM | [NSO Update] Luzon Grid-01/08/2024 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12867MW, PK=10335MW, RR=390MW, NetOpMargin: EVE=2142 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @220MW [WEBSMS] | CLUZ
1/8/2024 4:16:17 PM | Mindanao Grid-01/08/2024 16:20: WMPC DG04 shutdown at 1614H, RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/8/2024 3:40:48 PM | Mindanao Grid-01/08/2024 15:44: Pulangi 4 U3 manually shutdown at 1536H due to Low Water Elevation. Follow RTD. (Unplanned Outage) [WEBSMS] | CMIN
1/8/2024 2:42:02 PM | Mindanao Grid-01/08/2024 14:46: WMPC DG08 Online at 1422H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/8/2024 2:11:18 PM | Mindanao Grid-01/08/2024 14:15: STEAG U2 on emergency shutdown at 1400H due to Boiler Fouling. Follow RTD. (Unplanned Outage) [WEBSMS] | CMIN
1/8/2024 1:57:24 PM | Mindanao Grid-01/08/2024 14:01: TM2 U1 online at 1343H. SO Dispatched/MOT constrained "ON". [WEBSMS] | CMIN
1/8/2024 1:02:11 PM | Mindanao Grid-01/08/2024 13:06: Baloi-Agus 6 69KV tie line restored/Looped at 1257H. (Unplanned Outage) [WEBSMS] | CMIN
1/8/2024 12:44:54 PM | [NSO Update] Visayas Grid-01/08/2024 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2728MW, PK=2358MW, RR=95MW, NetOpMargin: PM=274, EVE=270 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @324MW, PGPP1 @76MW [WEBSMS] | CVIS
1/8/2024 12:39:10 PM | [NSO Update] Mindanao Grid-01/08/2024 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3220MW, PK=2392MW, RR=72MW, NetOpMargin: PM=757, EVE=768 Highest Unit O/L: GNPK 1,2 & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @54MW, AG2 @80MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @120MW [WEBSMS] | CMIN
1/8/2024 12:36:13 PM | [NSO Update] Luzon Grid-01/08/2024 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13498MW, PK=10785MW, RR=408MW, NetOpMargin: PM=2305, EVE=2076 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @220MW, SLPGC 1 @142MW, ILIJAN B @300MW [WEBSMS] | CLUZ
1/8/2024 12:29:11 PM | Mindanao Grid-01/08/2024 12:33: Baloi - Agus 2 69KV line 1 tripped at 1202H (Unplanned Outage) [WEBSMS] | CMIN
1/8/2024 10:35:28 AM | Mindanao Grid-01/08/2024 10:39: WMPC DG04 online at 1032H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/8/2024 8:55:27 AM | Mindanao Grid-01/08/2024 08:59: WMPC DG10 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/8/2024 5:47:19 AM | [NSO Update] Visayas Grid-01/08/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2593MW, PK=2233MW, RR=91MW, NetOpMargin: AM=269, PM=251, EVE=242 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @324MW, PGPP1 @76MW [WEBSMS] | CVIS
1/8/2024 5:43:42 AM | [NSO Update] Luzon Grid-01/08/2024 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13715MW, PK=10064MW, RR=414MW, NetOpMargin: AM=3237, PM=2664, EVE=2115 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 220MW, SLPGC 1 @ 142MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/8/2024 5:38:26 AM | [NSO Update] Mindanao Grid-01/08/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3169MW, PK=2353MW, RR=70MW, NetOpMargin: AM=746, PM=685, EVE=711 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @54MW, AG2 @80MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @60MW [WEBSMS] | CMIN
1/8/2024 4:04:09 AM | [NSO Update] Luzon Grid-01/08/2024 04:04: Weather Advisory: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CLUZ
1/8/2024 4:04:04 AM | [NSO Update] Visayas Grid-01/08/2024 04:04: Weather Advisory: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CVIS
1/8/2024 4:03:59 AM | [NSO Update] Mindanao Grid-01/08/2024 04:08: Weather Advisory: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CMIN
1/7/2024 10:36:36 PM | Mindanao Grid-01/07/2024 22:40: SMC (MCO) Unit 2 online at 2233H from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
1/7/2024 10:23:32 PM | Luzon Grid-01/07/2024 22:23: Sta. Rita Module 10 online at 2222H. (Unplanned Outage) [WEBSMS] | CLUZ
1/7/2024 10:20:35 PM | Luzon Grid-01/07/2024 22:20: Binan SS 300MVA T03 restored at 2219H. (Planned Outage) [WEBSMS] | CLUZ
1/7/2024 9:00:47 PM | Mindanao Grid-01/07/2024 21:04: SMCPC (MCO) tripped at 2055H with 10MW load. Indication: Drum Level Low-low. (Unplanned Outage) [WEBSMS] | CMIN
1/7/2024 8:09:21 PM | Mindanao Grid-01/07/2024 20:13: SMCPC Unit 2 cut-in at 2002H. (Unplanned Outage) [WEBSMS] | CMIN
1/7/2024 6:43:44 PM | Mindanao Grid-01/07/2024 18:47: SUPREME POWER Mati tripped with 3MW load at 1823H. Indication: Reverse Power Trip. (Unplanned Outage) [WEBSMS] | CMIN
1/7/2024 6:36:06 PM | Luzon Grid-01/07/2024 18:36: Sta. Rita 20 online at 1830H (Unplanned Outage) [WEBSMS] | CLUZ
1/7/2024 6:21:26 PM | Luzon Grid-01/07/2024 18:21: Batangas 300MVA T04 and T05 loop at 1820H (Planned Outage) [WEBSMS] | CLUZ
1/7/2024 6:16:47 PM | Luzon Grid-01/07/2024 18:16: Sta Rita and San Lorenzo 230kV Bus 1 and 2 unloop at 1816H (Planned Outage) [WEBSMS] | CLUZ
1/7/2024 6:08:31 PM | Luzon Grid-01/07/2024 18:08: Dasmarinas-Ilijan 500kV Line restored at 1808H (Planned Outage) [WEBSMS] | CLUZ
1/7/2024 5:51:41 PM | [NSO Update] Mindanao Grid-01/07/2024 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2982MW, PK=2096MW, RR=70MW, NetOpMargin: EVE=816 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @54MW, AG2 @80MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @80MW [WEBSMS] | CMIN
1/7/2024 5:50:04 PM | [NSO Update] Visayas Grid-01/07/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2430MW, PK=2106MW, RR=80MW, NetOpMargin: EVE=244 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @ 320MW, PGPP1 @ 76MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
1/7/2024 5:49:59 PM | [NSO Update] Luzon Grid-01/07/2024 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12422MW, PK=9230MW, RR=300MW, NetOpMargin: EVE=2892 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 240MW, SLPGC 1 @ 142MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/7/2024 5:28:36 PM | Visayas Grid-01/07/2024 17:28: CEDC U2 tripped at 1722H (Unplanned Outage) [WEBSMS] | CVIS
1/7/2024 2:07:34 PM | Mindanao Grid-01/07/2024 14:11: Supreme Power Mati online at 1351H (Unplanned Outage) [WEBSMS] | CMIN
1/7/2024 2:05:40 PM | Mindanao Grid-01/07/2024 14:09: SUPREME POWER Mati tripped with 3MW load at 1349H. Indication: Over current and Reverse Power Trip. (Unplanned Outage) [WEBSMS] | CMIN
1/7/2024 1:05:26 PM | Mindanao Grid-01/07/2024 13:09: TMI 1 declared available for CR at at 1301H. Unplanned Outage. [WEBSMS] | CMIN
1/7/2024 1:03:16 PM | Mindanao Grid-01/07/2024 13:07: TSI Unit 1 and 2 change setting at 1301H from APC OFF/ Free Governor-ON to APC ON/ Free Governor-OFF. AS-CR back to TMI 1 unit 1. [WEBSMS] | CMIN
1/7/2024 12:54:43 PM | [NSO Update] Mindanao Grid-01/07/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3088MW, PK=1957MW, RR=72MW, NetOpMargin: PM=1059, EVE=739 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @54MW, AG2 @80MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @80MW [WEBSMS] | CMIN
1/7/2024 12:53:39 PM | [NSO Update] Visayas Grid-01/07/2024 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2269MW, PK=1838MW, RR=77MW, NetOpMargin: PM=354, EVE=250 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 324MW, PGPP1 @ 76MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
1/7/2024 12:52:09 PM | [NSO Update] Luzon Grid-01/07/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13245MW, PK=8532MW, RR=321MW, NetOpMargin: PM=4344, EVE=2846 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 240MW, SLPGC 1 @ 142MW, SLPGC 2 @ 140MW, Ilijan B @ 295MW [WEBSMS] | CLUZ
1/7/2024 10:07:57 AM | Mindanao Grid-01/07/2024 10:11: SUPREME POWER Mati online at 0959H. MO Dispatched. [WEBSMS] | CMIN
1/7/2024 8:34:55 AM | Visayas Grid-01/07/2024 08:35: 138KV Cebu - Mandaue Line 2 de-energized @0832H. (Planned Outage) [WEBSMS] | CVIS
1/7/2024 8:33:06 AM | Visayas Grid-01/07/2024 08:33: Mandaue GIS 138KV 100MVA Transformer #2 de-energized @0822H. (Planned Outage) [WEBSMS] | CVIS
1/7/2024 6:58:16 AM | Luzon Grid-01/07/2024 06:58: Dasmarinas-Ilijan 500kV Line de-energized at 0655H (Planned Outage) [WEBSMS] | CLUZ
1/7/2024 6:17:36 AM | Luzon Grid-01/07/2024 06:17: Binan SS 300MVA T03 de-energized at 0613H (Planned Outage) [WEBSMS] | CLUZ
1/7/2024 6:05:25 AM | [NSO Update] Mindanao Grid-01/07/2024 06:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3048MW, PK=1877MW, RR=70MW, NetOpMargin: AM=1101, PM=1060, EVE=826 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @54MW, AG2 @80MW, AG4 @94MW, AG5 @29MW, AG6 @138MW, AG7 @26MW, PG4 @90MW [WEBSMS] | CMIN
1/7/2024 6:04:17 AM | [NSO Update] Visayas Grid-01/07/2024 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2554MW, PK=1798MW, RR=77MW, NetOpMargin: AM=679, PM=535, EVE=246 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @289MW, PGPP1 @76MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
1/7/2024 6:03:05 AM | [NSO Update] Luzon Grid-01/07/2024 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13521MW, PK=8775MW, RR=324MW, NetOpMargin: AM=4422, PM=4387, EVE=2766 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @240MW, SLPGC 1 @142MW, SLPGC 2 @92MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/7/2024 4:30:24 AM | [NSO Update] Mindanao Grid-01/07/2024 04:34: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CMIN
1/7/2024 4:30:00 AM | [NSO Update] Visayas Grid-01/07/2024 04:30: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CVIS
1/7/2024 4:29:45 AM | [NSO Update] Luzon Grid-01/07/2024 04:29: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CLUZ
1/7/2024 3:10:36 AM | Luzon Grid-01/07/2024 03:10: Sual Unit 1 online at 0306H (Unplanned Outage) [WEBSMS] | CLUZ
1/6/2024 8:15:01 PM | Mindanao Grid-01/06/2024 20:19: Pulangi 4 U1 Online at 1932H. Unplanned Outage. [WEBSMS] | CMIN
1/6/2024 8:14:14 PM | Mindanao Grid-01/06/2024 20:18: Pulangi 4 U2 manually shutdown at 1935H, due to Low Water Elevation. Unplanned Outage. [WEBSMS] | CMIN
1/6/2024 7:06:54 PM | Mindanao Grid-01/06/2024 19:10: Mati Diesel (MDP) with 3.0MW gross generation tripped again at 1859H. Indication: Overcurrent. Unplanned Outage. [WEBSMS] | CMIN
1/6/2024 7:01:53 PM | Mindanao Grid-01/06/2024 19:05: Mati Diesel (MDP) with 3.3MW gross generation tripped at 1847H. Indication: Overcurrent. Unplanned Outage. [WEBSMS] | CMIN
1/6/2024 6:38:25 PM | Mindanao Grid-01/06/2024 18:42: Peak Power Bukidnon Online at 1755H. SO Dispatched/MOT Constraint ON. [WEBSMS] | CMIN
1/6/2024 6:33:31 PM | Mindanao Grid-01/06/2024 18:37: Minergy ME2 (WARTSILA) Online at 1737H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/6/2024 6:30:09 PM | Mindanao Grid-01/06/2024 18:34: Peak Power San Frans Online at 1725H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/6/2024 6:09:20 PM | [NSO Update] Mindanao Grid-01/06/2024 18:13: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3022MW, PK=2114MW, RR=72MW, NetOpMargin: EVE=836 Highest Unit O/L: GNPK 1, 2, & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @70MW, AG2 @76MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
1/6/2024 6:08:09 PM | [NSO Update] Visayas Grid-01/06/2024 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2612MW, PK=2244MW, RR=84MW, NetOpMargin: EVE=284 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @326MW, PGPP1 @76MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
1/6/2024 6:06:40 PM | [NSO Update] Luzon Grid-01/06/2024 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11840MW, PK=9980MW, RR=388MW, NetOpMargin: EVE=1472 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @140MW, SLPGC 2 @92MW [WEBSMS] | CLUZ
1/6/2024 5:13:26 PM | Luzon Grid-01/06/2024 17:13: Sual 1 with 350MW tripped at 1709H. Lowest system frequency was 59.214Hz. (Unplanned Outage) [WEBSMS] | CLUZ
1/6/2024 3:33:12 PM | Mindanao Grid-01/06/2024 15:37: WMPC DG10 shutdown at 1514H from RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/6/2024 3:32:20 PM | Mindanao Grid-01/06/2024 15:36: Sibulan B U1 online at 0915H. Unplanned Outage. [WEBSMS] | CMIN
1/6/2024 12:56:05 PM | [NSO Update] Luzon Grid-01/06/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13391MW, PK=9593MW, RR=393MW, NetOpMargin: PM=3405, EVE=2372 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, SLPGC 1 @ 140MW, SLPGC 2 @ 92MW [WEBSMS] | CLUZ
1/6/2024 12:52:51 PM | [NSO Update] Mindanao Grid-01/06/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3076MW, PK=2023MW, RR=72MW, NetOpMargin: PM=981, EVE=826 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @70MW, AG2 @76MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
1/6/2024 12:51:26 PM | [NSO Update] Visayas Grid-01/06/2024 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2521MW, PK=2084MW, RR=84MW, NetOpMargin: PM=353, EVE=251 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 324MW, PGPP1 @ 76MW, TPC Carmen @ 30.3MW [WEBSMS] | CVIS
1/6/2024 12:21:45 PM | Mindanao Grid-01/06/2024 12:25: Manolo Fortich - Maramag 138KV LIne re-energized at 1218H (Planned Outage) [WEBSMS] | CMIN
1/6/2024 11:03:31 AM | Mindanao Grid-01/06/2024 11:07: Sibulan B U1 online at 0915H. Unplanned Outage. [WEBSMS] | CMIN
1/6/2024 9:59:11 AM | Mindanao Grid-01/06/2024 10:03: WMPC DG10 online at 0954H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/6/2024 9:33:13 AM | Mindanao Grid-01/06/2024 09:37: Tudaya 2 U1 online at 0923H. Unplanned Outage. [WEBSMS] | CMIN
1/6/2024 9:31:10 AM | Mindanao Grid-01/06/2024 09:35: Tudaya 2 U1 with 4MW gross generation manually shutdown at 0830H, due to Insufficient Water Supply (IWS). Unplanned Outage. [WEBSMS] | CMIN
1/6/2024 9:28:54 AM | Mindanao Grid-01/06/2024 09:32: Sibulan B U1 with 10MW gross generation tripped at 0828H, Indication: Common System Problem. Unplanned Outage. [WEBSMS] | CMIN
1/6/2024 8:44:24 AM | Mindanao Grid-01/06/2024 08:48: Erratum: Manolo Fortich - Maramag 138KV Line 1 shutdown at 0805H (Planned Outage) [WEBSMS] | CMIN
1/6/2024 8:23:33 AM | Mindanao Grid-01/06/2024 08:27: Manolo Fortich - Maramag 138KV Line 1 shutdown at 0802H (Planned Outage) [WEBSMS] | CMIN
1/6/2024 8:20:30 AM | Luzon Grid-01/06/2024 08:20: For info: Sta Rita and San Lorenzo 230kV Busses were looped at 0817H. [WEBSMS] | CLUZ
1/6/2024 8:18:04 AM | Luzon Grid-01/06/2024 08:18: For info: Batangas 300MVA T04 and T05 were un-looped at 0810H in the 69kV side in preparation for the looping of Sta Rita and San Lorenzo 230kV Busses. [WEBSMS] | CLUZ
1/6/2024 5:42:12 AM | [NSO Update] Mindanao Grid-01/06/2024 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3080MW, PK=2085MW, RR=70MW, NetOpMargin: AM=925, PM=881, EVE=791 Highest Unit O/L: GNPK 1,2 & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @70MW, AG2 @76MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
1/6/2024 5:40:52 AM | [NSO Update] Visayas Grid-01/06/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2491MW, PK=2082MW, RR=82MW, NetOpMargin: AM=328, PM=276, EVE=266 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @324MW, PGPP1 @76MW [WEBSMS] | CVIS
1/6/2024 5:38:53 AM | [NSO Update] Luzon Grid-01/06/2024 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13253MW, PK=9615MW, RR=324MW, NetOpMargin: AM=3314, PM=3170, EVE=2128 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @140MW, SLPGC 2 @92MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/6/2024 4:14:32 AM | [NSO Update] Mindanao Grid-01/06/2024 04:18: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CMIN
1/6/2024 4:14:11 AM | [NSO Update] Visayas Grid-01/06/2024 04:14: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CVIS
1/6/2024 4:14:04 AM | [NSO Update] Luzon Grid-01/06/2024 04:14: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CLUZ
1/6/2024 12:51:24 AM | Luzon Grid-01/06/2024 00:51: Sta. Rita 20 shutdown at 0050H (Unplanned Outage) [WEBSMS] | CLUZ
1/6/2024 12:46:38 AM | Luzon Grid-01/06/2024 00:46: Pagbilao 3 shutdown at 0046H (Planned Outage) [WEBSMS] | CLUZ
1/5/2024 11:46:24 PM | Luzon Grid-01/05/2024 23:46: Sta Rita Module 10 shutdown at 2345H (Unplanned Outage). [WEBSMS] | CLUZ
1/5/2024 9:37:08 PM | Mindanao Grid-01/05/2024 21:41: WMPC DG10 shutdown at 2121H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
1/5/2024 9:22:52 PM | Mindanao Grid-01/05/2024 21:26: NACSUR shutdown at 2105H. MO Dispatched. [WEBSMS] | CMIN
1/5/2024 8:34:40 PM | Mindanao Grid-01/05/2024 20:38: TSI Unit 1 and 2 change setting at 2001H from APC ON/ Free Governor-OFF to APC OFF/ Free Governor-ON. AS-CR replacement for TMI 1 unit 1. [WEBSMS] | CMIN
1/5/2024 7:32:31 PM | Luzon Grid-01/05/2024 19:32: Ilijan GT 2-2 shutdown at 1931H (Unplanned Outage) [WEBSMS] | CLUZ
1/5/2024 6:03:58 PM | [NSO Update] Visayas Grid-01/05/2024 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2615MW, PK=2296MW, RR=97MW, NetOpMargin: EVE=222 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @324MW, PGPP1 @76MW [WEBSMS] | CVIS
1/5/2024 6:03:02 PM | Mindanao Grid-01/05/2024 18:06: WMPC DG04 online at 1725H. MO Dispatched. [WEBSMS] | CMIN
1/5/2024 5:51:51 PM | Visayas Grid-01/05/2024 17:51: Magdugo 230 KV Bus 1 energized at 1748H. (Planned Outage) [WEBSMS] | CVIS
1/5/2024 5:41:31 PM | [NSO Update] Mindanao Grid-01/05/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2987MW, PK=2313MW, RR=72MW, NetOpMargin: EVE=602 Highest Unit O/L: GNPK 1,2 & 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @70MW, AG2 @76MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @25MW, PG4 @90MW [WEBSMS] | CMIN
1/5/2024 5:39:15 PM | [NSO Update] Luzon Grid-01/05/2024 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13202MW, PK=10157MW, RR=406MW, NetOpMargin: EVE=2639 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @140MW, ILIJAN B @180MW [WEBSMS] | CLUZ
1/5/2024 5:28:43 PM | Luzon Grid-01/05/2024 17:28: Ilijan GT 2-2 online at 1724H (Unplanned Outage) [WEBSMS] | CLUZ
1/5/2024 4:45:36 PM | Mindanao Grid-01/05/2024 16:49: WMPC DG04 shutdown at 1639H. MO Dispatched. [WEBSMS] | CMIN
1/5/2024 4:44:29 PM | Mindanao Grid-01/05/2024 16:48: WMPC shutdown at 1639H. MO Dispatched. [WEBSMS] | CMIN
1/5/2024 4:42:29 PM | Mindanao Grid-01/05/2024 16:46: WMPC DG08 shutdown at 1637H. MO Dispatched. [WEBSMS] | CMIN
1/5/2024 4:33:52 PM | Mindanao Grid-01/05/2024 16:37: WMPC DG01 shutdown at 1630H. MO Dispatched. [WEBSMS] | CMIN
1/5/2024 4:14:25 PM | Mindanao Grid-01/05/2024 16:18: WMPC DG04 RPS dispatched ends at 1600H, but continue running for MO dispatched of 10.2MW for interval 1605H onwards. Follow RTD. [WEBSMS] | CMIN
1/5/2024 3:58:56 PM | Mindanao Grid-01/05/2024 16:02: AGUS 1 Unit 1 online at 1547H. Extended APMS (GOMP). (Unplanned Outage). [WEBSMS] | CMIN
1/5/2024 3:03:00 PM | Mindanao Grid-01/05/2024 15:06: Lugait-Opol 138kV L energized at 1453H. After completed hotspot correction. [WEBSMS] | CMIN
1/5/2024 2:12:03 PM | Mindanao Grid-01/05/2024 14:16: Lugait-Opol 138kV L deenergized at 1337H. Emergency shutdown to facilitate hotspot correction. [WEBSMS] | CMIN
1/5/2024 1:35:48 PM | Mindanao Grid-01/05/2024 13:39: Peak Power San Francisco shutdown at 1332H. MO dispatch / Follow RTD. [WEBSMS] | CMIN
1/5/2024 1:33:12 PM | Mindanao Grid-01/05/2024 13:37: Peak Power San Francisco online at 1311H. MO Dispatch / Follow RTD. [WEBSMS] | CMIN
1/5/2024 1:29:06 PM | Mindanao Grid-01/05/2024 13:33: Update: WMPC DG08 online at 1307 not DG07. MO Dispatch / follow RTD. [WEBSMS] | CMIN
1/5/2024 1:26:27 PM | [NSO Update] Mindanao Grid-01/05/2024 13:30: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2989MW, PK=2337MW, RR=72MW, NetOpMargin: PM=579, EVE=587 Highest Unit O/L: GNPK 1, 2, and 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @35MW, AG2 @76MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
1/5/2024 1:23:07 PM | Mindanao Grid-01/05/2024 13:27: WMPC DG01 online 1317H. MO Dispatch / follow RTD. [WEBSMS] | CMIN
1/5/2024 1:22:05 PM | [NSO Update] Visayas Grid-01/05/2024 13:22: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2598MW, PK=2210MW, RR=93MW, NetOpMargin: PM=295, EVE=286 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @324MW, PGPP1 @76MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
1/5/2024 1:18:48 PM | [NSO Update] Luzon Grid-01/05/2024 13:18: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14009MW, PK=10371MW, RR=422MW, NetOpMargin: PM=3215, EVE=2583 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @140MW, ILIJAN A @555MW, ILIJAN B @180MW [WEBSMS] | CLUZ
1/5/2024 1:14:25 PM | Mindanao Grid-01/05/2024 13:18: WMPC DG07 online. MO Dispatch / follow RTD. [WEBSMS] | CMIN
1/5/2024 1:12:28 PM | Mindanao Grid-01/05/2024 13:16: KEGI TANDAG online at 1301H. MO dispatch (RTD). [WEBSMS] | CMIN
1/5/2024 1:05:31 PM | Mindanao Grid-01/05/2024 13:09: NACSUR Online at 1300H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/5/2024 1:02:52 PM | [NSO Update] Visayas Grid-01/05/2024 13:02: SO-initiated Market Intervention for Visayas has been lifted today at 1234H. Market operations will resume starting interval 1240H. [WEBSMS] | CVIS
1/5/2024 11:45:27 AM | Visayas Grid-01/05/2024 11:45: Panay Subgrid as of 1127H on process to full restoration. [WEBSMS] | CVIS
1/5/2024 10:53:30 AM | Mindanao Grid-01/05/2024 10:57: WMPC DG04 online at 1050H, RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/5/2024 10:38:44 AM | Mindanao Grid-01/05/2024 10:42: SUPREME POWER Mati online at 1020H. MO Dispatched. [WEBSMS] | CMIN
1/5/2024 10:37:16 AM | Mindanao Grid-01/05/2024 10:41: SUPREME POWER Mati tripped with 3MW load at 1005H. Indication: Reverse Power Trip. (Unplanned Outage) [WEBSMS] | CMIN
1/5/2024 10:02:42 AM | Mindanao Grid-01/05/2024 10:06: SUPREME POWER Mati online at 1001H. MO Dispatched. [WEBSMS] | CMIN
1/5/2024 9:32:47 AM | Mindanao Grid-01/05/2024 09:36: TSI Unit 1 and 2 change setting at 0901H from APC OFF/ Free Governor-ON to APC ON/ Free Governor-OFF. AS-CR back to TMI 1 unit 1. [WEBSMS] | CMIN
1/5/2024 9:28:29 AM | Mindanao Grid-01/05/2024 09:32: TMI 1 declared available for CR at at 0901H. Unplanned Outage. [WEBSMS] | CMIN
1/5/2024 9:25:53 AM | Mindanao Grid-01/05/2024 09:29: WMPC DG10 online at 0850H, RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/5/2024 9:12:03 AM | Visayas Grid-01/05/2024 09:12: Magdugo SS 230KV Bus 1 de-energized at 0841H. (Planned Outage) [WEBSMS] | CVIS
1/5/2024 6:59:07 AM | Mindanao Grid-01/05/2024 07:03: PULANGI 4 Unit 1 shutdown with 30MW load at 0639H. Reason: Low forebay elevation. Unplanned Outage. [WEBSMS] | CMIN
1/5/2024 6:05:05 AM | [NSO Update] Visayas Grid-01/05/2024 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2353MW, PK=2066MW, RR=93MW, NetOpMargin: AM=194, PM=251, EVE=254 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @324MW, PCPC @120MW, PGPP1 @76MW, [WEBSMS] | CVIS
1/5/2024 5:56:27 AM | [NSO Update] Mindanao Grid-01/05/2024 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3058MW, PK=2168MW, RR=70MW, NetOpMargin: AM=820, PM=705, EVE=629 Highest Unit O/L: GNPK 1,2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @35MW, AG2 @76MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
1/5/2024 5:52:46 AM | [NSO Update] Luzon Grid-01/05/2024 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13696MW, PK=10594MW, RR=416MW, NetOpMargin: AM=2686, PM=2488, EVE=1729 Highest Unit O/L: GNPD 1& 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, SLPGC 1 @ 135MW, Ilijan A @ 555MW, Ilijan B @ 180MW [WEBSMS] | CLUZ
1/5/2024 4:11:40 AM | [NSO Update] Luzon Grid-01/05/2024 04:11: Weather Advisory: Northeast Monsoon affecting Luzon. Easterlies affecting Visayas and Mindanao. [WEBSMS] | CLUZ
1/5/2024 4:10:48 AM | [NSO Update] Mindanao Grid-01/05/2024 04:14: Weather Advisory: Northeast Monsoon affecting Luzon. Easterlies affecting Visayas and Mindanao. [WEBSMS] | CMIN
1/5/2024 4:10:43 AM | [NSO Update] Visayas Grid-01/05/2024 04:10: Weather Advisory: Northeast Monsoon affecting Luzon. Easterlies affecting Visayas and Mindanao. [WEBSMS] | CVIS
1/4/2024 10:13:04 PM | Mindanao Grid-01/04/2024 22:17: TM2 Unit#1 shutdown at 2150H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/4/2024 10:11:36 PM | Mindanao Grid-01/04/2024 22:15: WMPC DG08 shutdown at 2122H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/4/2024 10:10:33 PM | Mindanao Grid-01/04/2024 22:14: WMPC DG05 shutdown at 2123H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/4/2024 10:04:37 PM | Mindanao Grid-01/04/2024 22:08: TM1 U2 shutdown at 2134H from MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/4/2024 9:52:20 PM | Mindanao Grid-01/04/2024 21:56: GNPK U4 online at 2143H. (Unplanned Outage). [WEBSMS] | CMIN
1/4/2024 9:51:25 PM | Mindanao Grid-01/04/2024 21:55: Maco SS 100MVA T1 restored at 2139H with clearance from MTD-B & D5 Manager. (Unplanned Outage) [WEBSMS] | CMIN
1/4/2024 7:43:57 PM | Mindanao Grid-01/04/2024 19:47: Mati Diesel with 3.0MW gross generation tripped at 1754H. Indication: Reversed Power. Unplanned Outage. [WEBSMS] | CMIN
1/4/2024 7:08:52 PM | Mindanao Grid-01/04/2024 19:12: TM1 U2 online at 1709H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/4/2024 6:48:56 PM | Mindanao Grid-01/04/2024 18:52: Maco SS 100MVA T1 tripped at 1751H. Unplanned Outage. [WEBSMS] | CMIN
1/4/2024 5:59:56 PM | [NSO Update] Visayas Grid-01/04/2024 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2433MW, PK=2110MW, RR=97MW, NetOpMargin: EVE=226 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 320MW, PGPP1 @ 76MW, TPC Carmen @ 20MW Note: Loads in Panay not yet fully restored. Full load restoration can be achieved upon availability of PCPC. [WEBSMS] | CVIS
1/4/2024 5:49:14 PM | [NSO Update] Mindanao Grid-01/04/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2849MW, PK=2287MW, RR=86MW, NetOpMargin: EVE=476 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @35MW, AG2 @76MW, AG4 @90MW, AG5 @28MW, AG6 @112MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
1/4/2024 5:29:35 PM | [NSO Update] Luzon Grid-01/04/2024 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12779MW, PK=10415MW, RR=393MW, NetOpMargin: EVE=1971 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, SLPGC 1 @ 105MW, Ilijan A @ 555MW, Ilijan B @ 180MW, GNPD 1@550MW, Masinloc 3 @300MW [WEBSMS] | CLUZ
1/4/2024 4:18:21 PM | Mindanao Grid-01/04/2024 16:22: GNPK Unit 4 tripped at 1602H with gross generation of 151.0MW, with ALD. Lowest Frequency of 59.105Hz (Unplanned Outage). [WEBSMS] | CMIN
1/4/2024 3:09:08 PM | Luzon Grid-01/04/2024 15:09: Sta. Rita Module 20 online at 1507H (Planned Outage) [WEBSMS] | CLUZ
1/4/2024 3:02:07 PM | [NSO Update] Visayas Grid-01/04/2024 15:02: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1457H with power going to Visayas. [WEBSMS] | CVIS
1/4/2024 3:02:00 PM | [NSO Update] Mindanao Grid-01/04/2024 15:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1457H with power going to Visayas. [WEBSMS] | CMIN
1/4/2024 2:47:18 PM | [NSO Update] Visayas Grid-01/04/2024 14:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1434H from reverse power direction. [WEBSMS] | CVIS
1/4/2024 2:37:45 PM | [NSO Update] Mindanao Grid-01/04/2024 14:41: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1434H from reverse power direction. [WEBSMS] | CMIN
1/4/2024 1:41:20 PM | Mindanao Grid-01/04/2024 13:45: TM2 Unit#1 Online at 1327H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/4/2024 1:35:28 PM | Mindanao Grid-01/04/2024 13:39: WMPC DG08 online at 1308H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/4/2024 1:07:31 PM | [NSO Update] Mindanao Grid-01/04/2024 13:11: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3087MW, PK=2306MW, RR=88MW, NetOpMargin: PM=694, EVE=604 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @35MW, AG2 @76MW, AG4 @90MW, AG5 @28MW, AG6 @112MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
1/4/2024 1:02:45 PM | Mindanao Grid-01/04/2024 13:06: NACSUR Online at 1300H. MO Dispatched/Follow RTD. [WEBSMS] | CMIN
1/4/2024 1:02:19 PM | [NSO Update] Visayas Grid-01/04/2024 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2486MW, PK=2113MW, RR=93MW, NetOpMargin: PM=280, EVE=289 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 324MW, PGPP1 @ 76MW, TPC Carmen @ 30MW Note: Loads in Panay not yet fully restored. Full load restoration can be achieved upon availability of PCPC. [WEBSMS] | CVIS
1/4/2024 12:59:31 PM | Mindanao Grid-01/04/2024 13:03: Peak Power SOCCSARGEN (PBF) online at 1001H, SO dispatched for MOT constraint ON due to high system demand. Frequency=59.69Hz. RTD Variance RTD=1922/Actual=1937 [WEBSMS] | CMIN
1/4/2024 12:55:33 PM | [NSO Update] Luzon Grid-01/04/2024 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13449MW, PK=10792MW, RR=403MW, NetOpMargin: PM=2255, EVE=1828 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, SLPGC 1 @ 75MW, Ilijan A @ 555MW, Ilijan B @ 180MW [WEBSMS] | CLUZ
1/4/2024 12:54:51 PM | Mindanao Grid-01/04/2024 12:58: Peak Power San Frans U2 online at 0951h, SO dispatched for MOT constraint ON due to high system demand. Frequency=59.63Hz. RTD Variance RTD=2089/Actual=2109 [WEBSMS] | CMIN
1/4/2024 12:51:49 PM | Mindanao Grid-01/04/2024 12:55: Peak Power Bukidnon online at 0903h, SO dispatched for MOT constraint ON due to high system demand. Frequency=59.69Hz. RTD Variance RTD=1922/Actual=1937 [WEBSMS] | CMIN
1/4/2024 12:07:56 PM | Mindanao Grid-01/04/2024 12:11: GN Power Unit #4 Online at 1205H, Follow RTD. [WEBSMS] | CMIN
1/4/2024 11:08:36 AM | [NSO Update] Mindanao Grid-01/04/2024 11:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1040H with power going to Mindanao [WEBSMS] | CMIN
1/4/2024 11:08:06 AM | [NSO Update] Visayas Grid-01/04/2024 11:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1040H with power going to Mindanao [WEBSMS] | CVIS
1/4/2024 10:30:31 AM | [NSO Update] Mindanao Grid-01/04/2024 10:34: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1024H from forward power direction [WEBSMS] | CMIN
1/4/2024 10:29:11 AM | [NSO Update] Visayas Grid-01/04/2024 10:29: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1024H from forward power direction [WEBSMS] | CVIS
1/4/2024 9:34:18 AM | Mindanao Grid-01/04/2024 09:38: WMPC DG10 online at 0856H, RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/4/2024 7:01:10 AM | Visayas Grid-01/04/2024 07:01: KSPC U1 emergency shutdown at 0653H due to boiler tube leak. (Unplanned Outage) [WEBSMS] | CVIS
1/4/2024 5:54:11 AM | [NSO Update] Mindanao Grid-01/04/2024 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3239MW, PK=2288MW, RR=87MW, NetOpMargin: AM=864, PM=873, EVE=868 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @35MW, AG2 @76MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
1/4/2024 5:53:17 AM | [NSO Update] Visayas Grid-01/04/2024 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2512MW, PK=2104MW, RR=93MW, NetOpMargin: AM=315, PM=344, EVE=318 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 324MW, PGPP1 @ 76MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
1/4/2024 5:51:23 AM | [NSO Update] Luzon Grid-01/04/2024 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13735MW, PK=10329MW, RR=404MW, NetOpMargin: AM=3003, PM=2759, EVE=2196 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 555MW, Ilijan B @ 180MW [WEBSMS] | CLUZ
1/4/2024 4:04:47 AM | [NSO Update] Mindanao Grid-01/04/2024 04:08: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
1/4/2024 4:04:32 AM | [NSO Update] Visayas Grid-01/04/2024 04:04: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
1/4/2024 4:04:06 AM | [NSO Update] Luzon Grid-01/04/2024 04:04: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
1/3/2024 11:32:01 PM | Mindanao Grid-01/03/2024 23:36: WMPC DG05 shutdown at 1907H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 11:31:19 PM | Mindanao Grid-01/03/2024 23:35: WMPC DG04 shutdown at 1856H. End of MO dispatch/ MOT Raise. [WEBSMS] | CMIN
1/3/2024 11:30:09 PM | Mindanao Grid-01/03/2024 23:34: WMPC DG05 online at 1800H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 11:29:21 PM | Mindanao Grid-01/03/2024 23:33: WMPC DG05 online at 1750H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 11:05:58 PM | Luzon Grid-01/03/2024 23:06: SLPGC Unit1 online at 2302H (Unplanned Outage) [WEBSMS] | CLUZ
1/3/2024 10:58:17 PM | Mindanao Grid-01/03/2024 23:02: MINERGY WARTSILA shutdown at 2048H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 9:34:50 PM | Luzon Grid-01/03/2024 21:35: Ilijan ST 2 online at 2132H (Unplanned Outage) [WEBSMS] | CLUZ
1/3/2024 9:31:36 PM | Mindanao Grid-01/03/2024 21:35: PEAK POWER SAN FRANCISCO Unit 2 shutdown at 1805H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 9:29:59 PM | Mindanao Grid-01/03/2024 21:34: WMPC DG08 shutdown at 2119H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 9:19:17 PM | Mindanao Grid-01/03/2024 21:23: WMPC DG10 shutdown at 2115H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
1/3/2024 9:17:43 PM | Mindanao Grid-01/03/2024 21:21: PEAK POWER SAN FRANCISCO Unit 2 shutdown at 2112H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 9:16:11 PM | Mindanao Grid-01/03/2024 21:20: NACSUR shutdown at 2100H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 9:15:07 PM | Mindanao Grid-01/03/2024 21:19: PEAK POWER SAN FRANCISCO Unit 2 online at 2059H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 9:08:06 PM | Mindanao Grid-01/03/2024 21:12: PEAK POWER BUKIDNON shutdown at 2044H. End of SO dispatch (MOT Raise). [WEBSMS] | CMIN
1/3/2024 8:59:45 PM | Mindanao Grid-01/03/2024 21:03: PEAK POWER SAN FRANCISCO Unit 2 shutdown at 2044H. End of SO dispatch (MOT Raise). [WEBSMS] | CMIN
1/3/2024 8:36:24 PM | Mindanao Grid-01/03/2024 20:40: SUPREEME POWER Mati online at 1819H (Unplanned Outage) [WEBSMS] | CMIN
1/3/2024 8:35:51 PM | Mindanao Grid-01/03/2024 20:40: SUPREME POWER Mati tripped with 3MW load at 1815H. Indication: Reverse Power Trip (Unplanned Outage) [WEBSMS] | CMIN
1/3/2024 8:34:18 PM | Mindanao Grid-01/03/2024 20:38: KEGI TANDAG shutdown at 1710H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 8:33:35 PM | Mindanao Grid-01/03/2024 20:37: (Correction) TM1 Unit 2 shutdown at 1817H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 8:32:36 PM | Mindanao Grid-01/03/2024 20:36: TM1shutdown at 1817H [WEBSMS] | CMIN
1/3/2024 8:29:40 PM | Luzon Grid-01/03/2024 20:29: Ilijan GT 2-1 online at 2026H (Unplanned Outage) [WEBSMS] | CLUZ
1/3/2024 8:14:31 PM | Mindanao Grid-01/03/2024 20:18: PEAK POWER BUKIDNON online at 2005H. SO dispatch (MOT Raise). [WEBSMS] | CMIN
1/3/2024 8:13:43 PM | Mindanao Grid-01/03/2024 20:17: PEAK POWER SAN FRANCISCO Unit 2 online at 2005H. SO dispatch (MOT Raise). [WEBSMS] | CMIN
1/3/2024 8:12:32 PM | Mindanao Grid-01/03/2024 20:16: TM2 Unit 1 shutdown at 1938H. End of MO dispatch/ MOT Raise. [WEBSMS] | CMIN
1/3/2024 8:10:59 PM | Mindanao Grid-01/03/2024 20:15: TM2 Unit 1 online at 1921H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 8:10:15 PM | Mindanao Grid-01/03/2024 20:14: TM2 Unit 2 shutdown at 1909H. End of MO dispatch/ MOT Raise. [WEBSMS] | CMIN
1/3/2024 7:09:10 PM | Mindanao Grid-01/03/2024 19:13: TM1 Unit 1 declared forced outage at 1901H due to HVAC issue. (Unplanned Outage) [WEBSMS] | CMIN
1/3/2024 6:16:24 PM | Visayas Grid-01/03/2024 18:16: 69KV Cadiz-San Carlos Emergency Load Drop @ 1814H with load of 9.7MW. [WEBSMS] | CVIS
1/3/2024 6:04:00 PM | Mindanao Grid-01/03/2024 18:08: PEAK POWER SAN FRANCISCO Unit 2 online at 1750H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 6:01:07 PM | Visayas Grid-01/03/2024 18:01: 69KV Mabinay - Bayawan Emergency Load Drop @ 1759H with load of 7.4MW. [WEBSMS] | CVIS
1/3/2024 5:58:26 PM | Mindanao Grid-01/03/2024 18:02: KEGI TANDAG online at 1746H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 5:57:52 PM | Visayas Grid-01/03/2024 17:58: 69KV Kabankalan-La Castellana Emergency Load Drop @1749H with load of 14.6MW. [WEBSMS] | CVIS
1/3/2024 5:54:21 PM | Mindanao Grid-01/03/2024 17:58: PEAK POWER SAN FRANCISCO Unit 1 on forced outage at 1510H. Failed to cut-in. Indication: Transformer differential (87T). (Unplanned Outage). [WEBSMS] | CMIN
1/3/2024 5:53:35 PM | [NSO Update] Luzon Grid-01/03/2024 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12504MW, PK=10472MW, RR=373MW, NetOpMargin: EVE=1659 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW [WEBSMS] | CLUZ
1/3/2024 5:50:27 PM | [NSO Update] Mindanao Grid-01/03/2024 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3009MW, PK=2263MW, RR=80MW, NetOpMargin: EVE=666 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @35MW, AG2 @76MW, AG4 @70MW, AG5 @28MW, AG6 @132MW, AG7 @25MW, PG4 @170MW [WEBSMS] | CMIN
1/3/2024 5:47:54 PM | Mindanao Grid-01/03/2024 17:52: PEAK POWER SAN FRANCISCO Unit 1 online at 1510H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 5:46:47 PM | [NSO Update] Visayas Grid-01/03/2024 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2473MW, PK=2105MW, RR=97MW, NetOpMargin: EVE=270 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @320MW, PGPP1 @76MW Note: Loads in Panay not yet fully restored. Full load restoration can be achieved upon availability of PCPC. [WEBSMS] | CVIS
1/3/2024 5:43:04 PM | Mindanao Grid-01/03/2024 17:47: NACSUR online at 1400H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 5:36:57 PM | Mindanao Grid-01/03/2024 17:41: WMPC DG01 declared available at 1700H. (Unplanned Outage) [WEBSMS] | CMIN
1/3/2024 5:33:53 PM | Mindanao Grid-01/03/2024 17:38: (Correction) WMPC DG01 tripped with 10.2MW load at 1335H. Indication: Oil mist high stop. (Unplanned Outage) [WEBSMS] | CMIN
1/3/2024 5:20:51 PM | Mindanao Grid-01/03/2024 17:25: WMPC DG08 shutdown at 1712H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 5:20:10 PM | Mindanao Grid-01/03/2024 17:24: WMPC DG05 shutdown at 1712H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 5:19:32 PM | Mindanao Grid-01/03/2024 17:23: WMPC DG04 shutdown at 1712H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 5:18:52 PM | Mindanao Grid-01/03/2024 17:23: WMPC DG02 shutdown at 1710H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 4:55:42 PM | Luzon Grid-01/03/2024 16:56: Angat HEPP 115kV Bus 2 energized at 1654H (Planned Outage) [WEBSMS] | CLUZ
1/3/2024 4:17:49 PM | Mindanao Grid-01/03/2024 16:22: WMPC DG08 end of RPS dispatch at 1600H. MO dispatch (RTD) as energy starting 1601H. [WEBSMS] | CMIN
1/3/2024 3:09:04 PM | Luzon Grid-01/03/2024 15:09: Ilijan GT 1-1 online at 1507H (Unplanned Outage) [WEBSMS] | CLUZ
1/3/2024 3:02:39 PM | Mindanao Grid-01/03/2024 15:06: TM1 Unit 2 online at 1457H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 2:49:03 PM | [NSO Update] Visayas Grid-01/03/2024 14:49: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1443H with power going to Visayas [WEBSMS] | CVIS
1/3/2024 2:48:29 PM | [NSO Update] Mindanao Grid-01/03/2024 14:52: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1443H with power going to Visayas [WEBSMS] | CMIN
1/3/2024 2:45:41 PM | [NSO Update] Mindanao Grid-01/03/2024 14:49: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1434H from reverse power direction [WEBSMS] | CMIN
1/3/2024 2:45:18 PM | [NSO Update] Visayas Grid-01/03/2024 14:45: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1434H from reverse power direction [WEBSMS] | CVIS
1/3/2024 2:15:43 PM | Mindanao Grid-01/03/2024 14:19: WMPC DG02 online at 1409H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 2:06:38 PM | Mindanao Grid-01/03/2024 14:10: STEAG Unit 1 online at 1348H (Unplanned Outage) [WEBSMS] | CMIN
1/3/2024 2:02:27 PM | Luzon Grid-01/03/2024 14:02: Ilijan ST 1-1 online at 1357H (Unplanned Outage) [WEBSMS] | CLUZ
1/3/2024 1:49:55 PM | Mindanao Grid-01/03/2024 13:54: WMPC DG04 online at 1348H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 1:39:23 PM | Mindanao Grid-01/03/2024 13:43: WMPC DG01 shutdown at 1335H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 1:33:51 PM | [NSO Update] Mindanao Grid-01/03/2024 13:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3008MW, PK=2218MW, RR=84MW, NetOpMargin: PM=706, EVE=606 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @35MW, AG2 @76MW, AG4 @70MW, AG5 @28MW, AG6 @132MW, AG7 @25MW, PG4 @170MW [WEBSMS] | CMIN
1/3/2024 1:31:10 PM | Mindanao Grid-01/03/2024 13:35: TM2 Unit 1 online at 1328H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 1:30:20 PM | Mindanao Grid-01/03/2024 13:34: WMPC DG05 online at 1324H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 1:29:42 PM | [NSO Update] Luzon Grid-01/03/2024 13:29: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12779MW, PK=10703MW, RR=368MW, NetOpMargin: PM=1708, EVE=1345 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW [WEBSMS] | CLUZ
1/3/2024 1:23:35 PM | Mindanao Grid-01/03/2024 13:27: MINERGY WARTSILA online at 1305H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 1:22:50 PM | Mindanao Grid-01/03/2024 13:27: WMPC DG01 online at 1305H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 1:22:10 PM | Mindanao Grid-01/03/2024 13:26: KEGI TANDAG online at 1305H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 1:21:27 PM | Mindanao Grid-01/03/2024 13:25: PEAK POWER SAN FRANCISCO Unit 2 online at 1302H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 1:03:36 PM | [NSO Update] Visayas Grid-01/03/2024 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2454MW, PK=1973MW, RR=93MW, NetOpMargin: PM=388, EVE=402 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @320MW, PGPP1 @76MW. Note: Loads in Panay not yet fully restored. Full load restoration can be achieved upon availability of PCPC. [WEBSMS] | CVIS
1/3/2024 12:56:57 PM | Luzon Grid-01/03/2024 12:57: Ilijan A GT1-2 online at 1255H. (Unplanned Outage) [WEBSMS] | CLUZ
1/3/2024 12:29:54 PM | Luzon Grid-01/03/2024 12:30: Santiago - NIA Baligatan tripped at 1225H. (Unplanned Outage) [WEBSMS] | CLUZ
1/3/2024 12:11:22 PM | Mindanao Grid-01/03/2024 12:15: SUPREME POWER Mati online at 1156H (Unplanned Outage) [WEBSMS] | CMIN
1/3/2024 12:09:12 PM | Mindanao Grid-01/03/2024 12:13: SUPREME POWER Mati tripped with 3MW load at 1153H. Indication: Reverse Power Trip. (Unplanned Outage) [WEBSMS] | CMIN
1/3/2024 11:32:00 AM | Mindanao Grid-01/03/2024 11:36: PEAK POWER SAN FRANCISCO Unit 2 shutdown at 1130H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 11:26:35 AM | Mindanao Grid-01/03/2024 11:30: PEAK POWER SAN FRANCISCO Unit 2 online at 1125H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 11:08:43 AM | Mindanao Grid-01/03/2024 11:12: PEAK POWER SAN FRANCISCO Unit 2 shutdown at 1032H. End of MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 11:07:12 AM | Mindanao Grid-01/03/2024 11:11: WMPC DG08 dispatched as RPS at 1051H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
1/3/2024 11:03:41 AM | Mindanao Grid-01/03/2024 11:07: WMPC DG08 online at 1036H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 11:02:56 AM | Mindanao Grid-01/03/2024 11:07: PEAK POWER SAN FRANCISCO Unit 2 online at 1020H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 10:28:53 AM | [NSO Update] Mindanao Grid-01/03/2024 10:33: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1006H with power going to Mindanao [WEBSMS] | CMIN
1/3/2024 10:13:26 AM | [NSO Update] Visayas Grid-01/03/2024 10:13: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1006H with power going to Mindanao [WEBSMS] | CVIS
1/3/2024 10:09:06 AM | [NSO Update] Mindanao Grid-01/03/2024 10:13: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0957H from forward power direction [WEBSMS] | CMIN
1/3/2024 10:06:59 AM | [NSO Update] Visayas Grid-01/03/2024 10:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0957H from forward power direction [WEBSMS] | CVIS
1/3/2024 10:04:16 AM | Mindanao Grid-01/03/2024 10:08: SUPREME POWER Mati online at 1003H. MO dispatch (RTD). [WEBSMS] | CMIN
1/3/2024 9:02:52 AM | Mindanao Grid-01/03/2024 09:07: TM1 Unit 1 declared available at 0901H. [WEBSMS] | CMIN
1/3/2024 8:55:04 AM | Mindanao Grid-01/03/2024 08:59: WMPC DG10 online at 0850H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
1/3/2024 6:47:18 AM | Luzon Grid-01/03/2024 06:47: Affected ALD feeders of MERALCO and NGCP restored at 0636H and 0639H, respectively. [WEBSMS] | CLUZ
1/3/2024 6:35:43 AM | Luzon Grid-01/03/2024 06:36: Update: ALD occurred at NGCP and MERALCO feeders at 0624H due to tripping of Ilijan GT1-2, ST-1, GT2-1, GT2-2 and ST-2 with approximately 932MW load. Lowest system frequency is 58.931Hz. [WEBSMS] | CLUZ
1/3/2024 6:31:12 AM | Luzon Grid-01/03/2024 06:31: ALD occurred at NGCP and MERALCO feeders at 0624H due to tripping of Ilijan GT1-2, ST-1, GT2-1, GT2-2 and ST-2. Lowest system frequency is 58.931Hz. [WEBSMS] | CLUZ
1/3/2024 6:25:19 AM | Luzon Grid-01/03/2024 06:25: Ilijan GT 1-1 tripped at 0623H. (Unplanned Outage) [WEBSMS] | CLUZ
1/3/2024 6:19:59 AM | [NSO Update] Visayas Grid-01/03/2024 06:20: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2353MW, PK=1992MW, RR=93MW, NetOpMargin: AM=268, PM=282, EVE=251 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @320MW, PGPP1 @76MW [WEBSMS] | CVIS
1/3/2024 5:49:49 AM | [NSO Update] Mindanao Grid-01/03/2024 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2972MW, PK=2116MW, RR=80MW, NetOpMargin: AM=776, PM=734, EVE=779 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @48MW, AG1 @35MW, AG2 @76MW, AG4 @70MW, AG5 @28MW, AG6 @132MW, AG7 @25MW, PG4 @170MW [WEBSMS] | CMIN
1/3/2024 5:46:57 AM | [NSO Update] Luzon Grid-01/03/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13928MW, PK=9794MW, RR=374MW, NetOpMargin: AM=3760, PM=3631, EVE=3136 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW [WEBSMS] | CLUZ
1/3/2024 5:24:20 AM | Mindanao Grid-01/03/2024 05:28: Tudaya 2 Unit 2 with 0.9MW gross generation tripped at 0411H, due to insufficient water supply (IWS). Unplanned Outage. [WEBSMS] | CMIN
1/3/2024 5:13:22 AM | Luzon Grid-01/03/2024 05:13: Ilijan GT1-1 online at 0511H (Unplanned Outage) [WEBSMS] | CLUZ
1/3/2024 4:13:14 AM | [NSO Update] Luzon Grid-01/03/2024 04:13: Weather Advisory: Northeast Monsoon affecting Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
1/3/2024 4:12:44 AM | [NSO Update] Mindanao Grid-01/03/2024 04:16: Weather Advisory: Northeast Monsoon affecting Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
1/3/2024 4:12:26 AM | [NSO Update] Visayas Grid-01/03/2024 04:12: Weather Advisory: Northeast Monsoon affecting Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
1/2/2024 9:28:28 PM | Mindanao Grid-01/02/2024 21:32: WMPC DG10 shutdown at 2122H, from RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/2/2024 9:21:13 PM | [NSO Update] Visayas Grid-01/02/2024 21:21: The Yellow Alert Notice issued for the Visayas Grid today, January 2, 2024, has been lifted effective 2101H [WEBSMS] | CVIS
1/2/2024 6:47:08 PM | Mindanao Grid-01/02/2024 18:51: ASIGA HEPP online at 1808H. Unplanned Outage. [WEBSMS] | CMIN
1/2/2024 6:45:29 PM | Mindanao Grid-01/02/2024 18:49: ASIGA HEPP with 8.12MW gross generation tripped at 1743H. Indication: Restricted Earth Fault (REF). Frequency Dipped=59.67Hz. Unplanned Outage. [WEBSMS] | CMIN
1/2/2024 5:58:29 PM | [NSO Update] Visayas Grid-01/02/2024 17:58: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=2223MW, PK=2001MW, RR=91MW, NetOpMargin: EVE=132 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @305MW, PGPP1 @76MW [WEBSMS] | CVIS
1/2/2024 5:42:59 PM | [NSO Update] Luzon Grid-01/02/2024 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12609MW, PK=9315MW, RR=336MW, NetOpMargin: EVE=2958 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @165MW, ILIJAN B @570MW [WEBSMS] | CLUZ
1/2/2024 5:31:01 PM | [NSO Update] Mindanao Grid-01/02/2024 17:35: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2936MW, PK=1961MW, RR=84MW, NetOpMargin: EVE=891 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @70MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
1/2/2024 4:16:36 PM | Mindanao Grid-01/02/2024 16:20: WMPC DG08 shutdown at 1613H, from RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/2/2024 3:35:37 PM | Visayas Grid-01/02/2024 15:35: Correction: Panay plants, PCPC, PEDC u# 2, PB 101, PDPP3 & Nabas auto tripped @1419H unplanned outage. [WEBSMS] | CVIS
1/2/2024 3:33:02 PM | [NSO Update] Visayas Grid-01/02/2024 15:33: Yellow Alert Notice issued for Visayas today, 02-Jan, for intervals 1600H-2100H. FO: SCBP @19.5MW, HPC1 @2MW, VMC1 @2.5MW, VMC2 @21.5MW, SCBI @7.4MW, NNBP @25MW, SNBP @25MW, CABI @4.7MW, CASA @15MW, FFHC @21MW, HPC2 @9.5MW, PEDCU1 @83.7MW, PEDCU2 @83.7MW, PCPC @135MW, PDPP3 @50MW, PDPP1 @15MW, URC @20MW, (Total: 570.5MW). De-rated: LeyteA @318MW, PGPP1 @76MW, TPC Carmen @20.3MW, (Total: 231.3MW) [WEBSMS] | CVIS
1/2/2024 3:19:37 PM | Visayas Grid-01/02/2024 15:19: Total tripping of Panay grid @ 1507H. ( Unplanned Outage ) [WEBSMS] | CVIS
1/2/2024 3:16:04 PM | [NSO Update] Visayas Grid-01/02/2024 15:16: SO initiated Market Intervention for Visayas is issued today starting interval 1510H due to partial blackout at Panay sub-grid [WEBSMS] | CVIS
1/2/2024 3:11:04 PM | Visayas Grid-01/02/2024 15:11: Total tripping of Negros Panay grid at 1507H.(Unplanned Outage) [WEBSMS] | CVIS
1/2/2024 2:27:17 PM | Visayas Grid-01/02/2024 14:27: Panay plants, CPPC, PEDC u# 2 auto tripped @1419H unplanned outage. [WEBSMS] | CVIS
1/2/2024 1:58:54 PM | Luzon Grid-01/02/2024 13:59: Ilijan GT2-2 online at 1354H (Unplanned Outage) [WEBSMS] | CLUZ
1/2/2024 12:54:17 PM | [NSO Update] Mindanao Grid-01/02/2024 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2985MW, PK=1945MW, RR=83MW, NetOpMargin: PM=957, EVE=922 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @70MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
1/2/2024 12:50:28 PM | [NSO Update] Visayas Grid-01/02/2024 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2603MW, PK=2156MW, RR=94MW, NetOpMargin: PM=353, EVE=268 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @318MW, PGPP1 @76MW, TPC (Carmen) @28MW [WEBSMS] | CVIS
1/2/2024 12:47:06 PM | [NSO Update] Luzon Grid-01/02/2024 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13474MW, PK=9785MW, RR=312MW, NetOpMargin: PM=3404, EVE=2918 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @295MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/2/2024 11:19:12 AM | Mindanao Grid-01/02/2024 11:23: WMPC DG08 online at 1048H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/2/2024 9:03:28 AM | Mindanao Grid-01/02/2024 09:07: Agus 5 Unit #2 online at 0807H. Unplanned Outage. [WEBSMS] | CMIN
1/2/2024 8:58:23 AM | Mindanao Grid-01/02/2024 09:02: WMPC DG10 online at 0852H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
1/2/2024 8:14:55 AM | Mindanao Grid-01/02/2024 08:19: Agus 5 Unit #2 with 3.6MW gross generation on Emergency Shutdown at 0749H due to gate limit problem. unplanned outage. [WEBSMS] | CMIN
1/2/2024 6:10:38 AM | Mindanao Grid-01/02/2024 06:14: Agus 5-Aurora 138kV line restored at 0608H from unplanned outage. [WEBSMS] | CMIN
1/2/2024 5:59:42 AM | [NSO Update] Luzon Grid-01/02/2024 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13550MW, PK=8872MW, RR=307MW, NetOpMargin: AM=4371, PM=3684, EVE=3292 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @295MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/2/2024 5:43:04 AM | [NSO Update] Mindanao Grid-01/02/2024 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3089MW, PK=1937MW, RR=79MW, NetOpMargin: AM=1072, PM=1054, EVE=891 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @70MW, AG4 @90MW, AG5 @28MW, AG6 @112MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
1/2/2024 5:41:49 AM | [NSO Update] Visayas Grid-01/02/2024 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2592MW, PK=2053MW, RR=89MW, NetOpMargin: AM=451, PM=250, EVE=252 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @318MW, PGPP1 @76MW, TPC (Carmen) @28MW [WEBSMS] | CVIS
1/2/2024 5:40:20 AM | [NSO Update] Visayas Grid-01/02/2024 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3089MW, PK=1937MW, RR=79MW, NetOpMargin: AM=1072, PM=1054, EVE=891 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @70MW, AG4 @90MW, AG5 @28MW, AG6 @112MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CVIS
1/2/2024 5:30:03 AM | [NSO Update] Luzon Grid-01/02/2024 05:30: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
1/2/2024 5:29:19 AM | [NSO Update] Mindanao Grid-01/02/2024 05:33: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
1/2/2024 5:29:06 AM | [NSO Update] Visayas Grid-01/02/2024 05:29: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
1/2/2024 2:14:10 AM | Mindanao Grid-01/02/2024 02:18: AGUS 5 HEP Unit 1 online at 0209H (Unplanned Outage) [WEBSMS] | CMIN
1/2/2024 2:00:21 AM | Mindanao Grid-01/02/2024 02:04: AGUS 5 HEP Unit 1 tripped with 11.2MW load at 0122H. Indication: Xmer Lockout (86T). Lowest frequency recorded was 59.81Hz. (Unplanned Outage) [WEBSMS] | CMIN
1/2/2024 1:45:49 AM | Mindanao Grid-01/02/2024 01:49: Agus 5 - Aurora 138kv line tripped at 0122H. Unplanned outage. [WEBSMS] | CMIN
1/2/2024 1:40:06 AM | Mindanao Grid-01/02/2024 01:44: TM1 Unit 1 declared unavailable at 0001H due to HVAC issue. With replacement power provided by TSI Unit 1 & Unit 2 as CR. [WEBSMS] | CMIN
1/2/2024 12:06:26 AM | Visayas Grid-01/02/2024 00:06: CEDC U3 cut-out at 0001H. (Planned Outage) [WEBSMS] | CVIS
1/1/2024 11:46:59 PM | Luzon Grid-01/01/2024 23:47: Sta Rita Module 20 shutdown at 2345H. (Planned Outage) [WEBSMS] | CLUZ
1/1/2024 6:18:31 PM | [NSO Update] Visayas Grid-01/01/2024 18:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1817H with power going to Visayas [WEBSMS] | CVIS
1/1/2024 6:18:04 PM | [NSO Update] Mindanao Grid-01/01/2024 18:22: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1817H with power going to Visayas [WEBSMS] | CMIN
1/1/2024 5:42:08 PM | Mindanao Grid-01/01/2024 17:46: SPC Mati online at 1625H from unplanned outage. MO dispatched. [WEBSMS] | CMIN
1/1/2024 5:41:47 PM | [NSO Update] Mindanao Grid-01/01/2024 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2907MW, PK=1750MW, RR=72MW, NetOpMargin: EVE=1084 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @70MW, AG4 @90MW, AG5 @28MW, AG6 @112MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
1/1/2024 5:39:46 PM | [NSO Update] Mindanao Grid-01/01/2024 17:43: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1736H from reverse power direction [WEBSMS] | CMIN
1/1/2024 5:39:16 PM | [NSO Update] Visayas Grid-01/01/2024 17:39: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1736H from reverse power direction [WEBSMS] | CVIS
1/1/2024 5:38:01 PM | [NSO Update] Visayas Grid-01/01/2024 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2300MW, PK=1903MW, RR=97MW, NetOpMargin: EVE=300 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @318MW, PGPP1 @76MW [WEBSMS] | CVIS
1/1/2024 5:33:25 PM | [NSO Update] Luzon Grid-01/01/2024 17:33: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12938MW, PK=8000MW, RR=283MW, NetOpMargin: EVE=4655 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @295MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/1/2024 4:27:25 PM | Mindanao Grid-01/01/2024 16:31: SPC Mati with 3MW tripped at 1620H. Cause: Reverse Power. (Unplanned Outage) [WEBSMS] | CMIN
1/1/2024 1:30:29 PM | Visayas Grid-01/01/2024 13:30: THVI U1 cut-in at 1328H (Unplanned Outage) [WEBSMS] | CVIS
1/1/2024 1:28:02 PM | Mindanao Grid-01/01/2024 13:32: TM1 Unit 1 declared available for CR at 1301H. [WEBSMS] | CMIN
1/1/2024 12:56:12 PM | [NSO Update] Luzon Grid-01/01/2024 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12595MW, PK=7357MW, RR=260MW, NetOpMargin: PM=4978, EVE=3961 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, ILIJAN A @295MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/1/2024 12:51:50 PM | [NSO Update] Visayas Grid-01/01/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2285MW, PK=1663MW, RR=88MW, NetOpMargin: PM=534, EVE=273 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: LEYTE A @318MW, PGPP1 @76MW [WEBSMS] | CVIS
1/1/2024 12:47:59 PM | [NSO Update] Mindanao Grid-01/01/2024 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3065MW, PK=1570MW, RR=72MW, NetOpMargin: PM=1423, EVE=1087 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @70MW, AG4 @90MW, AG5 @28MW, AG6 @112MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
1/1/2024 10:14:38 AM | Mindanao Grid-01/01/2024 10:18: SPC Mati online at 1001H. MO dispatched. [WEBSMS] | CMIN
1/1/2024 7:57:41 AM | [NSO Update] Mindanao Grid-01/01/2024 08:01: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0753H with power going to Mindanao [WEBSMS] | CMIN
1/1/2024 7:56:50 AM | [NSO Update] Visayas Grid-01/01/2024 07:57: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0753H with power going to Mindanao [WEBSMS] | CVIS
1/1/2024 7:45:59 AM | [NSO Update] Visayas Grid-01/01/2024 07:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0742H from forward power direction. [WEBSMS] | CVIS
1/1/2024 7:45:16 AM | [NSO Update] Mindanao Grid-01/01/2024 07:49: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0742H from forward power direction. [WEBSMS] | CMIN
1/1/2024 6:03:32 AM | [NSO Update] Mindanao Grid-01/01/2024 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2985MW, PK=1464MW, RR=70MW, NetOpMargin: AM=1452, PM=1418, EVE=1066 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @70MW, AG4 @90MW, AG5 @28MW, AG6 @112MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
1/1/2024 6:01:55 AM | [NSO Update] Visayas Grid-01/01/2024 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2335MW, PK=1649MW, RR=93MW, NetOpMargin: AM=593, PM=509, EVE=187 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @320MW, PGPP1 @76MW, TPC (Carmen) @20MW [WEBSMS] | CVIS
1/1/2024 6:00:10 AM | [NSO Update] Luzon Grid-01/01/2024 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13189MW, PK=7294MW, RR=274MW, NetOpMargin: AM=5621, PM=4921, EVE=3788 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @295MW, ILIJAN B @295MW [WEBSMS] | CLUZ
1/1/2024 4:07:04 AM | [NSO Update] Mindanao Grid-01/01/2024 04:11: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
1/1/2024 4:06:47 AM | [NSO Update] Visayas Grid-01/01/2024 04:06: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
1/1/2024 4:06:32 AM | [NSO Update] Luzon Grid-01/01/2024 04:06: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
1/1/2024 1:50:26 AM | Mindanao Grid-01/01/2024 01:54: FDC Unit 1 shutdown at 0142H. Reason: to inspect possible tube leak at cyclone A (Unplanned Outage) [WEBSMS] | CMIN
12/31/2023 10:21:19 PM | Mindanao Grid-12/31/2023 22:25: WMPC DG10 shutdown at 2114H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/31/2023 8:33:46 PM | Mindanao Grid-12/31/2023 20:37: SUPREME POWER Mati shutdown at 2005H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/31/2023 6:55:58 PM | Mindanao Grid-12/31/2023 19:00: TM1 Unit 1 declared on forced outage at 1828H. (Unplanned Outage) [WEBSMS] | CMIN
12/31/2023 6:18:45 PM | Mindanao Grid-12/31/2023 18:22: WMPC DG10 online at 1814H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/31/2023 5:46:00 PM | [NSO Update] Mindanao Grid-12/31/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2989MW, PK=2061MW, RR=76MW, NetOpMargin: EVE=852 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @70MW, AG4 @90MW, AG5 @28MW, AG6 @112MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
12/31/2023 5:45:05 PM | [NSO Update] Visayas Grid-12/31/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2401MW, PK=2069MW, RR=97MW, NetOpMargin: EVE=235 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @320MW, PGPP1 @76MW, TPC (Carmen) @20MW [WEBSMS] | CVIS
12/31/2023 5:42:50 PM | [NSO Update] Luzon Grid-12/31/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12961MW, PK=9253MW, RR=314MW, NetOpMargin: EVE=3394 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @295MW, ILIJAN B @295MW [WEBSMS] | CLUZ
12/31/2023 3:15:43 PM | Mindanao Grid-12/31/2023 15:19: Mt. Apo 3 online at 1511H (Unplanned Outage) [WEBSMS] | CMIN
12/31/2023 1:51:31 PM | Luzon Grid-12/31/2023 13:51: Sual 1 online at 1347H. (Unplanned Outage) [WEBSMS] | CLUZ
12/31/2023 1:01:56 PM | [NSO Update] Mindanao Grid-12/31/2023 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3099MW, PK=1804MW, RR=74MW, NetOpMargin: PM=1221, EVE=960 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @30MW, AG2 @55MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
12/31/2023 1:00:21 PM | [NSO Update] Visayas Grid-12/31/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2424MW, PK=1814MW, RR=91MW, NetOpMargin: PM=519, EVE=182 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @320MW, PGPP1 @76MW [WEBSMS] | CVIS
12/31/2023 12:58:29 PM | [NSO Update] Luzon Grid-12/31/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12569MW, PK=8001MW, RR=296MW, NetOpMargin: PM=4272, EVE=3218 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, ILIJAN A @300MW, ILIJAN B @295MW [WEBSMS] | CLUZ
12/31/2023 12:05:10 PM | Mindanao Grid-12/31/2023 12:09: TM1 Unit 1 declared available for CR at 1201H. [WEBSMS] | CMIN
12/31/2023 10:52:07 AM | Luzon Grid-12/31/2023 10:52: Sual Unit 1 (266MW) tripped at 1048H. Lowest system frequency is 59.337Hz. [WEBSMS] | CLUZ
12/31/2023 10:06:14 AM | Mindanao Grid-12/31/2023 10:10: SPC Mati online at 0949H. MO dispatched. [WEBSMS] | CMIN
12/31/2023 5:59:01 AM | [NSO Update] Luzon Grid-12/31/2023 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13946MW, PK=7699MW, RR=314MW, NetOpMargin: AM=5933, PM=5938, EVE=4645 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, ILIJAN A @295MW, ILIJAN B @295MW [WEBSMS] | CLUZ
12/31/2023 5:47:50 AM | [NSO Update] Mindanao Grid-12/31/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3326MW, PK=1754MW, RR=72MW, NetOpMargin: AM=1500, PM=1483, EVE=1285 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @70MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
12/31/2023 5:43:47 AM | [NSO Update] Visayas Grid-12/31/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2352MW, PK=1699MW, RR=93MW, NetOpMargin: AM=560, PM=578, EVE=213 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @320MW, PGPP1 @76MW, TPC(Carmen) @ 20.3MW [WEBSMS] | CVIS
12/31/2023 4:24:21 AM | [NSO Update] Mindanao Grid-12/31/2023 04:28: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
12/31/2023 4:23:41 AM | [NSO Update] Visayas Grid-12/31/2023 04:23: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
12/31/2023 4:23:20 AM | [NSO Update] Luzon Grid-12/31/2023 04:23: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
12/30/2023 10:36:13 PM | Mindanao Grid-12/30/2023 22:40: SUPREME POWER Mati shutdown at 2005H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/30/2023 8:19:14 PM | Mindanao Grid-12/30/2023 20:23: TM1 Unit 1 declared unavailable as CR at 2001H due to HVAC issue. Replacement power for CR provided by TSI Unit 1 & 2. [WEBSMS] | CMIN
12/30/2023 6:36:27 PM | Mindanao Grid-12/30/2023 18:40: SUPREME POWER Mati online at 1649H (Unplanned Outage) [WEBSMS] | CMIN
12/30/2023 6:35:26 PM | Mindanao Grid-12/30/2023 18:39: SUPREME POWER Mati tripped at 1646H. Indication: Reverse Power Trip (Unplanned Outage) [WEBSMS] | CMIN
12/30/2023 6:25:41 PM | [NSO Update] Mindanao Grid-12/30/2023 18:29: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1821H with power going to Visayas [WEBSMS] | CMIN
12/30/2023 6:24:53 PM | [NSO Update] Visayas Grid-12/30/2023 18:25: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1821H with power going to Visayas [WEBSMS] | CVIS
12/30/2023 6:06:10 PM | [NSO Update] Mindanao Grid-12/30/2023 18:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1802H from reverse power direction [WEBSMS] | CMIN
12/30/2023 6:04:52 PM | [NSO Update] Visayas Grid-12/30/2023 18:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1802H from reverse power direction [WEBSMS] | CVIS
12/30/2023 5:39:26 PM | [NSO Update] Mindanao Grid-12/30/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3039MW, PK=2070MW, RR=76MW, NetOpMargin: EVE=893 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @55MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
12/30/2023 5:37:36 PM | [NSO Update] Visayas Grid-12/30/2023 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2393MW, PK=2023MW, RR=97MW, NetOpMargin: EVE=273 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @311MW, PGPP1 @76MW [WEBSMS] | CVIS
12/30/2023 5:29:40 PM | [NSO Update] Luzon Grid-12/30/2023 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12980MW, PK=8876MW, RR=314MW, NetOpMargin: EVE=3790 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, ILIJAN A @295MW, ILIJAN B @295MW [WEBSMS] | CLUZ
12/30/2023 3:17:00 PM | Mindanao Grid-12/30/2023 15:21: WMPC DG10 shutdown at 1513H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/30/2023 2:34:09 PM | Luzon Grid-12/30/2023 14:34: Ilijan GT1-1 shutdown at 1429H. (Unplanned Outage due to fuel gas restriction.) [WEBSMS] | CLUZ
12/30/2023 12:52:14 PM | [NSO Update] Mindanao Grid-12/30/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3177MW, PK=1945MW, RR=74MW, NetOpMargin: PM=1158, EVE=796 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @55MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
12/30/2023 12:50:05 PM | [NSO Update] Luzon Grid-12/30/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13821MW, PK=8292MW, RR=315MW, NetOpMargin: PM=5215, EVE=3838 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, ILIJAN A @405MW, ILIJAN B @295MW [WEBSMS] | CLUZ
12/30/2023 12:45:22 PM | [NSO Update] Visayas Grid-12/30/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2479MW, PK=1925MW, RR=94MW, NetOpMargin: PM=460, EVE=250 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @311MW, PGPP1 @76MW, TPC (Carmen) @20MW [WEBSMS] | CVIS
12/30/2023 12:11:19 PM | Mindanao Grid-12/30/2023 12:15: TM1 Unit 1 declared available for CR at 1201H [WEBSMS] | CMIN
12/30/2023 10:05:00 AM | Mindanao Grid-12/30/2023 10:09: SUPREME POWER Mati online at 0959H. MO dispatched (RTD). [WEBSMS] | CMIN
12/30/2023 9:49:55 AM | Mindanao Grid-12/30/2023 09:53: WMPC DG10 online at 0948H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/30/2023 9:16:11 AM | Luzon Grid-12/30/2023 09:16: Mauban-SBPL 230kV Line 2 restored at 0916H (Planned Outage) [WEBSMS] | CLUZ
12/30/2023 9:09:31 AM | [NSO Update] Visayas Grid-12/30/2023 09:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0907H with power going to Mindanao. [WEBSMS] | CVIS
12/30/2023 9:08:48 AM | [NSO Update] Mindanao Grid-12/30/2023 09:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0907H with power going to Mindanao. [WEBSMS] | CMIN
12/30/2023 8:57:22 AM | [NSO Update] Visayas Grid-12/30/2023 08:57: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0854H from forward power direction. [WEBSMS] | CVIS
12/30/2023 8:56:39 AM | [NSO Update] Mindanao Grid-12/30/2023 09:00: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0854H from forward power direction. [WEBSMS] | CMIN
12/30/2023 8:04:20 AM | Luzon Grid-12/30/2023 08:04: Ilijan ST2 online at 0751H (Unplanned Outage) [WEBSMS] | CLUZ
12/30/2023 6:31:28 AM | Mindanao Grid-12/30/2023 06:35: SEC2 online at 0628H (Unplanned Outage) [WEBSMS] | CMIN
12/30/2023 6:08:55 AM | [NSO Update] Luzon Grid-12/30/2023 06:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13852MW, PK=8225MW, RR=314MW, NetOpMargin: AM=5313, PM=5421, EVE=4268 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW [WEBSMS] | CLUZ
12/30/2023 5:58:09 AM | [NSO Update] Mindanao Grid-12/30/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3170MW, PK=1865MW, RR=72MW, NetOpMargin: AM=1233, PM=1229, EVE=932 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @55MW, AG4 @90MW, AG5 @28MW, AG6 @132MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
12/30/2023 5:51:19 AM | [NSO Update] Visayas Grid-12/30/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2527MW, PK=1869MW, RR=93MW, NetOpMargin: AM=566, PM=561, EVE=259 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @320MW, PGPP1 @76MW, TPC (Carmen) @20MW [WEBSMS] | CVIS
12/30/2023 5:37:05 AM | Luzon Grid-12/30/2023 05:37: Ilijan GT2-1 online at 0535H. (From an unplanned outage) [WEBSMS] | CLUZ
12/30/2023 4:32:35 AM | Mindanao Grid-12/30/2023 04:36: SMC Unit 2 on emergency shutdown with 45MW load at 0412H, due to boiler problem. Unplanned Outage. [WEBSMS] | CMIN
12/30/2023 4:25:49 AM | [NSO Update] Mindanao Grid-12/30/2023 04:29: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
12/30/2023 4:25:09 AM | [NSO Update] Visayas Grid-12/30/2023 04:25: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
12/30/2023 4:22:44 AM | [NSO Update] Luzon Grid-12/30/2023 04:22: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
12/30/2023 12:14:09 AM | Mindanao Grid-12/30/2023 00:18: Southern Mindanao Coal-Fired Power Plant (SEC 2) auto-tripped at 2340H, with a gross generation loss of 90.45MW. The lowest system frequency recorded was 59.3882Hz. No ALD activated. Indication: Master Fuel Trip. (Unplanned Outage) [WEBSMS] | CMIN
12/29/2023 10:29:57 PM | Mindanao Grid-12/29/2023 22:34: TUDAYA 2 Unit 1 HEP online at 2153H. (Unplanned Outage) [WEBSMS] | CMIN
12/29/2023 10:27:15 PM | Mindanao Grid-12/29/2023 22:31: TUDAYA 2 Unit 1 HEP manually tripped at 2108H. Affected by the emergency shutdown of Toril-Digos 69kV line, for the removal of an entangle fiber optic cable at phase C conductor of the said line. (Unplanned Outage) [WEBSMS] | CMIN
12/29/2023 10:22:09 PM | Mindanao Grid-12/29/2023 22:26: Updated: AGUS 6 HEP Unit 1 synchronized/online at 2046H from PMS - GOMP. (Planned Outage) [WEBSMS] | CMIN
12/29/2023 10:19:00 PM | Mindanao Grid-12/29/2023 22:23: Updated: AGUS 6 HEP Unit 2 synchronized/onlined at 2110H from PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
12/29/2023 10:03:07 PM | Mindanao Grid-12/29/2023 22:07: MACO BESS online as AS-RR at 2156H from forced outage. (Unplanned Outage) [WEBSMS] | CMIN
12/29/2023 9:18:05 PM | Mindanao Grid-12/29/2023 21:22: AGUS 6 Unit 2 online at 2110H from PMS-GOMP. (Unplanned Outage) [WEBSMS] | CMIN
12/29/2023 9:11:07 PM | Mindanao Grid-12/29/2023 21:15: AGUS 6 Unit 1 online at 2046H from PMS - GOMP. (Planned Outage) [WEBSMS] | CMIN
12/29/2023 8:11:19 PM | Mindanao Grid-12/29/2023 20:15: TSI Unit 1 and 2 change setting at 2001H from APC ON/ Free Governor-OFF to APC OFF/ Free Governor-ON. Replacement AS-CR for TMI 1 unit 1. [WEBSMS] | CMIN
12/29/2023 7:06:12 PM | Mindanao Grid-12/29/2023 19:10: MACO BESS (AS-RR) tripped at 1828H. Indication: Transformer Over Voltage Protection Trip. (Unplanned Outage) [WEBSMS] | CMIN
12/29/2023 5:49:09 PM | [NSO Update] Mindanao Grid-12/29/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3163MW, PK=2187MW, RR=88MW, NetOpMargin: EVE=888 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @55MW, AG4 @90MW, AG5 @28MW, AG6 @118MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
12/29/2023 5:47:36 PM | [NSO Update] Visayas Grid-12/29/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2465MW, PK=2154MW, RR=97MW, NetOpMargin: EVE=214 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @310MW, PGPP1 @76MW, TPC (Carmen) @20MW [WEBSMS] | CVIS
12/29/2023 5:44:12 PM | [NSO Update] Luzon Grid-12/29/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12902MW, PK=9387MW, RR=347MW, NetOpMargin: EVE=3168 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW [WEBSMS] | CLUZ
12/29/2023 5:20:10 PM | Luzon Grid-12/29/2023 17:20: Mexico-Hermosa 230kV line 1 was restored at 1719H. (Planned Outage) [WEBSMS] | CLUZ
12/29/2023 5:17:46 PM | Mindanao Grid-12/29/2023 17:21: TMI Unit 1 (AS-CR provider) declared unavailable at 1505H, due to HVAC issue. No replacement CR. (Unplanned Outage) [WEBSMS] | CMIN
12/29/2023 5:10:47 PM | Mindanao Grid-12/29/2023 17:14: Agus 2 - Kibawe 138KV Line 2 restored up to tower 33 for anti pilferage purposes only at 1515H. Unplanned. [WEBSMS] | CMIN
12/29/2023 5:06:54 PM | Luzon Grid-12/29/2023 17:07: Tiwi A-Tiwi C 230kV Tie Line 1 was restored at 1659H. (Energization of New Tiwi C PCB 8-05CB04TWC and associated equipment was completed.) (Planned Outage) [WEBSMS] | CLUZ
12/29/2023 3:32:07 PM | Mindanao Grid-12/29/2023 15:36: Agus 2 - Kibawe 138KV line 2 restored at 1515H. Unplanned outage. [WEBSMS] | CMIN
12/29/2023 3:17:37 PM | Mindanao Grid-12/29/2023 15:21: restored at 1515H (Unplanned Outage) [WEBSMS] | CMIN
12/29/2023 2:23:36 PM | Mindanao Grid-12/29/2023 14:27: AGUS 7 Unit 2 HEP online at 1412H (Unplanned Outage). [WEBSMS] | CMIN
12/29/2023 2:21:01 PM | Luzon Grid-12/29/2023 14:21: Dasmarinas-Ternate(TMC) 115kV line (Customer Owned) was restored at 1417H. (Unplanned Outage) [WEBSMS] | CLUZ
12/29/2023 12:50:13 PM | [NSO Update] Mindanao Grid-12/29/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3186MW, PK=2255MW, RR=91MW, NetOpMargin: PM=840, EVE=855 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @55MW, AG4 @90MW, AG5 @28MW, AG6 @93MW, AG7 @14MW, PG4 @170MW [WEBSMS] | CMIN
12/29/2023 12:49:09 PM | [NSO Update] Visayas Grid-12/29/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2439MW, PK=2122MW, RR=93MW, NetOpMargin: PM=224, EVE=228 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @310MW, PGPP1 @76MW, TPC (Carmen) @20MW [WEBSMS] | CVIS
12/29/2023 12:46:59 PM | [NSO Update] Luzon Grid-12/29/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13668MW, PK=9451MW, RR=349MW, NetOpMargin: PM=3867, EVE=2944 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW [WEBSMS] | CLUZ
12/29/2023 12:40:37 PM | Mindanao Grid-12/29/2023 12:44: AGUS 7 Unit 1 online at 1236H from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
12/29/2023 12:38:35 PM | Mindanao Grid-12/29/2023 12:42: AGUS 7 Unit 1 with 20MW load conducted an emergency shutdown at 1230H. Reason: Emergency Generator excitation check-up. (Unplanned Outage) [WEBSMS] | CMIN
12/29/2023 12:06:02 PM | Mindanao Grid-12/29/2023 12:10: Mt. APO G03 (MA3) with 3.0MW load tripped at 1154H. Cause: Generator protection cumulative trip, High turbine speed. (Unplanned Outage). [WEBSMS] | CMIN
12/29/2023 11:04:10 AM | Mindanao Grid-12/29/2023 11:08: SPC Mati online at 1001H. MO dispatched. [WEBSMS] | CMIN
12/29/2023 11:01:24 AM | [NSO Update] Mindanao Grid-12/29/2023 11:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1053H with power going to Visayas. [WEBSMS] | CMIN
12/29/2023 11:01:04 AM | [NSO Update] Visayas Grid-12/29/2023 11:01: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1053H with power going to Visayas. [WEBSMS] | CVIS
12/29/2023 10:51:22 AM | Mindanao Grid-12/29/2023 10:55: WMPC DG08 online at 1048H as RPS. System voltage requirement. [WEBSMS] | CMIN
12/29/2023 10:48:29 AM | [NSO Update] Mindanao Grid-12/29/2023 10:52: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1045H from reverse power direction. [WEBSMS] | CMIN
12/29/2023 10:48:09 AM | [NSO Update] Visayas Grid-12/29/2023 10:48: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1045H from reverse power direction. [WEBSMS] | CVIS
12/29/2023 10:44:32 AM | Luzon Grid-12/29/2023 10:44: Labo-Gumaca 230kV Line 2 restored at 1043H. (Planned Outage) [WEBSMS] | CLUZ
12/29/2023 10:41:46 AM | Mindanao Grid-12/29/2023 10:45: Mt. Apo Unit 3 online at 0958H from forced outage. (Unplanned Outage) [WEBSMS] | CMIN
12/29/2023 10:37:36 AM | Mindanao Grid-12/29/2023 10:41: TSI Unit 1 and 2 change setting at 0901H from APC OFF/ Free Governor-ON to APC ON/ Free Governor-OFF. AS-CR back to TMI 1 unit 1. [WEBSMS] | CMIN
12/29/2023 10:34:54 AM | Mindanao Grid-12/29/2023 10:38: TMI 1 declared available for CR at at 0901H. [WEBSMS] | CMIN
12/29/2023 9:25:02 AM | Mindanao Grid-12/29/2023 09:29: AGUS 7 Unit 2 shutdown with 10MW Load at 0901H. Reason: Facilitate the installation of unit governor pump motor set. Non-GOM (Unplanned Outage). [WEBSMS] | CMIN
12/29/2023 9:11:25 AM | [NSO Update] Mindanao Grid-12/29/2023 09:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0908H with power going to Mindanao. [WEBSMS] | CMIN
12/29/2023 9:10:55 AM | [NSO Update] Visayas Grid-12/29/2023 09:11: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0908H with power going to Mindanao. [WEBSMS] | CVIS
12/29/2023 8:58:53 AM | [NSO Update] Mindanao Grid-12/29/2023 09:02: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0857H from forward power direction. [WEBSMS] | CMIN
12/29/2023 8:58:17 AM | [NSO Update] Visayas Grid-12/29/2023 08:58: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0857H from forward power direction. [WEBSMS] | CVIS
12/29/2023 8:05:31 AM | Luzon Grid-12/29/2023 08:05: Labo-Gumaca 230kV Line 2 de-energized at 0804H (Planned Outage) [WEBSMS] | CLUZ
12/29/2023 7:49:23 AM | Mindanao Grid-12/29/2023 07:53: Mt. APO GO3 (MA3) tripped with 3.0MW load at 0736H. Cause: Low Brine Discharge Pressure. (Unplanned Outage) [WEBSMS] | CMIN
12/29/2023 7:17:19 AM | Luzon Grid-12/29/2023 07:17: Mexico - Hermosa 230kV Line 1 de-energized at 0717H. (Planned Outage) [WEBSMS] | CLUZ
12/29/2023 5:42:54 AM | [NSO Update] Mindanao Grid-12/29/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3311MW, PK=2189MW, RR=86MW, NetOpMargin: AM=1036, PM=862, EVE=842 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @55MW, AG4 @90MW, AG5 @28MW, AG6 @93MW, AG7 @14MW, PG4 @170MW [WEBSMS] | CMIN
12/29/2023 5:41:47 AM | [NSO Update] Visayas Grid-12/29/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2506MW, PK=2096MW, RR=93MW, NetOpMargin: AM=316, PM=250, EVE=280 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @320MW, PGPP1 @76MW [WEBSMS] | CVIS
12/29/2023 5:38:52 AM | [NSO Update] Luzon Grid-12/29/2023 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13704MW, PK=9446MW, RR=356MW, NetOpMargin: AM=3901, PM=3569, EVE=2875 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW [WEBSMS] | CLUZ
12/29/2023 4:45:43 AM | Luzon Grid-12/29/2023 04:45: SLTEC Unit 1 online at 0442H (Unplanned Outage) [WEBSMS] | CLUZ
12/29/2023 4:22:28 AM | [NSO Update] Luzon Grid-12/29/2023 04:22: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
12/29/2023 4:18:36 AM | [NSO Update] Mindanao Grid-12/29/2023 04:22: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
12/29/2023 4:18:05 AM | [NSO Update] Visayas Grid-12/29/2023 04:18: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
12/29/2023 2:25:02 AM | Mindanao Grid-12/29/2023 02:29: ASIGA Hydro online at 0222H (Unplanned Outage) [WEBSMS] | CMIN
12/29/2023 2:17:56 AM | Mindanao Grid-12/29/2023 02:21: ASIGA Hydro tripped with 8.2MW load at 0159H. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 9:32:03 PM | Mindanao Grid-12/28/2023 21:36: WMPC DG10 shutdown at 2113H. End of RPS. System voltage requirement. [WEBSMS] | CMIN
12/28/2023 9:23:51 PM | Mindanao Grid-12/28/2023 21:27: TSI Unit 1 and 2 change setting at 2100H from APC ON/ Free Governor-OFF to APC OFF/ Free Governor-ON. Replacement AS-CR for TMI 1 unit 1. [WEBSMS] | CMIN
12/28/2023 8:19:57 PM | Mindanao Grid-12/28/2023 20:23: SPC Mati shutdown at 2005H. MO dispatched. (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 7:01:17 PM | Luzon Grid-12/28/2023 19:01: Dasmarinas-TMC II (Ternate) 115kV Line tripped at 1858H. (Unplanned Outage) [WEBSMS] | CLUZ
12/28/2023 5:35:57 PM | [NSO Update] Mindanao Grid-12/28/2023 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3169MW, PK=2176MW, RR=85MW, NetOpMargin: EVE=908 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @75MW, AG4 @90MW, AG5 @28MW, AG6 @93MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
12/28/2023 5:33:47 PM | [NSO Update] Visayas Grid-12/28/2023 17:33: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2486MW, PK=2178MW, RR=97MW, NetOpMargin: EVE=210 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @317MW, PGPP1 @76MW [WEBSMS] | CVIS
12/28/2023 5:31:19 PM | [NSO Update] Luzon Grid-12/28/2023 17:31: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12867MW, PK=9572MW, RR=363MW, NetOpMargin: EVE=2932 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW [WEBSMS] | CLUZ
12/28/2023 3:59:19 PM | Mindanao Grid-12/28/2023 16:03: SPC Mati DG03 online at 1545H from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 3:57:42 PM | Mindanao Grid-12/28/2023 16:01: SPC Mati DG03 with 3.3MW load tripped at 1536H. Indication: Over voltage and over current relay tripped. (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 3:29:41 PM | Mindanao Grid-12/28/2023 15:33: TM1 Unit 1 (Hybrid BESS-Diesel) declared unavailable at 1523H. Cause: HVAC Issue/repair. Note: No replacement power (CR) from 1600H to 2000H. [WEBSMS] | CMIN
12/28/2023 1:05:41 PM | [NSO Update] Mindanao Grid-12/28/2023 13:09: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3232MW, PK=2200MW, RR=85MW, NetOpMargin: PM=946, EVE=922 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @75MW, AG4 @90MW, AG5 @28MW, AG6 @93MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
12/28/2023 1:04:33 PM | [NSO Update] Visayas Grid-12/28/2023 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2471MW, PK=2103MW, RR=94MW, NetOpMargin: PM=274, EVE=223 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @313MW, PGPP1 @76MW, TPC (Carmen) @20MW [WEBSMS] | CVIS
12/28/2023 1:03:18 PM | [NSO Update] Luzon Grid-12/28/2023 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13323MW, PK=9549MW, RR=366MW, NetOpMargin: PM=3407, EVE=2602 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW [WEBSMS] | CLUZ
12/28/2023 12:07:06 PM | Mindanao Grid-12/28/2023 12:11: STEAG Unit on emergency shutdown with 100MW load at 1200H. Cause: Boiler fouling. (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 11:55:02 AM | Luzon Grid-12/28/2023 11:55: Labo-Naga 230kV Line 1 restored at 1154H. (Planned Outage) [WEBSMS] | CLUZ
12/28/2023 11:48:53 AM | Mindanao Grid-12/28/2023 11:52: WMPC DG08 on emergency shutdown at 1139H as RPS. Reason: Fuel Leak. (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 11:46:37 AM | Mindanao Grid-12/28/2023 11:50: WMPC DG05 online at 1125H as RPS replacement for WMPC DG08. System voltage requirement. (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 11:38:32 AM | Luzon Grid-12/28/2023 11:38: San Gabriel online at 1136H. (Unplanned Outage) [WEBSMS] | CLUZ
12/28/2023 10:57:56 AM | Mindanao Grid-12/28/2023 11:01: WMPC DG08 online at 1051H as RPS. System voltage requirement. (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 10:55:54 AM | Mindanao Grid-12/28/2023 10:59: WMPC online at 1051H as RPS. System voltage requirement. (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 9:09:49 AM | Mindanao Grid-12/28/2023 09:13: TMI 1 declared available for AS-CR at at 0901H. Setting: Frequency Response On. [WEBSMS] | CMIN
12/28/2023 9:04:52 AM | Mindanao Grid-12/28/2023 09:08: TSI Unit 1 and 2 change setting at 0901H from APC OFF/ Free Governor-ON to APC ON/ Free Governor-OFF. AS-CR back to TMI 1 unit 1. [WEBSMS] | CMIN
12/28/2023 8:54:35 AM | Mindanao Grid-12/28/2023 08:58: WMPC DG10 online at 1050H as RPS. System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 8:16:40 AM | Luzon Grid-12/28/2023 08:16: Tiwi Plant A-Tiwi Plant C 230kV Line 1 de-energized at 0816H. (Planned Outage) [WEBSMS] | CLUZ
12/28/2023 8:07:17 AM | Mindanao Grid-12/28/2023 08:11: Agus 2 Unit 1 shutdown with 30.0 MW load at 0803H. Reason: To facilitate leakage inspection at generators oil pan. Non-GOMP. Un-Planned Outage. [WEBSMS] | CMIN
12/28/2023 6:13:44 AM | Luzon Grid-12/28/2023 06:13: Labo-Naga 230kV Line 1 de-energized at 0613H. (Planned Outage) [WEBSMS] | CLUZ
12/28/2023 5:54:37 AM | [NSO Update] Luzon Grid-12/28/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13299MW, PK=9363MW, RR=369MW, NetOpMargin: AM=3567, PM=3465, EVE=2803 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW [WEBSMS] | CLUZ
12/28/2023 5:44:49 AM | Mindanao Grid-12/28/2023 05:48: ASIGA Hydro online at 0526H (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 5:44:16 AM | [NSO Update] Mindanao Grid-12/28/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3322MW, PK=2161MW, RR=82MW, NetOpMargin: AM=1078, PM=1060, EVE=1040 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @43MW, AG1 @35MW, AG2 @75MW, AG4 @90MW, AG5 @28MW, AG6 @93MW, AG7 @26MW, PG4 @170MW [WEBSMS] | CMIN
12/28/2023 5:43:05 AM | [NSO Update] Visayas Grid-12/28/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2417MW, PK=2051MW, RR=93MW, NetOpMargin: AM=273, PM=247, EVE=274 Highest Unit O/L: THVI U2 Derated Plant: Leyte A @ 320MW, PGPP1 @ 76MW, TPC Carmen @ 20.3MW [WEBSMS] | CVIS
12/28/2023 5:26:37 AM | Luzon Grid-12/28/2023 05:26: San Gabriel (8MW) tripped at 0524H (Unplanned Outage) [WEBSMS] | CLUZ
12/28/2023 5:18:23 AM | Mindanao Grid-12/28/2023 05:22: ASIGA Hydro tripped with 8.2MW load at 0452H. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 5:17:05 AM | Luzon Grid-12/28/2023 05:17: San Gabriel online at 0514H (Planned Outage) [WEBSMS] | CLUZ
12/28/2023 4:57:49 AM | Luzon Grid-12/28/2023 04:57: Batangas Transformer T04/T05 looped and San Lorenzo-Sta. Rita 230kV Tie bus 1 & 2 unlooped at 0457H and 0451H respectively (Planned Outage) [WEBSMS] | CLUZ
12/28/2023 4:42:05 AM | Mindanao Grid-12/28/2023 04:46: ASIGA Hydro online at 0439H (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 4:37:00 AM | Mindanao Grid-12/28/2023 04:41: ASIGA Hydro tripped with 8.2MW load at 0417H. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 4:17:35 AM | [NSO Update] Mindanao Grid-12/28/2023 04:21: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
12/28/2023 4:17:21 AM | [NSO Update] Visayas Grid-12/28/2023 04:17: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
12/28/2023 4:17:09 AM | [NSO Update] Luzon Grid-12/28/2023 04:17: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
12/28/2023 12:23:31 AM | Mindanao Grid-12/28/2023 00:27: ASIGA Hydro online at 2359H (Unplanned Outage) [WEBSMS] | CMIN
12/28/2023 12:22:04 AM | Mindanao Grid-12/28/2023 00:26: ASIGA Hydro tripped with 8.2MW load at 2337H. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 11:54:36 PM | Mindanao Grid-12/27/2023 23:58: (Corrected) Tudaya 2 Unit 2 online at 2252H (Note: outage since 24 Dec 2023 0916H due to insufficient water supply) (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 11:53:53 PM | Mindanao Grid-12/27/2023 23:57: Tudaya 2 Unit 2 online at 2252H (Note: outage since 24 Dec 2023 0916H due to insufficient water supply) (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 11:40:13 PM | Mindanao Grid-12/27/2023 23:44: Tudaya 2 Unit 1 online at 2252H (Note: outage since 24 Dec 2023 0916H due to insufficient water supply) (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 11:17:24 PM | Mindanao Grid-12/27/2023 23:21: ASIGA Hydro online at 2308H (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 10:56:06 PM | Mindanao Grid-12/27/2023 23:00: ASIGA Hydro tripped with 8.2MW load at 2245H. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 10:45:10 PM | Luzon Grid-12/27/2023 22:45: Tiwi C 230kV Bus 1 restored at 2244H (Planned Outage) [WEBSMS] | CLUZ
12/27/2023 9:15:50 PM | Mindanao Grid-12/27/2023 21:19: WMPC DG05 shutdown at 2113H. End of RPS. System voltage requirement. (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 8:24:40 PM | Mindanao Grid-12/27/2023 20:28: TSI Unit 1 and 2 change setting at 2006H from APC ON/ Free Governor-OFF to APC OFF/ Free Governor-ON. To served as replacement CR from TMI 1 unit 1. (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 8:14:47 PM | Mindanao Grid-12/27/2023 20:18: TM1 Unit 1 (Hybrid BESS-Diesel) shutdown at 2006H. Cause: HVAC inverter high temperature. Note: TSI Unit 1 & Unit 2 as replacement power (CR). (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 7:15:03 PM | Visayas Grid-12/27/2023 19:15: Cebu - Negros Submarine 138 kV Submarine Cable Line 2 re-energized at 1912H (Unplanned Outage) [WEBSMS] | CVIS
12/27/2023 7:08:03 PM | [NSO Update] Visayas Grid-12/27/2023 19:08: SO initiated Market Intervention for Visayas is lifted today at 1825H. Market Operation will resume starting interval 1835H [WEBSMS] | CVIS
12/27/2023 6:11:27 PM | [NSO Update] Luzon Grid-12/27/2023 18:11: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12466MW, PK=9642MW, RR=363MW, NetOpMargin: EVE=2461 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW [WEBSMS] | CLUZ
12/27/2023 6:00:03 PM | [NSO Update] Visayas Grid-12/27/2023 18:00: SO initiated Market Intervention for Visayas is issued today starting interval 1755H due to implementation of MLD to prevent overloading of Amlan-Samboan 138kV Line 1 [WEBSMS] | CVIS
12/27/2023 5:57:35 PM | Visayas Grid-12/27/2023 17:57: Manual Load Dropping at Negros Sub-grid at 1752H due to overloading of Cebu-Negros 138 kV Line 1 [WEBSMS] | CVIS
12/27/2023 5:53:21 PM | [NSO Update] Mindanao Grid-12/27/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3153MW, PK=2257MW, RR=86MW, NetOpMargin: EVE=810 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @118MW, AG7 @27MW, PG4 @170MW [WEBSMS] | CMIN
12/27/2023 5:34:58 PM | [NSO Update] Visayas Grid-12/27/2023 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2534MW, PK=2140MW, RR=97MW, NetOpMargin: EVE=297 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @320MW, PGPP1 @76MW [WEBSMS] | CVIS
12/27/2023 5:05:10 PM | Visayas Grid-12/27/2023 17:05: Amlan - Samboan 138 kV Line 2 auto-tripped at 1701H (Unplanned Outage) [WEBSMS] | CVIS
12/27/2023 3:10:47 PM | Mindanao Grid-12/27/2023 15:14: Supreme Power Mati online at 1449H (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 3:09:10 PM | Mindanao Grid-12/27/2023 15:13: Supreme Power Mati tripped with 3MW load at 1445H (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 2:17:49 PM | Mindanao Grid-12/27/2023 14:21: SPC Mati online at 1357H from unplanned outage. MO dispatched. [WEBSMS] | CMIN
12/27/2023 2:08:41 PM | Mindanao Grid-12/27/2023 14:12: SPC Mati with 3MW tripped at 1352H. Cause: Overcurrent. (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 12:50:26 PM | [NSO Update] Mindanao Grid-12/27/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3209MW, PK=2249MW, RR=84MW, NetOpMargin: PM=876, EVE=863 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @118MW, AG7 @27MW, PG4 @170MW [WEBSMS] | CMIN
12/27/2023 12:47:09 PM | [NSO Update] Visayas Grid-12/27/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2452MW, PK=2068MW, RR=93MW, NetOpMargin: PM=291, EVE=262 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @306MW, TPC (Carmen) @20MW [WEBSMS] | CVIS
12/27/2023 12:45:00 PM | [NSO Update] Luzon Grid-12/27/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13145MW, PK=9651MW, RR=360MW, NetOpMargin: PM=3134, EVE=2415 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW [WEBSMS] | CLUZ
12/27/2023 12:35:57 PM | Mindanao Grid-12/27/2023 12:39: Updated: WMPC DG05 cut-inonline at 0854H as RPS. System Voltage Requirement. [WEBSMS] | CMIN
12/27/2023 12:28:28 PM | Mindanao Grid-12/27/2023 12:32: Correction: Balo-i - Agus 6 69kV Tie Line tripped at 1125H (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 12:20:34 PM | Luzon Grid-12/27/2023 12:20: Masinloc 1 shutdown at 1220H. (Unplanned Outage) [WEBSMS] | CLUZ
12/27/2023 12:00:52 PM | Mindanao Grid-12/27/2023 12:04: Balo-i - Agus6 69kV Tie Line loop at 1143H. (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 11:53:41 AM | Mindanao Grid-12/27/2023 11:57: Balo-i - Agus 6 69kV Tie Line tripped at 2325H (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 11:38:46 AM | Luzon Grid-12/27/2023 11:38: Sta. Rita 20 online at 1137H. (Unplanned Outage) [WEBSMS] | CLUZ
12/27/2023 11:08:23 AM | Mindanao Grid-12/27/2023 11:12: SPC Mati online at 1100H. MO dispatched. [WEBSMS] | CMIN
12/27/2023 11:05:09 AM | Mindanao Grid-12/27/2023 11:09: WMPC DG03 cut-in at 1053H as RPS. System Voltage Requirement. [WEBSMS] | CMIN
12/27/2023 10:43:40 AM | Mindanao Grid-12/27/2023 10:47: Sibulan A Unit 1 shutdown with 4.0MW load at 1034H . Maintenance outage turbine inspection. (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 9:05:36 AM | Mindanao Grid-12/27/2023 09:09: TMI 1 declared available for CR at at 0901H. (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 8:59:53 AM | Mindanao Grid-12/27/2023 09:03: WMPC DG05 cut-in at 0854H as RPS. System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
12/27/2023 8:34:17 AM | Luzon Grid-12/27/2023 08:34: Tiwi C 230kV Bus 1 de-energized at 0833H. (Planned Outage) [WEBSMS] | CLUZ
12/27/2023 7:43:10 AM | Luzon Grid-12/27/2023 07:43: Sta. Rita 20 tripped at 0740H with 257MW load. Lowest system frequency is 59.265Hz. (Unplanned Outage) [WEBSMS] | CLUZ
12/27/2023 5:50:47 AM | [NSO Update] Mindanao Grid-12/27/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3220MW, PK=2143MW, RR=82MW, NetOpMargin: AM=995, PM=990, EVE=1111 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @118MW, AG7 @27MW, PG4 @170MW [WEBSMS] | CMIN
12/27/2023 5:50:03 AM | [NSO Update] Visayas Grid-12/27/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2556MW, PK=2070MW, RR=93MW, NetOpMargin: AM=393, PM=388, EVE=278 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: Leyte A @ 320MW, PGPP1 @ 73.5MW, TPC Carmen @ 30.4MW [WEBSMS] | CVIS
12/27/2023 5:48:43 AM | [NSO Update] Luzon Grid-12/27/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13244MW, PK=9123MW, RR=360MW, NetOpMargin: AM=3761, PM=3355, EVE=2687 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 105MW [WEBSMS] | CLUZ
12/27/2023 4:05:36 AM | [NSO Update] Luzon Grid-12/27/2023 04:05: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CLUZ
12/27/2023 4:05:22 AM | [NSO Update] Mindanao Grid-12/27/2023 04:09: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CMIN
12/27/2023 4:04:49 AM | [NSO Update] Visayas Grid-12/27/2023 04:04: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CVIS
12/27/2023 3:27:24 AM | Luzon Grid-12/27/2023 03:27: Dona Imelda (Araneta) - Sta. Mesa 115kV Line 1 restored at 0325H (Planned Outage) [WEBSMS] | CLUZ
12/26/2023 11:10:06 PM | Luzon Grid-12/26/2023 23:10: Dona Imelda (Araneta)-Sta. Mesa 115kV Line 1 de-energized at 2307H (Planned Outage) [WEBSMS] | CLUZ
12/26/2023 11:00:27 PM | Luzon Grid-12/26/2023 23:00: QPPL online at 2258H (Unplanned Outage) [WEBSMS] | CLUZ
12/26/2023 7:53:22 PM | Luzon Grid-12/26/2023 19:53: Salong - SLTEC 230kV Line 2 restored at 1952H (Planned Outage) [WEBSMS] | CLUZ
12/26/2023 7:27:23 PM | Luzon Grid-12/26/2023 19:27: Salong - SLTEC 230kV Line 1 restored at 1927H (Planned Outage) [WEBSMS] | CLUZ
12/26/2023 7:10:39 PM | Mindanao Grid-12/26/2023 19:14: SPC Mati with 3MW tripped at 1854H. Cause: Overcurrent and Overvoltage. (Unplanned Outage) [WEBSMS] | CMIN
12/26/2023 6:53:37 PM | Mindanao Grid-12/26/2023 18:57: SPC Mati with 3MW tripped at 1840H. Cause: Overcurrent and Overvoltage. Online back at 1843H. (Unplanned Outage) [WEBSMS] | CMIN
12/26/2023 6:12:07 PM | [NSO Update] Visayas Grid-12/26/2023 18:12: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2528MW, PK=2070MW, RR=97MW, NetOpMargin: EVE=362 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @320MW, PGPP1 @76MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
12/26/2023 6:09:58 PM | Luzon Grid-12/26/2023 18:10: Salong - Steel Asia 230kV Line restored at 1808H (Planned Outage) [WEBSMS] | CLUZ
12/26/2023 6:01:56 PM | [NSO Update] Mindanao Grid-12/26/2023 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3151MW, PK=2116MW, RR=76MW, NetOpMargin: EVE=959 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @118MW, AG7 @27MW, PG4 @170MW [WEBSMS] | CMIN
12/26/2023 5:58:24 PM | [NSO Update] Luzon Grid-12/26/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12140MW, PK=8697MW, RR=314MW, NetOpMargin: EVE=3129 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @105MW, MPGC 1 @120MW [WEBSMS] | CLUZ
12/26/2023 5:53:20 PM | Luzon Grid-12/26/2023 17:53: Calaca - Salong 230kV Line restored at 1752H (Planned Outage) [WEBSMS] | CLUZ
12/26/2023 5:39:44 PM | Luzon Grid-12/26/2023 17:39: Calaca 230kV Bus 1 restored at 1739H (Planned Outage) [WEBSMS] | CLUZ
12/26/2023 4:05:50 PM | Luzon Grid-12/26/2023 16:06: QPPL with 94MW load tripped at 1603H. Lowest Frequency is 59.61Hz (Unplanned Outage) [WEBSMS] | CLUZ
12/26/2023 3:19:27 PM | Mindanao Grid-12/26/2023 15:23: SPC Mati with 3MW tripped at 1505H. Cause: Overcurrent and Overvoltage. Online back at 1510H. (Unplanned Outage) [WEBSMS] | CMIN
12/26/2023 2:05:53 PM | Luzon Grid-12/26/2023 14:06: QPPL online at 1358H (Unplanned Outage) [WEBSMS] | CLUZ
12/26/2023 1:07:33 PM | [NSO Update] Mindanao Grid-12/26/2023 13:11: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3246MW, PK=1974MW, RR=74MW, NetOpMargin: PM=1198, EVE=1002 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @118MW, AG7 @27MW, PG4 @170MW [WEBSMS] | CMIN
12/26/2023 1:04:40 PM | [NSO Update] Visayas Grid-12/26/2023 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2451MW, PK=1904MW, RR=93MW, NetOpMargin: PM=454, EVE=277 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @300MW, PGPP1 @76MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
12/26/2023 12:59:07 PM | [NSO Update] Luzon Grid-12/26/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12877MW, PK=7963MW, RR=306MW, NetOpMargin: PM=4608, EVE=2998 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @105MW, MPGC 1 @120MW [WEBSMS] | CLUZ
12/26/2023 7:41:49 AM | Luzon Grid-12/26/2023 07:42: Calaca SS 230kV Bus 1 de-energized at 0741H. (Planned Outage) [WEBSMS] | CLUZ
12/26/2023 7:30:57 AM | Luzon Grid-12/26/2023 07:31: Calaca - Salong 230kV Line de-energized at 0731H. (Planned Outage) [WEBSMS] | CLUZ
12/26/2023 7:29:29 AM | Luzon Grid-12/26/2023 07:29: Salong - Steel Asia 230kV Line de-energized at 0729H. (Planned Outage) [WEBSMS] | CLUZ
12/26/2023 7:28:36 AM | Luzon Grid-12/26/2023 07:28: Salong - SLTEC 230kV Line 2 & 1 de-energized at 0727H & 0728H respectively. (Planned Outage) [WEBSMS] | CLUZ
12/26/2023 6:02:52 AM | [NSO Update] Mindanao Grid-12/26/2023 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3212MW, PK=1425MW, RR=72MW, NetOpMargin: AM=1714, PM=1428, EVE=1159 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @118MW, AG7 @27MW, PG4 @170MW [WEBSMS] | CMIN
12/26/2023 6:01:56 AM | [NSO Update] Visayas Grid-12/26/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2624MW, PK=1635MW, RR=93MW, NetOpMargin: AM=896, PM=776, EVE=323 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @320MW, PGPP1 @76MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
12/26/2023 6:00:34 AM | [NSO Update] Luzon Grid-12/26/2023 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13161MW, PK=7659MW, RR=314MW, NetOpMargin: AM=5188, PM=4176, EVE=3195 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @105MW, MPGC 1 @120MW [WEBSMS] | CLUZ
12/26/2023 5:57:59 AM | [NSO Update] Luzon Grid-12/26/2023 05:58: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CLUZ
12/26/2023 5:10:50 AM | [NSO Update] Mindanao Grid-12/26/2023 05:15: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CMIN
12/26/2023 5:09:58 AM | [NSO Update] Visayas Grid-12/26/2023 05:10: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CVIS
12/25/2023 11:38:38 PM | Mindanao Grid-12/25/2023 23:42: ASIGA HEPP (ASG) online at 2319H. Unplanned Outage. [WEBSMS] | CMIN
12/25/2023 11:05:12 PM | Mindanao Grid-12/25/2023 23:09: ASIGA (ASG) HEP Tripped at 2254H with 8MW load. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
12/25/2023 8:12:26 PM | Mindanao Grid-12/25/2023 20:16: SPC MATI cut-out at 2005H. MO Dispatched. (Unplanned Outage) [WEBSMS] | CMIN
12/25/2023 5:49:29 PM | [NSO Update] Mindanao Grid-12/25/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3189MW, PK=1727MW, RR=76MW, NetOpMargin: EVE=1387 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @68MW, AG7 @27MW, PG4 @170MW [WEBSMS] | CMIN
12/25/2023 5:47:38 PM | [NSO Update] Visayas Grid-12/25/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2258MW, PK=1832MW, RR=97MW, NetOpMargin: EVE=329 Highest Unit O/L: THVI 2 @169MW Derated Plant: LEYTE A @317MW, PGPP1 @76MW [WEBSMS] | CVIS
12/25/2023 5:44:18 PM | [NSO Update] Luzon Grid-12/25/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12069MW, PK=7810MW, RR=314MW, NetOpMargin: EVE=3945 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @105MW [WEBSMS] | CLUZ
12/25/2023 1:02:51 PM | [NSO Update] Mindanao Grid-12/25/2023 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3241MW, PK=1522MW, RR=72MW, NetOpMargin: PM=1647, EVE=1419 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @68MW, AG7 @27MW, PG4 @170MW [WEBSMS] | CMIN
12/25/2023 1:00:35 PM | [NSO Update] Visayas Grid-12/25/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2409MW, PK=1579MW, RR=91MW, NetOpMargin: PM=739, EVE=414 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: Leyte A @ 320MW, PGPP1 @ 76MW [WEBSMS] | CVIS
12/25/2023 12:57:31 PM | [NSO Update] Luzon Grid-12/25/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12685MW, PK=7037MW, RR=311MW, NetOpMargin: PM=5337, EVE=4181 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 105MW [WEBSMS] | CLUZ
12/25/2023 11:12:11 AM | Mindanao Grid-12/25/2023 11:16: SPC Mati online at 1100H. MO dispatched. [WEBSMS] | CMIN
12/25/2023 10:36:45 AM | Mindanao Grid-12/25/2023 10:40: Agus 1 U2 online at 1009H (Unplanned Outage) [WEBSMS] | CMIN
12/25/2023 6:59:46 AM | Luzon Grid-12/25/2023 06:59: Batangas Transformers unloop at 0657H, Sta-Rita-San Lorenzo 230kV Bus 1 and 2 looped at 0658H. [WEBSMS] | CLUZ
12/25/2023 5:44:39 AM | [NSO Update] Mindanao Grid-12/25/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3295MW, PK=1582MW, RR=72MW, NetOpMargin: AM=1640, PM=1621, EVE=1416 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @93MW, AG7 @27MW, PG4 @170MW [WEBSMS] | CMIN
12/25/2023 5:43:28 AM | [NSO Update] Visayas Grid-12/25/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2530MW, PK=1599MW, RR=93MW, NetOpMargin: AM=838, PM=770, EVE=437 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: TGPP @ 106.5MW, Leyte A @ 320MW, PGPP1 @ 76MW [WEBSMS] | CVIS
12/25/2023 5:42:15 AM | [NSO Update] Luzon Grid-12/25/2023 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13011MW, PK=7504MW, RR=314MW, NetOpMargin: AM=5193, PM=5185, EVE=3864 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 105MW [WEBSMS] | CLUZ
12/25/2023 4:31:06 AM | [NSO Update] Mindanao Grid-12/25/2023 04:35: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CMIN
12/25/2023 4:30:15 AM | [NSO Update] Visayas Grid-12/25/2023 04:30: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CVIS
12/25/2023 4:29:51 AM | [NSO Update] Luzon Grid-12/25/2023 04:30: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the eastern sections of Visayas and Mindanao. [WEBSMS] | CLUZ
12/25/2023 1:04:39 AM | Mindanao Grid-12/25/2023 01:08: Mt Apo U3 online at 0059H from extended PMS-GOMP. (Unplanned Outage) [WEBSMS] | CMIN
12/24/2023 11:49:24 PM | Luzon Grid-12/24/2023 23:49: San Gabriel offline at 2344H (Unplanned Outage) [WEBSMS] | CLUZ
12/24/2023 11:40:28 PM | Mindanao Grid-12/24/2023 23:44: Correction: Agus 1 Unit 2 with 30MW load tripped at 2237H due to loss of 125 DC supply. (Unplanned Outage). [WEBSMS] | CMIN
12/24/2023 11:26:55 PM | Mindanao Grid-12/24/2023 23:31: Agus 1 Unit 2 with 30MW load tripped at 2237H due to loss of 110 AC supply. (Unplanned Outage). [WEBSMS] | CMIN
12/24/2023 10:39:27 PM | Luzon Grid-12/24/2023 22:39: San Lorenzo Module 50 online at 2235H (Planned Outage) [WEBSMS] | CLUZ
12/24/2023 5:55:00 PM | [NSO Update] Mindanao Grid-12/24/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3211MW, PK=2021MW, RR=76MW, NetOpMargin: EVE=1114 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @93MW, AG7 @27MW, PG4 @170MW, STEAG U1 @ 45MW [WEBSMS] | CMIN
12/24/2023 5:53:00 PM | [NSO Update] Visayas Grid-12/24/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2382MW, PK=2026MW, RR=97MW, NetOpMargin: EVE=260 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: TGPP @ 106.5MW, Leyte A @ 320MW, PGPP1 @ 76MW [WEBSMS] | CVIS
12/24/2023 5:49:54 PM | [NSO Update] Luzon Grid-12/24/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12096MW, PK=8524MW, RR=314MW, NetOpMargin: EVE=3258 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 105MW, San Gabriel @ 330MW [WEBSMS] | CLUZ
12/24/2023 12:43:13 PM | [NSO Update] Mindanao Grid-12/24/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3327MW, PK=1852MW, RR=74MW, NetOpMargin: PM=1401, EVE=1162 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @93MW, AG7 @27MW, PG4 @170MW [WEBSMS] | CMIN
12/24/2023 12:41:37 PM | [NSO Update] Luzon Grid-12/24/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12940MW, PK=7670MW, RR=311MW, NetOpMargin: PM=4959, EVE=3483 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 105MW, San Gabriel @ 330MW [WEBSMS] | CLUZ
12/24/2023 12:39:43 PM | [NSO Update] Visayas Grid-12/24/2023 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2508MW, PK=1782MW, RR=94MW, NetOpMargin: PM=632, EVE=170 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: TGPP @106.5MW, LEYTE A @298MW, PGPP1 @76MW [WEBSMS] | CVIS
12/24/2023 11:41:03 AM | Luzon Grid-12/24/2023 11:41: Ilijan GT2-2 shutdown at 1140H (Unplanned Outage) [WEBSMS] | CLUZ
12/24/2023 11:32:08 AM | Luzon Grid-12/24/2023 11:32: Ilijan ST-2 shutdown at 1129H (Unplanned Outage) [WEBSMS] | CLUZ
12/24/2023 10:00:45 AM | Mindanao Grid-12/24/2023 10:04: TM1 Unit 1 (Hybrid BESS-Diesel) declared available for CR starting 0901H. Unplanned Outage. [WEBSMS] | CMIN
12/24/2023 9:20:28 AM | Mindanao Grid-12/24/2023 09:24: Tudaya 2 Unit 1 cut-in at 0916H. (Unplanned Outage) [WEBSMS] | CMIN
12/24/2023 8:46:56 AM | Mindanao Grid-12/24/2023 08:51: Tudaya 2 Unit 1(LD=0.59MW) and Unit 2(LD=2.66MW) tripped at 0829H. (Affected by Toril-Digos 69kV line tripping). [WEBSMS] | CMIN
12/24/2023 7:31:57 AM | Mindanao Grid-12/24/2023 07:36: LAMSAN (LSK) cut-in at 0700H (Unplanned Outage) [WEBSMS] | CMIN
12/24/2023 6:13:56 AM | [NSO Update] Mindanao Grid-12/24/2023 06:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3345MW, PK=1703MW, RR=72MW, NetOpMargin: AM=1569, PM=1428, EVE=1241 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @118MW, AG7 @27MW, PG4 @170MW [WEBSMS] | CMIN
12/24/2023 6:11:40 AM | [NSO Update] Visayas Grid-12/24/2023 06:11: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2383MW, PK=1765MW, RR=93MW, NetOpMargin: AM=525, PM=393, EVE=236 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: TGPP @ 106.5MW, Leyte A @ 320MW, PGPP1 @ 76MW [WEBSMS] | CVIS
12/24/2023 6:08:43 AM | [NSO Update] Luzon Grid-12/24/2023 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12870MW, PK=7619MW, RR=314MW, NetOpMargin: AM=4937, PM=5054, EVE=3905 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 105MW, Ilijan A @ 575MW, Ilijan B @ 165MW, San Gabriel @ 330MW [WEBSMS] | CLUZ
12/24/2023 4:25:00 AM | [NSO Update] Mindanao Grid-12/24/2023 04:29: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
12/24/2023 4:23:10 AM | [NSO Update] Visayas Grid-12/24/2023 04:23: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CVIS
12/24/2023 4:21:17 AM | [NSO Update] Luzon Grid-12/24/2023 04:21: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
12/24/2023 12:25:58 AM | Mindanao Grid-12/24/2023 00:30: Minergy Coal Unit 1 on economic shutdown at 0009H. (Unplanned Outage) [WEBSMS] | CMIN
12/23/2023 9:25:37 PM | Luzon Grid-12/23/2023 21:25: For info: Bauang 230kV Bus 1 successfully commissioned at 2101H. [WEBSMS] | CLUZ
12/23/2023 9:06:13 PM | Luzon Grid-12/23/2023 21:06: Balingueo-Bauang 230kV Line restored at 2055H (Planned Outage) [WEBSMS] | CLUZ
12/23/2023 8:34:26 PM | Luzon Grid-12/23/2023 20:34: Bauang 230kV Bus 1 energized at 2033H (On Commissioning) [WEBSMS] | CLUZ
12/23/2023 7:09:32 PM | Visayas Grid-12/23/2023 19:09: Carcon-Sangi 34.5kV Line 2 energized at 1907H per customer request.(Unplanned Outage) [WEBSMS] | CVIS
12/23/2023 7:07:50 PM | Visayas Grid-12/23/2023 19:07: Carcon-Sangi 34.5kV Line 1 energized at 1903H per customer request.(Unplanned Outage) [WEBSMS] | CVIS
12/23/2023 6:19:39 PM | Luzon Grid-12/23/2023 18:19: San Lorenzo Module 60 online at 1813H (Unplanned Outage) [WEBSMS] | CLUZ
12/23/2023 5:43:53 PM | [NSO Update] Mindanao Grid-12/23/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3274MW, PK=2101MW, RR=84MW, NetOpMargin: EVE=1090 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @118MW, AG7 @25MW, PG4 @170MW [WEBSMS] | CMIN
12/23/2023 5:42:58 PM | [NSO Update] Visayas Grid-12/23/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2453MW, PK=2146MW, RR=97MW, NetOpMargin: EVE=210 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: TGPP @ 106.5MW, Leyte A @ 315MW, PGPP1 @ 76MW [WEBSMS] | CVIS
12/23/2023 5:40:58 PM | [NSO Update] Luzon Grid-12/23/2023 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11619MW, PK=8783MW, RR=390MW, NetOpMargin: EVE=2446 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 105MW, Ilijan A @ 570MW, Ilijan B @ 165MW, San Gabriel @ 330MW [WEBSMS] | CLUZ
12/23/2023 4:22:51 PM | Mindanao Grid-12/23/2023 16:26: Libertad Power Biomass online at 1618H. (Unplanned Outage) [WEBSMS] | CMIN
12/23/2023 4:11:21 PM | Mindanao Grid-12/23/2023 16:15: Pulangi 4 Unit 2 online at 1521H. (Unplanned Outage). [WEBSMS] | CMIN
12/23/2023 4:06:31 PM | Luzon Grid-12/23/2023 16:06: Sual Unit 2 online at 1604H (Planned Outage) [WEBSMS] | CLUZ
12/23/2023 4:04:02 PM | Mindanao Grid-12/23/2023 16:08: Update: Libertad Power with 6MW emergency shutdown at 1422H. Affected by the relay testing of ZAMSURECO. (Unplanned Outage) [WEBSMS] | CMIN
12/23/2023 3:32:58 PM | Mindanao Grid-12/23/2023 15:37: WMPC DG05 shutdown at 1513H. End of RPS. System Voltage Requirement. [WEBSMS] | CMIN
12/23/2023 3:24:24 PM | Mindanao Grid-12/23/2023 15:28: Libertad Power with 6MW emergency shutdown at 1422H. Details to follow. (Unplanned Outage) [WEBSMS] | CMIN
12/23/2023 3:18:49 PM | Mindanao Grid-12/23/2023 15:22: Kibawe Solar (AGEC) with 6MW load tripped at 1433H affected by the tripping of Kibawe-Palma 69kV Line. (Unplanned Outage) [WEBSMS] | CMIN
12/23/2023 3:16:44 PM | Mindanao Grid-12/23/2023 15:20: SPC Mati with 3.3MW load tripped again at 1443H. Cause: overcurrent. (Unplanned Outage) [WEBSMS] | CMIN
12/23/2023 3:15:24 PM | Mindanao Grid-12/23/2023 15:19: SPC Mati with 3.3MW load tripped again at 1411H. Cause: overcurrent. Online back at 1427H. (Unplanned Outage) [WEBSMS] | CMIN
12/23/2023 3:10:00 PM | Mindanao Grid-12/23/2023 15:14: Correction: SPC Mati with 3.3MW load tripped at 1400H. Cause: overcurrent and overvoltage. Online back at 1406H. (Unplanned Outage) [WEBSMS] | CMIN
12/23/2023 3:03:31 PM | Mindanao Grid-12/23/2023 15:07: SPC Mati with 3.3MW load tripped at 1400H. Cause: overcurrent and overvoltage. Online back at 1411H. (Unplanned Outage) [WEBSMS] | CMIN
12/23/2023 12:59:08 PM | [NSO Update] Mindanao Grid-12/23/2023 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3325MW, PK=2011MW, RR=81MW, NetOpMargin: PM=1234, EVE=1079 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @118MW, AG7 @25MW, PG4 @170MW [WEBSMS] | CMIN
12/23/2023 12:57:39 PM | [NSO Update] Visayas Grid-12/23/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2440MW, PK=2031MW, RR=94MW, NetOpMargin: PM=315, EVE=201 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106.5MW, LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
12/23/2023 12:54:03 PM | [NSO Update] Luzon Grid-12/23/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11871MW, PK=8550MW, RR=388MW, NetOpMargin: PM=2933, EVE=1814 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @105MW, ILIJAN A @570MW, ILIJAN B @165MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/23/2023 12:28:08 PM | Visayas Grid-12/23/2023 12:28: TVI Unit#1 tripped with 130MW load at 1222H. (Unplanned outage) [WEBSMS] | CVIS
12/23/2023 10:08:27 AM | Mindanao Grid-12/23/2023 10:12: WMPC DG05 cut-in at 1002H as RPS. System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
12/23/2023 10:03:33 AM | Luzon Grid-12/23/2023 10:03: San Lorenzo Module 60 (163MW) tripped at 1000H. Lowest system frequency is 59.580Hz. [WEBSMS] | CLUZ
12/23/2023 9:45:03 AM | Mindanao Grid-12/23/2023 09:49: TM1 Unit 1 (Hybrid BESS-Diesel) declared available for CR starting 0901H. Unplanned Outage. [WEBSMS] | CMIN
12/23/2023 9:25:15 AM | Mindanao Grid-12/23/2023 09:29: Agusan Power Corp. emergency shutdown at 0910H (Unplanned Outage) [WEBSMS] | CMIN
12/23/2023 9:15:22 AM | Mindanao Grid-12/23/2023 09:19: Pulangi4 Unit 3 online at 0907H (Unplanned Outage). From MOT Off. [WEBSMS] | CMIN
12/23/2023 9:02:15 AM | Luzon Grid-12/23/2023 09:02: Mauban-SBPL 230kV Line 2 restored at 0901H (Planned Outage) [WEBSMS] | CLUZ
12/23/2023 7:36:12 AM | [NSO Update] Mindanao Grid-12/23/2023 07:40: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0731H with power going to Visayas. [WEBSMS] | CMIN
12/23/2023 7:21:50 AM | [NSO Update] Mindanao Grid-12/23/2023 07:25: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0718H from reverse power direction. For info: Lala-Dumanjug (Mindanao-Visayas) 350kV HVDC 450MW reverse power transfer test ended at 0718H (MVIP testing). [WEBSMS] | CMIN
12/23/2023 7:21:15 AM | [NSO Update] Visayas Grid-12/23/2023 07:21: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0718H from reverse power direction. For info: Lala-Dumanjug (Mindanao-Visayas) 350kV HVDC 450MW reverse power transfer test ended at 0718H (MVIP testing). [WEBSMS] | CVIS
12/23/2023 6:21:33 AM | Luzon Grid-12/23/2023 06:21: Balingueo-Bauang 230kV Line de-energized at 0620H (Planned Outage) [WEBSMS] | CLUZ
12/23/2023 5:54:26 AM | [NSO Update] Luzon Grid-12/23/2023 05:54: Weather Update: Shear Line affecting the eastern section of Luzon. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CLUZ
12/23/2023 5:53:00 AM | [NSO Update] Luzon Grid-12/23/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12240MW, PK=8729MW, RR=380MW, NetOpMargin: AM=3131, PM=2081, EVE=1518 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @105MW, ILIJAN A @570MW, ILIJAN B @165MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/23/2023 5:48:42 AM | [NSO Update] Visayas Grid-12/23/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2451MW, PK=1954MW, RR=93MW, NetOpMargin: AM=404, PM=269, EVE=183 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106.5MW, LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
12/23/2023 5:46:34 AM | [NSO Update] Mindanao Grid-12/23/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3271MW, PK=2028MW, RR=78MW, NetOpMargin: AM=1165, PM=1021, EVE=922 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @93MW, AG7 @50MW, PG4 @110MW [WEBSMS] | CMIN
12/23/2023 5:37:49 AM | Visayas Grid-12/23/2023 05:37: Carcon-Sangi 34.5kV Line 2 de-energized at 0535H per customer request. (Unplanned Outage) [WEBSMS] | CVIS
12/23/2023 5:22:54 AM | Visayas Grid-12/23/2023 05:22: TPC 1A synchronized at 0518H. [WEBSMS] | CVIS
12/23/2023 5:20:22 AM | Visayas Grid-12/23/2023 05:20: TPC 1A manually isolated from islanding operation and on houseload at 0500H to facilitate synchronization to the Grid. [WEBSMS] | CVIS
12/23/2023 5:19:38 AM | Mindanao Grid-12/23/2023 05:23: Agus 5 Unit 2 online at 0513H (Unplanned Outage). From MOT Off. [WEBSMS] | CMIN
12/23/2023 5:14:41 AM | Mindanao Grid-12/23/2023 05:18: Agus 4 Unit 3 online at 0513H. From MOT lower. [WEBSMS] | CMIN
12/23/2023 4:47:40 AM | Mindanao Grid-12/23/2023 04:51: Pulangi 4 Unit 3 cut out at 0429H (Unplanned Outage). MOT Off [WEBSMS] | CMIN
12/23/2023 4:46:00 AM | [NSO Update] Mindanao Grid-12/23/2023 04:50: For info: Lala-Dumanjug (Mindanao-Visayas) 350kV HVDC reached 450MW reverse power transfer at 0436H (MVIP testing). [WEBSMS] | CMIN
12/23/2023 4:45:55 AM | [NSO Update] Visayas Grid-12/23/2023 04:45: For info: Lala-Dumanjug (Mindanao-Visayas) 350kV HVDC reached 450MW reverse power transfer at 0436H (MVIP testing). [WEBSMS] | CVIS
12/23/2023 4:45:11 AM | Mindanao Grid-12/23/2023 04:49: Agus 5 shutdown at 0428H. MOT OFF [WEBSMS] | CMIN
12/23/2023 4:38:38 AM | Mindanao Grid-12/23/2023 04:42: Agus 4 HEP Unit 3 shutdown at 0429H (Unplanned Outage) MOT Off [WEBSMS] | CMIN
12/23/2023 4:26:28 AM | [NSO Update] Mindanao Grid-12/23/2023 04:30: Weather Update: Shear Line affecting the eastern section of Luzon. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CMIN
12/23/2023 4:26:08 AM | [NSO Update] Visayas Grid-12/23/2023 04:26: Weather Update: Shear Line affecting the eastern section of Luzon. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CVIS
12/23/2023 4:00:13 AM | Visayas Grid-12/23/2023 04:00: Magdugo SS 300MVA Transformer 3 energized at 0356H. [WEBSMS] | CVIS
12/23/2023 3:34:16 AM | Visayas Grid-12/23/2023 03:34: TPC 1A on islanding operation at 0318H due to tripping of 34.5kV Sangi-2nd Lift line. [WEBSMS] | CVIS
12/23/2023 3:03:41 AM | Visayas Grid-12/23/2023 03:03: 34.5kV Carcon-Sangi Line 1 tripped at 0238H (customer owned). [WEBSMS] | CVIS
12/23/2023 1:13:25 AM | Luzon Grid-12/23/2023 01:13: SLTEC Unit 1 shutdown at 0111H. (Unplanned Outage) [WEBSMS] | CLUZ
12/23/2023 12:01:18 AM | Luzon Grid-12/23/2023 00:01: SLPGC Unit 1 shutdown at 2359H. (Unplanned Outage) [WEBSMS] | CLUZ
12/22/2023 11:57:09 PM | Luzon Grid-12/22/2023 23:57: San Lorenzo Module 50 shutdown at 2355H. (Planned Outage) [WEBSMS] | CLUZ
12/22/2023 11:38:00 PM | [NSO Update] Visayas Grid-12/22/2023 23:38: For info: Lala-Dumanjug (Mindanao-Visayas) 350kV HVDC 450MW reverse power transfer test started at 2331H (MVIP testing) [WEBSMS] | CVIS
12/22/2023 11:37:52 PM | [NSO Update] Mindanao Grid-12/22/2023 23:41: For info: Lala-Dumanjug (Mindanao-Visayas) 350kV HVDC 450MW reverse power transfer test started at 2331H (MVIP testing) [WEBSMS] | CMIN
12/22/2023 11:34:26 PM | [NSO Update] Mindanao Grid-12/22/2023 23:38: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2331H with power going to Mindanao [WEBSMS] | CMIN
12/22/2023 11:34:18 PM | [NSO Update] Visayas Grid-12/22/2023 23:34: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2331H with power going to Mindanao [WEBSMS] | CVIS
12/22/2023 11:32:36 PM | [NSO Update] Mindanao Grid-12/22/2023 23:36: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2318H from forward power direction [WEBSMS] | CMIN
12/22/2023 11:32:32 PM | [NSO Update] Visayas Grid-12/22/2023 23:32: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2318H from forward power direction [WEBSMS] | CVIS
12/22/2023 11:15:37 PM | Mindanao Grid-12/22/2023 23:19: Mt Apo Unit 1 online at 2030H. (Planned Outage-GOMP) [WEBSMS] | CMIN
12/22/2023 9:19:41 PM | Mindanao Grid-12/22/2023 21:23: WMPC DG04 shutdown at 2113H. End of RPS. System Voltage Requirement. [WEBSMS] | CMIN
12/22/2023 8:07:18 PM | Mindanao Grid-12/22/2023 20:11: SPC MATI cut-out at 2005H. MO Dispatched. [WEBSMS] | CMIN
12/22/2023 6:30:08 PM | Visayas Grid-12/22/2023 18:30: THVI U-1 cut-in to the system at 1825H, initial load 8.0MW [WEBSMS] | CVIS
12/22/2023 6:10:01 PM | Luzon Grid-12/22/2023 18:10: Bauang 230kV Bus 1 was de-energized at 1809H. (Planned Outage) [WEBSMS] | CLUZ
12/22/2023 6:08:49 PM | Mindanao Grid-12/22/2023 18:12: Placer SS Power Transformer No.3 energized at 1759H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
12/22/2023 5:45:28 PM | [NSO Update] Visayas Grid-12/22/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2585MW, PK=2228MW, RR=97MW, NetOpMargin: EVE=260 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106.5MW, LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
12/22/2023 5:44:24 PM | [NSO Update] Luzon Grid-12/22/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12098MW, PK=9364MW, RR=405MW, NetOpMargin: EVE=2329 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 105MW, SLPGC 1 @ 130MW, Ilijan A @ 575MW, Ilijan B @ 165MW, San Gabriel @ 330MW [WEBSMS] | CLUZ
12/22/2023 5:41:30 PM | [NSO Update] Mindanao Grid-12/22/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3165MW, PK=2196MW, RR=83MW, NetOpMargin: EVE=885 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @93MW, AG7 @25MW, PG4 @110MW [WEBSMS] | CMIN
12/22/2023 3:59:28 PM | Mindanao Grid-12/22/2023 16:03: SPG with 5.7MW load tripped at 1122H. Cause: Control oil pressure fluctuation. ( Unplanned outage) [WEBSMS] | CMIN
12/22/2023 3:22:36 PM | Mindanao Grid-12/22/2023 15:26: WMPC DG01 with 8.5MW load tripped at 1509H. Indication Hight Temperature Low Pressure Stop. (Unplanned Outage) [WEBSMS] | CMIN
12/22/2023 12:44:20 PM | Luzon Grid-12/22/2023 12:44: Hermosa-Calaguiman 69kV Line restored at 1241H, tripped at 1133H (Unplanned Outage) [WEBSMS] | CLUZ
12/22/2023 12:42:37 PM | [NSO Update] Mindanao Grid-12/22/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3210MW, PK=2217MW, RR=82MW, NetOpMargin: PM=911, EVE=906 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @93MW, AG7 @25MW, PG4 @110MW [WEBSMS] | CMIN
12/22/2023 12:41:50 PM | [NSO Update] Visayas Grid-12/22/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2596MW, PK=2216MW, RR=94MW, NetOpMargin: PM=286, EVE=242 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: TGPP @ 106.5MW, Leyte A @ 310MW, PGPP1 @ 75.5MW [WEBSMS] | CVIS
12/22/2023 12:40:06 PM | [NSO Update] Luzon Grid-12/22/2023 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12500MW, PK=9670MW, RR=420MW, NetOpMargin: PM=2410, EVE=1945 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 105MW, SLPGC 1 @ 130MW, Ilijan A @ 575MW, Ilijan B @ 165MW, San Gabriel @ 330MW [WEBSMS] | CLUZ
12/22/2023 11:24:47 AM | Visayas Grid-12/22/2023 11:24: Calong-Calong-Daanlungsod 138kV Line 2 energized at 1123H. (Planned Outage) . [WEBSMS] | CVIS
12/22/2023 10:53:13 AM | Mindanao Grid-12/22/2023 10:57: WMPC DG01 cut-in at 1050H as RPS. System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
12/22/2023 9:25:06 AM | Mindanao Grid-12/22/2023 09:29: Agus 6 Unit 2 with 31MW load shutdown at 0914H. PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
12/22/2023 9:21:46 AM | Mindanao Grid-12/22/2023 09:25: AGUS 6 Unit 1 with load of 10MW shutdown at 0911H. PMS-GOMP (Planned Outage) [WEBSMS] | CMIN
12/22/2023 9:11:52 AM | Mindanao Grid-12/22/2023 09:15: TMI 1 declared available for CR at at 0901H. (Unplanned Outage) [WEBSMS] | CMIN
12/22/2023 9:04:55 AM | Mindanao Grid-12/22/2023 09:08: WMPC DG04 online at 0850H. MO dispatch (RTD). [WEBSMS] | CMIN
12/22/2023 9:02:45 AM | Luzon Grid-12/22/2023 09:02: Gamu - UPSI Gamu BESS 69kV Line restored at 0902H (Planned Outage) [WEBSMS] | CLUZ
12/22/2023 8:36:04 AM | Luzon Grid-12/22/2023 08:36: Gamu - UPSI Gamu BESS 69kV Line de-energized at 0834H (Planned Outage) [WEBSMS] | CLUZ
12/22/2023 8:22:33 AM | Visayas Grid-12/22/2023 08:22: Calong-Calong-Daanlungsod 138kV Line 2 de-energized at 0819H. (Planned Outage) . [WEBSMS] | CVIS
12/22/2023 7:17:32 AM | Luzon Grid-12/22/2023 07:17: Mauban-SBPL 230kV Line 2 de-energized at 0717H (Planned Outage) [WEBSMS] | CLUZ
12/22/2023 6:32:53 AM | Mindanao Grid-12/22/2023 06:36: Placer SS Power Transformer No.3 deenergized at 0614H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
12/22/2023 6:07:07 AM | [NSO Update] Mindanao Grid-12/22/2023 06:11: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3173MW, PK=2204MW, RR=92MW, NetOpMargin: AM=887, PM=894, EVE=855 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @118MW, AG7 @25MW, PG4 @110MW [WEBSMS] | CMIN
12/22/2023 6:00:38 AM | [NSO Update] Visayas Grid-12/22/2023 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2521MW, PK=2171MW, RR=93MW, NetOpMargin: AM=257, PM=234, EVE=288 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106.5MW, LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
12/22/2023 5:55:47 AM | [NSO Update] Luzon Grid-12/22/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12635MW, PK=10109MW, RR=404MW, NetOpMargin: AM=2122, PM=1650, EVE=1303 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @105MW, SLPGC 1 @130MW, ILIJAN A @575MW, ILIJAN B @165MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/22/2023 4:44:34 AM | [NSO Update] Luzon Grid-12/22/2023 04:44: Weather Update: Shear Line affecting the eastern sections of Luzon. Northeast Monsoon affecting the rest of Northern and Central Luzon. [WEBSMS] | CLUZ
12/22/2023 4:42:58 AM | [NSO Update] Luzon Grid-12/22/2023 04:42: at 0400H Weather Update: Shear Line affecting the eastern sections of Luzon. Northeast Monsoon affecting the rest of Northern and Central Luzon. [WEBSMS] | CLUZ
12/22/2023 4:42:25 AM | [NSO Update] Visayas Grid-12/22/2023 04:42: Weather Update: Shear Line affecting the eastern sections of Luzon. Northeast Monsoon affecting the rest of Northern and Central Luzon. [WEBSMS] | CVIS
12/22/2023 4:42:04 AM | [NSO Update] Mindanao Grid-12/22/2023 04:46: Weather Update: Shear Line affecting the eastern sections of Luzon. Northeast Monsoon affecting the rest of Northern and Central Luzon. [WEBSMS] | CMIN
12/22/2023 4:31:40 AM | [NSO Update] Visayas Grid-12/22/2023 04:31: Shear Line affecting the eastern sections of Luzon. Northeast Monsoon affecting the rest of Northern and Central Luzon. [WEBSMS] | CVIS
12/21/2023 10:07:07 PM | Luzon Grid-12/21/2023 22:07: SLTEC Unit 2 (69MW) tripped at 2203H. [WEBSMS] | CLUZ
12/21/2023 10:01:05 PM | Mindanao Grid-12/21/2023 22:05: PULANGI 4 UNIT 2 with 25MW load on emergency shutdown at 2155H. Cause: Excessive oil leak at unit 2 servo motor. (Unplanned Outage) [WEBSMS] | CMIN
12/21/2023 9:58:53 PM | Luzon Grid-12/21/2023 21:58: Muntinlupa(Sucat) 300MVA Transformer 4 restored at 2158H (Unplanned Outage) [WEBSMS] | CLUZ
12/21/2023 9:43:49 PM | Mindanao Grid-12/21/2023 21:47: WMPC DG04 shutdown at 2122H. End of RPS. System Voltage Requirement. [WEBSMS] | CMIN
12/21/2023 9:43:29 PM | Visayas Grid-12/21/2023 21:43: Magdugo-Dumanjug 230 KV Line 1 energized at 2141H, under test and commissioning. [WEBSMS] | CVIS
12/21/2023 7:25:32 PM | Luzon Grid-12/21/2023 19:25: Tiwi Plant A-Tiwi Plant C 230kV Line 2 restored at 1924H (Planned Outage) [WEBSMS] | CLUZ
12/21/2023 5:52:13 PM | [NSO Update] Visayas Grid-12/21/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2535MW, PK=2227MW, RR=97MW, NetOpMargin: EVE=211 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106.5MW, LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
12/21/2023 5:46:23 PM | [NSO Update] Luzon Grid-12/21/2023 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12253MW, PK=10247MW, RR=404MW, NetOpMargin: EVE=1602 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @105MW, SLPGC 1 @130MW, ILIJAN A @575MW, ILIJAN B @165MW, SAN GABRIEL @330MW, SLTEC 2 @98MW [WEBSMS] | CLUZ
12/21/2023 5:38:45 PM | [NSO Update] Mindanao Grid-12/21/2023 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3115MW, PK=2169MW, RR=76MW, NetOpMargin: EVE=871 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @112MW, AG7 @25MW, PG4 @170MW [WEBSMS] | CMIN
12/21/2023 4:38:29 PM | Luzon Grid-12/21/2023 16:38: Ilijan ST2 online at 1636H (Unplanned Outage) [WEBSMS] | CLUZ
12/21/2023 4:27:15 PM | Mindanao Grid-12/21/2023 16:31: WMPC DG01 shutdown at 1614H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/21/2023 3:27:00 PM | Luzon Grid-12/21/2023 15:27: Malaya-Lumban 230kV Line 2 restored at 1524H (Planned Outage) [WEBSMS] | CLUZ
12/21/2023 1:25:33 PM | Luzon Grid-12/21/2023 13:25: Ilijan GT2-2 online at 1324H. (Unplanned Outage) [WEBSMS] | CLUZ
12/21/2023 12:48:20 PM | [NSO Update] Mindanao Grid-12/21/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3163MW, PK=2218MW, RR=80MW, NetOpMargin: PM=865, EVE=756 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @112MW, AG7 @25MW, PG4 @170MW [WEBSMS] | CMIN
12/21/2023 12:47:31 PM | [NSO Update] Visayas Grid-12/21/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2571MW, PK=2249MW, RR=93MW, NetOpMargin: PM=229, EVE=221 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: TGPP @ 106.5MW, Leyte A @ 320MW, PGPP1 @ 75.5MW [WEBSMS] | CVIS
12/21/2023 12:45:40 PM | [NSO Update] Luzon Grid-12/21/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12673MW, PK=10684MW, RR=405MW, NetOpMargin: PM=1584, EVE=1254 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 105MW, SLPGC 1 @ 130MW, San Gabriel @ 330MW [WEBSMS] | CLUZ
12/21/2023 12:41:21 PM | Mindanao Grid-12/21/2023 12:45: AGUS 7 U1 online at 1230H from FO. (Unplanned Outage) [WEBSMS] | CMIN
12/21/2023 12:27:05 PM | Visayas Grid-12/21/2023 12:27: Calong-Calong-Daanlungsod 138kV Line 1 energized at 1209H. (Planned Outage) [WEBSMS] | CVIS
12/21/2023 12:16:54 PM | Mindanao Grid-12/21/2023 12:20: AGUS 7 U1 tripped at 1152H with 20MW load. Indication: Governor, 86T, excitation Transformer Alarm Trip. (Unplanned Outage) [WEBSMS] | CMIN
12/21/2023 11:14:38 AM | Mindanao Grid-12/21/2023 11:18: WMPC DG04 online at 1050H as RPS - System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
12/21/2023 10:32:10 AM | Luzon Grid-12/21/2023 10:32: San Jose PCB 8-08CB04SJO was opened at 1029H. (Unplanned Outage) [WEBSMS] | CLUZ
12/21/2023 9:52:50 AM | Luzon Grid-12/21/2023 09:52: Muntinlupa(Sucat) 300MVA Transformer No. 4 was de-energized at 0950H. (Unplanned Outage) [WEBSMS] | CLUZ
12/21/2023 9:11:28 AM | Mindanao Grid-12/21/2023 09:15: WMPC DG07 online at 0850H. MO dispatch (RTD). (Unplanned Outage) [WEBSMS] | CMIN
12/21/2023 9:06:53 AM | Mindanao Grid-12/21/2023 09:10: TM1 Unit 1 (Hybrid BESS-Diesel) declared available for CR starting 0901H. Unplanned Outage. [WEBSMS] | CMIN
12/21/2023 8:54:56 AM | Visayas Grid-12/21/2023 08:54: Calong-Calong-Daanbantayan 138kV Line 1 de-energized at 0831H. (Planned Outage) [WEBSMS] | CVIS
12/21/2023 6:21:08 AM | Luzon Grid-12/21/2023 06:21: Malaya-Lumban 230kV line 2 was de-energized at 0616H. (Planned Outage) [WEBSMS] | CLUZ
12/21/2023 5:57:08 AM | [NSO Update] Mindanao Grid-12/21/2023 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3168MW, PK=2047MW, RR=80MW, NetOpMargin: AM=1041, PM=866, EVE=793 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @80MW, AG4 @95MW, AG5 @30MW, AG6 @112MW, AG7 @25MW, PG4 @170MW [WEBSMS] | CMIN
12/21/2023 5:53:12 AM | [NSO Update] Visayas Grid-12/21/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2453MW, PK=2155MW, RR=93MW, NetOpMargin: AM=205, PM=275, EVE=235 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106.5MW, LEYTE A @320MW, PGPP1 @75.5MW [WEBSMS] | CVIS
12/21/2023 5:45:46 AM | [NSO Update] Luzon Grid-12/21/2023 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12816MW, PK=10606MW, RR=404MW, NetOpMargin: AM=1806, PM=1600, EVE=1181 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @105MW, SLPGC 1 @130MW SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/21/2023 4:04:22 AM | [NSO Update] Luzon Grid-12/21/2023 04:04: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the eastern sections of Southern Luzon, Visayas and Mindanao. [WEBSMS] | CLUZ
12/21/2023 4:04:20 AM | [NSO Update] Mindanao Grid-12/21/2023 04:08: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the eastern sections of Southern Luzon, Visayas and Mindanao. [WEBSMS] | CMIN
12/21/2023 4:04:03 AM | [NSO Update] Visayas Grid-12/21/2023 04:04: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting the eastern sections of Southern Luzon, Visayas and Mindanao. [WEBSMS] | CVIS
12/21/2023 12:09:33 AM | Luzon Grid-12/21/2023 00:09: Bacnotan New 100MVA Transformer 2 energized at high side (230kV) at 0008H. (Ongoing Commissioning) [WEBSMS] | CLUZ
12/20/2023 9:35:31 PM | Visayas Grid-12/20/2023 21:35: Magdugo SS 230kV Bus 2 energized at 2116H. (Planned Outage) [WEBSMS] | CVIS
12/20/2023 9:26:26 PM | Mindanao Grid-12/20/2023 21:30: WMPC shutdown at 2114H as RPS. System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
12/20/2023 8:22:08 PM | Mindanao Grid-12/20/2023 20:26: SPC MATI cut-out at 2005H. MO Dispatched. [WEBSMS] | CMIN
12/20/2023 8:06:43 PM | Mindanao Grid-12/20/2023 20:11: TM1 Unit 1 (Hybrid BESS-Diesel) on forced outage AT 2001H due to PCS inverter high temperature. Note: TSI Unit 1 & Unit 2 as replacement power (CR). [WEBSMS] | CMIN
12/20/2023 7:43:23 PM | Luzon Grid-12/20/2023 19:43: San Jose-Angat 115kV Line 1 energized at San Jose side at 1943H. (Planned Outage) [WEBSMS] | CLUZ
12/20/2023 7:22:05 PM | Luzon Grid-12/20/2023 19:22: Bay-Makban Plant B 230kV Line 2 restored at 1921H. (Planned Outage) [WEBSMS] | CLUZ
12/20/2023 6:45:29 PM | Mindanao Grid-12/20/2023 18:49: AGUS 7 Unit 1 online at 1734H. PMS (GOMP). Planned Outage. [WEBSMS] | CMIN
12/20/2023 5:59:13 PM | [NSO Update] Visayas Grid-12/20/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2548MW, PK=2267MW, RR=97MW, NetOpMargin: EVE=185 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106.5MW, LEYTE A @312MW, PGPP1 @75.5MW [WEBSMS] | CVIS
12/20/2023 5:52:54 PM | [NSO Update] Luzon Grid-12/20/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12117MW, PK=10636MW, RR=404MW, NetOpMargin: EVE=1077 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SCPC 3 @140MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/20/2023 5:49:58 PM | [NSO Update] Mindanao Grid-12/20/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3063MW, PK=2296MW, RR=83MW, NetOpMargin: EVE=684 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @112MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
12/20/2023 5:09:33 PM | Mindanao Grid-12/20/2023 17:13: Peak Power San Francisco U2 shutdown at 1648H. MO Dispatch. (Unplanned Outage) [WEBSMS] | CMIN
12/20/2023 5:02:40 PM | Mindanao Grid-12/20/2023 17:06: WMPC DG07 shutdown at 1656H. MO Dispatch. (Unplanned Outage) [WEBSMS] | CMIN
12/20/2023 4:59:32 PM | Mindanao Grid-12/20/2023 17:03: WMPC DG01 shutdown at 1624H as RPS. (Unplanned Outage) [WEBSMS] | CMIN
12/20/2023 3:10:32 PM | Mindanao Grid-12/20/2023 15:14: WMPC DG07 cut-in at 1418H. MO dispatch (RTD). [WEBSMS] | CMIN
12/20/2023 3:05:48 PM | Luzon Grid-12/20/2023 15:06: Lumban-Malaya 230kV Line 1 restored at 1504H. (Planned Outage) [WEBSMS] | CLUZ
12/20/2023 2:00:28 PM | Luzon Grid-12/20/2023 14:00: San Jose PCB 8-07CB08SJO restored at 1400H. (Unplanned Outage) [WEBSMS] | CLUZ
12/20/2023 1:51:30 PM | Mindanao Grid-12/20/2023 13:55: Peak Power San Francisco U2 cut-in at 1348H. MO Dispatch. [WEBSMS] | CMIN
12/20/2023 1:05:13 PM | Mindanao Grid-12/20/2023 13:09: Baloi-Agus 6 69kV Tie-Line energized at 1223H. Unplanned Outage. [WEBSMS] | CMIN
12/20/2023 1:00:55 PM | Mindanao Grid-12/20/2023 13:05: Baloi-Agus 6 69kV Tie-Line autotripped at 1131H. Unplanned Outage. [WEBSMS] | CMIN
12/20/2023 12:52:13 PM | Mindanao Grid-12/20/2023 12:56: Kauswagan-GNPK 230kV L4 energized at 1127H. After conducting leak repair of their Unit #4 outdoor GIS. (Shutdown requested by GNPK). [WEBSMS] | CMIN
12/20/2023 12:51:22 PM | [NSO Update] Mindanao Grid-12/20/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3111MW, PK=2264MW, RR=83MW, NetOpMargin: PM=763, EVE=742 Highest Unit O/L: GNPK 1&2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @112MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
12/20/2023 12:47:26 PM | [NSO Update] Luzon Grid-12/20/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12810MW, PK=10797MW, RR=405MW, NetOpMargin: PM=1607, EVE=1145 Highest Unit O/L: CALACA 2 @175MW, SLPGC 1 @130MW, SAN GABRIEL @330MW Derated Plant: CALACA 2 @175MW, SLPGC 1 @130MW, SCPC 3 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/20/2023 12:42:04 PM | [NSO Update] Visayas Grid-12/20/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2694MW, PK=2225MW, RR=93MW, NetOpMargin: PM=376, EVE=250 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106.5MW, LEYTE A @307MW, PGPP1 @75.5MW [WEBSMS] | CVIS
12/20/2023 11:27:29 AM | Mindanao Grid-12/20/2023 11:31: PEAK POWER SAN FRANCISCO Unit 2 cut-in at 1120H. MO dispatch (RTD). [WEBSMS] | CMIN
12/20/2023 11:24:27 AM | Mindanao Grid-12/20/2023 11:28: SPC MATI Cut-in with 6.0MW Load at 1100H. MO Dispatch. [WEBSMS] | CMIN
12/20/2023 11:19:37 AM | Mindanao Grid-12/20/2023 11:23: Tagoloan-Manolo 138kV L1 energized at 1100H. Emergency shutdown requested by NPD-MSO [WEBSMS] | CMIN
12/20/2023 11:15:01 AM | Mindanao Grid-12/20/2023 11:19: Tagoloan-Manolo 138kV L1 deenergized at 1038H. Emergency shutdown requested by NPD-MSO. [WEBSMS] | CMIN
12/20/2023 11:06:03 AM | Luzon Grid-12/20/2023 11:06: Kalayaan Unit 1 (183MW) tripped as generator at 1103H. Lowest System Frequency is 59.461Hz. [WEBSMS] | CLUZ
12/20/2023 10:54:59 AM | Mindanao Grid-12/20/2023 10:59: WMPC DG01 cut-in at 1051H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/20/2023 9:14:06 AM | Luzon Grid-12/20/2023 09:14: San Jose-Angat 115kV Line 1 de-energized at 0912H (Planned Outage) [WEBSMS] | CLUZ
12/20/2023 9:08:09 AM | Luzon Grid-12/20/2023 09:08: Kalayaan Unit 1 (183MW) tripped as generator at 0903H. Lowest System Frequency is 59.497Hz. [WEBSMS] | CLUZ
12/20/2023 8:54:35 AM | Mindanao Grid-12/20/2023 08:58: WMPC DG04 cut-in at 0851H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/20/2023 8:54:09 AM | Luzon Grid-12/20/2023 08:54: Tiwi Plant A-Tiwi Plant C 230kV Line 2 de-energized at 0853H (Planned Outage) [WEBSMS] | CLUZ
12/20/2023 8:02:55 AM | Mindanao Grid-12/20/2023 08:07: TM1 Unit 1 (Hybrid BESS-Diesel) declared available for CR starting 0801H. Unplanned Outage. [WEBSMS] | CMIN
12/20/2023 8:00:26 AM | Luzon Grid-12/20/2023 08:00: QPPL shutdown at 0800H (Unplanned Outage) [WEBSMS] | CLUZ
12/20/2023 7:18:45 AM | Luzon Grid-12/20/2023 07:19: Bay-Makban Plant B 230kV Line 2 de-energized at 0718H (Planned Outage) [WEBSMS] | CLUZ
12/20/2023 7:09:07 AM | Mindanao Grid-12/20/2023 07:13: Agus 4 unit 3 shutdown with 30.28MW load at 0701H. (Planned Outage- Non GOMP). [WEBSMS] | CMIN
12/20/2023 6:24:38 AM | Luzon Grid-12/20/2023 06:24: Lumban-Malaya 230kV Line 1 de-energized at 0623H (Planned Outage) [WEBSMS] | CLUZ
12/20/2023 6:09:16 AM | [NSO Update] Visayas Grid-12/20/2023 06:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2439MW, PK=2135MW, RR=93MW, NetOpMargin: AM=211, PM=244, EVE=241 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106.5MW, LEYTE A @307MW, PGPP1 @75.5MW [WEBSMS] | CVIS
12/20/2023 5:49:27 AM | [NSO Update] Luzon Grid-12/20/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13530MW, PK=10421MW, RR=404MW, NetOpMargin: AM=2705, PM=2524, EVE=1799 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @175MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/20/2023 5:47:38 AM | [NSO Update] Mindanao Grid-12/20/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3112MW, PK=2073MW, RR=81MW, NetOpMargin: AM=958, PM=905, EVE=811 Highest Unit O/L: GNPK 1&2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @112MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
12/20/2023 4:17:37 AM | [NSO Update] Mindanao Grid-12/20/2023 04:21: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 185 km South of Puerto Princesa City, Palawan (8.1�N, 118.6�E). Northeast Monsoon affecting Northern and Central Luzon. Shear Line affecting the eastern section of Southern Luzon. [WEBSMS] | CMIN
12/20/2023 4:17:18 AM | [NSO Update] Visayas Grid-12/20/2023 04:17: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 185 km South of Puerto Princesa City, Palawan (8.1�N, 118.6�E). Northeast Monsoon affecting Northern and Central Luzon. Shear Line affecting the eastern section of Southern Luzon. [WEBSMS] | CVIS
12/20/2023 4:16:54 AM | [NSO Update] Luzon Grid-12/20/2023 04:17: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 185 km South of Puerto Princesa City, Palawan (8.1�N, 118.6�E). Northeast Monsoon affecting Northern and Central Luzon. Shear Line affecting the eastern section of Southern Luzon. [WEBSMS] | CLUZ
12/20/2023 3:29:34 AM | Mindanao Grid-12/20/2023 03:33: Lamsan Biomass (LSK) on emergency shutdown at 0010H to conduct boiler inspection for possible leaking. Follow RTD. Unplanned Outage. [WEBSMS] | CMIN
12/20/2023 12:29:34 AM | Luzon Grid-12/20/2023 00:29: Kalayaan Unit 4 tripped as pump at 0017H. The highest frequency is 60.36Hz (Unplanned Outage) [WEBSMS] | CLUZ
12/20/2023 12:13:22 AM | Mindanao Grid-12/20/2023 00:17: Baloi-Villanueva 230KV L1 re-energized at 2324H. From NPD-MSO requested shutdown (Forced Outage / Non-GOMP). [WEBSMS] | CMIN
12/20/2023 12:06:58 AM | Mindanao Grid-12/20/2023 00:11: Baloi-Villanueva 230KV L1 de-energized at 2109H to continue the testing of Main 2 Protection to configure the line protection for implementation of 3rd line of Single- Pole Tripping and Auto-reclosing of TL in Mindanao. MSO-NPD requested shutdown. Forced Outage / Non-GOMP. [WEBSMS] | CMIN
12/19/2023 10:52:45 PM | Luzon Grid-12/19/2023 22:53: Tiwi C 230kV Bus 1 restored at 2252H (Unplanned Outage) [WEBSMS] | CLUZ
12/19/2023 9:28:52 PM | Luzon Grid-12/19/2023 21:29: Bay-Makban Plant B 230kV line 1 restored at 2128H (Planned Outage) [WEBSMS] | CLUZ
12/19/2023 9:27:37 PM | Mindanao Grid-12/19/2023 21:31: Update: TM1 Unit 1 (Hybrid BESS-Diesel) on forced outage AT 2001H due to PCS inverter high temperature. Note: TSI Unit 1 & Unit 2 as replacement power (CR). [WEBSMS] | CMIN
12/19/2023 8:59:37 PM | Mindanao Grid-12/19/2023 21:03: Emergency shutdown of LALA SS 230 kV PCB 8-06CB24LLA at 2053H as a hotspot is found at Phase B facing 8-06DS25LLA. [WEBSMS] | CMIN
12/19/2023 8:15:52 PM | Mindanao Grid-12/19/2023 20:20: TM1 Unit 1 (Hybrid BESS-Diesel) on forced outage AT 0801H due to PCS inverter high temperature. Note: TSI Unit 1 & Unit 2 as replacement power (CR). [WEBSMS] | CMIN
12/19/2023 8:01:03 PM | Mindanao Grid-12/19/2023 20:05: Baloi-Villanueva 230KV L2 energized back at 1951H and looped at Baloi SS at 1952H after completion of line protection configuration and associated BFRs for the implementation of the 4th line of Single- Pole Tripping and Auto-reclosing of TL in Mindanao. MSO-NPD requested a shutdown. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
12/19/2023 5:53:01 PM | [NSO Update] Mindanao Grid-12/19/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3078MW, PK=2151MW, RR=83MW, NetOpMargin: EVE=844 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @112MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
12/19/2023 5:47:06 PM | [NSO Update] Visayas Grid-12/19/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2559MW, PK=2207MW, RR=97MW, NetOpMargin: EVE=255 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: TGPP @ 106.5MW, Leyte A @ 320MW, PGPP1 @ 75.5MW [WEBSMS] | CVIS
12/19/2023 5:44:56 PM | [NSO Update] Luzon Grid-12/19/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12813MW, PK=10378MW, RR=432MW, NetOpMargin: EVE=2003 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, SCPC 3 @ 130MW, SLPGC 1 @ 130MW, San Gabriel @ 330MW [WEBSMS] | CLUZ
12/19/2023 5:06:45 PM | Luzon Grid-12/19/2023 17:07: San Jose-San Rafael (CND) 230kV line restored at 1706H (Unplanned Outage) [WEBSMS] | CLUZ
12/19/2023 4:17:03 PM | Mindanao Grid-12/19/2023 16:21: WMPC DG01 cut-out at 1613H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/19/2023 1:40:34 PM | Mindanao Grid-12/19/2023 13:44: (Correction) TM1 Unit 2 declared on forced outage. Failed to cut-in at 1305H for MO dispatch. Cause: For verification. [WEBSMS] | CMIN
12/19/2023 1:39:45 PM | Mindanao Grid-12/19/2023 13:44: TM2 Unit 2 declared on forced outage. Failed to cut-in at 1305H for MO dispatch. Cause: For verification. [WEBSMS] | CMIN
12/19/2023 1:03:02 PM | [NSO Update] Mindanao Grid-12/19/2023 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3112MW, PK=2102MW, RR=92MW, NetOpMargin: PM=919, EVE=919 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @112MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
12/19/2023 12:51:33 PM | [NSO Update] Visayas Grid-12/19/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2520MW, PK=2174MW, RR=94MW, NetOpMargin: PM=251, EVE=273 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106.5MW, LEYTE A @320MW, PGPP1 @75.5MW [WEBSMS] | CVIS
12/19/2023 12:50:09 PM | [NSO Update] Luzon Grid-12/19/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13389MW, PK=10523MW, RR=442MW, NetOpMargin: PM=2425, EVE=1887 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/19/2023 12:17:35 PM | Mindanao Grid-12/19/2023 12:21: AGUS 2 Unit 2 cut-in at 1211H. (Unplanned Outage) [WEBSMS] | CMIN
12/19/2023 11:44:41 AM | Luzon Grid-12/19/2023 11:44: San Jose-San Rafael (CND) 230kV line was de-energized at 1144H. (Unplanned Outage) [WEBSMS] | CLUZ
12/19/2023 11:03:00 AM | Mindanao Grid-12/19/2023 11:07: SUPREME POWER MATI cut-in at 1100H. MO dispatch (RTD). [WEBSMS] | CMIN
12/19/2023 11:01:45 AM | Mindanao Grid-12/19/2023 11:06: WMPC DG01 cut-in at 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/19/2023 10:53:47 AM | Mindanao Grid-12/19/2023 10:58: (Update) AGUS 2 Unit 2 tripped with 25.2MW load at 1019H. Indication: Excitation Fault, 5C. Lowest system frequency recorded was 59.67Hz. (Unplanned Outage). [WEBSMS] | CMIN
12/19/2023 10:50:40 AM | Mindanao Grid-12/19/2023 10:54: Agus2 -KIbawe 138 kV L2 attempted to re-energize at 1036H but failed due to SOTF relay indication. Advised Agus 2 Switchyard SEOD on duty to inform TL supervisor to conduct line patrol. ( Note: Said line was energized up tower # 33 only for anti-pilferage purposes) [WEBSMS] | CMIN
12/19/2023 10:41:27 AM | Mindanao Grid-12/19/2023 10:45: Agus2 HEP U2 with 25.2 MW load simultaneously tripped with Agus2 -KIbawe 138 kV L2 at 1019H with CN fault loop. ( Note: Said line was energized up tower # 33 only for anti-pilferage purposes) [WEBSMS] | CMIN
12/19/2023 10:31:21 AM | Luzon Grid-12/19/2023 10:31: Tiwi C 230kV Bus 1 was de-energized at 1030H. (Unplanned Outage) [WEBSMS] | CLUZ
12/19/2023 10:31:05 AM | Mindanao Grid-12/19/2023 10:35: AGUS 2 Unit 2 tripped with 25.2MW load at 1019H. Indication: to follow. Lowest system frequency recorded was 59.67Hz. (Unplanned Outage). [WEBSMS] | CMIN
12/19/2023 9:46:04 AM | Mindanao Grid-12/19/2023 09:50: Lala-Aurora 138KV L1 re-energized at 0859H & looped at Aurora SS at 0905H. From Unplanned Outage. Note: Tripping was caused by Tipolo tree from outside PLC, between tower str # 84 & 85, intentionally cut by unidentified person located at Cabilinan, ZDS. [WEBSMS] | CMIN
12/19/2023 9:16:24 AM | Mindanao Grid-12/19/2023 09:20: TM1 Unit 1 (Hybrid BESS-Diesel) declared available at 0801H providing CR at full capacity. [WEBSMS] | CMIN
12/19/2023 9:10:49 AM | Mindanao Grid-12/19/2023 09:15: WMPC DG04 cut-in at 0856H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/19/2023 9:06:48 AM | Mindanao Grid-12/19/2023 09:11: Aurora -Lala 138kV L1 was restored at 0905H from the forced outage. [WEBSMS] | CMIN
12/19/2023 7:59:38 AM | Mindanao Grid-12/19/2023 08:03: Aurora -Lala 138kV L1 tripped at 0730H with BC fault loop. Advised to conduct line patrol [WEBSMS] | CMIN
12/19/2023 7:58:45 AM | Mindanao Grid-12/19/2023 08:03: Correction: Baloi-Villanueva 230KV L2 de-energized at 0619H to configure the line protection and associated BFRs for the implementation of 4th line of Single- Pole Tripping and Auto-reclosing of TL in Mindanao. MSO-NPD requested shutdown. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
12/19/2023 7:39:57 AM | Luzon Grid-12/19/2023 07:40: Bay-Makban Plant B 230kV line 1 was de-energized at 0735H. (Planned Outage) [WEBSMS] | CLUZ
12/19/2023 7:12:50 AM | Luzon Grid-12/19/2023 07:13: Pagbilao Unit 2 online at 0709H. (From an unplanned outage) [WEBSMS] | CLUZ
12/19/2023 7:05:54 AM | Mindanao Grid-12/19/2023 07:10: Baloi-Villanueva 230KV L2 de-energized at 0619H to configure the line protection and associated BFRs for the implementation of first batch of Single- Pole Tripping and Auto-reclosing TL in Mindanao. MSO-NPD requested shutdown. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
12/19/2023 6:35:56 AM | Luzon Grid-12/19/2023 06:36: SCPC Unit 3 online at 0633H. (Planned Outage) [WEBSMS] | CLUZ
12/19/2023 5:36:01 AM | [NSO Update] Visayas Grid-12/19/2023 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2324MW, PK=2036MW, RR=93MW, NetOpMargin: AM=195, PM=244, EVE=232 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106.5MW, LEYTE A @320MW, PGPP1 @75.5MW [WEBSMS] | CVIS
12/19/2023 5:34:22 AM | [NSO Update] Luzon Grid-12/19/2023 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12848MW, PK=10237MW, RR=435MW, NetOpMargin: AM=2176, PM=1424, EVE=996 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @190MW, CLC2 @175MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/19/2023 5:30:58 AM | [NSO Update] Mindanao Grid-12/19/2023 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3113MW, PK=2052MW, RR=88MW, NetOpMargin: AM=973, PM=744, EVE=899 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @112MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
12/19/2023 4:22:08 AM | [NSO Update] Mindanao Grid-12/19/2023 04:26: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 290 km West Southwest of Zamboanga City, Zamboanga del Sur (6.0�N, 119.6�E). Northeast Monsoon affecting Northern and Central Luzon. Shear Line affecting the eastern section of Southern Luzon. [WEBSMS] | CMIN
12/19/2023 4:21:47 AM | [NSO Update] Luzon Grid-12/19/2023 04:22: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 290 km West Southwest of Zamboanga City, Zamboanga del Sur (6.0�N, 119.6�E). Northeast Monsoon affecting Northern and Central Luzon. Shear Line affecting the eastern section of Southern Luzon. [WEBSMS] | CLUZ
12/19/2023 4:21:37 AM | [NSO Update] Visayas Grid-12/19/2023 04:21: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 290 km West Southwest of Zamboanga City, Zamboanga del Sur (6.0�N, 119.6�E). Northeast Monsoon affecting Northern and Central Luzon. Shear Line affecting the eastern section of Southern Luzon. [WEBSMS] | CVIS
12/19/2023 2:40:23 AM | Visayas Grid-12/19/2023 02:40: Magdugo-Dumanjug 230 KV Line 1 energized at 0222H (Magdugo side) for soaking. [WEBSMS] | CVIS
12/19/2023 2:38:31 AM | Visayas Grid-12/19/2023 02:38: Magdugo-Dumanjug 230 KV Line 1 energized/de-energized at 0010H/0113H (Magdugo side), 0115H/0217H (Dumanjug side) for 1 hour soaking. [WEBSMS] | CVIS
12/19/2023 2:20:06 AM | [NSO Update] Mindanao Grid-12/19/2023 02:24: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0217H with power going to Visayas [WEBSMS] | CMIN
12/19/2023 2:19:49 AM | [NSO Update] Visayas Grid-12/19/2023 02:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0217H with power going to Visayas [WEBSMS] | CVIS
12/19/2023 12:09:29 AM | [NSO Update] Mindanao Grid-12/19/2023 00:13: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0004H from forward power direction [WEBSMS] | CMIN
12/19/2023 12:09:24 AM | [NSO Update] Visayas Grid-12/19/2023 00:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0004H from forward power direction [WEBSMS] | CVIS
12/18/2023 9:58:15 PM | Mindanao Grid-12/18/2023 22:02: (Correction) TM1 Unit 1 (Hybrid BESS-Diesel) on forced outage due to inverter high temperature. Note: TSI Unit 1 & Unit 2 as replacement power (CR). [WEBSMS] | CMIN
12/18/2023 9:46:05 PM | Mindanao Grid-12/18/2023 21:50: Forced outage due to high battery temperature. Note: TSI Unit 1 & Unit 2 as replacement power (CR). [WEBSMS] | CMIN
12/18/2023 9:16:17 PM | Mindanao Grid-12/18/2023 21:20: WMPC DG04 cut-out at 2114H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/18/2023 5:59:56 PM | [NSO Update] Luzon Grid-12/18/2023 18:00: Weather Disturbance Alert Notice (WDAN) has been lifted today, December 18, 2023 at 1700H. Tropical Depression KABAYAN has weakened into a Low Pressure Area and was estimated based on all available data in the vicinity of Impasug-ong, Bukidnon (8.3 N, 125.1 E) [WEBSMS] | CLUZ
12/18/2023 5:59:37 PM | [NSO Update] Mindanao Grid-12/18/2023 18:03: Weather Disturbance Alert Notice (WDAN) has been lifted today, December 18, 2023 at 1700H. Tropical Depression KABAYAN has weakened into a Low Pressure Area and was estimated based on all available data in the vicinity of Impasug-ong, Bukidnon (8.3 N, 125.1 E) [WEBSMS] | CMIN
12/18/2023 5:59:31 PM | [NSO Update] Visayas Grid-12/18/2023 17:59: Weather Disturbance Alert Notice (WDAN) has been lifted today, December 18, 2023 at 1700H. Tropical Depression KABAYAN has weakened into a Low Pressure Area and was estimated based on all available data in the vicinity of Impasug-ong, Bukidnon (8.3 N, 125.1 E) [WEBSMS] | CVIS
12/18/2023 5:51:55 PM | [NSO Update] Luzon Grid-12/18/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12383MW, PK=10239MW, RR=425MW, NetOpMargin: EVE=1719 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @240MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/18/2023 5:47:10 PM | [NSO Update] Visayas Grid-12/18/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2422MW, PK=2093MW, RR=97MW, NetOpMargin: EVE=232 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106MW, LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
12/18/2023 5:44:33 PM | Mindanao Grid-12/18/2023 17:48: PEAK POWER SAN FRANCISCO Unit 2 cut-in at 1740H. MO dispatch (RTD). [WEBSMS] | CMIN
12/18/2023 5:43:31 PM | [NSO Update] Mindanao Grid-12/18/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3063MW, PK=2063MW, RR=84MW, NetOpMargin: EVE=916 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @152MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
12/18/2023 4:21:21 PM | Mindanao Grid-12/18/2023 16:25: WMPC DG07 cut-out at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/18/2023 1:48:57 PM | Mindanao Grid-12/18/2023 13:53: SUPREME POWER MATI cut-in at 1246H, (Unplanned Outage) [WEBSMS] | CMIN
12/18/2023 1:48:21 PM | Mindanao Grid-12/18/2023 13:52: SUPREME POWER MATI tripped with 6MW load at 1241H. Indication: Reverse Power Trip. (Unplanned Outage) [WEBSMS] | CMIN
12/18/2023 1:24:39 PM | Mindanao Grid-12/18/2023 13:28: Maco-TM1 138kV L1 restore/energized 1320H. (Planned outage) [WEBSMS] | CMIN
12/18/2023 1:05:59 PM | [NSO Update] Luzon Grid-12/18/2023 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12762MW, PK=10432MW, RR=438MW, NetOpMargin: PM=1892, EVE=1817 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @240MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/18/2023 1:00:27 PM | [NSO Update] Visayas Grid-12/18/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2327MW, PK=2013MW, RR=94MW, NetOpMargin: PM=220, EVE=240 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106MW, LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
12/18/2023 12:45:36 PM | [NSO Update] Mindanao Grid-12/18/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3080MW, PK=2112MW, RR=86MW, NetOpMargin: PM=882, EVE=908 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @152MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
12/18/2023 11:19:45 AM | [NSO Update] Luzon Grid-12/18/2023 11:19: Weather Update: At 10:00 AM today, Tropical Storm �KABAYAN� weakens into Tropical Depression and has made landfall over Manay, Davao Oriental. [WEBSMS] | CLUZ
12/18/2023 11:18:27 AM | [NSO Update] Mindanao Grid-12/18/2023 11:22: Weather Update: At 10:00 AM today Tropical Storm �KABAYAN� weakens into Tropical Depression and has made landfall over Manay, Davao Oriental. [WEBSMS] | CMIN
12/18/2023 11:17:05 AM | [NSO Update] Visayas Grid-12/18/2023 11:17: Weather Update: At 10:00 AM today Tropical Storm �KABAYAN� weakens into Tropical Depression and has made landfall over Manay, Davao Oriental. [WEBSMS] | CVIS
12/18/2023 11:16:02 AM | [NSO Update] Visayas Grid-12/18/2023 11:16: Weather Update: At 10:00 AM today Tropical Storm �KABAYAN� weaken into Tropical Depression and has made landfall over Manay, Davao Oriental. [WEBSMS] | CVIS
12/18/2023 11:12:25 AM | Mindanao Grid-12/18/2023 11:16: PEAK POWER SAN FRANCISCO Unit 2 cut-in at 1106H. MO dispatch (RTD). [WEBSMS] | CMIN
12/18/2023 11:11:48 AM | Mindanao Grid-12/18/2023 11:16: SUPREME POWER MATI (MDP) cut-in at 1100H. MO dispatch (RTD). [WEBSMS] | CMIN
12/18/2023 11:06:02 AM | Mindanao Grid-12/18/2023 11:10: WMPC DG07 cut-in at 1103H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/18/2023 10:11:32 AM | Mindanao Grid-12/18/2023 10:15: ASIGA Hydro cut-in at 0738H. (Unplanned Outage) [WEBSMS] | CMIN
12/18/2023 10:10:52 AM | Mindanao Grid-12/18/2023 10:15: ASIGA Hydro tripped with 8.2MW load at 0716H. Indication: Restricted Earth Fault. Lowest frequency recorded was 59.91Hz. (Unplanned Outage) [WEBSMS] | CMIN
12/18/2023 9:09:38 AM | Mindanao Grid-12/18/2023 09:12: AGUS 6 Unit 5 shutdown at 0905H for PMS (Non-GOMP) [WEBSMS] | CMIN
12/18/2023 9:07:56 AM | Mindanao Grid-12/18/2023 09:11: WMPC DG04 cut-in at 0855H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/18/2023 5:40:28 AM | [NSO Update] Mindanao Grid-12/18/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3138MW, PK=2151MW, RR=82MW, NetOpMargin: AM=905, PM=880, EVE=745 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @112MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
12/18/2023 5:39:25 AM | [NSO Update] Visayas Grid-12/18/2023 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2494MW, PK=2143MW, RR=93MW, NetOpMargin: AM=257, PM=226, EVE=228 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106MW, LEYTE A @310MW, PGPP1 @76MW [WEBSMS] | CVIS
12/18/2023 5:38:10 AM | [NSO Update] Luzon Grid-12/18/2023 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12883MW, PK=9961MW, RR=429MW, NetOpMargin: AM=2493, PM=1273, EVE=958 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @240MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/18/2023 4:48:09 AM | [NSO Update] Mindanao Grid-12/18/2023 04:51: Weather Update: At 3:00 AM today, the center of Tropical Storm KABAYAN was estimated based on all available data 195 km East of Davao City (7.3 N, 127.4 E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CMIN
12/18/2023 4:47:55 AM | [NSO Update] Visayas Grid-12/18/2023 04:48: Weather Update: At 3:00 AM today, the center of Tropical Storm KABAYAN was estimated based on all available data 195 km East of Davao City (7.3 N, 127.4 E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CVIS
12/18/2023 4:47:40 AM | [NSO Update] Luzon Grid-12/18/2023 04:47: Weather Update: At 3:00 AM today, the center of Tropical Storm KABAYAN was estimated based on all available data 195 km East of Davao City (7.3 N, 127.4 E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CLUZ
12/18/2023 4:13:38 AM | Luzon Grid-12/18/2023 04:13: Sta. Rita Module 20 online at 0410H (Unplanned Outage) [WEBSMS] | CLUZ
12/18/2023 2:09:12 AM | Mindanao Grid-12/18/2023 02:12: Pulangi 4 Unit 2 cut-in at 0203H. (Unplanned Outage) Note: Planned outage up to December 17, 2023 at 2359H. [WEBSMS] | CMIN
12/18/2023 1:17:58 AM | Luzon Grid-12/18/2023 01:18: Sta. Rita Module 2 tripped at 0114H (Unplanned Outage) [WEBSMS] | CLUZ
12/17/2023 11:30:07 PM | Luzon Grid-12/17/2023 23:30: San Lorenzo Module 60 online at 2328H (Planned Outage) [WEBSMS] | CLUZ
12/17/2023 10:46:54 PM | Mindanao Grid-12/17/2023 22:50: Tagoloan-Manolo Fortich 138KV L2 re-energized at 2133H & looped at Manolo Fortich SS at 2135H. From Planned Outage / N-GOMP (Affected by P&E requested shutdown). [WEBSMS] | CMIN
12/17/2023 10:31:50 PM | Visayas Grid-12/17/2023 22:32: Magdugo SS 138 KV bus 1 energized at 2227H. (Planned Outage) [WEBSMS] | CVIS
12/17/2023 10:30:20 PM | Mindanao Grid-12/17/2023 22:33: Tagoloan SS 138KV 100MVA T1 re-energized at 2042H. From Planned Outage / N-GOMP (Affected by P&E requested shutdown). [WEBSMS] | CMIN
12/17/2023 10:21:26 PM | Mindanao Grid-12/17/2023 22:24: Tagoloan SS 138KV 100MVA T2 re-energized at 2034H. From Planned Outage / N-GOMP (Affected by P&E requested shutdown). [WEBSMS] | CMIN
12/17/2023 10:05:47 PM | Mindanao Grid-12/17/2023 22:09: Tagoloan-Villanueva 138KV L2 re-energized at 2030H & looped at Villanueva SS at 2031H. From Planned Outage / N-GOMP (Affected by P&E requested shutdown). [WEBSMS] | CMIN
12/17/2023 9:58:14 PM | Luzon Grid-12/17/2023 21:58: GMEC 1 with 17MW load tripped at 2152H while ongoing shutdown due to coal conveyor trouble (Unplanned Outage) [WEBSMS] | CLUZ
12/17/2023 9:54:15 PM | Mindanao Grid-12/17/2023 21:57: Tagoloan SS 138KV Bus 2 re-energized at 2030H. From Planned Outage /Non-GOMP (P&E requested activity). [WEBSMS] | CMIN
12/17/2023 9:45:01 PM | Luzon Grid-12/17/2023 21:45: GMEC 2 with 106MW tripped at 2130H while ongoing shutdown (Unplanned Outage) [WEBSMS] | CLUZ
12/17/2023 8:16:11 PM | Mindanao Grid-12/17/2023 20:19: SUPREME POWER Mati (MDP) cut-out at 2005H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/17/2023 7:09:58 PM | [NSO Update] Mindanao Grid-12/17/2023 19:13: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1639H with power going to Visayas. [WEBSMS] | CMIN
12/17/2023 7:07:57 PM | [NSO Update] Visayas Grid-12/17/2023 19:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1639H with power going to Visayas. [WEBSMS] | CVIS
12/17/2023 7:07:23 PM | [NSO Update] Mindanao Grid-12/17/2023 19:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3063MW, PK=2058MW, RR=76MW, NetOpMargin: EVE=929 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @152MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/17/2023 6:47:49 PM | [NSO Update] Mindanao Grid-12/17/2023 18:51: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1631H from reverse power direction. [WEBSMS] | CMIN
12/17/2023 6:47:21 PM | [NSO Update] Visayas Grid-12/17/2023 18:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1631H from reverse power direction. [WEBSMS] | CVIS
12/17/2023 6:47:11 PM | Mindanao Grid-12/17/2023 18:50: Gensan SS 138KV Busbar # 2 re-energized at 1823H. From Planned Outage / Non-GOMP (P&E requested shutdown). [WEBSMS] | CMIN
12/17/2023 6:09:58 PM | [NSO Update] Visayas Grid-12/17/2023 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2357MW, PK=2015MW, RR=97MW, NetOpMargin: EVE=245 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106MW, LEYTE A @318MW, PGPP1 @76MW [WEBSMS] | CVIS
12/17/2023 6:07:29 PM | [NSO Update] Luzon Grid-12/17/2023 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12088MW, PK=9038MW, RR=354MW, NetOpMargin: EVE=2696 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, GMEC 1 @90MW, GMEC 2 @90MW, MSLC3 @115MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/17/2023 4:56:02 PM | Luzon Grid-12/17/2023 16:56: Bayombong-Santiago 230kV Line 2 restored at 1655H (Planned Outage) [WEBSMS] | CLUZ
12/17/2023 3:06:20 PM | Mindanao Grid-12/17/2023 15:09: San Francisco SS 138KV 50MVA Power Transformer # 1 re-energized at 1446H. From Planned Outage /Non GOMP (P&E requested activity). [WEBSMS] | CMIN
12/17/2023 2:46:58 PM | Luzon Grid-12/17/2023 14:47: Bolo-Cayanga 230kV Line 2 restored at 1444H (Planned Outage) [WEBSMS] | CLUZ
12/17/2023 2:23:28 PM | Luzon Grid-12/17/2023 14:23: Botolan-Subic 230kV Line restored at 1423H (Planned Outage) [WEBSMS] | CLUZ
12/17/2023 1:58:11 PM | Visayas Grid-12/17/2023 13:58: Lugo SS Lugo-Cebeco 2 13.8KV line 1 energized at 1348H, activity completed. (Planned Outage). [WEBSMS] | CVIS
12/17/2023 1:18:20 PM | [NSO Update] Mindanao Grid-12/17/2023 13:21: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3094MW, PK=1806MW, RR=74MW, NetOpMargin: PM=1214, EVE=1028 Highest Unit O/L: GNPK 1&2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @152MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/17/2023 1:15:18 PM | [NSO Update] Visayas Grid-12/17/2023 13:15: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2449MW, PK=1811MW, RR=94MW, NetOpMargin: PM=2449, EVE=1811 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: Leyte A @ 310MW, PGPP1 @ 76MW, TGPP @ 106MW [WEBSMS] | CVIS
12/17/2023 1:09:05 PM | [NSO Update] Luzon Grid-12/17/2023 13:09: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13422MW, PK=8503MW, RR=355MW, NetOpMargin: PM=4564, EVE=3333 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 2 @175MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/17/2023 12:16:18 PM | Visayas Grid-12/17/2023 12:16: Lugo SS Lugo-Cebeco 2 13.8KV line 1 de-energized at 1206H. (Planned Outage). [WEBSMS] | CVIS
12/17/2023 11:41:49 AM | Mindanao Grid-12/17/2023 11:45: SUPREME POWER MATI (MDP) cut-in at 1101H. MO dispatch (RTD). [WEBSMS] | CMIN
12/17/2023 11:24:28 AM | Luzon Grid-12/17/2023 11:24: Bay-Batangas 230kV Line 1 restored at 1124H. (Planned Outage) [WEBSMS] | CLUZ
12/17/2023 11:20:56 AM | Luzon Grid-12/17/2023 11:21: Bay SS 230kV Bus 2 restored at 1120H. (Planned Outage) [WEBSMS] | CLUZ
12/17/2023 10:58:24 AM | Luzon Grid-12/17/2023 10:58: Dona Imelda (Araneta) 230kV Bus 2 restored at 1057H. (Planned Outage) [WEBSMS] | CLUZ
12/17/2023 10:56:22 AM | Visayas Grid-12/17/2023 10:56: Colon SS 69KV Colon-Veco-Aya fdr. energized at 1054H, activity completed. (Planned Outage) [WEBSMS] | CVIS
12/17/2023 10:50:19 AM | Luzon Grid-12/17/2023 10:50: Gamu-UPSI Gamu BESS 69kV Line energized at 1048H. (Unplanned Outage) [WEBSMS] | CLUZ
12/17/2023 10:34:55 AM | Luzon Grid-12/17/2023 10:35: Gamu-UPSI Gamu BESS 69kV Line de-energized at 1034H. (Unplanned Outage) [WEBSMS] | CLUZ
12/17/2023 9:53:14 AM | Visayas Grid-12/17/2023 09:53: Colon-Naga 138KV Line 1 energized at 0951H, activity completed. (Planned Outage) [WEBSMS] | CVIS
12/17/2023 9:32:46 AM | Mindanao Grid-12/17/2023 09:35: LAMSAN BIOMASS cut-in at 0806H. (Unplanned Outage) [WEBSMS] | CMIN
12/17/2023 9:32:10 AM | Mindanao Grid-12/17/2023 09:35: LAMSAN BIOMASS tripped with 13.5MW load at 0759H. Indication: 67N. Lowest frequency recorded was 60.01Hz. (Unplanned Outage) [WEBSMS] | CMIN
12/17/2023 9:15:07 AM | Visayas Grid-12/17/2023 09:15: Colon SS 69KV Colon-Veco-Aya fdr de-energized at 0912H. (Planned Outage). [WEBSMS] | CVIS
12/17/2023 9:11:06 AM | [NSO Update] Mindanao Grid-12/17/2023 09:14: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0902H with power going to Mindanao. [WEBSMS] | CMIN
12/17/2023 9:08:35 AM | [NSO Update] Visayas Grid-12/17/2023 09:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0902H with power going to Mindanao. [WEBSMS] | CVIS
12/17/2023 8:59:35 AM | [NSO Update] Mindanao Grid-12/17/2023 09:02: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0854H from forward power direction. [WEBSMS] | CMIN
12/17/2023 8:57:05 AM | [NSO Update] Visayas Grid-12/17/2023 08:57: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0854H from forward power direction. [WEBSMS] | CVIS
12/17/2023 8:09:09 AM | Luzon Grid-12/17/2023 08:09: Botolan-Subic 230kV Line de-energized at 0808H. (Planned Outage) [WEBSMS] | CLUZ
12/17/2023 7:51:59 AM | Mindanao Grid-12/17/2023 07:55: Gensan SS Busbar # 2 de-energized at 0739H for commissioning of new 7-03CB08GSA and its associated HVEs. P&E request shutdown. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
12/17/2023 7:46:50 AM | Visayas Grid-12/17/2023 07:47: Magdugo SS 138KV Bus 1 de-energized at 0741H. (Planned Outage) [WEBSMS] | CVIS
12/17/2023 7:37:31 AM | Luzon Grid-12/17/2023 07:37: Bayombong-Santiago 230kV Line 2 de-energized at 0737H. (Planned Outage) [WEBSMS] | CLUZ
12/17/2023 7:09:42 AM | Mindanao Grid-12/17/2023 07:12: San Francisco Power Transformer 1 deenergized at 0611H. (Planned Outage). [WEBSMS] | CMIN
12/17/2023 6:33:25 AM | [NSO Update] Luzon Grid-12/17/2023 06:33: The Mindanao Grid is on "BLUE ALERT" due the LPA developing into tropical depression "KABAYAN", which is likely to make landfall along the coast of Surigao del Sur of Davao Oriental tonight or tomorrow early morning, cross the rugged terrain of Mindanao before emerging over either the Bohol Sea or Sulu Sea tomorrow noon or afternoon. [WEBSMS] | CLUZ
12/17/2023 6:33:01 AM | [NSO Update] Visayas Grid-12/17/2023 06:33: The Mindanao Grid is on "BLUE ALERT" due the LPA developing into tropical depression "KABAYAN", which is likely to make landfall along the coast of Surigao del Sur of Davao Oriental tonight or tomorrow early morning, cross the rugged terrain of Mindanao before emerging over either the Bohol Sea or Sulu Sea tomorrow noon or afternoon. [WEBSMS] | CVIS
12/17/2023 6:32:41 AM | [NSO Update] Mindanao Grid-12/17/2023 06:35: The Mindanao Grid is on "BLUE ALERT" due the LPA developing into tropical depression "KABAYAN", which is likely to make landfall along the coast of Surigao del Sur of Davao Oriental tonight or tomorrow early morning, cross the rugged terrain of Mindanao before emerging over either the Bohol Sea or Sulu Sea tomorrow noon or afternoon. [WEBSMS] | CMIN
12/17/2023 6:28:18 AM | Luzon Grid-12/17/2023 06:28: Bay SS 230kV Bus 2 de-energized at 0626H. (Planned Outage) [WEBSMS] | CLUZ
12/17/2023 6:24:27 AM | Luzon Grid-12/17/2023 06:24: Bay-Batangas 230kV Line 1 de-energized at 0623H. (Planned Outage) [WEBSMS] | CLUZ
12/17/2023 6:24:21 AM | Visayas Grid-12/17/2023 06:24: Colon-Naga 138KV Line 1 de-energized at 0616H. (Planned Outage) [WEBSMS] | CVIS
12/17/2023 6:04:39 AM | [NSO Update] Visayas Grid-12/17/2023 06:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0559H with power going to Visayas. [WEBSMS] | CVIS
12/17/2023 6:04:17 AM | [NSO Update] Mindanao Grid-12/17/2023 06:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0559H with power going to Visayas. [WEBSMS] | CMIN
12/17/2023 5:57:28 AM | [NSO Update] Luzon Grid-12/17/2023 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13418MW, PK=8598MW, RR=354MW, NetOpMargin: AM=4466, PM=4246, EVE=3195 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 2 @175MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/17/2023 5:46:31 AM | [NSO Update] Mindanao Grid-12/17/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3269MW, PK=1735MW, RR=72MW, NetOpMargin: AM=1462, PM=1257, EVE=868 Highest Unit O/L: GNPK 1&2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @152MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/17/2023 5:43:51 AM | [NSO Update] Visayas Grid-12/17/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2591MW, PK=1785MW, RR=93MW, NetOpMargin: AM=713, PM=674, EVE=330 Highest Unit O/L: THVI 2@ 169MW Derated Plant: Leyte A @ 310MW, PGPP1 @ 76MW [WEBSMS] | CVIS
12/17/2023 5:40:00 AM | Mindanao Grid-12/17/2023 05:43: Tagoloan SS 100MVA Power Transformer 2 and Tagoloan SS 138kV Bus 2 de-energized 0524H. Planned outage. [WEBSMS] | CMIN
12/17/2023 5:37:30 AM | Mindanao Grid-12/17/2023 05:40: Tagoloan-Manolo Fortich 138kV L2 de-energized 0521H. (Planned outage) [WEBSMS] | CMIN
12/17/2023 5:35:43 AM | Mindanao Grid-12/17/2023 05:38: Tagoloan - Villanueva 138kV L2 de-energized 0519H. (Planned outage) [WEBSMS] | CMIN
12/17/2023 5:33:28 AM | Mindanao Grid-12/17/2023 05:36: Tagoloan SS 100MVA Power Transformer 1 de-energized 0516H. (planned outage). [WEBSMS] | CMIN
12/17/2023 5:08:51 AM | [NSO Update] Mindanao Grid-12/17/2023 05:12: Weather Disturbance Alert Notice (WDAN) is issued at 0500H. The Low-Pressure Area East of Surigao Del Sur has developed into Tropical Depression "KABAYAN". The center was estimated based on all available data 525 km East of Davao City (7.5�N, 130.4�E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving Westward at 10 km/h. [WEBSMS] | CMIN
12/17/2023 5:08:47 AM | [NSO Update] Visayas Grid-12/17/2023 05:08: Weather Disturbance Alert Notice (WDAN) is issued at 0500H. The Low-Pressure Area East of Surigao Del Sur has developed into Tropical Depression "KABAYAN". The center was estimated based on all available data 525 km East of Davao City (7.5�N, 130.4�E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving Westward at 10 km/h. [WEBSMS] | CVIS
12/17/2023 5:08:44 AM | [NSO Update] Luzon Grid-12/17/2023 05:08: Weather Disturbance Alert Notice (WDAN) is issued at 0500H. The Low-Pressure Area East of Surigao Del Sur has developed into Tropical Depression "KABAYAN". The center was estimated based on all available data 525 km East of Davao City (7.5�N, 130.4�E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving Westward at 10 km/h. [WEBSMS] | CLUZ
12/17/2023 3:44:10 AM | Luzon Grid-12/17/2023 03:44: Hermosa-Marilao(Duhat) 230kV Line restored at 0342H (Planned Outage) [WEBSMS] | CLUZ
12/17/2023 3:29:18 AM | Mindanao Grid-12/17/2023 03:32: FDC Unit 3 on emergency shutdown at 0229H due to tube leak at cyclone separator A (boiler-side). Note: implemented gradual unloading (followed RTD). (Unplanned Outage) [WEBSMS] | CMIN
12/17/2023 2:52:28 AM | [NSO Update] Visayas Grid-12/17/2023 02:52: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0249H from reverse power direction. [WEBSMS] | CVIS
12/17/2023 2:52:18 AM | [NSO Update] Mindanao Grid-12/17/2023 02:55: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0249H from reverse power direction. [WEBSMS] | CMIN
12/17/2023 2:02:58 AM | Luzon Grid-12/17/2023 02:03: Hermosa-Marilao(Duhat) 230kV Line de-energized at 0202H (Planned Outage) [WEBSMS] | CLUZ
12/17/2023 12:02:56 AM | Mindanao Grid-12/17/2023 00:06: LIBERTAD POWER cut-in at 2308H. (Unplanned Outage) [WEBSMS] | CMIN
12/17/2023 12:02:07 AM | Mindanao Grid-12/17/2023 00:05: LIBERTAD POWER tripped with 6MW load at 2259H. Indication: Earthfault. Lowest frequency recorded was 59.92Hz. (Unplanned Outage) [WEBSMS] | CMIN
12/16/2023 10:15:16 PM | [NSO Update] Mindanao Grid-12/16/2023 22:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2214H with power going to Mindanao. [WEBSMS] | CMIN
12/16/2023 10:15:02 PM | [NSO Update] Visayas Grid-12/16/2023 22:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2214H with power going to Mindanao. [WEBSMS] | CVIS
12/16/2023 10:04:10 PM | [NSO Update] Mindanao Grid-12/16/2023 22:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2200H from forward power direction. [WEBSMS] | CMIN
12/16/2023 10:03:56 PM | [NSO Update] Visayas Grid-12/16/2023 22:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2200H from forward power direction. [WEBSMS] | CVIS
12/16/2023 9:34:13 PM | Luzon Grid-12/16/2023 21:34: San Jose-San Rafael Line restored at 2133H (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 6:44:11 PM | [NSO Update] Mindanao Grid-12/16/2023 18:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3166MW, PK=2256MW, RR=87MW, NetOpMargin: EVE=823 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @44MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @152MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/16/2023 6:43:13 PM | [NSO Update] Visayas Grid-12/16/2023 18:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2587MW, PK=2209MW, RR=97MW, NetOpMargin: EVE=281 Highest Unit O/L: THVI 2 @ 169MW Derated Plant: TGPP @ 106.5MW, Leyte A @ 318MW, PGPP1 @ 38MW [WEBSMS] | CVIS
12/16/2023 6:42:17 PM | [NSO Update] Luzon Grid-12/16/2023 18:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12490MW, PK=9778MW, RR=404MW, NetOpMargin: EVE=2308 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, SLPGC 1 @ 130MW, Ilijan A @ 300MW [WEBSMS] | CLUZ
12/16/2023 6:20:25 PM | Luzon Grid-12/16/2023 18:20: Hermosa-BCCPP 230kV Line 3 restored at 1819H (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 6:13:58 PM | Luzon Grid-12/16/2023 18:14: Sual 230kV Bus 2 restored at 1810H (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 6:12:25 PM | Luzon Grid-12/16/2023 18:12: Salong-Steel Asia 230kV Line restored at 1810H (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 5:48:22 PM | Luzon Grid-12/16/2023 17:48: Balingueo-Bolo 230kV Line 2 restored at 1747H (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 5:36:02 PM | Luzon Grid-12/16/2023 17:36: Ilijan GT1-1 online at 1735H (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 5:29:14 PM | Luzon Grid-12/16/2023 17:29: San Jose-San Rafael Line de-energized at 1728H to conduct repair on the damaged connecting rod of 88DS09SJO (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 4:34:36 PM | Luzon Grid-12/16/2023 16:34: Ilijan ST1 online at 1632H (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 4:09:44 PM | Luzon Grid-12/16/2023 16:09: Bayombong-Santiago 230kV Line 1 restored at 1609H (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 3:41:31 PM | Luzon Grid-12/16/2023 15:41: Lamao-SCPC 230kV Tie Line 3 restored at 1541H (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 3:22:22 PM | Luzon Grid-12/16/2023 15:22: Ilijan GT1-2 online at 1519H (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 3:20:23 PM | Mindanao Grid-12/16/2023 15:23: WMPC DG04 cut-out at 1514H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/16/2023 1:46:26 PM | Mindanao Grid-12/16/2023 13:49: Bunawan-Don Ramon Aboitiz 138kV line 2 autotripped 1334H. Customer-owned and maintained line. (Unplanned outage). [WEBSMS] | CMIN
12/16/2023 1:40:38 PM | Visayas Grid-12/16/2023 13:40: Cebu SS 100MVA TR1 138/69/13.8KV energized at 1338H, activity completed. (Planned Outage) [WEBSMS] | CVIS
12/16/2023 1:33:45 PM | Luzon Grid-12/16/2023 13:33: Sta. Rita 40 online at 1332H. (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 1:19:24 PM | [NSO Update] Mindanao Grid-12/16/2023 13:22: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3207MW, PK=2175MW, RR=87MW, NetOpMargin: PM=945, EVE=865 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @44MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @152MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/16/2023 1:01:59 PM | [NSO Update] Visayas Grid-12/16/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2524MW, PK=2124MW, RR=94MW, NetOpMargin: PM=307, EVE=251 Highest Unit O/L: THVI 2 @169MW Derated Plant: TGPP @106.5MW, LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
12/16/2023 1:01:03 PM | Luzon Grid-12/16/2023 13:01: San Lorenzo 50 online at 1255H. (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 12:55:18 PM | [NSO Update] Luzon Grid-12/16/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11797MW, PK=9770MW, RR=433MW, NetOpMargin: PM=1594, EVE=934 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/16/2023 12:47:32 PM | Luzon Grid-12/16/2023 12:47: Balsik-Olongapo 230kV Line restored at 1247H. (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 12:39:28 PM | Luzon Grid-12/16/2023 12:39: Sta. Rita 30 online at 1237H. (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 12:35:33 PM | Visayas Grid-12/16/2023 12:35: Colon-Magdugo 138KV Line 2 energized at 1229H, activity completed. (Planned Outage) [WEBSMS] | CVIS
12/16/2023 12:04:30 PM | Luzon Grid-12/16/2023 12:04: Sta. Rita 10 online at 1200H. (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 11:39:47 AM | Luzon Grid-12/16/2023 11:39: Sta. Rita 20 online at 1136H. (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 11:33:47 AM | Mindanao Grid-12/16/2023 11:36: WMPC DG06 cut-out at 1131H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/16/2023 11:23:01 AM | Visayas Grid-12/16/2023 11:23: Dumanjug SS 230KV Bus 1 energized at 1121H, hotspot correction, activity completed. (Unplanned Outage) [WEBSMS] | CVIS
12/16/2023 11:13:32 AM | Mindanao Grid-12/16/2023 11:16: WMPC DG06 cut-in at 1034H. MO dispatch (RTD). [WEBSMS] | CMIN
12/16/2023 11:03:09 AM | Mindanao Grid-12/16/2023 11:06: SPC Mati cut in at 1100H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
12/16/2023 10:41:47 AM | Luzon Grid-12/16/2023 10:41: Affected ALD feeders of NGCP and MERALCO restored at 1028H and 1033H, respectively. [WEBSMS] | CLUZ
12/16/2023 10:23:07 AM | Luzon Grid-12/16/2023 10:23: San Lorenzo 50 with 163MW tripped at 1018H. Lowest system frequency is 59.57Hz. (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 10:22:21 AM | Mindanao Grid-12/16/2023 10:25: WMPC DG04 online at 1007H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
12/16/2023 10:20:51 AM | Luzon Grid-12/16/2023 10:20: ALD occurred at NGCP and MERALCO feeders at 1014H due to tripping of Sta. Rita Units 10 to 40 with 165MW, 163MW, 166MW & 164MW respectively. Lowest system frequency is 58.888Hz. [WEBSMS] | CLUZ
12/16/2023 10:10:23 AM | Luzon Grid-12/16/2023 10:10: Balsik-Olongapo 230kV Line de-energized at 1009H. (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 9:20:29 AM | Visayas Grid-12/16/2023 09:20: THVI Unit #1 tripped at 0916H, load 40MW, suspected boiler tube leak. [WEBSMS] | CVIS
12/16/2023 8:55:08 AM | [NSO Update] Mindanao Grid-12/16/2023 08:58: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0850H from reverse power direction. [WEBSMS] | CMIN
12/16/2023 8:54:25 AM | [NSO Update] Visayas Grid-12/16/2023 08:54: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0850H from reverse power direction. [WEBSMS] | CVIS
12/16/2023 8:28:47 AM | Luzon Grid-12/16/2023 08:28: Tayabas-Mauban 230kV Line 2 de-energized at 0828H. (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 8:08:11 AM | Visayas Grid-12/16/2023 08:08: Dumanjug SS 230KV Bus 1 de-energized at 0756H, hotspot correction. (Unplanned Outage) [WEBSMS] | CVIS
12/16/2023 7:47:37 AM | Luzon Grid-12/16/2023 07:47: Ilijan A GT 1-2 shutdown at 0746H. (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 7:44:21 AM | Luzon Grid-12/16/2023 07:44: Hermosa-BCCPP 230kV Line 3 de-energized at 0744H. (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 7:39:02 AM | Luzon Grid-12/16/2023 07:39: Bayombong-Santiago 230kV Line 1 de-energized at 0738H. (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 7:36:35 AM | Luzon Grid-12/16/2023 07:36: Ilijan A ST-1 shutdown at 0736H. (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 7:26:51 AM | Luzon Grid-12/16/2023 07:26: Ilijan A GT 1-1 shutdown at 0724H. (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2023 7:19:18 AM | Visayas Grid-12/16/2023 07:19: Cebu SS 100MVA TR1 138/69/13.8KV de-energized at 0715H. (Planned Outage) [WEBSMS] | CVIS
12/16/2023 7:14:38 AM | Luzon Grid-12/16/2023 07:14: Bolo-Cayanga 230kV Line 2 de-energized at 0713H. (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 7:11:45 AM | Luzon Grid-12/16/2023 07:11: Bacnotan-San Esteban 230kV Line restored at 0711H. (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 7:02:34 AM | Luzon Grid-12/16/2023 07:02: Sual SS 230kV Busbar 2 de-energized at 0702H. (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 6:40:39 AM | Visayas Grid-12/16/2023 06:40: Colon-Magdugo 138KV Line 2 de-energized at 0637H. (Planned Outage) [WEBSMS] | CVIS
12/16/2023 6:40:30 AM | Luzon Grid-12/16/2023 06:40: Balingueo-Bolo 230kV Line 2 de-energized at 0640H. (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 5:40:02 AM | [NSO Update] Mindanao Grid-12/16/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3435MW, PK=2029MW, RR=83MW, NetOpMargin: AM=1324, PM=1121, EVE=1038 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @44MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @152MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/16/2023 5:38:25 AM | [NSO Update] Visayas Grid-12/16/2023 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2838MW, PK=2045MW, RR=93MW, NetOpMargin: AM=701, PM=452, EVE=383 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @318MW, PGPP1 @76MW [WEBSMS] | CVIS
12/16/2023 5:32:33 AM | [NSO Update] Mindanao Grid-12/16/2023 05:35: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0530H with power going to Mindanao [WEBSMS] | CMIN
12/16/2023 5:32:08 AM | [NSO Update] Visayas Grid-12/16/2023 05:32: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0530H with power going to Mindanao [WEBSMS] | CVIS
12/16/2023 5:31:09 AM | [NSO Update] Luzon Grid-12/16/2023 05:31: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13273MW, PK=9606MW, RR=404MW, NetOpMargin: AM=3263, PM=2712, EVE=2254 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/16/2023 5:29:34 AM | Luzon Grid-12/16/2023 05:29: Dona Imelda (Araneta) 230kV Bus 2 de-energized at 0529H (Planned Outage) [WEBSMS] | CLUZ
12/16/2023 5:05:15 AM | Mindanao Grid-12/16/2023 05:08: LIBERTAD POWER cut-in at 0434H. (Unplanned Outage) [WEBSMS] | CMIN
12/16/2023 5:04:38 AM | Mindanao Grid-12/16/2023 05:07: LIBERTAD POWER tripped with 6MW load at 0423H. Indication: Line-to-Ground Fault. Lowest frequency recorded was 59.79Hz. (Unplanned Outage) [WEBSMS] | CMIN
12/16/2023 5:03:56 AM | [NSO Update] Visayas Grid-12/16/2023 05:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0500H from forward power direction [WEBSMS] | CVIS
12/16/2023 5:03:53 AM | [NSO Update] Mindanao Grid-12/16/2023 05:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0500H from forward power direction [WEBSMS] | CMIN
12/16/2023 4:27:04 AM | [NSO Update] Mindanao Grid-12/16/2023 04:30: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
12/16/2023 4:26:37 AM | [NSO Update] Visayas Grid-12/16/2023 04:26: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
12/16/2023 4:26:27 AM | [NSO Update] Luzon Grid-12/16/2023 04:26: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
12/15/2023 11:50:57 PM | Luzon Grid-12/15/2023 23:51: San Lorenzo 60 shutdown at 2349H (Planned Outage) [WEBSMS] | CLUZ
12/15/2023 10:38:24 PM | Mindanao Grid-12/15/2023 22:41: PEAK POWER SAN FRANCISCO Unit 2 cut-out at 2219H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/15/2023 10:37:50 PM | Mindanao Grid-12/15/2023 22:40: PEAK POWER SAN FRANCISCO Unit 2 cut-in at 2208H. MO dispatch (RTD). [WEBSMS] | CMIN
12/15/2023 9:33:09 PM | Mindanao Grid-12/15/2023 21:36: SUPREME POWER MATI cut-out at 2026H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/15/2023 9:30:01 PM | Mindanao Grid-12/15/2023 21:33: WMPC DG10 cut-out at 2113H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/15/2023 7:32:48 PM | Mindanao Grid-12/15/2023 19:35: KEGI TANDAG cut-out at 1834H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/15/2023 7:32:07 PM | Mindanao Grid-12/15/2023 19:35: MINERGY WARTSILA cut-out at 1748H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/15/2023 7:24:38 PM | Mindanao Grid-12/15/2023 19:27: WMPC DG06 cut-out at 1845H. End of SO dispatch (MOT Raise). [WEBSMS] | CMIN
12/15/2023 7:24:03 PM | Mindanao Grid-12/15/2023 19:27: PEAK POWER SAN FRANCISCO Unit 2 cut-out at 1837H. End of SO dispatch (MOT Raise). [WEBSMS] | CMIN
12/15/2023 7:23:18 PM | Mindanao Grid-12/15/2023 19:26: (Correction) PEAK POWER BUKIDNON cut-out at 1836H. End of SO dispatch (MOT Raise). [WEBSMS] | CMIN
12/15/2023 7:22:23 PM | Mindanao Grid-12/15/2023 19:25: PEAK POWER BUKIDNON cut-in at 1836H. End of SO dispatch (MOT Raise). [WEBSMS] | CMIN
12/15/2023 7:21:43 PM | Mindanao Grid-12/15/2023 19:24: PEAK POWER SOCSARGEN cut-out at 1836H. End of SO dispatch (MOT Raise). [WEBSMS] | CMIN
12/15/2023 7:21:01 PM | Mindanao Grid-12/15/2023 19:24: PEAK POWER SOCSARGEN cut-in at 1822H. SO dispatch (MOT Raise). [WEBSMS] | CMIN
12/15/2023 7:20:10 PM | Mindanao Grid-12/15/2023 19:23: PEAK POWER SAN FRANCISCO Unit 2 cut-in at 1818H. SO dispatch (MOT Raise). [WEBSMS] | CMIN
12/15/2023 7:19:12 PM | Mindanao Grid-12/15/2023 19:22: PEAK POWER BUKIDNON cut-in at 1818H. SO dispatch (MOT Raise). [WEBSMS] | CMIN
12/15/2023 7:18:32 PM | Mindanao Grid-12/15/2023 19:21: WMPC DG06 cut-in at 1817H. SO dispatch (MOT Raise). [WEBSMS] | CMIN
12/15/2023 7:13:17 PM | Mindanao Grid-12/15/2023 19:16: SUPREME POWER MATI cut-in at 1815H. (Unplanned Outage) [WEBSMS] | CMIN
12/15/2023 7:12:07 PM | Mindanao Grid-12/15/2023 19:15: SUPREME POWER MATI tripped with 4.5MW load at 1811H. Indication: Reverse Power Trip. (Unplanned Outage) [WEBSMS] | CMIN
12/15/2023 6:06:34 PM | Mindanao Grid-12/15/2023 18:09: WMPC DG06 cut-out at 1804H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/15/2023 6:00:42 PM | Luzon Grid-12/15/2023 18:00: Tayabas-Mauban 230kV Line 1 restored at 1757H (Planned Outage) [WEBSMS] | CLUZ
12/15/2023 5:57:40 PM | [NSO Update] Mindanao Grid-12/15/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3168MW, PK=2264MW, RR=87MW, NetOpMargin: EVE=817 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @44MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @152MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/15/2023 5:56:19 PM | [NSO Update] Visayas Grid-12/15/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2655MW, PK=2319MW, RR=97MW, NetOpMargin: EVE=239 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @106.5MW, LEYTE A @300MW, PGPP1 @76MW [WEBSMS] | CVIS
12/15/2023 5:54:50 PM | [NSO Update] Luzon Grid-12/15/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12683MW, PK=10152MW, RR=404MW, NetOpMargin: EVE=2127 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/15/2023 5:54:20 PM | Mindanao Grid-12/15/2023 17:57: KEGI TANDAG cut-in at 1739H. MO dispatch (RTD). [WEBSMS] | CMIN
12/15/2023 5:53:46 PM | Mindanao Grid-12/15/2023 17:56: MINERGY WARTSILA cut-in at 1735H. MO dispatch (RTD). [WEBSMS] | CMIN
12/15/2023 5:52:50 PM | Mindanao Grid-12/15/2023 17:55: WMPC DG06 cut-in at 1733H. MO dispatch (RTD). [WEBSMS] | CMIN
12/15/2023 5:14:54 PM | Luzon Grid-12/15/2023 17:15: Bacnotan-San Esteban 230kV Line de-energized at 1711H (Planned Outage) [WEBSMS] | CLUZ
12/15/2023 5:01:58 PM | Luzon Grid-12/15/2023 17:02: Nagsaag SS 600MVA T02 restored at 1701H (Planned Outage) [WEBSMS] | CLUZ
12/15/2023 4:24:56 PM | Luzon Grid-12/15/2023 16:25: Lumban-Gumaca 230kV Line 1 restored at 1614H (Planned Outage) [WEBSMS] | CLUZ
12/15/2023 4:15:32 PM | Mindanao Grid-12/15/2023 16:18: WMPC DG06 cut-out at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/15/2023 4:15:05 PM | Luzon Grid-12/15/2023 16:15: Lumban-Gumaca 230kV Line 1 restored at 0614H (Planned Outage) [WEBSMS] | CLUZ
12/15/2023 3:37:54 PM | Mindanao Grid-12/15/2023 15:41: 13MAGDBNK_G01 (SEDI, formerly EEI) declared available at 1535H. Declared capacity (total): 13MW. [WEBSMS] | CMIN
12/15/2023 3:26:14 PM | Mindanao Grid-12/15/2023 15:29: 13MAGDBNK_G01 (SEDI, formerly EEI) cut-out at 1509H (Commercial Testing). [WEBSMS] | CMIN
12/15/2023 3:11:30 PM | [NSO Update] Mindanao Grid-12/15/2023 15:14: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1452H with power going to Visayas. [WEBSMS] | CMIN
12/15/2023 3:11:06 PM | [NSO Update] Visayas Grid-12/15/2023 15:11: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1452H with power going to Visayas. [WEBSMS] | CVIS
12/15/2023 2:51:46 PM | [NSO Update] Mindanao Grid-12/15/2023 14:54: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1444H from reverse power direction. [WEBSMS] | CMIN
12/15/2023 2:51:12 PM | [NSO Update] Visayas Grid-12/15/2023 14:51: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1444H from reverse power direction. [WEBSMS] | CVIS
12/15/2023 2:04:31 PM | Luzon Grid-12/15/2023 14:04: Pagbilao 2 shutdown at 1358H (Unplanned Outage) [WEBSMS] | CLUZ
12/15/2023 1:59:46 PM | Mindanao Grid-12/15/2023 14:02: Nabunturan - Bislig 138KV Line autotripped and autoreclosed at 1339H. Unplanned Outage. [WEBSMS] | CMIN
12/15/2023 1:06:31 PM | Mindanao Grid-12/15/2023 13:09: SEDI EEI Unit no.2 online at 1301H to facilitate scheduled Plant performance test. Follow RTD. [WEBSMS] | CMIN
12/15/2023 12:55:16 PM | Luzon Grid-12/15/2023 12:55: Lumban-Gumaca 230kV Line 1 de-energized at 1253H, to repair DS 8-02DS05LMN ph A (Planned Outage) [WEBSMS] | CLUZ
12/15/2023 12:48:44 PM | Mindanao Grid-12/15/2023 12:51: TMI U1 Cut in at 1237H for SOC management of TMI BESS. [WEBSMS] | CMIN
12/15/2023 12:48:15 PM | [NSO Update] Luzon Grid-12/15/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13605MW, PK=10608MW, RR=436MW, NetOpMargin: PM=2560, EVE=2214 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, PAGBILAO 2 @188MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/15/2023 12:44:26 PM | [NSO Update] Visayas Grid-12/15/2023 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2614MW, PK=2261MW, RR=94MW, NetOpMargin: PM=258, EVE=199 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @106.5MW, LEYTE A @297MW, PGPP1 @76MW [WEBSMS] | CVIS
12/15/2023 12:43:05 PM | Luzon Grid-12/15/2023 12:43: Lumban-Gumaca 230kV Line 1 restored at 1236H, unlooped at 1237H at Lumban PCB 8-02CB04LMN due hot spot (Planned Outage) [WEBSMS] | CLUZ
12/15/2023 12:42:25 PM | [NSO Update] Mindanao Grid-12/15/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3207MW, PK=2324MW, RR=89MW, NetOpMargin: PM=794, EVE=817 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @44MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @152MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/15/2023 12:32:09 PM | [NSO Update] Visayas Grid-12/15/2023 12:32: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1224H with power going to Mindanao. [WEBSMS] | CVIS
12/15/2023 12:31:05 PM | [NSO Update] Mindanao Grid-12/15/2023 12:34: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1224H with power going to Mindanao. [WEBSMS] | CMIN
12/15/2023 12:14:50 PM | [NSO Update] Mindanao Grid-12/15/2023 12:17: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1212H from forward power direction. [WEBSMS] | CMIN
12/15/2023 12:14:46 PM | [NSO Update] Visayas Grid-12/15/2023 12:14: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1212H from forward power direction. [WEBSMS] | CVIS
12/15/2023 10:55:30 AM | Mindanao Grid-12/15/2023 10:58: TMI U1 cut out at 1042H. Cut in for SOC management of TMI BESS. [WEBSMS] | CMIN
12/15/2023 10:52:56 AM | Mindanao Grid-12/15/2023 10:56: WMPC DG6 as RPS online at 1050H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/15/2023 10:34:24 AM | Mindanao Grid-12/15/2023 10:37: TMI U1 cut in at 1020H, for SOC management of TMI BESS. [WEBSMS] | CMIN
12/15/2023 10:22:01 AM | Mindanao Grid-12/15/2023 10:25: SPC Mati cut in at 1101H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
12/15/2023 8:54:12 AM | Mindanao Grid-12/15/2023 08:57: WMPC DG10 as RPS online at 0850H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/15/2023 6:47:19 AM | Luzon Grid-12/15/2023 06:47: Lumban-Gumaca 230kV Line 1 de-energized at 0646H (Planned Outage) [WEBSMS] | CLUZ
12/15/2023 6:13:19 AM | Luzon Grid-12/15/2023 06:13: Nagsaag SS 600MVA T02 de-energized at 0611H (Planned Outage) [WEBSMS] | CLUZ
12/15/2023 5:58:05 AM | [NSO Update] Mindanao Grid-12/15/2023 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3405MW, PK=2213MW, RR=86MW, NetOpMargin: AM=1106, PM=986, EVE=916 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @44MW, AG1 @35MW, AG2 @89MW, AG4 @103MW, AG5 @33MW, AG6 @152MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/15/2023 5:55:24 AM | [NSO Update] Visayas Grid-12/15/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2749MW, PK=2232MW, RR=93MW, NetOpMargin: AM=423, PM=213, EVE=298 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 318MW, PGPP1 @ 76MW [WEBSMS] | CVIS
12/15/2023 5:50:19 AM | [NSO Update] Luzon Grid-12/15/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13661MW, PK=2790MW, RR=404MW, NetOpMargin: AM=2790, PM=2222, EVE=1967 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, PBL2 @188MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/15/2023 4:46:00 AM | Visayas Grid-12/15/2023 04:46: Dumanjug-Magdugo 230KV line 2 de-energized at 0443H. (Planned Outage) [WEBSMS] | CVIS
12/15/2023 4:18:41 AM | [NSO Update] Luzon Grid-12/15/2023 04:18: at 0400H Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
12/15/2023 4:17:57 AM | [NSO Update] Mindanao Grid-12/15/2023 04:21: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
12/15/2023 4:14:56 AM | [NSO Update] Visayas Grid-12/15/2023 04:15: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
12/15/2023 4:12:20 AM | Luzon Grid-12/15/2023 04:12: San Jose-San Rafael 230kV Line restored at 0411H (Planned Outage) [WEBSMS] | CLUZ
12/15/2023 12:27:56 AM | Mindanao Grid-12/15/2023 00:31: Baloi-Villanueva 230kV L1 energized at 0007H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
12/14/2023 10:51:52 PM | Mindanao Grid-12/14/2023 22:54: Libertad Power (LPE) tripped with 6.0MW load at 2237H, Cause: for further investigation. (Unplanned Outage). [WEBSMS] | CMIN
12/14/2023 9:48:27 PM | Mindanao Grid-12/14/2023 21:51: WMPC DG06 cut-out at 2144H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/14/2023 9:25:22 PM | Luzon Grid-12/14/2023 21:25: San Jose-San Rafael 230kV Line de-energized at 2125H (Planned Outage) [WEBSMS] | CLUZ
12/14/2023 9:23:03 PM | Mindanao Grid-12/14/2023 21:26: WMPC DG06 cut-in at 2108H. MO dispatch (RTD). [WEBSMS] | CMIN
12/14/2023 9:22:09 PM | Mindanao Grid-12/14/2023 21:25: WMPC DG10 cut-out at 2113H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/14/2023 7:52:44 PM | Visayas Grid-12/14/2023 19:52: CEDC unit #3 breaker before Transformer energized @1943H after detached DS phase A was cleared and is scheduled for repair soonest. [WEBSMS] | CVIS
12/14/2023 7:23:24 PM | Visayas Grid-12/14/2023 19:23: 138KV DSW (7-04DS07DNU) emergency opened @ 1911H due to detached disconnect Arm phase A of DS-7-05DS07DNU. CEDC unit#3 was affected on house-load. [WEBSMS] | CVIS
12/14/2023 6:40:24 PM | Mindanao Grid-12/14/2023 18:43: PEAK POWER SAN FRANCISCO Unit 2 cut-out at 1812H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/14/2023 6:03:20 PM | [NSO Update] Luzon Grid-12/14/2023 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12816MW, PK=10493MW, RR=436MW, NetOpMargin: EVE=1887 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, GMEC 1 @240MW, GMEC 2 @240MW, PBL2 @188MW, SLPGC 1 @130MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
12/14/2023 5:56:35 PM | [NSO Update] Mindanao Grid-12/14/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3165MW, PK=2339MW, RR=95MW, NetOpMargin: EVE=731 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @45MW, AG1 @35MW, AG2 @70MW, AG4 @120MW, AG5 @37MW, AG6 @155MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/14/2023 5:50:07 PM | Mindanao Grid-12/14/2023 17:53: PEAK POWER SAN FRANCISCO Unit 2 cut-in at 1740H. MO dispatch (RTD). [WEBSMS] | CMIN
12/14/2023 5:44:21 PM | [NSO Update] Visayas Grid-12/14/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2733MW, PK=2348MW, RR=97MW, NetOpMargin: EVE=288 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 80MW, Leyte A @ 350MW, PGPP1 @ 76MW [WEBSMS] | CVIS
12/14/2023 4:52:55 PM | Mindanao Grid-12/14/2023 16:56: Agus 2 Unit 2 cut-in at 1612H. (Unplanned Outage re: to RTU interfacing activity) . [WEBSMS] | CMIN
12/14/2023 4:38:59 PM | Mindanao Grid-12/14/2023 16:42: Agus 2-Agus 2 HEP U2 138kV L energized at 1609H. Planned Outage/Non-GOMP (OO07AD). Customers (Agus 2 HEP) requested shutdown. [WEBSMS] | CMIN
12/14/2023 4:31:55 PM | Mindanao Grid-12/14/2023 16:35: WMPC DG06 cut-out at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/14/2023 3:30:37 PM | [NSO Update] Mindanao Grid-12/14/2023 15:33: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1526H with power going to Visayas. [WEBSMS] | CMIN
12/14/2023 3:29:21 PM | [NSO Update] Visayas Grid-12/14/2023 15:29: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1526H with power going to Visayas. [WEBSMS] | CVIS
12/14/2023 3:24:57 PM | [NSO Update] Mindanao Grid-12/14/2023 15:28: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1517H from reverese power direction. [WEBSMS] | CMIN
12/14/2023 3:20:53 PM | [NSO Update] Visayas Grid-12/14/2023 15:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1517H from reverese power direction. [WEBSMS] | CVIS
12/14/2023 3:17:13 PM | Mindanao Grid-12/14/2023 15:20: WMPC DG06 tripped with 8.5MW load at 1505H. Indication: Generator Under Reactance. (Unplanned Outage) [WEBSMS] | CMIN
12/14/2023 3:09:09 PM | Mindanao Grid-12/14/2023 15:12: LAMSAN Biomass cut-in at 1416H. (Unplanned Outage) [WEBSMS] | CMIN
12/14/2023 3:08:33 PM | Mindanao Grid-12/14/2023 15:11: LAMSAN Biomass tripped with 13.5MW at 1402H. Indication: 67N. (Unplanned Outage) [WEBSMS] | CMIN
12/14/2023 2:30:44 PM | Luzon Grid-12/14/2023 14:30: MPGC 500kV Bus 2 de-energized at 1418H (Unplanned Outage) [WEBSMS] | CLUZ
12/14/2023 1:12:11 PM | [NSO Update] Visayas Grid-12/14/2023 13:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1307H with power going to Mindanao. [WEBSMS] | CVIS
12/14/2023 1:11:59 PM | [NSO Update] Mindanao Grid-12/14/2023 13:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1307H with power going to Mindanao. [WEBSMS] | CMIN
12/14/2023 1:11:18 PM | [NSO Update] Mindanao Grid-12/14/2023 13:14: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1247H from forward power direction. [WEBSMS] | CMIN
12/14/2023 1:11:02 PM | [NSO Update] Visayas Grid-12/14/2023 13:11: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1247H from forward power direction. [WEBSMS] | CVIS
12/14/2023 12:47:02 PM | [NSO Update] Luzon Grid-12/14/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13861MW, PK=10942MW, RR=445MW, NetOpMargin: PM=2474, EVE=2245 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, SLPGC 1 @ 130MW [WEBSMS] | CLUZ
12/14/2023 12:42:06 PM | [NSO Update] Mindanao Grid-12/14/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3206MW, PK=2307MW, RR=92MW, NetOpMargin: PM=807, EVE=807 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @45MW, AG1 @35MW, AG2 @70MW, AG4 @120MW, AG5 @37MW, AG6 @155MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/14/2023 12:41:16 PM | [NSO Update] Visayas Grid-12/14/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2606MW, PK=2321MW, RR=94MW, NetOpMargin: PM=192, EVE=246 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 80MW, Leyte A @ 305MW, PGPP1 @ 76MW [WEBSMS] | CVIS
12/14/2023 12:33:49 PM | Mindanao Grid-12/14/2023 12:36: TMI U1 cut in at 1227H, for SOC management of TMI BESS. [WEBSMS] | CMIN
12/14/2023 11:44:26 AM | [NSO Update] Mindanao Grid-12/14/2023 11:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1143H with power going to Visayas. [WEBSMS] | CMIN
12/14/2023 11:44:12 AM | [NSO Update] Visayas Grid-12/14/2023 11:44: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1143H with power going to Visayas. [WEBSMS] | CVIS
12/14/2023 11:33:37 AM | [NSO Update] Mindanao Grid-12/14/2023 11:36: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1133H from reverse power direction. [WEBSMS] | CMIN
12/14/2023 11:33:22 AM | [NSO Update] Visayas Grid-12/14/2023 11:33: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1133H from reverse power direction. [WEBSMS] | CVIS
12/14/2023 11:02:40 AM | Mindanao Grid-12/14/2023 11:05: WMPC DG6 as RPS online at 1050H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/14/2023 9:44:38 AM | Mindanao Grid-12/14/2023 09:47: Kauswagan-GNPK 230kV L4 deenergized at 0908H. GNPK request shutdown to conduct leak repair of their Unit #4 outdoor GIS. [WEBSMS] | CMIN
12/14/2023 9:23:03 AM | [NSO Update] Visayas Grid-12/14/2023 09:23: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0922H with power going to Mindanao. [WEBSMS] | CVIS
12/14/2023 9:22:50 AM | [NSO Update] Mindanao Grid-12/14/2023 09:25: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0922H with power going to Mindanao. [WEBSMS] | CMIN
12/14/2023 9:18:12 AM | Mindanao Grid-12/14/2023 09:21: WMPC DG10 as RPS online at 0910H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/14/2023 9:13:22 AM | [NSO Update] Mindanao Grid-12/14/2023 09:16: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0912H from forward power direction. [WEBSMS] | CMIN
12/14/2023 9:13:08 AM | [NSO Update] Visayas Grid-12/14/2023 09:13: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0912H from forward power direction. [WEBSMS] | CVIS
12/14/2023 8:57:17 AM | Mindanao Grid-12/14/2023 09:00: Agus 2-Agus 2 HEP U2 138kV L deenergized at 0807H. Planned Outage/Non-GOMP (OO07AD). Customers (Agus 2 HEP) request shutdown. [WEBSMS] | CMIN
12/14/2023 8:15:42 AM | Mindanao Grid-12/14/2023 08:18: Agus2 HEP U2 shutdown at 0807H . (Planned outage). [WEBSMS] | CMIN
12/14/2023 7:52:59 AM | Visayas Grid-12/14/2023 07:53: Magdugo SS 138kV Bus 1 de-energized at 0751H. (Planned Outage) [WEBSMS] | CVIS
12/14/2023 7:50:41 AM | Visayas Grid-12/14/2023 07:50: Daanlungsod SS 138kV Bus 2 de-energized at 0747H. (Planned Outage) [WEBSMS] | CVIS
12/14/2023 7:33:37 AM | Luzon Grid-12/14/2023 07:33: Salong-Steel Asia 230kV Line de-energized at 0733H (Planned Outage) [WEBSMS] | CLUZ
12/14/2023 7:21:16 AM | Visayas Grid-12/14/2023 07:21: Dumanjug SS 138kV Bus 2 de-energized at 0718H. (Planned Outage) [WEBSMS] | CVIS
12/14/2023 6:52:46 AM | Mindanao Grid-12/14/2023 06:55: Baloi-Villanueva 230kV L1 deenergized at 0622H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
12/14/2023 6:42:40 AM | Luzon Grid-12/14/2023 06:42: San Jose 230kV Bus 1 restored at 0642H (Planned Outage) [WEBSMS] | CLUZ
12/14/2023 5:49:54 AM | [NSO Update] Mindanao Grid-12/14/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3213MW, PK=2111MW, RR=88MW, NetOpMargin: AM=1014, PM=905, EVE=851 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @45MW, AG1 @35MW, AG2 @70MW, AG4 @120MW, AG5 @37MW, AG6 @155MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/14/2023 5:47:33 AM | [NSO Update] Visayas Grid-12/14/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2621MW, PK=2282MW, RR=93MW, NetOpMargin: AM=247, PM=221, EVE=181 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80MW, LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
12/14/2023 5:45:45 AM | [NSO Update] Luzon Grid-12/14/2023 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13943MW, PK=10727MW, RR=437MW, NetOpMargin: AM=2779, PM=2078, EVE=1800 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @130MW [WEBSMS] | CLUZ
12/14/2023 4:10:34 AM | [NSO Update] Luzon Grid-12/14/2023 04:10: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
12/14/2023 4:10:22 AM | [NSO Update] Visayas Grid-12/14/2023 04:10: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
12/14/2023 4:10:07 AM | [NSO Update] Mindanao Grid-12/14/2023 04:13: Weather Update: Northeast Monsoon affecting Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
12/13/2023 9:22:58 PM | Mindanao Grid-12/13/2023 21:26: SUPREME POWER Mati (MDP) cut-out at 2105H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/13/2023 9:18:07 PM | Mindanao Grid-12/13/2023 21:21: WMPC DG10 cut-out at 2113H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/13/2023 8:47:54 PM | Mindanao Grid-12/13/2023 20:50: SEC 1 (SMF) G01 tripped with 30.31MW load at 2038H. Cause: Turbine High Vibration. (Unplanned Outage). [WEBSMS] | CMIN
12/13/2023 7:41:13 PM | Luzon Grid-12/13/2023 19:41: San Jose 230kV Bus 1 de-energized at 1940H (Planned Outage) [WEBSMS] | CLUZ
12/13/2023 7:11:41 PM | Mindanao Grid-12/13/2023 19:14: Tudaya 2 Unit 1 cut-in at 1856H. (Unplanned Outage) [WEBSMS] | CMIN
12/13/2023 7:09:29 PM | Mindanao Grid-12/13/2023 19:12: Tudaya 2 Unit 1 tripped with 2.1MW load at 1840H. Cause: For further investigation. (Unplanned Outage) [WEBSMS] | CMIN
12/13/2023 7:04:32 PM | Mindanao Grid-12/13/2023 19:07: Update: Tudaya 2 Unit 2 shutdown with 0.9MW load at 1838H. Cause: Insufficient Water Supply. [WEBSMS] | CMIN
12/13/2023 6:58:05 PM | Mindanao Grid-12/13/2023 19:01: Tudaya 2 Unit 1 shutdown with 0.9MW load at 1838H. Cause: Insufficient Water Supply. (Unplanned Outage) [WEBSMS] | CMIN
12/13/2023 6:05:47 PM | Mindanao Grid-12/13/2023 18:08: SEC 1 online at 1801H from Forced Outage. (Uplanned outage). [WEBSMS] | CMIN
12/13/2023 5:51:40 PM | [NSO Update] Luzon Grid-12/13/2023 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13175MW, PK=10984MW, RR=444MW, NetOpMargin: EVE=1747 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @130MW [WEBSMS] | CLUZ
12/13/2023 5:36:48 PM | [NSO Update] Mindanao Grid-12/13/2023 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3195MW, PK=2273MW, RR=95MW, NetOpMargin: EVE=827 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @45MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @37MW, AG6 @155MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/13/2023 5:36:21 PM | [NSO Update] Visayas Grid-12/13/2023 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2648MW, PK=2306MW, RR=97MW, NetOpMargin: EVE=245 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @350MW, PGPP1 @74MW [WEBSMS] | CVIS
12/13/2023 5:00:36 PM | Mindanao Grid-12/13/2023 17:03: Balo-i - Aurora 138kV Line energized at 1651H. (Planned Outage) [WEBSMS] | CMIN
12/13/2023 4:15:37 PM | Mindanao Grid-12/13/2023 16:18: WMPC DG06 cut-out at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/13/2023 2:24:58 PM | [NSO Update] Mindanao Grid-12/13/2023 14:28: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1422H with power going to Visayas [WEBSMS] | CMIN
12/13/2023 2:24:52 PM | [NSO Update] Visayas Grid-12/13/2023 14:24: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1422H with power going to Visayas [WEBSMS] | CVIS
12/13/2023 2:12:31 PM | [NSO Update] Visayas Grid-12/13/2023 14:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1404H from reverse power direction [WEBSMS] | CVIS
12/13/2023 2:12:22 PM | [NSO Update] Mindanao Grid-12/13/2023 14:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1404H from reverse power direction [WEBSMS] | CMIN
12/13/2023 12:59:31 PM | [NSO Update] Mindanao Grid-12/13/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3304MW, PK=2311MW, RR=96MW, NetOpMargin: PM=897, EVE=813 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @45MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @37MW, AG6 @155MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/13/2023 12:57:50 PM | [NSO Update] Visayas Grid-12/13/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2661MW, PK=2277MW, RR=94MW, NetOpMargin: PM=289, EVE=255 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 340MW, PGPP1 @ 68MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
12/13/2023 12:56:04 PM | [NSO Update] Luzon Grid-12/13/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13998MW, PK=11372MW, RR=445MW, NetOpMargin: PM=2182, EVE=1840 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, SLPGC 1 @ 130MW [WEBSMS] | CLUZ
12/13/2023 12:01:26 PM | Mindanao Grid-12/13/2023 12:04: Aurora SS 138KV Bus 2 restored at 1153H. Planned Outage. [WEBSMS] | CMIN
12/13/2023 10:03:29 AM | Mindanao Grid-12/13/2023 10:06: Nagamin SS Power Transformer No. 3 / SVC energized at 0952H. (Unplanned Outage) [WEBSMS] | CMIN
12/13/2023 10:02:43 AM | Mindanao Grid-12/13/2023 10:05: SPC Mati cut in at 0900H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
12/13/2023 8:27:04 AM | [NSO Update] Mindanao Grid-12/13/2023 08:30: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0826H with power going to Mindanao. [WEBSMS] | CMIN
12/13/2023 8:26:52 AM | [NSO Update] Visayas Grid-12/13/2023 08:26: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0826H with power going to Mindanao. [WEBSMS] | CVIS
12/13/2023 8:17:31 AM | [NSO Update] Mindanao Grid-12/13/2023 08:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0816H from forward power direction. [WEBSMS] | CMIN
12/13/2023 8:17:10 AM | [NSO Update] Visayas Grid-12/13/2023 08:17: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0816H from forward power direction. [WEBSMS] | CVIS
12/13/2023 7:57:54 AM | Mindanao Grid-12/13/2023 08:00: WMPC DG6 as RPS online at 0750H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/13/2023 7:28:51 AM | Mindanao Grid-12/13/2023 07:31: Aurora SS 138KV Bus 2 deenergized at 0718H. Planned Outage. [WEBSMS] | CMIN
12/13/2023 7:26:52 AM | Mindanao Grid-12/13/2023 07:29: Baloi - Aurora 138KV Line deenergized at 0701H. Planned Outage. [WEBSMS] | CMIN
12/13/2023 6:44:51 AM | Luzon Grid-12/13/2023 06:44: Tayabas-San Jose 500kV Line 2 energized at 0641H - Tayabas side only (Planned Outage) [WEBSMS] | CLUZ
12/13/2023 5:50:17 AM | [NSO Update] Luzon Grid-12/13/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13982MW, PK=10862MW, RR=444MW, NetOpMargin: AM=2676, PM=2066, EVE=1497 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @280MW, SLPGC 1 @130MW [WEBSMS] | CLUZ
12/13/2023 5:30:11 AM | [NSO Update] Mindanao Grid-12/13/2023 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3433MW, PK=2217MW, RR=92MW, NetOpMargin: AM=1124, PM=930, EVE=719 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @45MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @37MW, AG6 @155MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/13/2023 5:27:51 AM | [NSO Update] Visayas Grid-12/13/2023 05:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2781MW, PK=2188MW, RR=93MW, NetOpMargin: AM=500, PM=410, EVE=237 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @350MW, PGPP1 @74MW [WEBSMS] | CVIS
12/13/2023 4:13:42 AM | [NSO Update] Visayas Grid-12/13/2023 04:13: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
12/13/2023 4:13:25 AM | [NSO Update] Mindanao Grid-12/13/2023 04:16: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
12/13/2023 4:12:46 AM | [NSO Update] Visayas Grid-12/13/2023 04:12: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
12/13/2023 4:12:22 AM | [NSO Update] Luzon Grid-12/13/2023 04:12: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
12/13/2023 12:59:04 AM | Luzon Grid-12/13/2023 00:59: Olongapo-SBMA 230kV line restored at 0057H (Planned Outage) [WEBSMS] | CLUZ
12/12/2023 10:56:10 PM | Luzon Grid-12/12/2023 22:56: Tayabas PCB 9-02CB24TAY was closed at 2254H. (From an unplanned outage) [WEBSMS] | CLUZ
12/12/2023 9:20:21 PM | Mindanao Grid-12/12/2023 21:23: WMPC DG06 cut-out at 2114H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/12/2023 9:09:31 PM | Mindanao Grid-12/12/2023 21:12: SUPREME POWER Mati (MDP) cut-out at 2105H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/12/2023 8:08:14 PM | Luzon Grid-12/12/2023 20:08: Ilijan GT1-1 online at 2006H. (From an unplanned outage) [WEBSMS] | CLUZ
12/12/2023 7:24:23 PM | Mindanao Grid-12/12/2023 19:27: NACSUR cut-out at 1904H. MO dispatched (RTD). [WEBSMS] | CMIN
12/12/2023 6:51:28 PM | Mindanao Grid-12/12/2023 18:54: NACSUR cut-in at 1830H. Unplanned Outage. [WEBSMS] | CMIN
12/12/2023 6:47:34 PM | Mindanao Grid-12/12/2023 18:50: NACSUR isolated with 4.92MW load at 1759H, affected by the tripping of Placer-Surigao 69kV STL. Unplanned Outage. [WEBSMS] | CMIN
12/12/2023 6:05:35 PM | Luzon Grid-12/12/2023 18:05: Ilijan ST1 online at 1804H. (From an unplanned outage) [WEBSMS] | CLUZ
12/12/2023 5:56:46 PM | Mindanao Grid-12/12/2023 18:00: Nagamin SS Static VAR Compensator (SVC) Transformer deenergized at 1603H. Emergency shutdown to facilitate repair of Water Cooling System leak. [WEBSMS] | CMIN
12/12/2023 5:42:53 PM | [NSO Update] Luzon Grid-12/12/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12601MW, PK=10858MW, RR=428MW, NetOpMargin: EVE=1315 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @130MW [WEBSMS] | CLUZ
12/12/2023 5:40:57 PM | [NSO Update] Visayas Grid-12/12/2023 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2589MW, PK=2260MW, RR=97MW, NetOpMargin: EVE=232 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @350MW, PGPP1 @71MW, NASULO @28MW [WEBSMS] | CVIS
12/12/2023 5:38:49 PM | Mindanao Grid-12/12/2023 17:42: NACSUR cut-in at 1735H. MO dispatched. Follow RTD. [WEBSMS] | CMIN
12/12/2023 5:36:51 PM | [NSO Update] Mindanao Grid-12/12/2023 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3196MW, PK=2315MW, RR=92MW, NetOpMargin: EVE=789 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @37MW, AG6 @155MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/12/2023 4:50:11 PM | Luzon Grid-12/12/2023 16:50: Ilijan GT1-2 online at 1649H. (Unplanned Outage) [WEBSMS] | CLUZ
12/12/2023 4:11:27 PM | Mindanao Grid-12/12/2023 16:14: WMPC DG04 cut-in at 1600H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/12/2023 4:08:53 PM | Mindanao Grid-12/12/2023 16:12: Update: WMPC DG04 cut-out at 1425H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
12/12/2023 4:05:34 PM | Mindanao Grid-12/12/2023 16:08: WMPC DG04 cut-in at 1425H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
12/12/2023 3:51:24 PM | Luzon Grid-12/12/2023 15:51: Tayabas PCB 9-02CB24TAY was opened at 1546H (Unplanned Outage to facilitate correction of air leak at compressor system) [WEBSMS] | CLUZ
12/12/2023 3:35:39 PM | Visayas Grid-12/12/2023 15:35: Compostela-Consolacion 69KV fdr. @ Compostela SS tripped @ 1514H, restored 1530H. (Unplanned Outage) [WEBSMS] | CVIS
12/12/2023 1:50:59 PM | Mindanao Grid-12/12/2023 13:54: WMPC DG04 cut-in at 1331H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
12/12/2023 1:45:39 PM | Mindanao Grid-12/12/2023 13:48: Agus 2-Kibawe 138kV L2 auto-tripped at 1210H. Unplanned Outage. (The line is energized up to str# 33 only, to prevent pilferage). [WEBSMS] | CMIN
12/12/2023 1:23:32 PM | Mindanao Grid-12/12/2023 13:26: KEGI TANDAG (KE TANDAG) cut-in at 1317H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
12/12/2023 1:08:25 PM | Mindanao Grid-12/12/2023 13:11: AGUS 2 Unit 2 cut-in at 1250H. (Unplanned Outage) [WEBSMS] | CMIN
12/12/2023 1:06:30 PM | [NSO Update] Mindanao Grid-12/12/2023 13:09: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3267MW, PK=2305MW, RR=94MW, NetOpMargin: PM=868, EVE=863 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @37MW, AG6 @155MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/12/2023 1:05:27 PM | [NSO Update] Visayas Grid-12/12/2023 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2672MW, PK=2270MW, RR=94MW, NetOpMargin: PM=308, EVE=243 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @350MW, PGPP1 @71MW, NASULO @28MW [WEBSMS] | CVIS
12/12/2023 1:03:16 PM | [NSO Update] Luzon Grid-12/12/2023 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13366MW, PK=10904MW, RR=443MW, NetOpMargin: PM=2019, EVE=1660 Highest Unit O/L: GNPD 1&2 @169MW Derated Plant: CLC2 @175MW, SLPGC 1 @130MW [WEBSMS] | CLUZ
12/12/2023 1:02:35 PM | Mindanao Grid-12/12/2023 13:05: AGUS 2 Unit 2 tripped with load of 30MW at 1210H. Indication: 86T Tripped. (Unplanned Outage) [WEBSMS] | CMIN
12/12/2023 12:47:09 PM | Mindanao Grid-12/12/2023 12:50: LAMSAN (LSK) cut-in at 1235H. (Unplanned Outage) [WEBSMS] | CMIN
12/12/2023 12:41:31 PM | Mindanao Grid-12/12/2023 12:44: LAMSAN (LSK) tripped at 1216H with 13.5MW load. Indication: 67N Directional Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
12/12/2023 12:03:57 PM | Mindanao Grid-12/12/2023 12:07: Tagoloan-Manolo 138kV L1 energized at 1139H. Planned Outage. (Shutdown was requested by STEAG to conduct correction of thermal anomaly at their DS 7Z-05DS23TAG, phase ABC). [WEBSMS] | CMIN
12/12/2023 11:17:13 AM | Mindanao Grid-12/12/2023 11:20: WMPC DG06 cut-in at 1050H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/12/2023 9:49:18 AM | Mindanao Grid-12/12/2023 09:52: (Addendum) Tagoloan-Manolo 138kV L1 deenergized at 0809H. Planned Outage. (Shutdown was requested by STEAG to conduct correction of thermal anomaly at their DS 7Z-05DS23TAG, phase ABC). [WEBSMS] | CMIN
12/12/2023 9:17:41 AM | Mindanao Grid-12/12/2023 09:20: Tagoloan-Manolo 138kV L1 deenergized at 0809H. Planned Outage. (Shutdown requested by STEAG) [WEBSMS] | CMIN
12/12/2023 9:10:16 AM | Mindanao Grid-12/12/2023 09:13: SPC Mati cut in at 0901H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
12/12/2023 8:57:01 AM | Mindanao Grid-12/12/2023 09:00: WMPC DG10 cut-in at 0850H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/12/2023 8:49:32 AM | Mindanao Grid-12/12/2023 08:52: Tagoloan-Manolo 138kV L1 deenergized at 0809H. Planned Outage. (Shutdown requested by STEAG) [WEBSMS] | CMIN
12/12/2023 8:19:54 AM | Luzon Grid-12/12/2023 08:20: Tayabas-San Jose 500kV Line 2 de-energized at 0817H (Planned Outage) [WEBSMS] | CLUZ
12/12/2023 5:53:15 AM | [NSO Update] Luzon Grid-12/12/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13178MW, PK=10371MW, RR=432MW, NetOpMargin: AM=2375, PM=1940, EVE=1615 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @280MW, SLPGC 1 @130MW [WEBSMS] | CLUZ
12/12/2023 5:41:28 AM | [NSO Update] Visayas Grid-12/12/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2682MW, PK=2238MW, RR=93MW, NetOpMargin: AM=350, PM=340, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @345MW, PGPP1 @74MW [WEBSMS] | CVIS
12/12/2023 5:39:49 AM | [NSO Update] Mindanao Grid-12/12/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3282MW, PK=2207MW, RR=91MW, NetOpMargin: AM=984, PM=972, EVE=809 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @37MW, AG6 @155MW, AG7 @25MW, PG4 @80MW [WEBSMS] | CMIN
12/12/2023 5:34:38 AM | Luzon Grid-12/12/2023 05:34: San Jose 750MVA Transformer Bank No.5 was restored at 0533H. (Planned Outage) [WEBSMS] | CLUZ
12/12/2023 4:47:38 AM | Luzon Grid-12/12/2023 04:47: Duhat 300MVA T01 energized at 0444H (Planned Outage) [WEBSMS] | CLUZ
12/12/2023 4:20:46 AM | [NSO Update] Mindanao Grid-12/12/2023 04:24: Weather Advisory: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CMIN
12/12/2023 4:20:28 AM | [NSO Update] Luzon Grid-12/12/2023 04:20: Weather Advisory: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
12/12/2023 4:19:52 AM | [NSO Update] Visayas Grid-12/12/2023 04:20: Weather Advisory: Northeast Monsoon affecting Extreme Northern Luzon. Easterlies affecting the rest of the country. [WEBSMS] | CVIS
12/12/2023 2:41:30 AM | Luzon Grid-12/12/2023 02:41: Ilijan Block A (383MW) tripped at 0230H. Lowest frequency is 59.098 Hz. (Unplanned Outage) [WEBSMS] | CLUZ
12/12/2023 2:04:51 AM | Luzon Grid-12/12/2023 02:05: Duhat 300MVA T01 de-energized at 0202H (Planned Outage) [WEBSMS] | CLUZ
12/11/2023 10:20:57 PM | Luzon Grid-12/11/2023 22:21: San Jose 750MVA Transformer Bank No. 5 was de-energized at 2219H. (Planned Outage) [WEBSMS] | CLUZ
12/11/2023 9:34:37 PM | Mindanao Grid-12/11/2023 21:37: WMPC DG05 cut-out at 2113H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/11/2023 9:16:03 PM | Mindanao Grid-12/11/2023 21:19: SUPREME POWER Mati (MDP) cut-out at 2105H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/11/2023 8:49:36 PM | Luzon Grid-12/11/2023 20:49: Commissioning and energization of San Marcelino Solar Power Plant as load was completed at 2047H. [WEBSMS] | CLUZ
12/11/2023 8:30:12 PM | Luzon Grid-12/11/2023 20:30: Balsik-San Marcelino 230kV line 2 was looped at 2026H (San Marcelino side) at the same time energizing San Marcelino 230kV Bus 2. (On-going commissioning ang energization of San Marcelino Solar Power Plant as load) [WEBSMS] | CLUZ
12/11/2023 8:12:42 PM | Luzon Grid-12/11/2023 20:12: Labrador New PCB 8-02CB24LAB was energized at 2011H. (Commissioning completed) [WEBSMS] | CLUZ
12/11/2023 7:50:56 PM | Luzon Grid-12/11/2023 19:51: Balsik-San Marcelino 230kV line 1 commissioning and energization was completed at 1947H. [WEBSMS] | CLUZ
12/11/2023 6:38:19 PM | Luzon Grid-12/11/2023 18:38: Balsik-San Marcelino 230kV line 1 was looped at 1833H(San Marcelino side) at the same time energizing San Marcelino 230kV Bus 1. (On-going commissioning ang energization of San Marcelino Solar Power Plant as load) [WEBSMS] | CLUZ
12/11/2023 6:00:30 PM | [NSO Update] Luzon Grid-12/11/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13416MW, PK=10766MW, RR=444MW, NetOpMargin: EVE=2206 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @135MW [WEBSMS] | CLUZ
12/11/2023 5:57:50 PM | [NSO Update] Visayas Grid-12/11/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2672MW, PK=2303MW, RR=97MW, NetOpMargin: EVE=272 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @332MW, PGPP1 @76MW [WEBSMS] | CVIS
12/11/2023 5:55:28 PM | [NSO Update] Mindanao Grid-12/11/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3261MW, PK=2354MW, RR=86MW, NetOpMargin: EVE=821 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
12/11/2023 4:18:23 PM | Mindanao Grid-12/11/2023 16:21: WMPC DG06 cut-out at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/11/2023 3:51:03 PM | Luzon Grid-12/11/2023 15:51: Bolo-Labrador 230kV line 2 was restored at 1548H. (Planned Outage) [WEBSMS] | CLUZ
12/11/2023 2:44:50 PM | [NSO Update] Mindanao Grid-12/11/2023 14:48: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1437H with power going to Visayas [WEBSMS] | CMIN
12/11/2023 2:44:45 PM | Luzon Grid-12/11/2023 14:44: Tayabas PCB 9-06CB08TAY was closed at 1443H. (Unplanned Outage) [WEBSMS] | CLUZ
12/11/2023 2:44:07 PM | [NSO Update] Visayas Grid-12/11/2023 14:44: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1437H with power going to Visayas [WEBSMS] | CVIS
12/11/2023 2:40:46 PM | [NSO Update] Mindanao Grid-12/11/2023 14:44: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1427H from reverse power direction [WEBSMS] | CMIN
12/11/2023 2:39:42 PM | [NSO Update] Visayas Grid-12/11/2023 14:39: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1427H from reverse power direction [WEBSMS] | CVIS
12/11/2023 2:16:27 PM | [NSO Update] Visayas Grid-12/11/2023 14:16: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1230H with power going to Mindanao. [WEBSMS] | CVIS
12/11/2023 1:58:36 PM | Visayas Grid-12/11/2023 13:58: Mandaue GIS 100 MVA TR1 loaded at 1356H. (Planned Outage) [WEBSMS] | CVIS
12/11/2023 1:50:45 PM | Visayas Grid-12/11/2023 13:50: Cebu-Mandaue 138 KV Line 1 loaded at 1349H upon energization of Mandaue GIS 138 KV by pass CB. [WEBSMS] | CVIS
12/11/2023 1:37:09 PM | [NSO Update] Mindanao Grid-12/11/2023 13:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3372MW, PK=2364MW, RR=84MW, NetOpMargin: PM=923, EVE=868 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
12/11/2023 1:17:03 PM | [NSO Update] Visayas Grid-12/11/2023 13:17: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2693MW, PK=2249MW, RR=94MW, NetOpMargin: PM=351, EVE=252 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @334MW, PGPP1 @76MW, NASULO @26MW [WEBSMS] | CVIS
12/11/2023 1:13:33 PM | [NSO Update] Luzon Grid-12/11/2023 13:13: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14176MW, PK=11026MW, RR=445MW, NetOpMargin: PM=2705, EVE=2352 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, SLPGC 1 @135MW [WEBSMS] | CLUZ
12/11/2023 1:11:13 PM | Mindanao Grid-12/11/2023 13:14: LIBERTAD POWER (LPE) online at 1306H. (Unplanned Outage) [WEBSMS] | CMIN
12/11/2023 12:38:24 PM | Mindanao Grid-12/11/2023 12:41: TMI U1 cut out at 1236H. Cut in for SOC management of TMI BESS. [WEBSMS] | CMIN
12/11/2023 12:25:03 PM | [NSO Update] Mindanao Grid-12/11/2023 12:28: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1220H from forward power direction. [WEBSMS] | CMIN
12/11/2023 12:24:38 PM | [NSO Update] Visayas Grid-12/11/2023 12:24: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1220H from forward power direction. [WEBSMS] | CVIS
12/11/2023 11:59:34 AM | Mindanao Grid-12/11/2023 12:02: TMI U1 cut in at 1156H, for SOC management of TMI BESS. [WEBSMS] | CMIN
12/11/2023 11:12:40 AM | Mindanao Grid-12/11/2023 11:15: LIBERTAD POWER (LPE) tripped with 6MW load at 1052H. Cause: Affected by line fault of ZAMSURECO feeder. [WEBSMS] | CMIN
12/11/2023 11:03:12 AM | Mindanao Grid-12/11/2023 11:06: TMI U1 cut out at 1055H. Cut in for SOC management of TMI BESS. [WEBSMS] | CMIN
12/11/2023 11:02:11 AM | Mindanao Grid-12/11/2023 11:05: WMPC DG06 online as RPS at 1050H. For RPS System VOLTAGE REQUIREMENT. [WEBSMS] | CMIN
12/11/2023 9:45:40 AM | Mindanao Grid-12/11/2023 09:48: TMI U1 cut in at 0936H, for SOC management of TMI BESS. [WEBSMS] | CMIN
12/11/2023 9:20:57 AM | Mindanao Grid-12/11/2023 09:24: TMI U1 cut out at 0847H. Cut in for SOC management of TMI BESS. [WEBSMS] | CMIN
12/11/2023 9:19:05 AM | Mindanao Grid-12/11/2023 09:22: WMPC DG05 online as RPS at 0915H. For RPS System VOLTAGE REQUIREMENT. [WEBSMS] | CMIN
12/11/2023 8:36:38 AM | Mindanao Grid-12/11/2023 08:39: TMI U1 cut in at 0827H, for SOC management of TMI BESS. [WEBSMS] | CMIN
12/11/2023 8:11:09 AM | Mindanao Grid-12/11/2023 08:14: Pulangi 4 Unit 2 shutdown at 0802H. (Planned outage - GOMP) [WEBSMS] | CMIN
12/11/2023 6:25:46 AM | Luzon Grid-12/11/2023 06:25: Bolo-Labrador 230kV Line 2 de-energized at 0624H (Planned Outage) [WEBSMS] | CLUZ
12/11/2023 5:36:04 AM | [NSO Update] Mindanao Grid-12/11/2023 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3296MW, PK=2227MW, RR=82MW, NetOpMargin: AM=987, PM=942, EVE=787 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
12/11/2023 5:31:51 AM | [NSO Update] Visayas Grid-12/11/2023 05:31: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2576MW, PK=2189MW, RR=93MW, NetOpMargin: AM=294, PM=258, EVE=224 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @338MW, PGPP1 @76MW [WEBSMS] | CVIS
12/11/2023 5:29:14 AM | [NSO Update] Luzon Grid-12/11/2023 05:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14375MW, PK=10714MW, RR=444MW, NetOpMargin: AM=3218, PM=2689, EVE=2410 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @ 175MW, SLPGC 1@ 130MW [WEBSMS] | CLUZ
12/11/2023 3:55:23 AM | [NSO Update] Luzon Grid-12/11/2023 03:55: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CLUZ
12/11/2023 3:55:17 AM | [NSO Update] Mindanao Grid-12/11/2023 03:58: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CMIN
12/11/2023 3:55:00 AM | [NSO Update] Visayas Grid-12/11/2023 03:55: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CVIS
12/11/2023 3:52:53 AM | Luzon Grid-12/11/2023 03:53: Ilijan A GT-1 online at 0350H (Unplanned Outage) [WEBSMS] | CLUZ
12/11/2023 2:57:53 AM | Luzon Grid-12/11/2023 02:58: Tayabas 600MVA T05 energized at 0256H (Unplanned Outage). [WEBSMS] | CLUZ
12/10/2023 11:32:31 PM | Mindanao Grid-12/10/2023 23:35: Butuan-San Francisco 138kV line energized 2328H. Planned outage. [WEBSMS] | CMIN
12/10/2023 11:16:00 PM | Mindanao Grid-12/10/2023 23:19: Polanco SS 100MVA Power Transformer 3 successfully energized without load at 2310H with approved ERFP-23-11-05. P&E energization request. [WEBSMS] | CMIN
12/10/2023 9:52:52 PM | Luzon Grid-12/10/2023 21:53: Nagsaag - San Manuel 230kV Line 1 restored at 2152H. (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 8:50:19 PM | Mindanao Grid-12/10/2023 20:53: TMI U1 cut out at 1847H, for SOC management of TMI BESS. [WEBSMS] | CMIN
12/10/2023 7:20:18 PM | Luzon Grid-12/10/2023 19:20: Tayabas - Pagbilao 500kV Line 1 looped at Tayabas side at 1918H. (Unplanned Outage) [WEBSMS] | CLUZ
12/10/2023 6:47:22 PM | Mindanao Grid-12/10/2023 18:50: Polanco SS 138kV Bus 02 energized 1842H. Planned outage. [WEBSMS] | CMIN
12/10/2023 6:33:02 PM | Luzon Grid-12/10/2023 18:33: Balsik SS 230kV Bus 1 restored at 1832H. (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 6:17:04 PM | Luzon Grid-12/10/2023 18:17: Gamu-UPSI Gamu BESS 69kV Line restored at 1815H. (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 5:53:02 PM | Mindanao Grid-12/10/2023 17:56: TMI U1 cut in at 1750H, for SOC management of TMI BESS. [WEBSMS] | CMIN
12/10/2023 5:49:43 PM | [NSO Update] Visayas Grid-12/10/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2543MW, PK=2099MW, RR=97MW, NetOpMargin: EVE=347 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @340MW, PGPP1 @76MW [WEBSMS] | CVIS
12/10/2023 5:38:59 PM | Luzon Grid-12/10/2023 17:39: Ilijan A ST1 online at 1735H. (Unplanned Outage) [WEBSMS] | CLUZ
12/10/2023 5:29:01 PM | [NSO Update] Mindanao Grid-12/10/2023 17:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3253MW, PK=2107MW, RR=76MW, NetOpMargin: EVE=1070 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
12/10/2023 5:27:22 PM | [NSO Update] Luzon Grid-12/10/2023 17:27: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12640MW, PK=9611MW, RR=354MW, NetOpMargin: EVE=2675 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 340MW, SLPGC 1 @ 140MW [WEBSMS] | CLUZ
12/10/2023 5:22:51 PM | Luzon Grid-12/10/2023 17:22: Bolo-Sual 230kV line 2 restored at 1720H. (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 5:21:32 PM | Luzon Grid-12/10/2023 17:21: Labrador 100MVA T01 energized at low side (69kV) at 1718H. End of Commissioning [WEBSMS] | CLUZ
12/10/2023 5:00:28 PM | Mindanao Grid-12/10/2023 17:03: Butuan SS 138kV Bus 01 re-energized 1657H. Planned outage [WEBSMS] | CMIN
12/10/2023 4:54:15 PM | Luzon Grid-12/10/2023 16:54: Muntinlupa (Sucat)-Binan 230kV Line 4 restored at 1653H. (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 4:15:15 PM | Luzon Grid-12/10/2023 16:15: Ilijan A GT 1-2 online at 1612H. (Unplanned Outage) [WEBSMS] | CLUZ
12/10/2023 4:09:51 PM | Luzon Grid-12/10/2023 16:09: San Jose 230kV Bus 1 restored at 1608H. (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 3:50:25 PM | Luzon Grid-12/10/2023 15:50: San Rafael-Cabanatuan 230kV Line restored at 1549H. (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 3:27:23 PM | Mindanao Grid-12/10/2023 15:30: LIBERTAD POWER (LPE) cut-in at 1500H. (Unplanned Outage) [WEBSMS] | CMIN
12/10/2023 3:26:32 PM | Mindanao Grid-12/10/2023 15:29: LIBERTAD POWER (LPE) tripped with 6MW load at 1453H. Cause: Affected by line fault of ZAMSURECO feeder. (Unplanned Outage) [WEBSMS] | CMIN
12/10/2023 2:29:19 PM | Luzon Grid-12/10/2023 14:29: Correction: Tayabas 600MVA T05 tripped at 1339H (Unplanned Outage) [WEBSMS] | CLUZ
12/10/2023 2:13:42 PM | Visayas Grid-12/10/2023 14:13: Mandaue GIS 100MVA TR 1 energized at 1410H without load. (Planned Outage) [WEBSMS] | CVIS
12/10/2023 2:12:01 PM | Visayas Grid-12/10/2023 14:12: Cebu-Mandaue 138kV Line 1 energized at 1404H without load. (Planned Outage) [WEBSMS] | CVIS
12/10/2023 2:00:57 PM | Luzon Grid-12/10/2023 14:01: Pagbilao 600MVA T05 tripped at 1339H (Unplanned Outage) [WEBSMS] | CLUZ
12/10/2023 1:55:45 PM | Luzon Grid-12/10/2023 13:55: Correction: Tayabas - Pagbilao 500kV Line 1 tripped on Tayabas side at 1338H (Unplanned Outage) [WEBSMS] | CLUZ
12/10/2023 1:52:28 PM | Luzon Grid-12/10/2023 13:52: Tayabas - Pagbilao 500kV Line 1 auto-tripped at 1338H (Unplanned Outage) [WEBSMS] | CLUZ
12/10/2023 1:28:55 PM | Mindanao Grid-12/10/2023 13:32: Butuan SS 138kV Bus 01 de-energized 1322H. Planned outage. [WEBSMS] | CMIN
12/10/2023 1:12:59 PM | [NSO Update] Mindanao Grid-12/10/2023 13:16: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3292MW, PK=1372MW, RR=74MW, NetOpMargin: PM=1372, EVE=1147 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
12/10/2023 1:06:46 PM | [NSO Update] Visayas Grid-12/10/2023 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2500MW, PK=601MW, RR=94MW, NetOpMargin: PM=601, EVE=241 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 320MW, PGPP1 @ 76MW [WEBSMS] | CVIS
12/10/2023 12:41:30 PM | [NSO Update] Luzon Grid-12/10/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13325MW, PK=8974MW, RR=344MW, NetOpMargin: PM=4007, EVE=2698 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW [WEBSMS] | CLUZ
12/10/2023 11:10:02 AM | Mindanao Grid-12/10/2023 11:13: TMI U1 cut in at 1054H, for SOC management of TMI BESS. [WEBSMS] | CMIN
12/10/2023 11:05:23 AM | Mindanao Grid-12/10/2023 11:08: Placer SS 50MVA Power Transformer 2 re-energized 1103H. Planned outage. [WEBSMS] | CMIN
12/10/2023 9:01:15 AM | Luzon Grid-12/10/2023 09:01: Muntinlupa (Sucat) SS 230kV Bus 2 & Bus Coupler 8-10CB04MUN restored at 0900H (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 8:53:27 AM | [NSO Update] Mindanao Grid-12/10/2023 08:56: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0844H with power going to Visayas. [WEBSMS] | CMIN
12/10/2023 8:52:12 AM | [NSO Update] Visayas Grid-12/10/2023 08:52: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0844H with power going to Visayas. [WEBSMS] | CVIS
12/10/2023 8:41:51 AM | Luzon Grid-12/10/2023 08:41: Balsik SS 230kV Bus 1 de-energized at 0841H (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 8:31:50 AM | Mindanao Grid-12/10/2023 08:35: Placer SS 50MVA Power Transformer 2 de-energized 0825H. Planned outage. [WEBSMS] | CMIN
12/10/2023 8:23:14 AM | Mindanao Grid-12/10/2023 08:26: TMI U1 cut out at 0819H, for SOC management of TMI BESS. [WEBSMS] | CMIN
12/10/2023 8:22:29 AM | Mindanao Grid-12/10/2023 08:25: TMI U1 cut in at 0726H, for SOC management of TMI BESS. [WEBSMS] | CMIN
12/10/2023 8:22:02 AM | Luzon Grid-12/10/2023 08:22: San Rafael-Cabanatuan 230kV Line de-energized at 0821H (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 8:03:55 AM | [NSO Update] Mindanao Grid-12/10/2023 08:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0800H from reverse power direction. [WEBSMS] | CMIN
12/10/2023 8:03:11 AM | [NSO Update] Visayas Grid-12/10/2023 08:03: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0800H from reverse power direction. [WEBSMS] | CVIS
12/10/2023 7:49:17 AM | Luzon Grid-12/10/2023 07:49: San Jose 230kV Bus 1 de-energized at 0748H (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 7:44:17 AM | [NSO Update] Mindanao Grid-12/10/2023 07:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0738H with power going to Mindanao. [WEBSMS] | CMIN
12/10/2023 7:42:56 AM | [NSO Update] Visayas Grid-12/10/2023 07:43: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0738H with power going to Mindanao. [WEBSMS] | CVIS
12/10/2023 7:30:04 AM | Luzon Grid-12/10/2023 07:30: Calaca-Binan 230kV Line restored at 0726H (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 7:26:29 AM | Luzon Grid-12/10/2023 07:26: Nagsaag - San Manuel 230kV Line 1 de-energized at 0723H (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 7:25:47 AM | [NSO Update] Mindanao Grid-12/10/2023 07:29: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0721H from forward power direction. [WEBSMS] | CMIN
12/10/2023 7:25:09 AM | [NSO Update] Visayas Grid-12/10/2023 07:25: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0721H from forward power direction. [WEBSMS] | CVIS
12/10/2023 6:32:32 AM | Mindanao Grid-12/10/2023 06:35: Butuan-San Francisco 138kV Line de-energized 0625H. Planned outage. [WEBSMS] | CMIN
12/10/2023 6:00:46 AM | Luzon Grid-12/10/2023 06:00: Ilijan 1-2 shutdown at 0559H (Unplanned Outage) [WEBSMS] | CLUZ
12/10/2023 5:52:51 AM | [NSO Update] Mindanao Grid-12/10/2023 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3301MW, PK=1777MW, RR=72MW, NetOpMargin: AM=1452, PM=1375, EVE=1104 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
12/10/2023 5:50:49 AM | [NSO Update] Visayas Grid-12/10/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2461MW, PK=1812MW, RR=93MW, NetOpMargin: AM=556, PM=473, EVE=172 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 268MW, PGPP1 @ 76MW [WEBSMS] | CVIS
12/10/2023 5:48:30 AM | [NSO Update] Luzon Grid-12/10/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13406MW, PK=8785MW, RR=347MW, NetOpMargin: AM=4273, PM=4051, EVE=2863 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 340MW, Masinloc 2 @ 340MW, SLPGC 1 @ 140MW [WEBSMS] | CLUZ
12/10/2023 5:48:16 AM | Luzon Grid-12/10/2023 05:48: Ilijan ST1shutdown at 0547H (Unplanned Outage) [WEBSMS] | CLUZ
12/10/2023 5:35:04 AM | Luzon Grid-12/10/2023 05:35: Ilijan 1-1 shutdown at 0534H (Unplanned Outage) [WEBSMS] | CLUZ
12/10/2023 5:12:18 AM | Luzon Grid-12/10/2023 05:12: Calaca-Binan 230kV Line de-energized at 0511H (Unplanned Outage) [WEBSMS] | CLUZ
12/10/2023 4:41:57 AM | [NSO Update] Luzon Grid-12/10/2023 04:42: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
12/10/2023 4:41:00 AM | [NSO Update] Mindanao Grid-12/10/2023 04:44: Weather Update: Easterlies affecting the country. [WEBSMS] | CMIN
12/10/2023 4:40:56 AM | Luzon Grid-12/10/2023 04:41: Ilijan GT2-2 shutdown at 0439H (Unplanned Outage) [WEBSMS] | CLUZ
12/10/2023 4:40:42 AM | [NSO Update] Visayas Grid-12/10/2023 04:40: Weather Update: Easterlies affecting the country. [WEBSMS] | CVIS
12/10/2023 4:33:02 AM | Luzon Grid-12/10/2023 04:33: Muntinlupa (Sucat) SS 230kV Bus 2 & Bus Coupler 8-10CB04MUN de-energized at 0432H (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 4:28:03 AM | Luzon Grid-12/10/2023 04:28: Ilijan ST2 shutdown at 0426H (Unplanned Outage) [WEBSMS] | CLUZ
12/10/2023 4:17:51 AM | Luzon Grid-12/10/2023 04:17: Muntinlupa (Sucat)-Binan 230kV Line 4 de-energized at 0416H (Planned Outage) [WEBSMS] | CLUZ
12/10/2023 3:05:43 AM | Luzon Grid-12/10/2023 03:05: Muntinlupa (Sucat)-Sun Valley 115kV Line de-energized at 0305H (Planned Outage). [WEBSMS] | CLUZ
12/9/2023 10:52:48 PM | Luzon Grid-12/09/2023 22:52: Kalayaan 1 Load rejection test at 180MW at 2249H, frequency reached at 59.66Hz (Planned Outage) [WEBSMS] | CLUZ
12/9/2023 10:27:18 PM | Luzon Grid-12/09/2023 22:27: Kalayaan 1 online from LRT at 2225H (Planned Outage) [WEBSMS] | CLUZ
12/9/2023 10:23:26 PM | Luzon Grid-12/09/2023 22:23: Kalayaan 1 Load rejection test at 90MW at 2222H (Planned Outage) [WEBSMS] | CLUZ
12/9/2023 10:23:03 PM | Visayas Grid-12/09/2023 22:23: Cebu - Mandaue 138 kV Line 1 energized without load at 2208H. (Planned Outage) [WEBSMS] | CVIS
12/9/2023 9:51:48 PM | Mindanao Grid-12/09/2023 21:54: WMPC DG05 cut-out at 1514H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/9/2023 8:45:05 PM | Luzon Grid-12/09/2023 20:45: GNPD-Alas-asin was unlooped at 2037H by openng the 230kV side PCB 8CB04(9XF03GPO) of GNPD Transformer No. 3. [WEBSMS] | CLUZ
12/9/2023 8:36:06 PM | Luzon Grid-12/09/2023 20:36: Lamao-Alas-asin 230kV line 2 commisioned at 2034H (Planned Outage). [WEBSMS] | CLUZ
12/9/2023 8:12:47 PM | Luzon Grid-12/09/2023 20:12: Lamao-Alas-asin 230kV line 2 restored at 2011H, on commissioning. [WEBSMS] | CLUZ
12/9/2023 7:28:23 PM | Mindanao Grid-12/09/2023 19:31: Agus 7 Unit 2 cut in at 1925H. (Unplanned Outage). [WEBSMS] | CMIN
12/9/2023 6:39:43 PM | Mindanao Grid-12/09/2023 18:42: SMCPC Unit 2 cut in at 1828Hz from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
12/9/2023 6:28:02 PM | Mindanao Grid-12/09/2023 18:31: Balo-i 230kV/138kV 300MVA Transformer no. 1 with restored at 1818H. No customers affected. (Unplanned Outage) [WEBSMS] | CMIN
12/9/2023 6:27:01 PM | Luzon Grid-12/09/2023 18:27: Nagsaag 230kV Bus 2 restored at 1826H (Planned Outage) [WEBSMS] | CLUZ
12/9/2023 5:50:56 PM | [NSO Update] Mindanao Grid-12/09/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3158MW, PK=2245MW, RR=82MW, NetOpMargin: EVE=831 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @40MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
12/9/2023 5:50:17 PM | [NSO Update] Visayas Grid-12/09/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2485MW, PK=2174MW, RR=97MW, NetOpMargin: EVE=214 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 115.5MW, Leyte A @ 270MW, PGPP1 @ 76MW [WEBSMS] | CVIS
12/9/2023 5:49:08 PM | [NSO Update] Luzon Grid-12/09/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13457MW, PK=10202MW, RR=398MW, NetOpMargin: EVE=2857 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 180MW, SLPGC 1 @ 135MW, Ilijan A 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
12/9/2023 5:39:35 PM | Mindanao Grid-12/09/2023 17:42: Balo-i Transformer no. 1 with 300MVA rating tripped at 1729H. No customers affected. (Unplanned Outage) [WEBSMS] | CMIN
12/9/2023 5:36:38 PM | Mindanao Grid-12/09/2023 17:39: Agus 7 Unit 2 with 25MW load auto tripped at 1729H. (Unplanned outage) [WEBSMS] | CMIN
12/9/2023 5:27:14 PM | Luzon Grid-12/09/2023 17:27: San Juan (Kalayaan) 230kV Bus 2 restored at 1726H (Planned Outage) [WEBSMS] | CLUZ
12/9/2023 4:47:59 PM | Visayas Grid-12/09/2023 16:48: Cebu SS 138 KV bus 2 energized at 1644. (Planned Outage) [WEBSMS] | CVIS
12/9/2023 4:46:31 PM | Luzon Grid-12/09/2023 16:46: Binan-Muntinlupa 230kV line 3 restored at 1638H (Planned Outage) [WEBSMS] | CLUZ
12/9/2023 4:25:30 PM | Mindanao Grid-12/09/2023 16:28: Baloi - Agus2 138kV L2 energized at 1618H. (Planned Outage) [WEBSMS] | CMIN
12/9/2023 4:21:34 PM | Mindanao Grid-12/09/2023 16:24: Baloi - Agus2 138kV L2 energized at 1619H. (Planned Outage) [WEBSMS] | CMIN
12/9/2023 3:48:37 PM | Luzon Grid-12/09/2023 15:48: Daraga 230kV Bus 2 restored at 1545H (Planned Outage). [WEBSMS] | CLUZ
12/9/2023 3:32:51 PM | Visayas Grid-12/09/2023 15:32: Compostela-Daanbantayan 230kV Line 1 energized at 1532H. (Planned Outage) [WEBSMS] | CVIS
12/9/2023 2:36:35 PM | Mindanao Grid-12/09/2023 14:39: Supreme Power Mati cut-in at 1406H. (Unplanned outage). [WEBSMS] | CMIN
12/9/2023 2:33:39 PM | Mindanao Grid-12/09/2023 14:36: Supreme Power Mati with Load of 5.5MW tripped at 1400H. (Unplanned outage). [WEBSMS] | CMIN
12/9/2023 2:16:03 PM | Mindanao Grid-12/09/2023 14:19: SMCPC Unit 2 with Gross generated load of 120MW auto-tripped at 1401H. (Unplanned outage). Note: No ALD activation. Lowest System Freq. recorded: 59.2887Hz. [WEBSMS] | CMIN
12/9/2023 2:13:34 PM | Mindanao Grid-12/09/2023 14:16: Baloi - Agus2 138kV L2 de-energized at 1407H. (Planned Outage) [WEBSMS] | CMIN
12/9/2023 2:12:51 PM | Mindanao Grid-12/09/2023 14:16: Baloi - Agus2 138kV L1 energized at 1355H. (Planned Outage) [WEBSMS] | CMIN
12/9/2023 1:28:32 PM | Visayas Grid-12/09/2023 13:28: Colon-Naga 138 KV Line 2 energized at 1327H. (Planned Outage) [WEBSMS] | CVIS
12/9/2023 1:09:04 PM | [NSO Update] Mindanao Grid-12/09/2023 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3322MW, PK=2157MW, RR=80MW, NetOpMargin: PM=2157, EVE=2210 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @40MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
12/9/2023 1:04:22 PM | [NSO Update] Visayas Grid-12/09/2023 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2677MW, PK=2086MW, RR=94MW, NetOpMargin: PM=497, EVE=273 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @284MW, PGPP1 @76MW [WEBSMS] | CVIS
12/9/2023 1:00:41 PM | [NSO Update] Luzon Grid-12/09/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14161MW, PK=10157MW, RR=405MW, NetOpMargin: PM=3599, EVE=3033 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @180MW, SLPGC 1 @135MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
12/9/2023 10:59:14 AM | [NSO Update] Mindanao Grid-12/09/2023 11:02: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1050H with power going to Visayas. [WEBSMS] | CMIN
12/9/2023 10:58:42 AM | Mindanao Grid-12/09/2023 11:01: MDP onlineat 1053H. (Unplanned outage). [WEBSMS] | CMIN
12/9/2023 10:58:33 AM | [NSO Update] Visayas Grid-12/09/2023 10:58: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1050H with power going to Visayas. [WEBSMS] | CVIS
12/9/2023 10:57:44 AM | Mindanao Grid-12/09/2023 11:00: MDP tripped at 1043H. (Unplanned outage). [WEBSMS] | CMIN
12/9/2023 10:34:05 AM | [NSO Update] Mindanao Grid-12/09/2023 10:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1026H from reverse power direction. [WEBSMS] | CMIN
12/9/2023 10:32:48 AM | [NSO Update] Visayas Grid-12/09/2023 10:32: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1026H from reverse power direction. [WEBSMS] | CVIS
12/9/2023 9:55:44 AM | Mindanao Grid-12/09/2023 09:58: WMPC DG 5 online as RPS at 0950H. For RPS System VOLTAGE REQUIREMENT. [WEBSMS] | CMIN
12/9/2023 9:55:23 AM | Mindanao Grid-12/09/2023 09:58: Baloi-Agus2 138kV Line 1 de-energized at 0952H. (Planned Outage) [WEBSMS] | CMIN
12/9/2023 9:26:33 AM | Luzon Grid-12/09/2023 09:26: San Juan(Kalayaan) 230kV Bus 2 was de-energized at 0924H. (Planned Outage) [WEBSMS] | CLUZ
12/9/2023 9:14:35 AM | Mindanao Grid-12/09/2023 09:17: MDP Online at 0900H. Follow RTD. [WEBSMS] | CMIN
12/9/2023 8:57:27 AM | Visayas Grid-12/09/2023 08:57: Cebu 138 KV bus 2 de-energized at 0713H. (Planned Outage) [WEBSMS] | CVIS
12/9/2023 8:45:08 AM | Luzon Grid-12/09/2023 08:45: Olongapo-SBMA 230kV line was de-energized at 0843H. (Planned Outage) [WEBSMS] | CLUZ
12/9/2023 8:17:41 AM | Luzon Grid-12/09/2023 08:17: Bolo-Sual 230kV line 2 was de-energized at 0815H. (Planned Outage) [WEBSMS] | CLUZ
12/9/2023 8:11:24 AM | Visayas Grid-12/09/2023 08:11: Dumanjug 138 KV bus 1 de-energized at 0810H. (Planned Outage) [WEBSMS] | CVIS
12/9/2023 8:09:12 AM | Mindanao Grid-12/09/2023 08:12: Polanco 138kV Bus 2 de-energized at 0802H. (Planned Outage) [WEBSMS] | CMIN
12/9/2023 7:50:10 AM | Mindanao Grid-12/09/2023 07:53: SEC 2 online at 0748H. (Uplanned outage). [WEBSMS] | CMIN
12/9/2023 7:34:23 AM | Luzon Grid-12/09/2023 07:34: Daraga 230kV Bus 2 was de-energized at 0733H. (Planned Outage) [WEBSMS] | CLUZ
12/9/2023 7:21:16 AM | Mindanao Grid-12/09/2023 07:24: Talomo 3 U2 with a load of 0.68MW tripped at 0519H. (Unplanned outage). [WEBSMS] | CMIN
12/9/2023 7:17:19 AM | Luzon Grid-12/09/2023 07:17: Nagsaag 230kV Bus 2 was de-energized at 0713H. (Planned Outage) [WEBSMS] | CLUZ
12/9/2023 6:42:01 AM | Luzon Grid-12/09/2023 06:42: Binan-Muntinlupa 230kV line 3 was de-energized at 0639H. (Planned Outage) [WEBSMS] | CLUZ
12/9/2023 6:38:56 AM | Visayas Grid-12/09/2023 06:39: Colon-Naga 138 KV Line 2 de-energized at 0636H. (Planned Outage) [WEBSMS] | CVIS
12/9/2023 6:37:44 AM | [NSO Update] Mindanao Grid-12/09/2023 06:40: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0618H with power going to Mindanao. [WEBSMS] | CMIN
12/9/2023 6:37:09 AM | [NSO Update] Visayas Grid-12/09/2023 06:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0618H with power going to Mindanao. [WEBSMS] | CVIS
12/9/2023 6:34:41 AM | [NSO Update] Mindanao Grid-12/09/2023 06:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0607H from forward power direction. [WEBSMS] | CMIN
12/9/2023 6:32:57 AM | [NSO Update] Visayas Grid-12/09/2023 06:33: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0607H from forward power direction. [WEBSMS] | CVIS
12/9/2023 5:45:14 AM | [NSO Update] Mindanao Grid-12/09/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3460MW, PK=2087MW, RR=77MW, NetOpMargin: AM=1296, PM=1267, EVE=1141 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @40MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @40MW, AG6 @155MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
12/9/2023 5:42:20 AM | [NSO Update] Visayas Grid-12/09/2023 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2842MW, PK=1989MW, RR=93MW, NetOpMargin: AM=760, PM=732, EVE=436 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @309MW, PGPP1 @76MW [WEBSMS] | CVIS
12/9/2023 5:37:55 AM | [NSO Update] Luzon Grid-12/09/2023 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14347MW, PK=9839MW, RR=396MW, NetOpMargin: AM=4112, PM=3374, EVE=2923 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @180MW, SLPGC 1 @140MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
12/9/2023 5:15:06 AM | Visayas Grid-12/09/2023 05:15: Compostela-Daanbantayan 230kV Line 1 de-energized at 0510H. (Planned Outage) [WEBSMS] | CVIS
12/9/2023 5:02:18 AM | Luzon Grid-12/09/2023 05:02: San Gabriel online at 0501H. (Unplanned Outage) [WEBSMS] | CLUZ
12/9/2023 4:06:17 AM | [NSO Update] Mindanao Grid-12/09/2023 04:09: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CMIN
12/9/2023 4:06:08 AM | [NSO Update] Visayas Grid-12/09/2023 04:06: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CVIS
12/9/2023 4:05:59 AM | [NSO Update] Luzon Grid-12/09/2023 04:06: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
12/9/2023 2:14:38 AM | Mindanao Grid-12/09/2023 02:17: Euro Hydro (NBT) with 1.5MW load tripped at 0138H affected by the forced outage of Nabunturan-Monkayo 69kV Line. Euro Hydro (NBT) on line back at 0206H. (Unplanned Outage) [WEBSMS] | CMIN
12/9/2023 12:42:40 AM | Luzon Grid-12/09/2023 00:42: San Gabriel offline at 0039H (Planned Outage) [WEBSMS] | CLUZ
12/8/2023 9:30:27 PM | Mindanao Grid-12/08/2023 21:33: PSF U2 Shutdown at 2112H. Follow RTD. [WEBSMS] | CMIN
12/8/2023 9:27:17 PM | Luzon Grid-12/08/2023 21:27: Kalayaan 1 with 92MW tripped at 2124H. Lowest system frequency was 59.640Hz. (On-going testing/Online tuning). [WEBSMS] | CLUZ
12/8/2023 9:12:57 PM | Mindanao Grid-12/08/2023 21:16: PSF U2 Online at 2101H. Follow RTD. [WEBSMS] | CMIN
12/8/2023 9:07:29 PM | Mindanao Grid-12/08/2023 21:10: MDP Shutdown at 2105H. Follow RTD. [WEBSMS] | CMIN
12/8/2023 8:45:07 PM | Mindanao Grid-12/08/2023 20:48: SEC 2 with a load of 73.2MW tripped at 2035H. (Unplanned Outage). Lowest Frequency was 59.212Hz. No ALD. [WEBSMS] | CMIN
12/8/2023 8:34:34 PM | Mindanao Grid-12/08/2023 20:37: PSF U2 Shutdown at 1757H. Follow RTD. [WEBSMS] | CMIN
12/8/2023 7:02:59 PM | Mindanao Grid-12/08/2023 19:06: AG5 U2 Online at 1900H. (Planned Outage). PMS(GOMP). [WEBSMS] | CMIN
12/8/2023 6:43:09 PM | Luzon Grid-12/08/2023 18:43: Taytay 300MVA T02 restored at 1842H. (Planned Outage) [WEBSMS] | CLUZ
12/8/2023 5:59:41 PM | [NSO Update] Mindanao Grid-12/08/2023 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3260MW, PK=2296MW, RR=86MW, NetOpMargin: EVE=878 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
12/8/2023 5:54:55 PM | [NSO Update] Visayas Grid-12/08/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2495MW, PK=2175MW, RR=97MW, NetOpMargin: EVE=223 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @65MW, TGPP @115.5MW, LEYTE A @300MW, PGPP1 @76MW [WEBSMS] | CVIS
12/8/2023 5:54:03 PM | [NSO Update] Luzon Grid-12/08/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13308MW, PK=10427MW, RR=404MW, NetOpMargin: EVE=2477 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
12/8/2023 5:52:56 PM | Luzon Grid-12/08/2023 17:52: Kalayaan 1 with 93MW tripped at 1748H. Lowest system frequency was 59.815Hz. (On-going testing/Online tuning). [WEBSMS] | CLUZ
12/8/2023 5:37:50 PM | Mindanao Grid-12/08/2023 17:41: PSF U2 Online at 1736H. Follow RTD. [WEBSMS] | CMIN
12/8/2023 5:37:48 PM | Luzon Grid-12/08/2023 17:37: Bolo-Balingueo 230kV line 1 restored at 1736H. (Planned Outage) [WEBSMS] | CLUZ
12/8/2023 4:28:27 PM | Luzon Grid-12/08/2023 16:28: Daraga 230kV Bus 1 was restored at 1622H (Planned Outage) [WEBSMS] | CLUZ
12/8/2023 3:02:48 PM | Mindanao Grid-12/08/2023 15:05: LPE Online at 1500H. Follow RTD. [WEBSMS] | CMIN
12/8/2023 2:41:45 PM | Mindanao Grid-12/08/2023 14:44: MDP Online at 1425H. (Unplanned Outage). [WEBSMS] | CMIN
12/8/2023 2:39:28 PM | Mindanao Grid-12/08/2023 14:42: MDP with a load of 6MW Tripped at 1423H. (Unplanned Outage). [WEBSMS] | CMIN
12/8/2023 1:55:13 PM | [NSO Update] Mindanao Grid-12/08/2023 13:58: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1354H with power going to Visayas. [WEBSMS] | CMIN
12/8/2023 1:55:04 PM | [NSO Update] Visayas Grid-12/08/2023 13:55: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1354H with power going to Visayas. [WEBSMS] | CVIS
12/8/2023 1:47:42 PM | [NSO Update] Visayas Grid-12/08/2023 13:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1344H from reverse power direction. [WEBSMS] | CVIS
12/8/2023 1:47:20 PM | [NSO Update] Mindanao Grid-12/08/2023 13:50: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1344H from reverse power direction. [WEBSMS] | CMIN
12/8/2023 1:36:51 PM | Luzon Grid-12/08/2023 13:36: For info: EERI 540MVA T01 was energized at 1335H. [WEBSMS] | CLUZ
12/8/2023 1:16:36 PM | Luzon Grid-12/08/2023 13:16: For info: Ilijan-EERI 500kV line 2 was looped at 1305H in EERI side, at the same time, EERI 500kV Bus 2 was energized. Afterwards, EERI 500kV Bus 1 was energized at 1308H. [WEBSMS] | CLUZ
12/8/2023 12:51:28 PM | [NSO Update] Luzon Grid-12/08/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13993MW, PK=10097MW, RR=405MW, NetOpMargin: PM=3491, EVE=2583 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
12/8/2023 12:43:17 PM | [NSO Update] Visayas Grid-12/08/2023 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2613MW, PK=2046MW, RR=94MW, NetOpMargin: PM=473, EVE=321 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @115.5MW, LEYTE A @284MW, PGPP1 @76MW [WEBSMS] | CVIS
12/8/2023 12:41:17 PM | [NSO Update] Mindanao Grid-12/08/2023 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3282MW, PK=2112MW, RR=84MW, NetOpMargin: PM=1085, EVE=1051 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
12/8/2023 11:57:51 AM | [NSO Update] Visayas Grid-12/08/2023 11:57: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1156H with power going to Mindanao. [WEBSMS] | CVIS
12/8/2023 11:57:28 AM | [NSO Update] Mindanao Grid-12/08/2023 12:00: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1156H with power going to Mindanao. [WEBSMS] | CMIN
12/8/2023 11:28:43 AM | [NSO Update] Visayas Grid-12/08/2023 11:28: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1126H from forward power direction. [WEBSMS] | CVIS
12/8/2023 11:27:28 AM | [NSO Update] Mindanao Grid-12/08/2023 11:30: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1126H from forward power direction. [WEBSMS] | CMIN
12/8/2023 11:18:54 AM | Mindanao Grid-12/08/2023 11:22: Agus 5 HEP Unit 2 and Baloi - Agus5 138kV line energized at 1117H. (Planned Outage) [WEBSMS] | CMIN
12/8/2023 10:23:30 AM | Mindanao Grid-12/08/2023 10:26: Agus 5 HEP Unit 2 and Baloi - Agus5 138kV line de-energized at 1020H. (Planned Outage) [WEBSMS] | CMIN
12/8/2023 9:10:04 AM | Mindanao Grid-12/08/2023 09:13: MDP Online at 0900H. Follow RTD. [WEBSMS] | CMIN
12/8/2023 8:41:22 AM | Luzon Grid-12/08/2023 08:41: Mauban PCB 8-07CB04MBA was closed at 0838H after the completion of SF6 gas refilling. (Unplanned Outage) [WEBSMS] | CLUZ
12/8/2023 8:35:01 AM | Luzon Grid-12/08/2023 08:35: Lamao-Alas-asin 230kV line 2 was de-energized at 0832H. (Planned Outage) [WEBSMS] | CLUZ
12/8/2023 8:27:31 AM | Luzon Grid-12/08/2023 08:27: GNPD-Alas-asin was looped at 0818H by closing the 230kV side PCB 8CB04(9XF03GPO) of GNPD Transformer No. 3. [WEBSMS] | CLUZ
12/8/2023 7:59:27 AM | Luzon Grid-12/08/2023 07:59: Taytay 300MVA T02 was de-energized at 0758H. (Planned Outage) [WEBSMS] | CLUZ
12/8/2023 7:40:05 AM | Luzon Grid-12/08/2023 07:40: Daraga 230kV Bus 1 was de-energized at 0737H. (Planned Outage) [WEBSMS] | CLUZ
12/8/2023 7:23:46 AM | Luzon Grid-12/08/2023 07:23: Mauban PCB 8-07CB04MBA was opened at 0717H to facilitate SF6 gas refilling. (Unplanned Outage) [WEBSMS] | CLUZ
12/8/2023 6:21:05 AM | Luzon Grid-12/08/2023 06:21: Bolo-Balingueo 230kV line 1 was de-energized at 0618H. (Planned Outage) [WEBSMS] | CLUZ
12/8/2023 5:48:29 AM | [NSO Update] Mindanao Grid-12/08/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3444MW, PK=2078MW, RR=81MW, NetOpMargin: AM=1286, PM=1235, EVE=1013 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @43MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
12/8/2023 5:47:36 AM | [NSO Update] Visayas Grid-12/08/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2731MW, PK=1884MW, RR=93MW, NetOpMargin: AM=753, PM=733, EVE=389 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 115.5MW, Leyte A @ 284MW, PGPP1 @ 76MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
12/8/2023 5:46:15 AM | [NSO Update] Luzon Grid-12/08/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14121MW, PK=10075MW, RR=399MW, NetOpMargin: AM=3647, PM=3220, EVE=2340 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
12/8/2023 4:08:51 AM | [NSO Update] Mindanao Grid-12/08/2023 04:12: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CMIN
12/8/2023 4:08:33 AM | [NSO Update] Luzon Grid-12/08/2023 04:08: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
12/8/2023 4:08:15 AM | [NSO Update] Visayas Grid-12/08/2023 04:08: Weather Update: Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CVIS
12/8/2023 12:26:42 AM | Luzon Grid-12/08/2023 00:26: San Gabriel online at 0024H (Planned Outage) [WEBSMS] | CLUZ
12/7/2023 10:32:19 PM | Visayas Grid-12/07/2023 22:32: TPC1A cut in at 2230H. (Planned Outage) [WEBSMS] | CVIS
12/7/2023 10:03:52 PM | Mindanao Grid-12/07/2023 22:07: WMPC DG10 cut-in at 2158H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/7/2023 9:36:21 PM | Mindanao Grid-12/07/2023 21:39: WMPC DG04 cut-out at 2114H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/7/2023 9:10:10 PM | Mindanao Grid-12/07/2023 21:13: SPC Mati Diesel cut out at 2105H. MO dispatched. [WEBSMS] | CMIN
12/7/2023 6:28:50 PM | Luzon Grid-12/07/2023 18:28: MERALCO New Mauban SS 50MVA T01 restored at 1826H (Planned Outage) [WEBSMS] | CLUZ
12/7/2023 5:53:21 PM | [NSO Update] Mindanao Grid-12/07/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3300MW, PK=2307MW, RR=90MW, NetOpMargin: EVE=903 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @40MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/7/2023 5:52:36 PM | [NSO Update] Visayas Grid-12/07/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2457MW, PK=2182MW, RR=97MW, NetOpMargin: EVE=178 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 115MW, Leyte A @ 280MW, PGPP1 @ 75MW [WEBSMS] | CVIS
12/7/2023 5:51:15 PM | [NSO Update] Luzon Grid-12/07/2023 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13198MW, PK=10734MW, RR=429MW, NetOpMargin: EVE=2035 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
12/7/2023 5:13:34 PM | Luzon Grid-12/07/2023 17:13: San Gabriel shutdown at 1710H, LNG commissioning. [WEBSMS] | CLUZ
12/7/2023 4:52:27 PM | Luzon Grid-12/07/2023 16:52: Tiwi C 50MVA T01 energized (230kV side) at 1649H, on commissioning. [WEBSMS] | CLUZ
12/7/2023 4:20:05 PM | Mindanao Grid-12/07/2023 16:23: WMPC DG06 cut-out at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/7/2023 4:05:48 PM | Luzon Grid-12/07/2023 16:05: Labrador 100MVA T01 energized (230kV side) at 1601H (Planned Outage) [WEBSMS] | CLUZ
12/7/2023 3:55:42 PM | Mindanao Grid-12/07/2023 15:58: WMPC DG10 cut-in at 1552H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/7/2023 3:18:44 PM | Visayas Grid-12/07/2023 15:18: Carcon - Sangi 34.5 kV Line 2 energized at 1516H. (Planned Outage) [WEBSMS] | CVIS
12/7/2023 3:02:53 PM | Mindanao Grid-12/07/2023 15:06: NACSUR cut-out at 1500H. MO dispatched (RTD). [WEBSMS] | CMIN
12/7/2023 3:02:24 PM | Mindanao Grid-12/07/2023 15:05: NACSUR cut-in at 1400H. MO dispatched (RTD). [WEBSMS] | CMIN
12/7/2023 2:43:03 PM | Mindanao Grid-12/07/2023 14:46: Agus 2 SY 138KV Bus 1 restored at 1437H. Planned Outage. [WEBSMS] | CMIN
12/7/2023 1:43:01 PM | Mindanao Grid-12/07/2023 13:46: MDP Online at 1335H. Follow RTD. [WEBSMS] | CMIN
12/7/2023 1:03:47 PM | Mindanao Grid-12/07/2023 13:06: MDP SHUTDOWN at 1153H. DUE TO FEEDER BOOSTER HEATER BREAKER BURNT. [WEBSMS] | CMIN
12/7/2023 12:52:17 PM | [NSO Update] Mindanao Grid-12/07/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3330MW, PK=2205MW, RR=92MW, NetOpMargin: PM=1033, EVE=1042 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @40MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/7/2023 12:49:00 PM | [NSO Update] Visayas Grid-12/07/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2662MW, PK=2194MW, RR=94MW, NetOpMargin: PM=374, EVE=243 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115MW, LEYTE A @280MW, PGPP1 @75MW [WEBSMS] | CVIS
12/7/2023 12:43:45 PM | [NSO Update] Luzon Grid-12/07/2023 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13703MW, PK=11129MW, RR=445MW, NetOpMargin: PM=2129, EVE=1897 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, GMEC 2 @240MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
12/7/2023 10:57:08 AM | Mindanao Grid-12/07/2023 11:00: WMPC DG6 Online as RPS. at 1053H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/7/2023 9:02:01 AM | Mindanao Grid-12/07/2023 09:05: WMPC DG4 Online as RPS at 0856H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/7/2023 8:45:39 AM | Visayas Grid-12/07/2023 08:45: Carcon - Sangi 34.5KV Line 2 de-energized at 0834H. (Planned Outage) [WEBSMS] | CVIS
12/7/2023 8:40:46 AM | Mindanao Grid-12/07/2023 08:43: Agus 2 SY 138KV Bus 1 deenergized at 0836H. Planned Outage. [WEBSMS] | CMIN
12/7/2023 7:23:56 AM | Luzon Grid-12/07/2023 07:23: MERALCO New Mauban SS 50MVA T01 de-energized at 0722H. (Planned Outage) [WEBSMS] | CLUZ
12/7/2023 5:45:11 AM | [NSO Update] Mindanao Grid-12/07/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3325MW, PK=2125MW, RR=88MW, NetOpMargin: AM=1112, PM=1000, EVE=948 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @40MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
12/7/2023 5:40:30 AM | [NSO Update] Visayas Grid-12/07/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2667MW, PK=2137MW, RR=93MW, NetOpMargin: AM=437, PM=401, EVE=255 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @284MW, PGPP1 @76MW [WEBSMS] | CVIS
12/7/2023 5:38:34 AM | [NSO Update] Luzon Grid-12/07/2023 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13873MW, PK=11177MW, RR=439MW, NetOpMargin: AM=2257, PM=1969, EVE=1925 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
12/7/2023 5:11:10 AM | [NSO Update] Mindanao Grid-12/07/2023 05:14: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
12/7/2023 5:10:55 AM | [NSO Update] Visayas Grid-12/07/2023 05:10: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
12/7/2023 5:10:39 AM | [NSO Update] Luzon Grid-12/07/2023 05:10: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
12/6/2023 9:11:45 PM | Mindanao Grid-12/06/2023 21:15: SPC Mati Diesel cut out at 2105H. MO dispatched. [WEBSMS] | CMIN
12/6/2023 8:16:58 PM | Mindanao Grid-12/06/2023 20:20: WMPC DG05 cut-out at 2002. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/6/2023 7:13:09 PM | Mindanao Grid-12/06/2023 19:16: WMPC DG01 cut-out at 1859H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/6/2023 5:57:38 PM | [NSO Update] Luzon Grid-12/06/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12802MW, PK=10916MW, RR=404MW, NetOpMargin: EVE=1482 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @200MW, CLC2 @175MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
12/6/2023 5:47:04 PM | [NSO Update] Mindanao Grid-12/06/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3305MW, PK=2217MW, RR=89MW, NetOpMargin: EVE=999 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @40MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/6/2023 5:45:30 PM | [NSO Update] Visayas Grid-12/06/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2568MW, PK=2203MW, RR=97MW, NetOpMargin: EVE=268 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @280MW, PGPP1 @76MW [WEBSMS] | CVIS
12/6/2023 5:28:02 PM | Luzon Grid-12/06/2023 17:28: Gumaca-Labo 230kV Line 2 restored at 1727H (Planned Outage) [WEBSMS] | CLUZ
12/6/2023 5:12:20 PM | Luzon Grid-12/06/2023 17:12: SLTEC 2 online at 1659H (Unplanned Outage) [WEBSMS] | CLUZ
12/6/2023 4:56:52 PM | Mindanao Grid-12/06/2023 17:00: Update: WMPC DG10 with 4.26MW tripped at 1640H as RPS - System Voltage Requirement. Indication: Turbo charger shock pulse alarm turbine side. [WEBSMS] | CMIN
12/6/2023 4:44:22 PM | Mindanao Grid-12/06/2023 16:47: WMPC DG10 with 4.26MW tripped at 1640H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/6/2023 3:53:12 PM | Mindanao Grid-12/06/2023 15:56: WMPC DG06 cut-in at 1001H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/6/2023 3:32:28 PM | Visayas Grid-12/06/2023 15:32: Carcon-Sangi 34.5KV line 1 energized at 1527H. (Planned Outage) [WEBSMS] | CVIS
12/6/2023 3:17:50 PM | Mindanao Grid-12/06/2023 15:21: WMPC DG06 cut-out at 1516H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/6/2023 2:54:05 PM | Mindanao Grid-12/06/2023 14:57: Nagamin SS Static VAR Compensator (SVC) with 3rd & 5th Harmonics Filters, and Thyristor-controlled Reactor (TCR), successfully restored at 1419H. From emergency shutdown due to Water Cooling System Problem (Unplanned Outage). [WEBSMS] | CMIN
12/6/2023 2:22:36 PM | Visayas Grid-12/06/2023 14:22: Lugo-CEBECO 2 13.8 KV line 2 energized at 1411H. Planned Outage [WEBSMS] | CVIS
12/6/2023 2:10:21 PM | Mindanao Grid-12/06/2023 14:13: WMPC DG10 online at 1408H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
12/6/2023 1:29:27 PM | Mindanao Grid-12/06/2023 13:32: WWPC DG10 cut in at 1239H and cut out at 1325H. MO dispatched. RTD. [WEBSMS] | CMIN
12/6/2023 12:42:55 PM | [NSO Update] Mindanao Grid-12/06/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3328MW, PK=2241MW, RR=94MW, NetOpMargin: PM=993, EVE=991 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @40MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/6/2023 12:42:07 PM | [NSO Update] Visayas Grid-12/06/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2648MW, PK=2217MW, RR=94MW, NetOpMargin: PM=336, EVE=239 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 115.5MW, Leyte A @ 280MW, PGPP1 @ 73MW [WEBSMS] | CVIS
12/6/2023 12:40:50 PM | [NSO Update] Luzon Grid-12/06/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13435MW, PK=11382MW, RR=434MW, NetOpMargin: PM=1619, EVE=1237 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 200MW, Calaca 2 @ 175MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
12/6/2023 9:57:33 AM | Mindanao Grid-12/06/2023 10:00: WMPC DG04 shutdown at 0948H due to cylinder exhaust gas leak. [WEBSMS] | CMIN
12/6/2023 9:55:35 AM | Mindanao Grid-12/06/2023 09:58: WMPC DG05 online at 0933H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
12/6/2023 9:11:00 AM | [NSO Update] Mindanao Grid-12/06/2023 09:14: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0910H with power going to Visayas. (Unplanned Outage) [WEBSMS] | CMIN
12/6/2023 9:10:43 AM | [NSO Update] Visayas Grid-12/06/2023 09:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0910H with power going to Visayas. (Unplanned Outage) [WEBSMS] | CVIS
12/6/2023 9:01:28 AM | Mindanao Grid-12/06/2023 09:04: SUPREME POWER Mati (MDP) cut-in at 0859H. MO dispatch (RTD). [WEBSMS] | CMIN
12/6/2023 8:34:41 AM | Mindanao Grid-12/06/2023 08:38: WMPC DG01 online at 0828H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
12/6/2023 8:34:19 AM | Mindanao Grid-12/06/2023 08:37: WMPC DG04 online at 0805H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
12/6/2023 6:42:26 AM | Visayas Grid-12/06/2023 06:42: Carcon-Sangi 34.5KV line 1 de-energized at 0636H. (Planned Outage) [WEBSMS] | CVIS
12/6/2023 6:14:11 AM | Luzon Grid-12/06/2023 06:14: Gumaca-Labo 230kV Line 2 de-energized at 0613H. (Planned Outage) [WEBSMS] | CLUZ
12/6/2023 6:12:17 AM | [NSO Update] Mindanao Grid-12/06/2023 06:15: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3334MW, PK=2208MW, RR=90MW, NetOpMargin: AM=1036, PM=888, EVE=951 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @40MW, AG1 @35MW, AG2 @100MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/6/2023 6:05:53 AM | [NSO Update] Visayas Grid-12/06/2023 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2557MW, PK=2284MW, RR=89MW, NetOpMargin: AM=184, PM=185, EVE=267 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @115.5MW, LEYTE A @284MW, PGPP1 @76MW [WEBSMS] | CVIS
12/6/2023 6:01:44 AM | [NSO Update] Luzon Grid-12/06/2023 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13693MW, PK=10772MW, RR=404MW, NetOpMargin: AM=2518, PM=1864, EVE=1581 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 200MW, Calaca 2 @ 175MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
12/6/2023 4:36:03 AM | [NSO Update] Luzon Grid-12/06/2023 04:36: Weather Update: Easterlies affecting the eastern section of the country. Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
12/6/2023 4:33:57 AM | [NSO Update] Luzon Grid-12/06/2023 04:34: Weather Update: Easterlies affecting the eastern section of the country. Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
12/6/2023 4:32:43 AM | [NSO Update] Visayas Grid-12/06/2023 04:32: Weather Update: Easterlies affecting the eastern section of the country. Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CVIS
12/6/2023 4:31:54 AM | [NSO Update] Mindanao Grid-12/06/2023 04:35: Weather Update: Easterlies affecting the eastern section of the country. Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CMIN
12/6/2023 12:15:45 AM | Mindanao Grid-12/06/2023 00:19: Nagamin SVC deenergized at 0001H. Planned Outage. [WEBSMS] | CMIN
12/5/2023 10:41:18 PM | Luzon Grid-12/05/2023 22:41: San Jose-Angat 115kV Line 1 restored at 2240H (Planned Outage) [WEBSMS] | CLUZ
12/5/2023 9:48:07 PM | Mindanao Grid-12/05/2023 21:51: Tagoloan - Manolo line 1 auto tripped and autoreclosed at 2125H. Unplanned Outage. [WEBSMS] | CMIN
12/5/2023 9:19:32 PM | Mindanao Grid-12/05/2023 21:22: WMPC DG05 cut-out at 2113H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/5/2023 7:40:18 PM | [NSO Update] Mindanao Grid-12/05/2023 19:43: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1931H from forward power direction (Unplanned Outage) . [WEBSMS] | CMIN
12/5/2023 7:38:04 PM | [NSO Update] Visayas Grid-12/05/2023 19:38: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1931H from forward power direction (Unplanned Outage) . [WEBSMS] | CVIS
12/5/2023 6:27:00 PM | [NSO Update] Mindanao Grid-12/05/2023 18:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3263MW, PK=2297MW, RR=88MW, NetOpMargin: EVE=878 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @30MW, AG1 @35MW, AG2 @70MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/5/2023 6:17:10 PM | [NSO Update] Luzon Grid-12/05/2023 18:17: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12807MW, PK=10710MW, RR=431MW, NetOpMargin: EVE=1666 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 200MW, Calaca 2 @ 175MW, PBL3 @400MW, QPPL @ 420MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
12/5/2023 6:09:07 PM | [NSO Update] Visayas Grid-12/05/2023 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2737MW, PK=2315MW, RR=97MW, NetOpMargin: EVE=325 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @115.5MW, LEYTE A @284MW, PGPP1 @69MW [WEBSMS] | CVIS
12/5/2023 5:45:35 PM | [NSO Update] Mindanao Grid-12/05/2023 17:48: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1738H with power going to Visayas. (Planned Outage) [WEBSMS] | CMIN
12/5/2023 5:44:16 PM | [NSO Update] Visayas Grid-12/05/2023 17:44: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1738H with power going to Visayas. (Planned Outage) [WEBSMS] | CVIS
12/5/2023 5:35:22 PM | Luzon Grid-12/05/2023 17:35: Malaya-Ingrid 230kV Line 2 restored at 1730H (Planned Outage) [WEBSMS] | CLUZ
12/5/2023 5:06:01 PM | [NSO Update] Mindanao Grid-12/05/2023 17:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1702H from forward power direction. (Planned Outage) [WEBSMS] | CMIN
12/5/2023 5:04:40 PM | [NSO Update] Visayas Grid-12/05/2023 17:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1702H from forward power direction. (Planned Outage) [WEBSMS] | CVIS
12/5/2023 4:56:35 PM | Luzon Grid-12/05/2023 16:55: For info: LRCC resumed normal dispatch function at 1653H. [WEBSMS] | CLUZ
12/5/2023 4:49:16 PM | Luzon Grid-12/05/2023 16:49: For info: LRCC was evacuated at 1625H due to an earthquake. The dispatch function was performed at MDC building. ACCs were informed and advised to monitor the transmission lines and equipment under their AOR. No tripping of generating plant, transmission lines, and feeders. However, System Frequency rose to 60.480Hz. [WEBSMS] | CLUZ
12/5/2023 1:48:54 PM | Luzon Grid-12/05/2023 13:49: Quezon-Mexico 230kV Line restored at 1348H (Unplanned Outage) [WEBSMS] | CLUZ
12/5/2023 1:36:58 PM | Luzon Grid-12/05/2023 13:37: Quezon-Mexico 230kV Line tripped at 1333H (Unplanned Outage) [WEBSMS] | CLUZ
12/5/2023 12:51:34 PM | [NSO Update] Mindanao Grid-12/05/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3296MW, PK=2336MW, RR=88MW, NetOpMargin: PM=872, EVE=875 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @30MW, AG1 @35MW, AG2 @70MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/5/2023 12:50:46 PM | [NSO Update] Visayas Grid-12/05/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2582MW, PK=2294MW, RR=94MW, NetOpMargin: PM=194, EVE=229 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 115.5MW, Leyte A @ 284MW [WEBSMS] | CVIS
12/5/2023 12:49:40 PM | [NSO Update] Luzon Grid-12/05/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13595MW, PK=11095MW, RR=442MW, NetOpMargin: PM=2058, EVE=1687 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 190MW, Calaca 2 @ 175MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
12/5/2023 12:13:55 PM | Mindanao Grid-12/05/2023 12:17: Agus 6 SY 69KV Bus 1 restored at 1208H. Planned Outage. [WEBSMS] | CMIN
12/5/2023 11:10:33 AM | Luzon Grid-12/05/2023 11:10: EERI 500kV Bus 1 & 2 2 de-energized at 1108H, on commissioning. [WEBSMS] | CLUZ
12/5/2023 10:35:15 AM | Mindanao Grid-12/05/2023 10:38: Supreme Power Mati tripped with 4.0MW load at 0939H. Indication: Lube Oil High Temp. (Unplanned outage). [WEBSMS] | CMIN
12/5/2023 9:06:10 AM | Luzon Grid-12/05/2023 09:06: San Jose-Angat 115kV Line 1 de-energized at 0903H (Planned Outage) [WEBSMS] | CLUZ
12/5/2023 8:54:34 AM | Mindanao Grid-12/05/2023 08:57: WMPC DG05 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
12/5/2023 8:36:18 AM | Mindanao Grid-12/05/2023 08:39: Agus 6 SY 69KV Bus 1 deenergized at 0827H. Planned Outage. [WEBSMS] | CMIN
12/5/2023 7:16:01 AM | Mindanao Grid-12/05/2023 07:19: Kidapawan-Mt Apo 3 69KV L1 de-energized at 0207H. Maintenance outage requested by Mt Apo management. [WEBSMS] | CMIN
12/5/2023 7:12:32 AM | Mindanao Grid-12/05/2023 07:15: Kidapawan-Mt Apo 1 138KV L1 de-energized at 0200H. Maintenance outage requested by Mt Apo management. [WEBSMS] | CMIN
12/5/2023 5:51:50 AM | [NSO Update] Mindanao Grid-12/05/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3373MW, PK=2249MW, RR=84MW, NetOpMargin: AM=1040, PM=941, EVE=882 Highest Unit O/L: GNPK 1&2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA2 @30MW, AG1 @35MW, AG2 @70MW, AG4 @120MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/5/2023 5:46:14 AM | [NSO Update] Visayas Grid-12/05/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2640MW, PK=2195MW, RR=93MW, NetOpMargin: AM=352, PM=260, EVE=250 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @115.5MW, LEYTE A @284MW, PGPP1 @69MW [WEBSMS] | CVIS
12/5/2023 5:44:12 AM | [NSO Update] Luzon Grid-12/05/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13656MW, PK=10930MW, RR=435MW, NetOpMargin: AM=2291, PM=2085, EVE=1651 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 1 @190MW, CALACA 2 @175MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
12/5/2023 5:18:30 AM | Luzon Grid-12/05/2023 05:18: San Gabriel online at 0518H (Unplanned Outage) [WEBSMS] | CLUZ
12/5/2023 4:19:55 AM | Mindanao Grid-12/05/2023 04:23: Tudaya 2 Unit 2 cut-in at 0408H. (Unplanned Outage) [WEBSMS] | CMIN
12/5/2023 4:12:31 AM | [NSO Update] Mindanao Grid-12/05/2023 04:15: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CMIN
12/5/2023 4:12:06 AM | [NSO Update] Visayas Grid-12/05/2023 04:12: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CVIS
12/5/2023 4:11:51 AM | [NSO Update] Luzon Grid-12/05/2023 04:12: Weather Advisory: Easterlies affecting the country. [WEBSMS] | CLUZ
12/5/2023 4:08:49 AM | Mindanao Grid-12/05/2023 04:12: Tudaya 2 Unit 2 tripped with 0.9MW load at 0335H. Indication: flow lubrication oil NDE bearing radial too low. (Unplanned Outage) [WEBSMS] | CMIN
12/5/2023 2:01:31 AM | Luzon Grid-12/05/2023 02:01: San Gabriel shutdown at 0154H (Unplanned Outage) [WEBSMS] | CLUZ
12/5/2023 12:26:43 AM | Mindanao Grid-12/05/2023 00:30: Mt. Apo 3 shutdown at 0005H. (Planned Outage) [WEBSMS] | CMIN
12/5/2023 12:26:10 AM | Mindanao Grid-12/05/2023 00:29: Mt. Apo 1 shutdown at 0002H. (Planned Outage) [WEBSMS] | CMIN
12/5/2023 12:24:58 AM | Mindanao Grid-12/05/2023 00:28: LIBERTAD POWER (LPE) tripped with 6MW load at 2214H. Cause: Affected by line fault of ZAMSURECO feeder. (Unplanned Outage). LIBERTAD POWER also scheduled for shutdown at 2400H for maintenance. [WEBSMS] | CMIN
12/4/2023 9:24:54 PM | Mindanao Grid-12/04/2023 21:28: WMPC DG05 cut-out at 2114H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/4/2023 9:11:28 PM | Mindanao Grid-12/04/2023 21:14: SUPREME POWER Mati (MDP) cut-out at 2105H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/4/2023 6:27:16 PM | Visayas Grid-12/04/2023 18:27: 2nd lift-Sangi 34.5 KV line energized at 1747H. Planned Outage [WEBSMS] | CVIS
12/4/2023 6:17:31 PM | Mindanao Grid-12/04/2023 18:20: WMPC (DG01) cut-in at 1051H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/4/2023 5:55:18 PM | [NSO Update] Mindanao Grid-12/04/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3343MW, PK=2253MW, RR=86MW, NetOpMargin: EVE=1004 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @90MW, AG4 @125MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/4/2023 5:50:04 PM | [NSO Update] Visayas Grid-12/04/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2600MW, PK=2257MW, RR=97MW, NetOpMargin: EVE=246 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @278MW, PGPP1 @76MW [WEBSMS] | CVIS
12/4/2023 5:45:41 PM | [NSO Update] Luzon Grid-12/04/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12887MW, PK=10642MW, RR=404MW, NetOpMargin: EVE=1841 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
12/4/2023 4:21:35 PM | Mindanao Grid-12/04/2023 16:24: WMPC DG01 cut-out at 1614H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/4/2023 3:58:28 PM | Mindanao Grid-12/04/2023 16:01: Tudaya 2 Unit 1 cut-in at 0536H. (Unplanned Outage) [WEBSMS] | CMIN
12/4/2023 1:52:30 PM | Mindanao Grid-12/04/2023 13:55: Toril-Matanao 230KV L2 tripped at 1321H. Ind: At Toril SS= CN, 13.5KM; At Matanao SS= CN, 34.3KM. Re-energized at 1327H & looped at Matanao SS at 1328H. Unplanned Outage. [WEBSMS] | CMIN
12/4/2023 12:46:28 PM | [NSO Update] Mindanao Grid-12/04/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3379MW, PK=2259MW, RR=88MW, NetOpMargin: PM=1032, EVE=1047 Highest Unit O/L: GNPK 1&2 Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @90MW, AG4 @125MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/4/2023 12:44:44 PM | [NSO Update] Visayas Grid-12/04/2023 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2662MW, PK=2225MW, RR=94MW, NetOpMargin: PM=343, EVE=229 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @278MW, PGPP1 @76MW [WEBSMS] | CVIS
12/4/2023 12:43:31 PM | [NSO Update] Luzon Grid-12/04/2023 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13659MW, PK=10887MW, RR=405MW, NetOpMargin: PM=2367, EVE=1876 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
12/4/2023 12:42:07 PM | Visayas Grid-12/04/2023 12:42: Magdugo SS 138kV Bus 1 energized at 1205H. (Planned Outage) [WEBSMS] | CVIS
12/4/2023 11:59:11 AM | Luzon Grid-12/04/2023 11:59: EERI 500kV Bus 2 energized at 1156H, for soaking for 24 hours. [WEBSMS] | CLUZ
12/4/2023 11:53:51 AM | Luzon Grid-12/04/2023 11:54: Ilijan-EERI 500kV L2 EERI 500kV commissioned at 1147H. [WEBSMS] | CLUZ
12/4/2023 11:38:48 AM | Mindanao Grid-12/04/2023 11:42: AGUS 2 Unit 2 HEP tripped with 20MW load at 1120H. Indication: 86T Trip. Unplanned Outage. [WEBSMS] | CMIN
12/4/2023 11:28:21 AM | Luzon Grid-12/04/2023 11:28: Ilijan-EERI 500kV L2 looped thru EERI 500kV bus 1 at 1126H, on commissioning. [WEBSMS] | CLUZ
12/4/2023 11:12:49 AM | Luzon Grid-12/04/2023 11:12: Ilijan ST 2 online at 1111H (Unplanned Outage) [WEBSMS] | CLUZ
12/4/2023 11:05:03 AM | Luzon Grid-12/04/2023 11:05: Ilijan 500kV Bus 1, Ilijan-EERI 500kV L2 de-energized at 1104H, on commissioning. [WEBSMS] | CLUZ
12/4/2023 10:31:57 AM | Luzon Grid-12/04/2023 10:32: Ilijan 500kV Bus 1, Ilijan-EERI 500kV L2 energized at 1029H, on commissioning. [WEBSMS] | CLUZ
12/4/2023 9:52:08 AM | Luzon Grid-12/04/2023 09:52: Ilijan GT2-2 online at 0949H (Unplanned Outage) [WEBSMS] | CLUZ
12/4/2023 9:08:54 AM | Mindanao Grid-12/04/2023 09:12: WMPC DG05 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
12/4/2023 7:56:56 AM | Visayas Grid-12/04/2023 07:57: Magdugo SS 138kV Bus 1 de-energized at 0753H. (Planned Outage) [WEBSMS] | CVIS
12/4/2023 7:53:54 AM | Visayas Grid-12/04/2023 07:54: 2nd lift-Sangi 34.5 KV line de-energized at 0741H. Planned Outage [WEBSMS] | CVIS
12/4/2023 6:02:07 AM | Luzon Grid-12/04/2023 06:02: Ilijan GT1-1 online at 0600H (Unplanned Outage) [WEBSMS] | CLUZ
12/4/2023 5:53:12 AM | [NSO Update] Mindanao Grid-12/04/2023 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3389MW, PK=2174MW, RR=84MW, NetOpMargin: AM=1132, PM=931, EVE=956 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @90MW, AG4 @125MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/4/2023 5:49:48 AM | [NSO Update] Visayas Grid-12/04/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2550MW, PK=2167MW, RR=93MW, NetOpMargin: AM=290, PM=207, EVE=191 Highest Unit O/L: THVI 1&2@ 169MW Derated Plant: TGPP @115.5MW, LEYTE A @280MW, PGPP1 @69MW [WEBSMS] | CVIS
12/4/2023 5:48:50 AM | [NSO Update] Luzon Grid-12/04/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13269MW, PK=10571MW, RR=404MW, NetOpMargin: AM=2294, PM=1878, EVE=1662 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, ILIJAN A @295MW [WEBSMS] | CLUZ
12/4/2023 5:44:32 AM | Mindanao Grid-12/04/2023 05:47: LAKE MAINIT Hydro tripped with 13MW load at 0400H. Cause: Power loss (outage of 69 kV Line). (Unplanned Outage) [WEBSMS] | CMIN
12/4/2023 5:37:39 AM | Mindanao Grid-12/04/2023 05:40: Tudaya 2 Unit 1 tripped with 5.5MW load at 0523H. Cause: for verification. (Unplanned Outage) [WEBSMS] | CMIN
12/4/2023 4:36:57 AM | Mindanao Grid-12/04/2023 04:40: Tudaya 2 Unit 1 cut-in at 0250H. (Affected by Planned Outage of DLPC). [WEBSMS] | CMIN
12/4/2023 4:15:51 AM | [NSO Update] Luzon Grid-12/04/2023 04:16: Weather Advisory: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
12/4/2023 4:15:41 AM | [NSO Update] Mindanao Grid-12/04/2023 04:18: Weather Advisory: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
12/4/2023 4:14:54 AM | [NSO Update] Visayas Grid-12/04/2023 04:15: Weather Advisory: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
12/4/2023 3:48:58 AM | Mindanao Grid-12/04/2023 03:52: Tudaya 1 Unit 1 cut-in at 0231H. (Planned Outage by DLPC). [WEBSMS] | CMIN
12/4/2023 3:48:02 AM | Mindanao Grid-12/04/2023 03:51: Sibulan B Unit 2 cut-in at 0245H. (Planned Outage by DLPC). [WEBSMS] | CMIN
12/4/2023 3:47:28 AM | Mindanao Grid-12/04/2023 03:50: Sibulan B Unit 1 cut-in at 0235H. (Planned Outage by DLPC). [WEBSMS] | CMIN
12/4/2023 3:46:22 AM | Mindanao Grid-12/04/2023 03:49: Sibulan A Unit 1 cut-in at 0226H. (Planned Outage by DLPC). [WEBSMS] | CMIN
12/4/2023 3:45:27 AM | Mindanao Grid-12/04/2023 03:48: Sibulan A Unit 2 cut-in at 0238H. (Unplanned Outage) [WEBSMS] | CMIN
12/4/2023 3:32:11 AM | Luzon Grid-12/04/2023 03:32: Ilijan ST1 online at 0331H (Unplanned Outage) [WEBSMS] | CLUZ
12/4/2023 1:58:55 AM | Luzon Grid-12/04/2023 01:59: Ilijan GT1-2 online at 0154H (Unplanned Outage) [WEBSMS] | CLUZ
12/4/2023 12:25:40 AM | Mindanao Grid-12/04/2023 00:28: (Correction) Tudaya 2 Unit 1 shutdown with 4.95MW load at 2256H (03 Dec 2023). Insufficient water supply. [WEBSMS] | CMIN
12/4/2023 12:19:43 AM | Mindanao Grid-12/04/2023 00:23: Tudaya 1 Unit 1 shutdown with 4.4MW load at 2301H (03 Dec 2023). Affected by DLPCs line switching activity. [WEBSMS] | CMIN
12/4/2023 12:19:11 AM | Mindanao Grid-12/04/2023 00:22: Sibulan B Unit 2 shutdown with 7MW load at 2301H (03 Dec 2023). Affected by DLPCs line switching activity. [WEBSMS] | CMIN
12/4/2023 12:18:36 AM | Mindanao Grid-12/04/2023 00:21: Sibulan B Unit 1 shutdown with 8.5MW load at 2301H (03 Dec 2023). Affected by DLPCs line switching activity. [WEBSMS] | CMIN
12/4/2023 12:17:36 AM | Mindanao Grid-12/04/2023 00:20: Sibulan A Unit 1 shutdown with 7MW load at 2301H (03 Dec 2023). Affected by DLPCs line switching activity. [WEBSMS] | CMIN
12/4/2023 12:15:55 AM | Mindanao Grid-12/04/2023 00:19: Tudaya 2 Unit 1 shutdown with 4.95MW load at 2256H. Affected by DLPCs line switching activity. [WEBSMS] | CMIN
12/4/2023 12:13:11 AM | Mindanao Grid-12/04/2023 00:16: Sibulan A Unit 2 tripped with 5.5MW load at 2222H (03 Dec 2023). Cause: Affected by tripping of DPLC Bajada Line. [WEBSMS] | CMIN
12/3/2023 10:21:44 PM | Mindanao Grid-12/03/2023 22:25: LAMSAN Biomass cut-in at 1733H. (Planned Outage) [WEBSMS] | CMIN
12/3/2023 10:20:00 PM | Mindanao Grid-12/03/2023 22:23: LAMSAN Biomass shutdown with 13.6MW load at 1629H. Normalization of load related to scheduled TL maintenance activity along Kibawe-Sultan Kudarat 138 kV line. [WEBSMS] | CMIN
12/3/2023 10:07:12 PM | Luzon Grid-12/03/2023 22:07: San Gabriel online at 2206H (Unplanned Outage) [WEBSMS] | CLUZ
12/3/2023 8:33:06 PM | Mindanao Grid-12/03/2023 20:36: WMPC DG04 declared available at 1600H. [WEBSMS] | CMIN
12/3/2023 7:56:52 PM | Luzon Grid-12/03/2023 19:57: SLTEC 2 emergency shutdown at 1952H (Unplanned Outage) [WEBSMS] | CLUZ
12/3/2023 7:50:49 PM | Mindanao Grid-12/03/2023 19:54: Davao - Bajada 138kV line energized at 1948H. (Planned Outage) [WEBSMS] | CMIN
12/3/2023 6:35:11 PM | Visayas Grid-12/03/2023 18:35: Mandaue-Pakna-an 69kV Feeder energized at 1832H. [WEBSMS] | CVIS
12/3/2023 6:29:05 PM | Mindanao Grid-12/03/2023 18:32: Therma Marine 2 (TM2) Unit 2 cut-out at 1351H. End of DR. Time of call (to lower load to 0MW): 1348H. [WEBSMS] | CMIN
12/3/2023 6:27:41 PM | Mindanao Grid-12/03/2023 18:30: Therma Marine 2 (TM2) Unit 2 cut-in at 1343H as DR. Time of call: 1330H. DR=20MW. [WEBSMS] | CMIN
12/3/2023 6:22:40 PM | [NSO Update] Mindanao Grid-12/03/2023 18:25: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3277MW, PK=2041MW, RR=76MW, NetOpMargin: EVE=1160 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @90MW, AG4 @125MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/3/2023 6:18:11 PM | [NSO Update] Visayas Grid-12/03/2023 18:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2525MW, PK=2063MW, RR=97MW, NetOpMargin: EVE=365 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @280MW, PGPP1 @75MW [WEBSMS] | CVIS
12/3/2023 6:14:20 PM | [NSO Update] Luzon Grid-12/03/2023 18:14: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11728MW, PK=9452MW, RR=354MW, NetOpMargin: EVE=1922 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CLC2 @175MW, GNPD 1 @334MW [WEBSMS] | CLUZ
12/3/2023 6:10:25 PM | Luzon Grid-12/03/2023 18:10: Nagsaag-San Jose 500kV Line 1 restored at 1808H (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 5:57:36 PM | [NSO Update] Visayas Grid-12/03/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2525MW, PK=2200MW, RR=97MW, NetOpMargin: EVE=228 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @280MW, PGPP1 @75MW [WEBSMS] | CVIS
12/3/2023 5:29:47 PM | Mindanao Grid-12/03/2023 17:33: Bunawan 138kV Bus no. 2 energized at 1707H. (Planned Outage) [WEBSMS] | CMIN
12/3/2023 5:22:58 PM | Mindanao Grid-12/03/2023 17:26: Sultan Kudarat Transformer No. 3 energized at 1702H. (Planned Outage) [WEBSMS] | CMIN
12/3/2023 5:20:55 PM | Mindanao Grid-12/03/2023 17:24: Kibawe - Sultan Kudarat 138kV L energized at 1658H. (Planned Outage) [WEBSMS] | CMIN
12/3/2023 5:15:06 PM | Luzon Grid-12/03/2023 17:15: Quezon (Balintawak) - San Jose 230kV Line 1 restored at 1713H (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 5:02:11 PM | Mindanao Grid-12/03/2023 17:05: SUPREME POWER Mati (MDP) cut-in at 1652H. (Unplanned Outage) [WEBSMS] | CMIN
12/3/2023 5:01:40 PM | Mindanao Grid-12/03/2023 17:04: SUPREME POWER Mati (MDP) tripped with 4.5MW load at 1648H. Indication: Reverse Power Trip. (Unplanned Outage) [WEBSMS] | CMIN
12/3/2023 4:54:01 PM | Luzon Grid-12/03/2023 16:54: Las Pinas (Zapote) 230kV Tie Line restored at 1653H (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 4:51:18 PM | Luzon Grid-12/03/2023 16:51: Las Pinas (Zapote) 230kV Bus 2 restored at 1651H (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 4:29:32 PM | Luzon Grid-12/03/2023 16:29: Binan 230kV Bus 2 restored at 1628H (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 4:22:19 PM | Luzon Grid-12/03/2023 16:22: Naga-Daraga 230kV Line restored at 1620H (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 3:42:49 PM | Mindanao Grid-12/03/2023 15:46: SUPREME POWER Mati (MDP) cut-in at 1351H. (Unplanned Outage) [WEBSMS] | CMIN
12/3/2023 3:42:24 PM | Mindanao Grid-12/03/2023 15:45: SUPREME POWER Mati (MDP) tripped with 5.5MW load at 1347H. Indication: Reverse Power Trip. (Unplanned Outage) [WEBSMS] | CMIN
12/3/2023 3:41:58 PM | Mindanao Grid-12/03/2023 15:45: SUPREME POWER Mati (MDP) cut-in at 1339H. (Unplanned Outage) [WEBSMS] | CMIN
12/3/2023 3:41:30 PM | Mindanao Grid-12/03/2023 15:44: SUPREME POWER Mati (MDP) tripped with 5.5MW load at 1338H. Indication: Reverse Power Trip. (Unplanned Outage) [WEBSMS] | CMIN
12/3/2023 3:29:53 PM | Luzon Grid-12/03/2023 15:30: Hermosa-BCCPP 230kV Line 1 restored at 1529H (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 2:53:54 PM | Luzon Grid-12/03/2023 14:54: San Gabriel shutdown at 1452H (Unplanned Outage) [WEBSMS] | CLUZ
12/3/2023 2:49:07 PM | Mindanao Grid-12/03/2023 14:52: LAKE MAINIT Hydro cut-in at 1342H. (Unplanned Outage) [WEBSMS] | CMIN
12/3/2023 2:48:20 PM | Mindanao Grid-12/03/2023 14:51: LAKE MAINIT Hydro tripped with 13.8MW load at 1328H. Indication: Overfluxing. Lowest frequency recorded was 59.107Hz (Note: with tripping of SEC1 and unexpected lowering of TM1 U1 load when dispatched as CR). With ALD of 23.68MW. (Unplanned Outage) [WEBSMS] | CMIN
12/3/2023 2:04:03 PM | Mindanao Grid-12/03/2023 14:07: SEC1 tripped with 94.5MW load at 1326H. Cause: Turbine high vibration. Lowest system frequency recorded was 59.44Hz. SIPS activated with a total load drop of 50.75MW (Gensan - Lledo 30.25 MW and Gensan - Tupi 20.5 MW). (Unplanned Outage) [WEBSMS] | CMIN
12/3/2023 1:19:33 PM | Mindanao Grid-12/03/2023 13:22: Bunawan 138kV Bus no. 2 de-energized at 1308H. (Planned Outage) [WEBSMS] | CMIN
12/3/2023 12:50:25 PM | [NSO Update] Luzon Grid-12/03/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12724MW, PK=9011MW, RR=315MW, NetOpMargin: PM=3398, EVE=2180 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CLC2 @175MW, GNPD 1 @334MW [WEBSMS] | CLUZ
12/3/2023 12:48:35 PM | [NSO Update] Mindanao Grid-12/03/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3415MW, PK=1853MW, RR=74MW, NetOpMargin: PM=1487, EVE=1287 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @90MW, AG4 @125MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/3/2023 12:36:06 PM | [NSO Update] Visayas Grid-12/03/2023 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2480MW, PK=1835MW, RR=94MW, NetOpMargin: PM=551, EVE=287 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @280MW, PGPP1 @38MW [WEBSMS] | CVIS
12/3/2023 11:18:40 AM | Mindanao Grid-12/03/2023 11:21: (Correction) LAMSAN Biomass cut-in at 0742H. (Planned Outage) [WEBSMS] | CMIN
12/3/2023 8:41:46 AM | Visayas Grid-12/03/2023 08:41: Cebu - Mandaue 138 kV Line 1 de-energized at 0841H. (Planned Outage) [WEBSMS] | CVIS
12/3/2023 8:22:52 AM | Luzon Grid-12/03/2023 08:22: Binan SS 230kV Bus 2 de-energized at 0822H. (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 7:55:50 AM | Mindanao Grid-12/03/2023 07:59: LAMSAN Biomass cut-in at 0659H. (Planned Outage) [WEBSMS] | CMIN
12/3/2023 7:53:12 AM | Mindanao Grid-12/03/2023 07:56: LAMSAN Biomass shutdown with 12.9MW load at 0659H. Affected by load transfer activity brought by the scheduled TL maintenance activity along Kibawe-Sultan Kudarat 138 kV line. [WEBSMS] | CMIN
12/3/2023 7:36:37 AM | Mindanao Grid-12/03/2023 07:39: Sultan Kudarat - Lamsan 69kV L energized at 0735H. (Planned Outage) [WEBSMS] | CMIN
12/3/2023 7:23:49 AM | Luzon Grid-12/03/2023 07:23: Hermosa-BCCPP 230kV Line 1 de-energized at 0722H. (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 7:20:48 AM | Visayas Grid-12/03/2023 07:20: Colon - Toledo 138 kV Line de-energized at 0720H. (Planned Outage) [WEBSMS] | CVIS
12/3/2023 7:17:48 AM | Mindanao Grid-12/03/2023 07:21: Kibawe - Sultan Kudarat 138kV L de-energized at 0712H. (Planned Outage) [WEBSMS] | CMIN
12/3/2023 7:17:03 AM | Mindanao Grid-12/03/2023 07:20: Sultan Kudarat Transformer No. 3 de-energized at 0709H. (Planned Outage) [WEBSMS] | CMIN
12/3/2023 7:16:01 AM | Mindanao Grid-12/03/2023 07:19: Sultan Kudarat - Lamsan 69kV L de-energized at 0703H. (Planned Outage) [WEBSMS] | CMIN
12/3/2023 6:58:52 AM | Luzon Grid-12/03/2023 06:58: Nagsaag-San Jose 500kV Line 1 de-energized at 0657H. (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 6:43:01 AM | Luzon Grid-12/03/2023 06:43: Las Pinas (Zapote) SS 230kV Bus 2 de-energized at 0642H. (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 6:40:50 AM | Luzon Grid-12/03/2023 06:40: Naga-Daraga 230kV Line de-energized at 0640H. (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 6:29:37 AM | Luzon Grid-12/03/2023 06:29: Las Pinas (Zapote) SS 230kV Tie Line de-energized at 0629H. (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 6:22:31 AM | Luzon Grid-12/03/2023 06:22: Quezon (Balintawak) - San Jose 230kV Line 1 de-energized at 0622H. (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 5:52:15 AM | [NSO Update] Mindanao Grid-12/03/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3408MW, PK=1738MW, RR=72MW, NetOpMargin: AM=1598, PM=1431, EVE=1231 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @90MW, AG4 @110MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @200MW [WEBSMS] | CMIN
12/3/2023 5:51:38 AM | [NSO Update] Visayas Grid-12/03/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2630MW, PK=1765MW, RR=93MW, NetOpMargin: AM=772, PM=551, EVE=265 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 115.5MW, Leyte A @ 284MW, PGPP1 @ 38MW [WEBSMS] | CVIS
12/3/2023 5:50:37 AM | [NSO Update] Luzon Grid-12/03/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13116MW, PK=8728MW, RR=309MW, NetOpMargin: AM=4079, PM=3060, EVE=2200 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: GNPD 1 @ 334MW, Calaca 2 @ 175MW [WEBSMS] | CLUZ
12/3/2023 5:33:17 AM | Visayas Grid-12/03/2023 05:33: Mandaue-Paknaan 69kV Feeder de-energized at 0531H. Planned Outage [WEBSMS] | CVIS
12/3/2023 4:24:00 AM | [NSO Update] Mindanao Grid-12/03/2023 04:27: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
12/3/2023 4:23:49 AM | [NSO Update] Luzon Grid-12/03/2023 04:23: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
12/3/2023 4:23:23 AM | [NSO Update] Visayas Grid-12/03/2023 04:23: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
12/3/2023 2:14:25 AM | Mindanao Grid-12/03/2023 02:17: Davao-Bajada 138kV Line de-energized 0210H. Planned outage. [WEBSMS] | CMIN
12/3/2023 1:01:51 AM | Luzon Grid-12/03/2023 01:01: Lamao-SCPC 230kV Tie Line 3 was de-energized at 0058H. (Planned Outage) [WEBSMS] | CLUZ
12/3/2023 12:47:44 AM | Mindanao Grid-12/03/2023 00:50: ASG Online at 2310H. (Unplanned Outage). [WEBSMS] | CMIN
12/3/2023 12:47:00 AM | Mindanao Grid-12/03/2023 00:50: AGC Online at 2321H. (Unplanned Outage). [WEBSMS] | CMIN
12/3/2023 12:22:12 AM | Mindanao Grid-12/03/2023 00:25: PG4 U3 Online at 0019H. (Unplanned Outage). [WEBSMS] | CMIN
12/2/2023 11:56:20 PM | Mindanao Grid-12/02/2023 23:59: PG4 U1 Online at 2353H. (Unplanned Outage). [WEBSMS] | CMIN
12/2/2023 11:47:46 PM | Luzon Grid-12/02/2023 23:47: Commissioning and energization of the new BFRs for Hermosa PCBs 8-02CB08HER and 8-02CB24HER was completed at 2342H. [WEBSMS] | CLUZ
12/2/2023 11:40:49 PM | Mindanao Grid-12/02/2023 23:44: ASG with a load of 8MW tripped at 2238H. (Unplanned Outage). [WEBSMS] | CMIN
12/2/2023 11:40:14 PM | Mindanao Grid-12/02/2023 23:43: AGC with a load of 13MW tripped at 2238H. (Unplanned Outage). [WEBSMS] | CMIN
12/2/2023 11:39:44 PM | Mindanao Grid-12/02/2023 23:43: PG4 U3 with a load of 25MW tripped at 2238H. (Unplanned Outage). [WEBSMS] | CMIN
12/2/2023 11:39:03 PM | Mindanao Grid-12/02/2023 23:42: PG4 U1 with a load of 35MW tripped at 2238H. (Unplanned Outage). [WEBSMS] | CMIN
12/2/2023 11:12:06 PM | Mindanao Grid-12/02/2023 23:15: PG4 U1 and U3 with a load of 35MW and MW respectively tripped at 2238H. Unplanned Outage. Affected by the earthquake. [WEBSMS] | CMIN
12/2/2023 10:33:44 PM | Mindanao Grid-12/02/2023 22:37: TU2 U1 shutdown at 2146H. (Planned Outage). [WEBSMS] | CMIN
12/2/2023 10:32:31 PM | Mindanao Grid-12/02/2023 22:35: TU1 U1 shutdown at 2147H. (Planned Outage). [WEBSMS] | CMIN
12/2/2023 10:30:41 PM | Mindanao Grid-12/02/2023 22:33: SBL B U2 shutdown at 2153H. (Planned Outage). [WEBSMS] | CMIN
12/2/2023 10:29:52 PM | Mindanao Grid-12/02/2023 22:33: SBL B U1 shutdown at 2152H. (Planned Outage). [WEBSMS] | CMIN
12/2/2023 10:28:59 PM | Mindanao Grid-12/02/2023 22:32: SBL A U2 Shutdown at 2153H. (Planned Outage). [WEBSMS] | CMIN
12/2/2023 10:26:39 PM | Mindanao Grid-12/02/2023 22:29: SBL A U1 shutdown at 2149H. (Planned Outage). [WEBSMS] | CMIN
12/2/2023 9:37:51 PM | Mindanao Grid-12/02/2023 21:41: SUPREME POWER Mati (MDP) cut-out at 2105H. End of MO dispatch (RTD). [WEBSMS] | CMIN
12/2/2023 9:16:32 PM | Luzon Grid-12/02/2023 21:16: Hermosa-Mexico 230kV line 1 was restored at 2115H. (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 7:45:51 PM | Luzon Grid-12/02/2023 19:45: Hermosa 230kV Bus 2 was energized at 1943H. (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 7:43:51 PM | Luzon Grid-12/02/2023 19:43: Dona Imelda(Araneta)-Sta Mesa 115kV line 2 was restored at 1942H. (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 5:57:07 PM | [NSO Update] Mindanao Grid-12/02/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3345MW, PK=2192MW, RR=88MW, NetOpMargin: EVE=1065 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @110MW, AG4 @125MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @115MW [WEBSMS] | CMIN
12/2/2023 5:55:12 PM | [NSO Update] Visayas Grid-12/02/2023 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2465MW, PK=2082MW, RR=97MW, NetOpMargin: EVE=286 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 115.5MW, Leyte A @ 284MW, PGPP1 @ 38MW [WEBSMS] | CVIS
12/2/2023 5:52:13 PM | [NSO Update] Luzon Grid-12/02/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11981MW, PK=10180MW, RR=406MW, NetOpMargin: EVE=1395 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: CLC1 @190MW, CLC2 @175MW, DINGININ 1 @334MW, QPPL @390MW [WEBSMS] | CLUZ
12/2/2023 5:33:53 PM | Visayas Grid-12/02/2023 17:33: Toledo - Calong-calong 138 kV Line energized at 1732H. (Planned Outage) [WEBSMS] | CVIS
12/2/2023 4:47:22 PM | Mindanao Grid-12/02/2023 16:50: WMPC DG05 cut-out at 1513H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/2/2023 3:30:01 PM | Luzon Grid-12/02/2023 15:30: Binan 230kV Bus 1 was energized at 1525H. (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 2:57:58 PM | Luzon Grid-12/02/2023 14:57: Angat-San Jose 115kV Line 3 restored at 1452H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 2:57:52 PM | Luzon Grid-12/02/2023 14:57: Angat-San Jose 115kV Line 3 restored at 1452H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 1:43:20 PM | Mindanao Grid-12/02/2023 13:46: WMPC DG04 emergency shutdown at 1326H due to exhaust gas leak at cylinder A2. Replaced with WMPC DG05 which cut-in at 1313H. [WEBSMS] | CMIN
12/2/2023 1:39:02 PM | Mindanao Grid-12/02/2023 13:42: WMPC DG05 cut-in at 1313H as replacement power for WMPC DG04. RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/2/2023 1:08:07 PM | [NSO Update] Mindanao Grid-12/02/2023 13:11: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3379MW, PK=2115MW, RR=86MW, NetOpMargin: PM=1178, EVE=1087 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @110MW, AG4 @125MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @115MW [WEBSMS] | CMIN
12/2/2023 1:02:52 PM | [NSO Update] Visayas Grid-12/02/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2599MW, PK=2037MW, RR=94MW, NetOpMargin: PM=468, EVE=249 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 115.5MW, Leyte A @ 280MW, PGPP1 @ 38MW [WEBSMS] | CVIS
12/2/2023 12:58:10 PM | "[NSO Update] Luzon Grid-12/02/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12925MW, PK=10264MW, RR=411MW, NetOpMargin: PM=2250, EVE=1689 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @190MW, Calaca 2 @ 175MW, QPPL @390MW [WEBSMS]" | CLUZ
12/2/2023 12:58:04 PM | [NSO Update] Luzon Grid-12/02/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12925MW, PK=10264MW, RR=411MW, NetOpMargin: PM=2250, EVE=1689 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @190MW, Calaca 2 @ 175MW, QPPL @390MW [WEBSMS] | CLUZ
12/2/2023 12:31:01 PM | Luzon Grid-12/02/2023 12:31: Bolo 500kV Bus 1 restored at 1230H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 12:30:56 PM | Luzon Grid-12/02/2023 12:31: Bolo 500kV Bus 1 restored at 1230H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 12:27:53 PM | Mindanao Grid-12/02/2023 12:31: ASIGA Hydro cut-in at 1034H. (Unplanned Outage) [WEBSMS] | CMIN
12/2/2023 12:27:24 PM | Mindanao Grid-12/02/2023 12:30: Aurora-Nagamin 138kV L1 autotripped and autoreclosed at 1214H. Unplanned outage. [WEBSMS] | CMIN
12/2/2023 12:26:58 PM | Mindanao Grid-12/02/2023 12:30: ASIGA Hydro tripped with 8.16MW load at 1008H. Lowest frequency recorded was 60.07Hz. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
12/2/2023 10:17:23 AM | Mindanao Grid-12/02/2023 10:20: WMPC DG04 cut-in at 0950H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/2/2023 10:15:12 AM | Mindanao Grid-12/02/2023 10:18: LIBERTAD POWER (LPE) cut-in at 0845H. (Unplanned Outage) [WEBSMS] | CMIN
12/2/2023 10:13:13 AM | Mindanao Grid-12/02/2023 10:16: LIBERTAD POWER (LPE) tripped with 4MW load at 0756H. Lowest frequency recorded was 59.95Hz. Cause: Turbine Trip. (Unplanned Outage) [WEBSMS] | CMIN
12/2/2023 9:21:25 AM | Luzon Grid-12/02/2023 09:21: Angat-San Jose 115kV Line 3 de-energized at 0913H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 9:21:20 AM | Luzon Grid-12/02/2023 09:21: Angat-San Jose 115kV Line 3 de-energized at 0913H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 9:18:09 AM | "Luzon Grid-12/02/2023 09:18: System Advisory: Affected ALD feeders of NGCP and MERALCO restored at 0903H and 0901H, respectively [WEBSMS]" | CLUZ
12/2/2023 9:18:04 AM | Luzon Grid-12/02/2023 09:18: System Advisory: Affected ALD feeders of NGCP and MERALCO restored at 0903H and 0901H, respectively [WEBSMS] | CLUZ
12/2/2023 9:14:22 AM | Luzon Grid-12/02/2023 09:14: Correction: System Advisory: ALD occurred at NGCP and MERALCO feeders at 0858H due to tripping of Ilijan A & B. It de-load from 610MW to 379MW then eventually tripped . Lowest Frequency=59.09Hz (Unplanned Outage) [WEBSMS] | CLUZ
12/2/2023 9:14:17 AM | Luzon Grid-12/02/2023 09:14: Correction: System Advisory: ALD occurred at NGCP and MERALCO feeders at 0858H due to tripping of Ilijan A & B. It de-load from 610MW to 379MW then eventually tripped . Lowest Frequency=59.09Hz (Unplanned Outage) [WEBSMS] | CLUZ
12/2/2023 9:12:48 AM | Luzon Grid-12/02/2023 08:49: Dona Imelda-Sta Mesa 115kV Line 2 de-energized at 0844H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 9:12:43 AM | Luzon Grid-12/02/2023 09:12: System Advisory: ALD occurred at NGCP and MERALCO feeders at 0958H due to tripping of Ilijan A & B. It de-load from 610MW to 379MW then eventually tripped . Lowest Frequency=59.09Hz (Unplanned Outage) [WEBSMS] | CLUZ
12/2/2023 9:02:29 AM | Mindanao Grid-12/02/2023 09:05: SUPREME POWER Mati (MDP) cut-in at 0900H. MO dispatch (RTD). [WEBSMS] | CMIN
12/2/2023 8:49:23 AM | Luzon Grid-12/02/2023 08:49: Dona Imelda-Sta Mesa 115kV Line 2 de-energized at 0844H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 8:49:18 AM | Luzon Grid-12/02/2023 08:49: Dona Imelda-Sta Mesa 115kV Line 2 de-energized at 0844H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 8:31:27 AM | Mindanao Grid-12/02/2023 08:34: ASIGA Hydro cut-in at 0627H. (Unplanned Outage) [WEBSMS] | CMIN
12/2/2023 8:29:37 AM | Mindanao Grid-12/02/2023 08:32: ASIGA Hydro tripped with 8.1MW load at 0603H. Lowest frequency recorded was 59.69Hz. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
12/2/2023 8:25:08 AM | Luzon Grid-12/02/2023 08:25: Binan 230kV Bus 1 de-energized at 0818H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 8:25:03 AM | Luzon Grid-12/02/2023 08:25: Binan 230kV Bus 1 de-energized at 0818H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 8:06:47 AM | Mindanao Grid-12/02/2023 08:10: Bunawan SS 300MVA Power Transformer de-energized 0801H. Planned outage [WEBSMS] | CMIN
12/2/2023 7:37:17 AM | Luzon Grid-12/02/2023 07:37: Hermosa 230kV Bus 2 de-energized at 0737H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 7:37:12 AM | Luzon Grid-12/02/2023 07:37: Hermosa 230kV Bus 2 de-energized at 0737H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 7:28:25 AM | Mindanao Grid-12/02/2023 07:31: LIBERTAD POWER (LPE) cut-in at 0720H. (Unplanned Outage) [WEBSMS] | CMIN
12/2/2023 7:27:52 AM | Luzon Grid-12/02/2023 07:26: Bolo 500kV Bus 1 de-energized at 0706H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 7:27:47 AM | Luzon Grid-12/02/2023 07:27: Hermosa-Mexico 230kV Line 1 de-energized at 0724H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 7:26:15 AM | Luzon Grid-12/02/2023 07:26: Bolo 500kV Bus 1 de-energized at 0706H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 7:26:10 AM | Luzon Grid-12/02/2023 07:26: Bolo 500kV Bus 1 de-energized at 0706H (Planned Outage) [WEBSMS] | CLUZ
12/2/2023 6:55:45 AM | Visayas Grid-12/02/2023 06:55: Toledo - Calong-calong 138 kV Line de-energized at 0655H. (Planned Outage) [WEBSMS] | CVIS
12/2/2023 5:59:43 AM | [NSO Update] Mindanao Grid-12/02/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3382MW, PK=2018MW, RR=82MW, NetOpMargin: AM=1282, PM=1232, EVE=1156 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @110MW, AG4 @125MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @115MW [WEBSMS] | CMIN
12/2/2023 5:58:48 AM | [NSO Update] Visayas Grid-12/02/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2521MW, PK=2038MW, RR=93MW, NetOpMargin: AM=390, PM=342, EVE=240 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 115.5MW, Leyte A @ 284MW, PGPP1 @ 38MW [WEBSMS] | CVIS
12/2/2023 5:57:18 AM | [NSO Update] Visayas Grid-12/02/2023 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13613MW, PK=10023MW, RR=403MW, NetOpMargin: AM=3187, PM=3157, EVE=2494 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 190MW, Calaca 2 @ 175MW, Masinloc 3 @ 300MW, Ilijan A @ 420MW, Ilijan B @ 190MW [WEBSMS] | CVIS
12/2/2023 5:26:12 AM | Mindanao Grid-12/02/2023 05:29: LPE (Libertad Power) with a load of 6MW tripped at 0522H. (Unplanned Outage). [WEBSMS] | CMIN
12/2/2023 4:05:38 AM | [NSO Update] Mindanao Grid-12/02/2023 04:08: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
12/2/2023 4:05:17 AM | [NSO Update] Visayas Grid-12/02/2023 04:05: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
12/2/2023 4:05:08 AM | [NSO Update] Luzon Grid-12/02/2023 04:05: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
12/2/2023 4:05:03 AM | [NSO Update] Luzon Grid-12/02/2023 04:05: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
12/1/2023 9:19:06 PM | Mindanao Grid-12/01/2023 21:22: WMPC DG4 as RPS Shutdown at 2113H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/1/2023 9:15:23 PM | Mindanao Grid-12/01/2023 21:18: AGC Online at 1955H. (Unplanned Outage). [WEBSMS] | CMIN
12/1/2023 9:12:56 PM | Mindanao Grid-12/01/2023 21:16: SMF1 Online at 2111H. (Unplanned Outage) From FO. [WEBSMS] | CMIN
12/1/2023 9:10:37 PM | Mindanao Grid-12/01/2023 21:13: MDP shutdown at 2105H. (Planned Outage). Follow RTD. [WEBSMS] | CMIN
12/1/2023 8:04:05 PM | Mindanao Grid-12/01/2023 20:07: SMF1 with load of 20MW tripped at 1952H. (Unplanned Outage). [WEBSMS] | CMIN
12/1/2023 8:02:34 PM | Mindanao Grid-12/01/2023 20:05: SMF1 Online at 1941H. (Planned Outage). Extended PMS. [WEBSMS] | CMIN
12/1/2023 6:34:50 PM | Mindanao Grid-12/01/2023 18:38: Kauswagan - GNPK 230kV L3 energized at 1832H. (Planned Outage) [WEBSMS] | CMIN
12/1/2023 5:51:33 PM | [NSO Update] Mindanao Grid-12/01/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3240MW, PK=2233MW, RR=76MW, NetOpMargin: EVE=932 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @110MW, AG4 @125MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @115MW [WEBSMS] | CMIN
12/1/2023 5:51:31 PM | Mindanao Grid-12/01/2023 17:54: Agus 2 HEP Unit no. 2 138kV line energized at 1735H. (Unplanned Outage) [WEBSMS] | CMIN
12/1/2023 5:50:02 PM | [NSO Update] Visayas Grid-12/01/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2604MW, PK=2254MW, RR=97MW, NetOpMargin: EVE=253 Highest Unit O/L: THVI 1 & 2 @ 168MW Derated Plant: TGPP @ 115.5MW, Leyte A @ 280MW [WEBSMS] | CVIS
12/1/2023 5:48:04 PM | "[NSO Update] Luzon Grid-12/01/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13042MW, PK=10539MW, RR=404MW, NetOpMargin: EVE=2099 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS]" | CLUZ
12/1/2023 5:48:00 PM | [NSO Update] Luzon Grid-12/01/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13042MW, PK=10539MW, RR=404MW, NetOpMargin: EVE=2099 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
12/1/2023 5:45:46 PM | Mindanao Grid-12/01/2023 17:48: AG2 U2 Online at 1739H. (Unplanned Outage). From Emergency Shutdown. [WEBSMS] | CMIN
12/1/2023 5:34:36 PM | Mindanao Grid-12/01/2023 17:37: Agus 2 HEP Unit No. 2 138kVL de-energized at 1432H. (Unplanned Outage) [WEBSMS] | CMIN
12/1/2023 5:26:40 PM | Visayas Grid-12/01/2023 17:26: 2nd lift - Sangi 34.5 KV line energized at 1725H. Planned Outage [WEBSMS] | CVIS
12/1/2023 4:38:45 PM | Mindanao Grid-12/01/2023 16:41: Jasaan Transformer No. 2 energized at 1634H. (Planned Outage) [WEBSMS] | CMIN
12/1/2023 4:15:31 PM | Mindanao Grid-12/01/2023 16:18: WMPC DG7 shutdown as RPS at 1613H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/1/2023 3:56:31 PM | Mindanao Grid-12/01/2023 15:59: ASG Online at 1550H. (Unplanned Outage). From FO. [WEBSMS] | CMIN
12/1/2023 3:35:53 PM | Mindanao Grid-12/01/2023 15:39: ASG with a load of 8MW tripped at 1527H. (Unplanned Outage). [WEBSMS] | CMIN
12/1/2023 3:34:31 PM | Mindanao Grid-12/01/2023 15:37: AGC with a load of 12.5MW tripped at 1527H. (Unplanned Outage). [WEBSMS] | CMIN
12/1/2023 3:30:48 PM | Luzon Grid-12/01/2023 15:30: Bolo (Kadampat) 600MVA Transformer Bank 4 restored at 1529H (Planned Outage) [WEBSMS] | CLUZ
12/1/2023 3:30:44 PM | Luzon Grid-12/01/2023 15:30: Bolo (Kadampat) 600MVA Transformer Bank 4 restored at 1529H (Planned Outage) [WEBSMS] | CLUZ
12/1/2023 2:42:52 PM | Luzon Grid-12/01/2023 14:42: Tayabas PCB 9-06CB24TAY energized at 1440H (Planned Outage) [WEBSMS] | CLUZ
12/1/2023 2:42:49 PM | Luzon Grid-12/01/2023 14:42: Tayabas PCB 9-06CB24TAY energized at 1440H (Planned Outage) [WEBSMS] | CLUZ
12/1/2023 2:38:21 PM | Mindanao Grid-12/01/2023 14:41: Agus 2 HEP Unit no. 2 138kV line de-energized. (Unplanned Outage) [WEBSMS] | CMIN
12/1/2023 2:36:37 PM | Mindanao Grid-12/01/2023 14:39: AG2 U2 Shutdown at 1432H. (Unplanned Outage). Emergency Shutdown requested by the Plant. [WEBSMS] | CMIN
12/1/2023 12:58:42 PM | [NSO Update] Luzon Grid-12/01/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13526MW, PK=11019MW, RR=405MW, NetOpMargin: PM=2102, EVE=1747 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @510MW, ILIJAN B @190MW, SAN GABRIEL @272MW [WEBSMS] | CLUZ
12/1/2023 12:51:13 PM | Mindanao Grid-12/01/2023 12:54: NagaMin - Zamboanga 138kV L2 energized at 1248H. (Planned Outage) [WEBSMS] | CMIN
12/1/2023 12:43:57 PM | [NSO Update] Mindanao Grid-12/01/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3275MW, PK=2267MW, RR=87MW, NetOpMargin: PM=921, EVE=924 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @110MW, AG4 @125MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @115MW [WEBSMS] | CMIN
12/1/2023 12:40:51 PM | [NSO Update] Visayas Grid-12/01/2023 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2646MW, PK=2222MW, RR=94MW, NetOpMargin: PM=331, EVE=173 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @284MW [WEBSMS] | CVIS
12/1/2023 9:58:38 AM | Luzon Grid-12/01/2023 09:58: San Gabriel online at 0955H. (Unplanned Outage) [WEBSMS] | CLUZ
12/1/2023 9:16:16 AM | Mindanao Grid-12/01/2023 09:19: SUPREME POWER Mati (MDP) cut-in at 0900H. MO dispatch (RTD). [WEBSMS] | CMIN
12/1/2023 8:46:20 AM | Luzon Grid-12/01/2023 08:46: Tayabas-Mauban 230kV line was de-energized at 0841H. (Planned Outage) [WEBSMS] | CLUZ
12/1/2023 8:39:18 AM | Mindanao Grid-12/01/2023 08:42: (Correction) Agus 1 Unit 1 shutdown at 0810H for PMS (GOMP). (Planned Outage) [WEBSMS] | CMIN
12/1/2023 8:34:45 AM | Mindanao Grid-12/01/2023 08:37: Agus 1 Unit 1 shutdown at 0810H for PMS (GOMP). (Unplanned Outage) [WEBSMS] | CMIN
12/1/2023 8:34:32 AM | Luzon Grid-12/01/2023 08:34: Mauban-SBPL 230kV line was de-energized at 0828H. (Planned Outage) [WEBSMS] | CLUZ
12/1/2023 8:29:25 AM | Luzon Grid-12/01/2023 08:29: Malaya-Ingrid 230kV line 2 was de-energized at 0825H. (Planned Outage) [WEBSMS] | CLUZ
12/1/2023 8:27:50 AM | Luzon Grid-12/01/2023 08:27: Tayabas PCB 9-06CB24TAY was de-energized at 0826H. (Planned Outage) [WEBSMS] | CLUZ
12/1/2023 8:08:53 AM | Mindanao Grid-12/01/2023 08:12: Jasaan Transformer No. 2 de-energized at 0805H. (Planned Outage) [WEBSMS] | CMIN
12/1/2023 7:32:56 AM | Mindanao Grid-12/01/2023 07:36: WMPC DG07 cut-in at 0720H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/1/2023 7:16:26 AM | Mindanao Grid-12/01/2023 07:19: WMPC DG04 cut-in at 0715H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
12/1/2023 7:14:59 AM | Mindanao Grid-12/01/2023 07:18: NagaMin - Zamboanga 138kV L2 de-energized at 0702H. (Planned Outage) [WEBSMS] | CMIN
12/1/2023 6:53:41 AM | Visayas Grid-12/01/2023 06:53: Carcon-Sangi 34.5 KV L3 de-energized at 0653H. Planned Outage [WEBSMS] | CVIS
12/1/2023 6:42:57 AM | Luzon Grid-12/01/2023 06:43: Bolo(Kadampat) 600MVA Transformer Bank 4 was de-energized at 0640H. (Planned Outage) [WEBSMS] | CLUZ
12/1/2023 5:59:31 AM | [NSO Update] Mindanao Grid-12/01/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3286MW, PK=2123MW, RR=86MW, NetOpMargin: AM=1077, PM=1002, EVE=1183 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @110MW, AG4 @125MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @115MW [WEBSMS] | CMIN
12/1/2023 5:58:22 AM | [NSO Update] Visayas Grid-12/01/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2552MW, PK=2196MW, RR=93MW, NetOpMargin: AM=263, PM=187, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @284MW [WEBSMS] | CVIS
12/1/2023 5:56:55 AM | [NSO Update] Luzon Grid-12/01/2023 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13070MW, PK=10880MW, RR=404MW, NetOpMargin: AM=1787, PM=1574, EVE=1378 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
12/1/2023 5:25:20 AM | [NSO Update] Mindanao Grid-12/01/2023 05:28: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
12/1/2023 5:25:03 AM | [NSO Update] Visayas Grid-12/01/2023 05:25: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CVIS
12/1/2023 5:24:40 AM | [NSO Update] Luzon Grid-12/01/2023 05:24: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
12/1/2023 4:08:56 AM | Luzon Grid-12/01/2023 04:08: SCPC Unit 3 shutdown at 0407H (Planned Outage) [WEBSMS] | CLUZ
12/1/2023 12:50:22 AM | Mindanao Grid-12/01/2023 00:53: Maco-TMI 138KV L1 de-energized at 0023H. Requested by TMI management (customer). Planned Outage. [WEBSMS] | CMIN
11/30/2023 11:58:23 PM | Mindanao Grid-12/01/2023 00:01: Davao-Bunawan 138KV L1 re-energized at 2254H & looped at Davao SS at 2255H. P & E requested shutdown under ERC-approved MSUP, Stage 1, Schedule 1. From PO/N-GOMP. [WEBSMS] | CMIN
11/30/2023 11:36:24 PM | Luzon Grid-11/30/2023 23:36: Sual Unit 2 shutdown at 2335H (Planned Outage) [WEBSMS] | CLUZ
11/30/2023 11:29:24 PM | Mindanao Grid-11/30/2023 23:32: Bunawan SS 138KV Bus 1 re-energized at 1645H. Part of ERC-approved MSRP, Stage 1, Schedule 1. From P&E requested shutdown. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
11/30/2023 9:15:11 PM | Mindanao Grid-11/30/2023 21:18: WMPC DG04 cut-out at 2113H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/30/2023 9:09:11 PM | Mindanao Grid-11/30/2023 21:12: SUPREME POWER Mati (MDP) cut-out at 2105H. End of MO dispatch (RTD). [WEBSMS] | CMIN
11/30/2023 7:54:53 PM | Luzon Grid-11/30/2023 19:54: San Gabriel shutdown at 1952H. (Unplanned Outage) [WEBSMS] | CLUZ
11/30/2023 6:06:27 PM | [NSO Update] Mindanao Grid-11/30/2023 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3307MW, PK=2198MW, RR=88MW, NetOpMargin: EVE=1022 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @125MW, AG5 @27MW, AG6 @155MW, AG7 @25MW, PG4 @125MW [WEBSMS] | CMIN
11/30/2023 6:04:56 PM | Luzon Grid-11/30/2023 18:04: Taytay-Malaya 230kV line 2 was restored at 1804H. (Planned Outage) [WEBSMS] | CLUZ
11/30/2023 6:04:52 PM | [NSO Update] Visayas Grid-11/30/2023 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2546MW, PK=2213MW, RR=97MW, NetOpMargin: EVE=236 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @317MW [WEBSMS] | CVIS
11/30/2023 6:01:09 PM | [NSO Update] Luzon Grid-11/30/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13579MW, PK=10767MW, RR=429MW, NetOpMargin: EVE=2383 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @422MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/30/2023 5:26:53 PM | Visayas Grid-11/30/2023 17:26: 2nd lift-Sangi 34.5 KV line energized at 1724H. Planned Outage [WEBSMS] | CVIS
11/30/2023 5:13:08 PM | Visayas Grid-11/30/2023 17:13: Carcon-Sangi 34.5 KV L3 energized at 1707H. Planned Outage [WEBSMS] | CVIS
11/30/2023 4:34:31 PM | Mindanao Grid-11/30/2023 16:37: WMPC DG07 cut-out at 1616H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/30/2023 4:25:57 PM | Luzon Grid-11/30/2023 16:25: Tayabas PCB 9-06CB08TAY was energized at 1624H. (Planned Outage) [WEBSMS] | CLUZ
11/30/2023 4:24:05 PM | Mindanao Grid-11/30/2023 16:27: Manolo Fortich 2 (MN2) Unit 3 cut-in at 1607H from PMS (cut-out at 0702H). [WEBSMS] | CMIN
11/30/2023 4:03:47 PM | Mindanao Grid-11/30/2023 16:06: Baloi SS 138KV 100MVA T3 re-energized at 1540H. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
11/30/2023 2:58:27 PM | Luzon Grid-11/30/2023 14:58: San Gabriel online at 1456H. (Unplanned Outage) [WEBSMS] | CLUZ
11/30/2023 2:30:02 PM | Luzon Grid-11/30/2023 14:30: Sta Rita and San Lorenzo 230kV Bus A and B were unlooped at 1422H while Batangas 300MVA T04 and T05 were looped at 1425H. (Preparation for the synchronization of San Gabriel) [WEBSMS] | CLUZ
11/30/2023 2:17:06 PM | Luzon Grid-11/30/2023 14:17: Las Pinas(Zapote) 300MVA T03 was de-energized at 1416H. (Planned Outage) [WEBSMS] | CLUZ
11/30/2023 2:07:40 PM | Mindanao Grid-11/30/2023 14:10: NACSUR cut-in at 1400H. MO dispatched (RTD). [WEBSMS] | CMIN
11/30/2023 1:33:38 PM | Mindanao Grid-11/30/2023 13:36: Bunawan SS 138KV Bus 1 de-energized at 1310H to undertake simulation tripping of reconfigured 7-02CB04BUN new BFR protection to integrate into the new 7LI1DAVBUN Line Protection. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
11/30/2023 1:03:03 PM | Luzon Grid-11/30/2023 13:03: Calaca-Binan 230kV line was restored at 1302H. (Unplanned Outage) [WEBSMS] | CLUZ
11/30/2023 12:58:09 PM | Luzon Grid-11/30/2023 12:58: Sta Rita-San Gabriel 230kV line was restored at 1254H. (Unplanned Outage) [WEBSMS] | CLUZ
11/30/2023 12:51:40 PM | [NSO Update] Luzon Grid-11/30/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14353MW, PK=11102MW, RR=444MW, NetOpMargin: PM=2807, EVE=2468 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 300MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/30/2023 12:42:06 PM | [NSO Update] Mindanao Grid-11/30/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3330MW, PK=2228MW, RR=88MW, NetOpMargin: PM=1013, EVE=1017 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @125MW, AG5 @27MW, AG6 @155MW, AG7 @25MW, PG4 @125MW [WEBSMS] | CMIN
11/30/2023 12:38:06 PM | [NSO Update] Visayas Grid-11/30/2023 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2713MW, PK=2225MW, RR=94MW, NetOpMargin: PM=394, EVE=240 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @319MW [WEBSMS] | CVIS
11/30/2023 11:33:55 AM | Mindanao Grid-11/30/2023 11:37: Asiga HEPP with 7.97MW load Tripped at 1129H. (Unplanned Outage). [WEBSMS] | CMIN
11/30/2023 10:52:27 AM | Mindanao Grid-11/30/2023 10:55: WMPC DG7 Online as RPS at 1051H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/30/2023 10:48:40 AM | Mindanao Grid-11/30/2023 10:51: Asiga HEPP Online at 1036H. (Unplanned Outage). [WEBSMS] | CMIN
11/30/2023 10:47:51 AM | Mindanao Grid-11/30/2023 10:51: Asiga HEPP with 8MW load tripped at 1012H. (Unplanned Outage). [WEBSMS] | CMIN
11/30/2023 10:20:43 AM | Mindanao Grid-11/30/2023 10:23: Kauswagan-GNPK 230KV L3 de-energized at 0914H to conduct OFR & UFR testing, and inspection/testing of RTU, meters & transmitters of U3. Planned Outage requested by GNPK management. [WEBSMS] | CMIN
11/30/2023 10:19:24 AM | Mindanao Grid-11/30/2023 10:22: WMPC DG4 Online as RPS at 0850H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/30/2023 9:50:26 AM | Mindanao Grid-11/30/2023 09:53: PG4 U3 Online at 0940H. From Reserved shutdown. [WEBSMS] | CMIN
11/30/2023 9:26:40 AM | Mindanao Grid-11/30/2023 09:29: MDP(Supreme Mati) Online at 0900H. Follow RTD. [WEBSMS] | CMIN
11/30/2023 9:03:14 AM | Mindanao Grid-11/30/2023 09:06: Baloi SS 138KV 100MVA T3 de-energized at 0815H. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
11/30/2023 8:32:23 AM | Visayas Grid-11/30/2023 08:32: Carcon-Sangi 34.5 KV L3 de-energized at 0830H. Planned Outage [WEBSMS] | CVIS
11/30/2023 8:20:37 AM | Mindanao Grid-11/30/2023 08:23: Baloi SS 100MVA Power Transformer no. 3 deenergized at 0815H. Planned Outage. [WEBSMS] | CMIN
11/30/2023 8:19:41 AM | Visayas Grid-11/30/2023 08:19: 2nd lift-Sangi 34.5 KV line de-energized at 0808H. Planned Outage [WEBSMS] | CVIS
11/30/2023 8:18:38 AM | Luzon Grid-11/30/2023 08:18: Tayabas PCB 9-06CB08TAY was de-energized at 0817H. (Planned Outage) [WEBSMS] | CLUZ
11/30/2023 8:04:53 AM | Mindanao Grid-11/30/2023 08:08: ASIGA HEPP with 7.83MW load tripped at 0756H. (Unplanned Outage). [WEBSMS] | CMIN
11/30/2023 8:03:29 AM | Mindanao Grid-11/30/2023 08:06: ASIGA HEPP Online at 0736H. (Unplanned Outage) From FO. [WEBSMS] | CMIN
11/30/2023 7:26:26 AM | Mindanao Grid-11/30/2023 07:29: WMPC DG6 shutdown at 0723H. Follow RTD. [WEBSMS] | CMIN
11/30/2023 7:25:41 AM | Mindanao Grid-11/30/2023 07:28: WMPC DG5 shutdown at 0723H. Follow RTD. [WEBSMS] | CMIN
11/30/2023 7:15:38 AM | Mindanao Grid-11/30/2023 07:18: Asiga HEPP with 7.78MW Load tripped at 0707H. (Unplanned Outage). [WEBSMS] | CMIN
11/30/2023 7:07:55 AM | Mindanao Grid-11/30/2023 07:11: MN2 U3 Shutdown at 0700H. (Planned Outage). PMS. [WEBSMS] | CMIN
11/30/2023 6:52:23 AM | Mindanao Grid-11/30/2023 06:55: WMPC DG6 Online at 0600H. Follow RTD. [WEBSMS] | CMIN
11/30/2023 6:51:38 AM | Mindanao Grid-11/30/2023 06:54: WMPC DG5 Online at 0559H. Follow RTD. [WEBSMS] | CMIN
11/30/2023 6:49:26 AM | Luzon Grid-11/30/2023 06:49: Taytay-Malaya 230kV line 2 was de-energized at 0648H. (Planned Outage) [WEBSMS] | CLUZ
11/30/2023 6:37:23 AM | Luzon Grid-11/30/2023 06:37: Calaca-Binan 230kV line was de-energized at 0634H. (Unplanned Outage) [WEBSMS] | CLUZ
11/30/2023 5:46:27 AM | [NSO Update] Mindanao Grid-11/30/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3310MW, PK=2184MW, RR=88MW, NetOpMargin: AM=1038, PM=901, EVE=965 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @125MW, AG5 @27MW, AG6 @155MW, AG7 @25MW, PG4 @90MW [WEBSMS] | CMIN
11/30/2023 5:44:15 AM | [NSO Update] Visayas Grid-11/30/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2620MW, PK=2252MW, RR=93MW, NetOpMargin: AM=275, PM=189, EVE=251 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @319MW [WEBSMS] | CVIS
11/30/2023 5:41:19 AM | [NSO Update] Luzon Grid-11/30/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14387MW, PK=10998MW, RR=432MW, NetOpMargin: AM=2957, PM=2655, EVE=2396 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 300MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/30/2023 4:26:47 AM | [NSO Update] Luzon Grid-11/30/2023 04:26: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting Southern Luzon, Visayas, Mindanao. [WEBSMS] | CLUZ
11/30/2023 4:26:41 AM | [NSO Update] Mindanao Grid-11/30/2023 04:29: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting Southern Luzon, Visayas, Mindanao. [WEBSMS] | CMIN
11/30/2023 4:26:23 AM | [NSO Update] Visayas Grid-11/30/2023 04:26: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Easterlies affecting Southern Luzon, Visayas, Mindanao. [WEBSMS] | CVIS
11/29/2023 11:37:50 PM | Luzon Grid-11/29/2023 23:38: SLPGC Unit 2 online at 2335H (Unplanned Outage) [WEBSMS] | CLUZ
11/29/2023 9:18:57 PM | Mindanao Grid-11/29/2023 21:22: Supreme Mati(MDP) cut out at 2105H. Follow RTD. [WEBSMS] | CMIN
11/29/2023 9:16:15 PM | Luzon Grid-11/29/2023 21:16: For info: Batangas 300MVA T04 and T05 on split configuration at 2107H. San Lorenzo-Sta Rita 230kV Bus 1 and 2 tie breakers were closed at 2110H, looping Sta Rita and San Lorenzo. [WEBSMS] | CLUZ
11/29/2023 9:14:10 PM | Mindanao Grid-11/29/2023 21:17: WMPC DG04 shutdown at 2113H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/29/2023 6:10:08 PM | Luzon Grid-11/29/2023 18:10: Bay-Makban E 69kV Line restored at 1807H (Planned Outage) [WEBSMS] | CLUZ
11/29/2023 6:08:09 PM | Luzon Grid-11/29/2023 18:08: Bay-Makban Plant Ormat 69kV Line restored at 1805H (Planned Outage) [WEBSMS] | CLUZ
11/29/2023 5:55:47 PM | [NSO Update] Mindanao Grid-11/29/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3251MW, PK=2215MW, RR=91MW, NetOpMargin: EVE=945 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @27MW, AG6 @155MW, AG7 @25MW, PG4 @90MW [WEBSMS] | CMIN
11/29/2023 5:37:55 PM | [NSO Update] Visayas Grid-11/29/2023 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2580MW, PK=2254MW, RR=97MW, NetOpMargin: EVE=230 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @319MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/29/2023 5:36:05 PM | [NSO Update] Luzon Grid-11/29/2023 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13543MW, PK=10659MW, RR=425MW, NetOpMargin: EVE=2459 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 300MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/29/2023 5:22:39 PM | Visayas Grid-11/29/2023 17:22: 2nd Lift - Sangi 34.5 kV Line energized at 1719H. Planned Outage [WEBSMS] | CVIS
11/29/2023 4:53:30 PM | Visayas Grid-11/29/2023 16:53: Carcon - Sangi 34.5 kV Line 3 energized at 1652H. (Planned Outage) [WEBSMS] | CVIS
11/29/2023 4:53:06 PM | Luzon Grid-11/29/2023 16:53: Taytay-Malaya 230kV Line 1 restored at 1652H (Planned Outage) [WEBSMS] | CLUZ
11/29/2023 4:18:54 PM | Luzon Grid-11/29/2023 16:19: Ambuklao SS 230kV Bus 1 restored at 1618H (Planned Outage) [WEBSMS] | CLUZ
11/29/2023 4:14:11 PM | Mindanao Grid-11/29/2023 16:17: WMPC DG06 shutdown at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/29/2023 12:46:08 PM | [NSO Update] Mindanao Grid-11/29/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3311MW, PK=2328MW, RR=93MW, NetOpMargin: PM=890, EVE=934 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @27MW, AG6 @155MW, AG7 @25MW, PG4 @90MW [WEBSMS] | CMIN
11/29/2023 12:44:32 PM | [NSO Update] Visayas Grid-11/29/2023 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2605MW, PK=2279MW, RR=94MW, NetOpMargin: PM=232, EVE=187 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @115.5MW, LEYTE A @319MW [WEBSMS] | CVIS
11/29/2023 12:41:41 PM | [NSO Update] Luzon Grid-11/29/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13825MW, PK=11111MW, RR=439MW, NetOpMargin: PM=2275, EVE=2180 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 310MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/29/2023 11:57:12 AM | Luzon Grid-11/29/2023 11:57: Bay-Makban E 69kV line was de-energized at 1156H. (Planned Outage) [WEBSMS] | CLUZ
11/29/2023 10:52:39 AM | Mindanao Grid-11/29/2023 10:56: WMPC DG6 Online as RPS at 1047H. Cut-in as RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/29/2023 10:01:11 AM | Luzon Grid-11/29/2023 10:01: Subic(Hanjin) 230kV Bus 1 was de-energized at 0958H. (Planned Outage) [WEBSMS] | CLUZ
11/29/2023 9:11:06 AM | Mindanao Grid-11/29/2023 09:14: Supreme Mati(MDP) Online at 0901H. Follow RTD. [WEBSMS] | CMIN
11/29/2023 8:54:07 AM | Mindanao Grid-11/29/2023 08:57: WMPC DG4 Online as RPS at 0850H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/29/2023 8:14:08 AM | Mindanao Grid-11/29/2023 08:17: Davao - Bunawan 138KV Line 1 deenergized at 0802H. Planned Outage. [WEBSMS] | CMIN
11/29/2023 7:00:26 AM | Luzon Grid-11/29/2023 07:00: Bay-Makban Plant Ormat 69kV line was de-energized at 0658H. (Planned Outage) [WEBSMS] | CLUZ
11/29/2023 6:45:22 AM | Luzon Grid-11/29/2023 06:45: Ambuklao Substation 230kV Bus 1 was de-energized at 0643H. (Planned Outage) [WEBSMS] | CLUZ
11/29/2023 6:44:05 AM | Luzon Grid-11/29/2023 06:44: Taytay-Malaya 230kV line 1 was de-energized at 0642H. (Planned Outage) [WEBSMS] | CLUZ
11/29/2023 6:25:57 AM | Luzon Grid-11/29/2023 06:26: Ilijan 500kV Bus 1 was de-energized at 0622H. (To facilitate the tapping of Ilijan-EERI 500kV line) [WEBSMS] | CLUZ
11/29/2023 5:45:24 AM | [NSO Update] Mindanao Grid-11/29/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3391MW, PK=2307MW, RR=90MW, NetOpMargin: AM=994, PM=1018, EVE=925 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @27MW, AG6 @155MW, AG7 @25MW, PG4 @90MW [WEBSMS] | CMIN
11/29/2023 5:44:16 AM | [NSO Update] Visayas Grid-11/29/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2546MW, PK=2218MW, RR=93MW, NetOpMargin: AM=235, PM=180, EVE=254 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 310MW [WEBSMS] | CVIS
11/29/2023 5:42:53 AM | [NSO Update] Luzon Grid-11/29/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13842MW, PK=10782MW, RR=422MW, NetOpMargin: AM=2638, PM=2257, EVE=2025 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 300MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/29/2023 4:08:24 AM | [NSO Update] Mindanao Grid-11/29/2023 04:11: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting Southern Luzon and Visayas. [WEBSMS] | CMIN
11/29/2023 4:08:09 AM | [NSO Update] Visayas Grid-11/29/2023 04:08: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting Southern Luzon and Visayas. [WEBSMS] | CVIS
11/29/2023 4:07:47 AM | [NSO Update] Luzon Grid-11/29/2023 04:08: Weather Update: Northeast Monsoon affecting Northern Luzon. Easterlies affecting Southern Luzon and Visayas. [WEBSMS] | CLUZ
11/29/2023 3:05:02 AM | Visayas Grid-11/29/2023 03:05: Ormoc-Maasin-Ubay 138 KV Line 1 and 2 tripped at 0247H. [WEBSMS] | CVIS
11/28/2023 11:45:42 PM | Luzon Grid-11/28/2023 23:45: San Jose - Angat 115kV Line 4 restored at 2345H (Unplanned Outage) [WEBSMS] | CLUZ
11/28/2023 10:49:45 PM | Luzon Grid-11/28/2023 22:50: San Jose - Angat 115kV Line 4 auto-tripped at 2247H (Unplanned Outage) [WEBSMS] | CLUZ
11/28/2023 9:16:06 PM | Mindanao Grid-11/28/2023 21:19: WMPC DG04 shutdown at 2113H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/28/2023 7:47:06 PM | Luzon Grid-11/28/2023 19:47: For info: The commissioning and energization of New Hermosa SS PCBs 5-03CB08HER, 5-05CB04HER, 5-05CB24HER, 5-05CB08HER, and associated equipment , New 69kV Line Protections, and New 69kV Bus 1 and 69kV Bus 2 Protections was completed at 1941H. [WEBSMS] | CLUZ
11/28/2023 6:58:29 PM | Luzon Grid-11/28/2023 18:58: San Gabriel shutdown at 1855H. (Planned Outage) [WEBSMS] | CLUZ
11/28/2023 5:50:24 PM | [NSO Update] Mindanao Grid-11/28/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3279MW, PK=2351MW, RR=87MW, NetOpMargin: EVE=841 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @27MW, AG6 @155MW, AG7 @25MW, PG4 @90MW [WEBSMS] | CMIN
11/28/2023 5:48:09 PM | [NSO Update] Visayas Grid-11/28/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2674MW, PK=2323MW, RR=97MW, NetOpMargin: EVE=254 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 120MW, Leyte A @ 303MW [WEBSMS] | CVIS
11/28/2023 5:45:23 PM | [NSO Update] Luzon Grid-11/28/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13875MW, PK=10748MW, RR=435MW, NetOpMargin: EVE=2692 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 185MW, Calaca 2 @ 175MW, Masinloc 3 @ 300MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/28/2023 5:34:32 PM | Luzon Grid-11/28/2023 17:34: Lumban-Gumaca 230kV line 1 was restored at 1733H. (Planned Outage) [WEBSMS] | CLUZ
11/28/2023 5:21:50 PM | Mindanao Grid-11/28/2023 17:25: Baloi - Agus5 138kV line energized at 1718H. (Planned Outage) [WEBSMS] | CMIN
11/28/2023 5:13:00 PM | Visayas Grid-11/28/2023 17:13: 2nd Lift - Sangi 34.5 kV Line energized at 1712H. (Planned Outage) [WEBSMS] | CVIS
11/28/2023 4:56:08 PM | Mindanao Grid-11/28/2023 16:59: Agus 5 HEP 138kV Line 2 and Baloi - Agus5 138kV line de-energized at 1650H. (Planned Outage) [WEBSMS] | CMIN
11/28/2023 4:51:58 PM | Visayas Grid-11/28/2023 16:52: Carcon - Sangi 34.5 kV Line 3 energized at 1651H. (Planned Outage) [WEBSMS] | CVIS
11/28/2023 4:48:49 PM | Luzon Grid-11/28/2023 16:49: Dasmarinas-Ternate 115kV line(Customer Owned and Maintained line) was energized at 1646H. (Planned Outage) [WEBSMS] | CLUZ
11/28/2023 4:16:10 PM | Mindanao Grid-11/28/2023 16:19: WMPC DG06 shutdown at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/28/2023 2:39:37 PM | Luzon Grid-11/28/2023 14:39: Subic(Hanjin) 230kV Bus 2 was energized at 1438H. (Planned Outage) [WEBSMS] | CLUZ
11/28/2023 2:21:50 PM | Luzon Grid-11/28/2023 14:22: For info: Makban B-Makban C 230kV tie line and Makban C Unit 5 Main Transformer were energized at 1417H and 1418H respectively. [WEBSMS] | CLUZ
11/28/2023 12:45:05 PM | [NSO Update] Luzon Grid-11/28/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14432MW, PK=10921MW, RR=446MW, NetOpMargin: PM=3066, EVE=3004 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @180MW, CLC2 @175MW, MSLC3 @300MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/28/2023 12:42:23 PM | [NSO Update] Mindanao Grid-11/28/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3364MW, PK=2350MW, RR=88MW, NetOpMargin: PM=926, EVE=955 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @27MW, AG6 @155MW, AG7 @25MW, PG4 @90MW [WEBSMS] | CMIN
11/28/2023 12:39:31 PM | [NSO Update] Visayas Grid-11/28/2023 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2608MW, PK=2256MW, RR=94MW, NetOpMargin: PM=258, EVE=253 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @300MW [WEBSMS] | CVIS
11/28/2023 10:54:33 AM | Mindanao Grid-11/28/2023 10:57: WMPC DG06 online at 1050H. Online as RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/28/2023 9:30:38 AM | Luzon Grid-11/28/2023 09:30: Dasmarinas-Ternate 115kV line(Customer Owned and Maintained Line) was de-energized at 0922H. (Planned Outage) [WEBSMS] | CLUZ
11/28/2023 8:53:34 AM | Mindanao Grid-11/28/2023 08:57: WMPC DG04 online at 0851H. Online as RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/28/2023 8:06:36 AM | Luzon Grid-11/28/2023 08:06: Subic(Hanjin) 230kV Bus 2 was de-energized at 0804H. (Planned Outage) [WEBSMS] | CLUZ
11/28/2023 7:15:14 AM | Mindanao Grid-11/28/2023 07:18: MINERGY COAL (MCC) Unit 1 online at 0708H. Unplanned Outage. [WEBSMS] | CMIN
11/28/2023 7:09:44 AM | Mindanao Grid-11/28/2023 07:13: MANOLO FORTICH 2 Unit 2 with 1.3MW load shutdown at 0700H - PMS. (Planned Outage) [WEBSMS] | CMIN
11/28/2023 7:05:11 AM | Luzon Grid-11/28/2023 07:05: Lumban-Gumaca 230kV line 1 - de-energized at 0704H (Planned Outage) [WEBSMS] | CLUZ
11/28/2023 6:25:44 AM | Luzon Grid-11/28/2023 06:25: Correction: Binan 300MVA T01 shutdown at 0615H. (Planned Outage) [WEBSMS] | CLUZ
11/28/2023 6:21:57 AM | [NSO Update] Mindanao Grid-11/28/2023 06:25: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3372MW, PK=2252MW, RR=85MW, NetOpMargin: AM=1035, PM=1022, EVE=962 Highest Unit O/L: GNPK 1&2 @668MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @27MW, AG6 @155MW, AG7 @25MW, PG4 @90MW [WEBSMS] | CMIN
11/28/2023 6:20:55 AM | Luzon Grid-11/28/2023 06:21: Binan 300MVA T01 - tripped at 0615H. (Unplanned Outage) [WEBSMS] | CLUZ
11/28/2023 5:56:29 AM | [NSO Update] Visayas Grid-11/28/2023 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2507MW, PK=2225MW, RR=93MW, NetOpMargin: AM=188, PM=220, EVE=284 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @300MW [WEBSMS] | CVIS
11/28/2023 5:55:20 AM | [NSO Update] Luzon Grid-11/28/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14649MW, PK=10759MW, RR=440MW, NetOpMargin: AM=3450, PM=3437, EVE=3272 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @150MW, CLC2 @175MW, MSLC3 @300MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/28/2023 5:21:11 AM | [NSO Update] Luzon Grid-11/28/2023 05:21: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
11/28/2023 5:20:29 AM | [NSO Update] Mindanao Grid-11/28/2023 05:23: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
11/28/2023 5:20:02 AM | [NSO Update] Visayas Grid-11/28/2023 05:20: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
11/28/2023 5:11:42 AM | Luzon Grid-11/28/2023 05:11: Las Pinas (Zapote) 300MVA T01 restored at 0509H (Planned Outage) [WEBSMS] | CLUZ
11/28/2023 5:08:01 AM | Luzon Grid-11/28/2023 05:08: Dasmarinas-Las Pinas 230kV Line 1 restored at 0504H (Planned Outage) [WEBSMS] | CLUZ
11/28/2023 1:08:53 AM | Luzon Grid-11/28/2023 01:09: San Gabriel online at 0107H (LNG commissioning) [WEBSMS] | CLUZ
11/28/2023 12:00:40 AM | Luzon Grid-11/28/2023 00:00: SBPL shutdown at 2359H (Unplanned Outage) [WEBSMS] | CLUZ
11/27/2023 11:40:35 PM | Luzon Grid-11/27/2023 23:40: San Gabriel shutdown at 2339H (LNG commissioing) [WEBSMS] | CLUZ
11/27/2023 9:15:38 PM | Luzon Grid-11/27/2023 21:15: Las Pinas 230kV Bus 2 restored at 2115H (Planned Outage) [WEBSMS] | CLUZ
11/27/2023 9:07:06 PM | Mindanao Grid-11/27/2023 21:10: SPC Mati shutdown at 2105H. MO Dispatch [WEBSMS] | CMIN
11/27/2023 7:25:39 PM | Mindanao Grid-11/27/2023 19:29: SPC Mati tripped with 4.5MW load at 1811H due to reverse power indication. (unplanned outage). Cut in @ 1815H. SPC Mati tripped again with 4.5MW load at 1831H due to reverse power indication. Cut in @ 1844H. (Unplanned outage). [WEBSMS] | CMIN
11/27/2023 6:58:06 PM | [NSO Update] Mindanao Grid-11/27/2023 19:01: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1847H with power going to Visayas. (Planned Outage) [WEBSMS] | CMIN
11/27/2023 6:57:43 PM | [NSO Update] Visayas Grid-11/27/2023 18:57: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1847H with power going to Visayas. (Planned Outage) [WEBSMS] | CVIS
11/27/2023 6:02:21 PM | Visayas Grid-11/27/2023 18:02: 2nd Lift - Sangi 34.5 kV Line energized at 1801H. (Planned Outage) [WEBSMS] | CVIS
11/27/2023 5:57:33 PM | [NSO Update] Luzon Grid-11/27/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14511MW, PK=9671MW, RR=400MW, NetOpMargin: EVE=4440 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @160MW, CLC2 @175MW, MSLC3 @300MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/27/2023 5:53:43 PM | [NSO Update] Mindanao Grid-11/27/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3291MW, PK=2253MW, RR=83MW, NetOpMargin: EVE=955 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @45MW, AG6 @155MW, AG7 @25MW, PG4 @90MW [WEBSMS] | CMIN
11/27/2023 5:50:39 PM | Luzon Grid-11/27/2023 17:50: Nagsaag-San Manuel 230kV Line 2 energized at 1750H (Planned Outage) [WEBSMS] | CLUZ
11/27/2023 5:33:10 PM | [NSO Update] Visayas Grid-11/27/2023 17:33: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2471MW, PK=2118MW, RR=97MW, NetOpMargin: EVE=256 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @120.5MW, LEYTE A @310MW [WEBSMS] | CVIS
11/27/2023 5:32:39 PM | Visayas Grid-11/27/2023 17:32: Carcon - Sangi 34.5 kV Line 3 energized at 1730H. (Planned Outage) [WEBSMS] | CVIS
11/27/2023 5:28:47 PM | Mindanao Grid-11/27/2023 17:32: Lamsan Power Corp tripped with 13.5MW load at 1707H with Indication: Directional Earth Fault. Cut in back at 1712H (Unplanned outage) [WEBSMS] | CMIN
11/27/2023 4:39:54 PM | Visayas Grid-11/27/2023 16:40: Magdugo - Dumanjug 230 kV Line 2 energized at 1639H. (Planned Outage) [WEBSMS] | CVIS
11/27/2023 3:58:48 PM | Mindanao Grid-11/27/2023 16:02: Bunawan SS 230kV Bus 2 energized at 1552H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
11/27/2023 12:57:02 PM | [NSO Update] Visayas Grid-11/27/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2449MW, PK=1998MW, RR=94MW, NetOpMargin: PM=357, EVE=264 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @305MW [WEBSMS] | CVIS
11/27/2023 12:56:53 PM | Luzon Grid-11/27/2023 12:57: Laoag-Pagudpud Wind Farm 115kV Line restored at 1255H (Planned Outage) [WEBSMS] | CLUZ
11/27/2023 12:52:58 PM | [NSO Update] Luzon Grid-11/27/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15153MW, PK=9198MW, RR=414MW, NetOpMargin: PM=5541, EVE=4608 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @160MW, CLC2 @175MW, MSLC3 @300MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/27/2023 12:34:39 PM | [NSO Update] Mindanao Grid-11/27/2023 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3314MW, PK=2069MW, RR=78MW, NetOpMargin: PM=1167, EVE=1049 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @45MW, AG6 @92MW, AG7 @25MW, PG4 @90MW [WEBSMS] | CMIN
11/27/2023 9:55:34 AM | [NSO Update] Visayas Grid-11/27/2023 09:55: Ormoc-Naga 350kV HVDC (Visayas-Luzon) auto-blocked at 0941H from reverse power direction. Lowest Visayas frequency recorded at 59.112Hz [WEBSMS] | CVIS
11/27/2023 9:54:02 AM | [NSO Update] Luzon Grid-11/27/2023 09:54: Ormoc-Naga 350kV HVDC (Visayas-Luzon) auto-blocked at 0941H from reverse power direction. Lowest Visayas frequency recorded at 59.112Hz [WEBSMS] | CLUZ
11/27/2023 9:21:07 AM | Visayas Grid-11/27/2023 09:21: Sangi-2nd lift 34.5KV line de-energized at 0811H. Sangi - Carcon 34.5 KV line 3 de-energized at 0844H. (Planned Outage) [WEBSMS] | CVIS
11/27/2023 9:11:01 AM | Visayas Grid-11/27/2023 09:11: Cebu SS 300MVA TR2 230/138/13.8 KV de-energized at 0903H. Under Test & Commissioning. [WEBSMS] | CVIS
11/27/2023 8:46:22 AM | Visayas Grid-11/27/2023 08:46: Mandaue SS 138KV Bus 1 de-energized at 0841H. (Planned Outage) [WEBSMS] | CVIS
11/27/2023 8:37:03 AM | Visayas Grid-11/27/2023 08:37: Mandaue SS 100MVA 138/69/13.8KV TR1 de-energized at 0832H. (Planned Outage) [WEBSMS] | CVIS
11/27/2023 8:15:59 AM | Mindanao Grid-11/27/2023 08:19: Bunawan SS 230kV Bus 2 deenergized at 0804H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
11/27/2023 7:20:38 AM | Luzon Grid-11/27/2023 07:20: Laoag-Pagudpud Wind Farm 115kV Line de-energized at 0717H (Planned Outage) [WEBSMS] | CLUZ
11/27/2023 6:35:52 AM | Luzon Grid-11/27/2023 06:36: Nagsaag-San Manuel 230kV Line 2 de-energized at 0635H (Planned Outage) [WEBSMS] | CLUZ
11/27/2023 6:15:51 AM | [NSO Update] Mindanao Grid-11/27/2023 06:19: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3326MW, PK=2000MW, RR=78MW, NetOpMargin: AM=1248, PM=1217, EVE=1118 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @45MW, AG6 @92MW, AG7 @25MW, PG4 @90MW [WEBSMS] | CMIN
11/27/2023 6:13:28 AM | [NSO Update] Visayas Grid-11/27/2023 06:13: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2617MW, PK=1718MW, RR=93MW, NetOpMargin: AM=806, PM=805, EVE=370 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @ 108.5MW, Leyte A @ 300MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
11/27/2023 6:06:56 AM | [NSO Update] Luzon Grid-11/27/2023 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15211MW, PK=8683MW, RR=400MW, NetOpMargin: AM=6128, PM=5889, EVE=4739 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 160MW, Calaca 2 @ 175MW, Masinloc 3 @ 300MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/27/2023 4:40:03 AM | [NSO Update] Mindanao Grid-11/27/2023 04:43: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
11/27/2023 4:39:28 AM | [NSO Update] Luzon Grid-11/27/2023 04:39: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
11/27/2023 4:39:05 AM | [NSO Update] Visayas Grid-11/27/2023 04:39: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
11/27/2023 4:25:52 AM | Visayas Grid-11/27/2023 04:26: 230KV Magdugo-Dumanjug line 2 de-energized at 0419H. ( Planned Outage ) [WEBSMS] | CVIS
11/26/2023 11:15:41 PM | Mindanao Grid-11/26/2023 23:19: SUPREME POWER Mati (MDP) cut-out at 2105H. End of RTD. [WEBSMS] | CMIN
11/26/2023 9:04:22 PM | Luzon Grid-11/26/2023 21:04: Sta Rita 30 online at 2103H (Planned Outage) [WEBSMS] | CLUZ
11/26/2023 8:21:14 PM | Luzon Grid-11/26/2023 20:21: San Jose 300MVA T01 looped at 2019H, T03 unlooped at 2020H (Planned Outage) [WEBSMS] | CLUZ
11/26/2023 8:10:39 PM | Luzon Grid-11/26/2023 20:10: San Jose-Hermosa 230kV Line restored at 2010H (Planned Outage) [WEBSMS] | CLUZ
11/26/2023 7:57:19 PM | Mindanao Grid-11/26/2023 20:00: Manolo Fortich 2 (MN2) Unit 4 tripped with 1MW load at 1908H. Cause: Insufficient Water Supply. (Unplanned Outage) [WEBSMS] | CMIN
11/26/2023 7:53:47 PM | Mindanao Grid-11/26/2023 19:57: Manolo Fortich 2 (MN2) Unit 4 cut-in at 1836H. (Unplanned Outage) [WEBSMS] | CMIN
11/26/2023 6:32:32 PM | Luzon Grid-11/26/2023 18:32: SCPC 2 online at 1831H (Unplanned Outage) [WEBSMS] | CLUZ
11/26/2023 6:07:42 PM | Luzon Grid-11/26/2023 18:07: Bolo-Cayanga 230kV Line 1 restored at 1807H (Planned Outage) [WEBSMS] | CLUZ
11/26/2023 5:53:07 PM | [NSO Update] Mindanao Grid-11/26/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3296MW, PK=2021MW, RR=78MW, NetOpMargin: EVE=1198 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @129MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @45MW, AG6 @155MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/26/2023 5:49:27 PM | [NSO Update] Visayas Grid-11/26/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2406MW, PK=2008MW, RR=97MW, NetOpMargin: EVE=301 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @ 108.5MW, Leyte A @ 248MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
11/26/2023 5:43:45 PM | [NSO Update] Luzon Grid-11/26/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14163MW, PK=9087MW, RR=356MW, NetOpMargin: EVE=4720 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 160MW, Calaca 2 @ 175MW, Masinloc 3 @ 300MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/26/2023 5:29:42 PM | Luzon Grid-11/26/2023 17:29: Daraga-Bacman 230kV Line 1 restored at 1729H (Planned Outage) [WEBSMS] | CLUZ
11/26/2023 4:07:21 PM | Mindanao Grid-11/26/2023 16:10: Butuan - Placer 138 KV Line 2 restored at 1605H. Planned Outage. [WEBSMS] | CMIN
11/26/2023 3:39:48 PM | Mindanao Grid-11/26/2023 15:43: Manolo - Maramag 138KV Line 1 restored at 1536H. Planned Outage. [WEBSMS] | CMIN
11/26/2023 3:38:26 PM | Mindanao Grid-11/26/2023 15:41: Bunawan SS 230KV Bus 1 restored at 1516H. Planned Outage. [WEBSMS] | CMIN
11/26/2023 1:12:48 PM | Mindanao Grid-11/26/2023 13:16: Manolo - Maramag 138KV Line 1 deenergized at 1303H. Planned Outage. [WEBSMS] | CMIN
11/26/2023 1:02:34 PM | Mindanao Grid-11/26/2023 13:05: Pulangi 4 Unit 2 cut-in at 1300H. (Planned Outage) [WEBSMS] | CMIN
11/26/2023 12:59:01 PM | Luzon Grid-11/26/2023 12:59: San Jose 300MVA T01 looped at 1248H, T03 unlooped at 1251H, Planned Outage. [WEBSMS] | CLUZ
11/26/2023 12:56:09 PM | Luzon Grid-11/26/2023 12:56: San Jose-Hermosa 230kV Line de-energized at 1254H (Planned Outage) [WEBSMS] | CLUZ
11/26/2023 12:45:37 PM | [NSO Update] Mindanao Grid-11/26/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3357MW, PK=1827MW, RR=78MW, NetOpMargin: PM=1452, EVE=1264 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @129MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @45MW, AG6 @155MW, AG7 @25MW, PG4 @90MW [WEBSMS] | CMIN
11/26/2023 12:44:39 PM | [NSO Update] Visayas Grid-11/26/2023 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2435MW, PK=1785MW, RR=94MW, NetOpMargin: PM=556, EVE=350 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 108.5MW, Leyte A @ 268MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
11/26/2023 12:43:40 PM | [NSO Update] Luzon Grid-11/26/2023 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14777MW, PK=8548MW, RR=356MW, NetOpMargin: PM=5874, EVE=4879 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 180MW, Calaca 2 @ 175MW, Masinloc 3 @ 300MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/26/2023 12:06:50 PM | Mindanao Grid-11/26/2023 12:10: Pulangi 4 Unit 1 cut-in at 1158H. (Planned Outage) [WEBSMS] | CMIN
11/26/2023 11:34:10 AM | Luzon Grid-11/26/2023 11:34: Las Pinas (Zapote) 300MVA T03 restored at 1132H (Planned Outage) [WEBSMS] | CLUZ
11/26/2023 11:33:05 AM | Luzon Grid-11/26/2023 11:33: Las Pinas (Zapote) 300MVA T02 restored at 1131H (Planned Outage) [WEBSMS] | CLUZ
11/26/2023 11:27:28 AM | Luzon Grid-11/26/2023 11:27: Las Pinas 230kV Bus 1 restored at 1127H (Planned Outage) [WEBSMS] | CLUZ
11/26/2023 11:13:52 AM | Mindanao Grid-11/26/2023 11:17: SUPREME POWER Mati (MDP) cut-in at 0900H. MO dispatched (RTD). [WEBSMS] | CMIN
11/26/2023 10:50:51 AM | Luzon Grid-11/26/2023 10:51: Malolos-Hermosa 230kV Line restored at 1050H (Planned Outage) [WEBSMS] | CLUZ
11/26/2023 8:13:32 AM | Mindanao Grid-11/26/2023 08:16: Bunawan SS 230KV Bus 1 deenergized at 0802H. Planned Outage. [WEBSMS] | CMIN
11/26/2023 8:11:18 AM | Mindanao Grid-11/26/2023 08:14: (Correction) Pulangi 4 Unit 1 shutdown at 0605H to facilitate drawdown activity (GOMP). (Planned Outage) [WEBSMS] | CMIN
11/26/2023 8:10:52 AM | Mindanao Grid-11/26/2023 08:14: (Correction) Pulangi 4 Unit 2 shutdown at 0604H to facilitate drawdown activity (GOMP). (Planned Outage) [WEBSMS] | CMIN
11/26/2023 8:10:24 AM | Mindanao Grid-11/26/2023 08:13: (Correction) Pulangi 4 Unit 3 shutdown at 0601H to facilitate drawdown activity (GOMP). (Planned Outage) [WEBSMS] | CMIN
11/26/2023 8:09:13 AM | Mindanao Grid-11/26/2023 08:12: (Correction) Pulangi 4 Unit 1 shutdown at 0601H to facilitate drawdown activity (GOMP). (Planned Outage) [WEBSMS] | CMIN
11/26/2023 7:57:12 AM | Luzon Grid-11/26/2023 07:57: Sta. Rita 30 shutdown at 0755H (Planned Outage) [WEBSMS] | CLUZ
11/26/2023 7:25:23 AM | Mindanao Grid-11/26/2023 07:28: Pulangi 4 Unit 1 shutdown at 0605H to facilitate drawdown activity (GOMP). (Unplanned Outage) [WEBSMS] | CMIN
11/26/2023 7:24:53 AM | Mindanao Grid-11/26/2023 07:28: Pulangi 4 Unit 2 shutdown at 0602H to facilitate drawdown activity (GOMP). (Unplanned Outage) [WEBSMS] | CMIN
11/26/2023 7:24:31 AM | Mindanao Grid-11/26/2023 07:27: Pulangi 4 Unit 3 shutdown at 0601H to facilitate drawdown activity (GOMP). (Unplanned Outage) [WEBSMS] | CMIN
11/26/2023 7:16:47 AM | Mindanao Grid-11/26/2023 07:20: Maramag-Pulangui 4 HEP Line 3 deenergized at 0600H. Planned Outage. [WEBSMS] | CMIN
11/26/2023 7:15:26 AM | Mindanao Grid-11/26/2023 07:18: Maramag-Pulangui 4 HEP 138KV Line 2 deenergized at 0603H. Planned Outage. [WEBSMS] | CMIN
11/26/2023 7:08:52 AM | Mindanao Grid-11/26/2023 07:12: MARAMAG-PULANGUI 4 HEP 138kv Line 1 deenergized at 0605H. Planned Outage. [WEBSMS] | CMIN
11/26/2023 6:59:38 AM | Mindanao Grid-11/26/2023 07:03: Butuan-Placer 138KV Line 2 deenergized at 0649H. Planned Outage. [WEBSMS] | CMIN
11/26/2023 6:41:36 AM | Luzon Grid-11/26/2023 06:41: Nagsaag SS 500kV Bus 2 at 0641H (Planned Outage) [WEBSMS] | CLUZ
11/26/2023 6:23:44 AM | [NSO Update] Mindanao Grid-11/26/2023 06:27: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0620H from forward power direction. (Planned Outage) [WEBSMS] | CMIN
11/26/2023 6:23:30 AM | [NSO Update] Visayas Grid-11/26/2023 06:23: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0620H from forward power direction. (Planned Outage) [WEBSMS] | CVIS
11/26/2023 6:11:26 AM | Luzon Grid-11/26/2023 06:11: SCPC 2 shutdown at 0607H (Unplanned Outage) [WEBSMS] | CLUZ
11/26/2023 5:55:20 AM | [NSO Update] Mindanao Grid-11/26/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3271MW, PK=1803MW, RR=78MW, NetOpMargin: AM=1390, PM=1305, EVE=1097 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @129MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @45MW, AG6 @155MW, AG7 @25MW [WEBSMS] | CMIN
11/26/2023 5:54:13 AM | [NSO Update] Visayas Grid-11/26/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2558MW, PK=1760MW, RR=93MW, NetOpMargin: AM=705, PM=630, EVE=404 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @108.5MW, LEYTE A @300MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/26/2023 5:53:09 AM | [NSO Update] Luzon Grid-11/26/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14832MW, PK=8258MW, RR=356MW, NetOpMargin: AM=6218, PM=6143, EVE=5159 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @180MW, CLC2 @175MW, MSLC3 @300MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/26/2023 5:15:55 AM | [NSO Update] Mindanao Grid-11/26/2023 05:19: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting Visayas and Mindanao. [WEBSMS] | CMIN
11/26/2023 5:15:41 AM | [NSO Update] Visayas Grid-11/26/2023 05:15: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting Visayas and Mindanao. [WEBSMS] | CVIS
11/26/2023 5:15:29 AM | [NSO Update] Luzon Grid-11/26/2023 05:15: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. Easterlies affecting Visayas and Mindanao. [WEBSMS] | CLUZ
11/25/2023 11:19:21 PM | Mindanao Grid-11/25/2023 23:22: Zamboanga SS 138KV 50MVA T2 re-energized at 2259H. Part of ERC-approved MSRP Stage 1 Schedule 4. From Planned Outage / Non-GOMP [WEBSMS] | CMIN
11/25/2023 9:15:57 PM | Mindanao Grid-11/25/2023 21:19: SPC Mati shutdown at 2105H. MO Dispatch [WEBSMS] | CMIN
11/25/2023 8:21:10 PM | Mindanao Grid-11/25/2023 20:24: WMPC DG04 cut-out at 2014H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/25/2023 5:59:43 PM | [NSO Update] Mindanao Grid-11/25/2023 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3325MW, PK=2198MW, RR=80MW, NetOpMargin: EVE=1046 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @45MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
11/25/2023 5:58:45 PM | [NSO Update] Visayas Grid-11/25/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2458MW, PK=2076MW, RR=97MW, NetOpMargin: EVE=285 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @108.5MW, LEYTE A @270MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/25/2023 5:57:45 PM | [NSO Update] Luzon Grid-11/25/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14415MW, PK=9590MW, RR=383MW, NetOpMargin: EVE=4442 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @160MW, CLC2 @175MW, MSLC3 @300MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/25/2023 5:42:06 PM | Mindanao Grid-11/25/2023 17:45: MT Apo U3 cut in at 1740H. (Planned Outage) [WEBSMS] | CMIN
11/25/2023 5:04:18 PM | Luzon Grid-11/25/2023 17:04: Bayombong-Matuno HEPP 69kV Line restored at 1704H (Planned Outage) [WEBSMS] | CLUZ
11/25/2023 4:50:02 PM | Mindanao Grid-11/25/2023 16:53: Marawi SS 138KV T1 re-energized at 1631H after conducting HV testing of said transformer and verification/testing of its bushings. From Planned Outage/GOMP. [WEBSMS] | CMIN
11/25/2023 4:40:59 PM | Luzon Grid-11/25/2023 16:41: Ambuklao SS 230kV Bus 2 restored at 1640H (Planned Outage) [WEBSMS] | CLUZ
11/25/2023 4:40:06 PM | Luzon Grid-11/25/2023 16:40: San Juan (Kalayaan)-Calauan 230kV Line 2 restored at 1635H (Planned Outage) [WEBSMS] | CLUZ
11/25/2023 4:24:04 PM | Visayas Grid-11/25/2023 16:24: Cebu SS new 300 MVA TR2 energized at 1617H. (Planned Outage) [WEBSMS] | CVIS
11/25/2023 3:36:49 PM | Mindanao Grid-11/25/2023 15:40: Kidapawan - Mt APO 3 69KV line re-energized at 1513H. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
11/25/2023 3:31:36 PM | Visayas Grid-11/25/2023 15:31: Calong-calong-Toledo 138kV Line energized at 1530H. Planned Outage [WEBSMS] | CVIS
11/25/2023 12:46:52 PM | [NSO Update] Mindanao Grid-11/25/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3358MW, PK=2130MW, RR=80MW, NetOpMargin: PM=1147, EVE=1074 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @45MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
11/25/2023 12:45:09 PM | [NSO Update] Visayas Grid-11/25/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2575MW, PK=1976MW, RR=94MW, NetOpMargin: PM=505, EVE=338 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 108.5MW, Leyte A @ 264MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
11/25/2023 12:43:50 PM | [NSO Update] Luzon Grid-11/25/2023 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14204MW, PK=9577MW, RR=389MW, NetOpMargin: PM=4238, EVE=3647 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 290MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/25/2023 11:43:35 AM | Luzon Grid-11/25/2023 11:43: Tayabas SS PCB 9Z-04CB24TAY closed at 1142H (Planned Outage) [WEBSMS] | CLUZ
11/25/2023 11:05:16 AM | Mindanao Grid-11/25/2023 11:08: Manolo 1 U 3 cut in at 1018H. ( Unplanned outage) [WEBSMS] | CMIN
11/25/2023 10:53:27 AM | Mindanao Grid-11/25/2023 10:56: Mt Apo U3 cut out at 0828H. (Planned outage) [WEBSMS] | CMIN
11/25/2023 10:50:38 AM | Mindanao Grid-11/25/2023 10:53: WMPC DG04 cut-in at 0930H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/25/2023 10:33:16 AM | Mindanao Grid-11/25/2023 10:36: Marawi SS 138KV T1 de-energized at 0845H to conduct HV testing of said transformer and verification / testing of its bushings. Planned Outage /GOMP. [WEBSMS] | CMIN
11/25/2023 9:29:47 AM | Mindanao Grid-11/25/2023 09:33: Manolo 1 U 3 tripped with 3MW load at 0910H. Indication: Failure positioning of needle pipe. (Unplanned Outage) [WEBSMS] | CMIN
11/25/2023 9:03:15 AM | Mindanao Grid-11/25/2023 09:06: SPC Mati cut in at 0900H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
11/25/2023 8:29:00 AM | Luzon Grid-11/25/2023 08:29: Daraga-Bacman 230kV Line 1 de-energized at 0828H (Planned Outage) [WEBSMS] | CLUZ
11/25/2023 8:17:18 AM | Luzon Grid-11/25/2023 08:17: Bayombong-Matuno HEPP 69kV Line (CO) de-energized at 0816H (Planned Outage) [WEBSMS] | CLUZ
11/25/2023 7:39:53 AM | Luzon Grid-11/25/2023 07:40: Tayabas SS PCB 9Z-04CB24TAY open at 0738H (Planned Outage) [WEBSMS] | CLUZ
11/25/2023 7:17:08 AM | Visayas Grid-11/25/2023 07:17: Calong-calong-Toledo 138kV Line de-energized at 0708H. Planned Outage [WEBSMS] | CVIS
11/25/2023 7:11:39 AM | Mindanao Grid-11/25/2023 07:14: Zamboanga SS 138KV 50MVA T2 de-energized at 0613H to conduct replacement of OLTC upper gear unit, and correction of minimal oil leaks in phase A tertiary bushing. Part of ERC-approved MSRP Stage 1 Schedule 4. Planned Outage / Non-GOMP [WEBSMS] | CMIN
11/25/2023 7:11:10 AM | Luzon Grid-11/25/2023 07:11: San Juan (Kalayaan)-Calauan 230kV Line 2 de-energized at 0709H (Planned Outage) [WEBSMS] | CLUZ
11/25/2023 7:08:30 AM | Luzon Grid-11/25/2023 07:08: Ambuklao SS 230kV Bus 2 de-energized at 0708H (Planned Outage) [WEBSMS] | CLUZ
11/25/2023 6:21:06 AM | Luzon Grid-11/25/2023 06:21: Bolo-Cayanga 230kV Line 1 (CO) de-energized at 0620H (Planned Outage) [WEBSMS] | CLUZ
11/25/2023 6:01:06 AM | [NSO Update] Luzon Grid-11/25/2023 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14129MW, PK=9883MW, RR=356MW, NetOpMargin: AM=3890, PM=3980, EVE=3407 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, GMEC 2 @160MW, MASINLOC 3 @290MW, ILIJAN A @510MW, ILIJAN B @190MW, [WEBSMS] | CLUZ
11/25/2023 5:39:19 AM | [NSO Update] Visayas Grid-11/25/2023 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2475MW, PK=1939MW, RR=93MW, NetOpMargin: AM=443, PM=441, EVE=218 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @108.5MW, LEYTE A @267MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/25/2023 5:33:56 AM | [NSO Update] Mindanao Grid-11/25/2023 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3370MW, PK=2080MW, RR=80MW, NetOpMargin: AM=1210, PM=1139, EVE=1031 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @45MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
11/25/2023 4:21:54 AM | [NSO Update] Luzon Grid-11/25/2023 04:22: Weather Advisory: Shear Line affecting the eastern section of Southern Luzon. Easterlies affecting Visayas and Mindanao. [WEBSMS] | CLUZ
11/25/2023 4:21:36 AM | [NSO Update] Visayas Grid-11/25/2023 04:21: Weather Advisory: Shear Line affecting the eastern section of Southern Luzon. Easterlies affecting Visayas and Mindanao. [WEBSMS] | CVIS
11/25/2023 4:21:28 AM | [NSO Update] Mindanao Grid-11/25/2023 04:24: Weather Advisory: Shear Line affecting the eastern section of Southern Luzon. Easterlies affecting Visayas and Mindanao. [WEBSMS] | CMIN
11/25/2023 3:39:47 AM | Luzon Grid-11/25/2023 03:39: Concepcion-Concepcion 1 Solar PP 69kV Line restored at 0339H (Planned Outage) [WEBSMS] | CLUZ
11/25/2023 3:07:32 AM | Luzon Grid-11/25/2023 03:07: Correction San Gabriel energized at 0259H (Planned Outage) [WEBSMS] | CLUZ
11/25/2023 3:04:07 AM | Luzon Grid-11/25/2023 03:04: energized at 0259H (Planned Outage) [WEBSMS] | CLUZ
11/25/2023 1:23:16 AM | Luzon Grid-11/25/2023 01:23: Malolos-Hermosa 230kV Line de-energized at 0122H (Planned Outage) [WEBSMS] | CLUZ
11/24/2023 11:57:40 PM | Luzon Grid-11/24/2023 23:57: SLPGC Unit 2 shutdown at 2356H (Unplanned Outage) [WEBSMS] | CLUZ
11/24/2023 11:10:15 PM | Mindanao Grid-11/24/2023 23:13: Agus 4 Unit 3 cut-in at 2303H. (Unplanned Outage) [WEBSMS] | CMIN
11/24/2023 10:02:22 PM | Luzon Grid-11/24/2023 22:02: Dasmarinas-Las Pinas (Zapote) 230kV Line 1 de-energized at 2201H (Planned Outage) [WEBSMS] | CLUZ
11/24/2023 10:01:16 PM | Luzon Grid-11/24/2023 22:01: Las Pinas 230kV Bus 1 de-energized at 2159H (Planned Outage) [WEBSMS] | CLUZ
11/24/2023 10:00:01 PM | Luzon Grid-11/24/2023 22:00: Las Pinas (Zapote) 230kV Tie Line & Las Pinas 230kV Bus 2 de-energized at 2158H (Planned Outage) [WEBSMS] | CLUZ
11/24/2023 9:54:58 PM | Luzon Grid-11/24/2023 21:55: Las Pinas (Zapote) 300MVA T03 de-energized at 2153H (Planned Outage) [WEBSMS] | CLUZ
11/24/2023 9:40:18 PM | Luzon Grid-11/24/2023 21:40: Las Pinas (Zapote) 300MVA T01 & T02 de-energized at 2131H & 2132H, respectively (Planned Outage) [WEBSMS] | CLUZ
11/24/2023 9:22:51 PM | Mindanao Grid-11/24/2023 21:26: WMPC DG04 cut-out at 2114H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/24/2023 9:16:14 PM | Mindanao Grid-11/24/2023 21:19: Lamsan Biomass (LSK) cut in back at 2112H. Unplanned Outage. [WEBSMS] | CMIN
11/24/2023 9:13:31 PM | Mindanao Grid-11/24/2023 21:16: Update: Lamsan Power Corp tripped with 10MW load at 2048H with the same Indication: Boiler tripped. (Unplanned outage) [WEBSMS] | CMIN
11/24/2023 9:02:46 PM | Mindanao Grid-11/24/2023 21:06: Lamsan Power Corp tripped with 10MW load at 2048H, Indication: for investigation. (Unplanned outage) [WEBSMS] | CMIN
11/24/2023 8:53:50 PM | Mindanao Grid-11/24/2023 20:57: LIBERTAD POWER (LPE) on line at 2042H from Forced outage. Indication: Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
11/24/2023 7:48:25 PM | Luzon Grid-11/24/2023 19:48: San Gabriel shutdown at 1947H (Planned Outage) [WEBSMS] | CLUZ
11/24/2023 7:38:52 PM | Luzon Grid-11/24/2023 19:38: Concepcion-Concepcion 1 Solar PP 69kV Line de-energized at 1937H (Planned Outage) [WEBSMS] | CLUZ
11/24/2023 7:15:14 PM | Mindanao Grid-11/24/2023 19:18: Lamsan Biomass (LSK) online at 1855H. Unplanned Outage. [WEBSMS] | CMIN
11/24/2023 7:11:25 PM | Mindanao Grid-11/24/2023 19:14: LIBERTAD POWER (LPE) tripped with 6MW load at 1900H. Indication: for verification. (Unplanned Outage) [WEBSMS] | CMIN
11/24/2023 7:01:24 PM | Luzon Grid-11/24/2023 19:01: For info: Commissioning of New M1 Protection for Bolo-Labrador 230kV Line 1 completed at 1859H [WEBSMS] | CLUZ
11/24/2023 6:30:14 PM | Mindanao Grid-11/24/2023 18:33: Lamsan Power Corp. tripped with 10MW load at 1814H due to Boiler tripped indication. (Unplanned outage) [WEBSMS] | CMIN
11/24/2023 6:10:27 PM | Luzon Grid-11/24/2023 18:10: Bolo-Labrador 230kV Line 1 energized & looped at 1746H & 1808H, respectively. On-going commissioning of New M1 Protection (Planned Outage) [WEBSMS] | CLUZ
11/24/2023 6:08:11 PM | [NSO Update] Mindanao Grid-11/24/2023 18:11: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3282MW, PK=2299MW, RR=80MW, NetOpMargin: EVE=903 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @100MW, AG5 @45MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
11/24/2023 5:55:55 PM | [NSO Update] Luzon Grid-11/24/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14671MW, PK=10350MW, RR=408MW, NetOpMargin: EVE=3913 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 300MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/24/2023 5:53:04 PM | [NSO Update] Visayas Grid-11/24/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2491MW, PK=2152MW, RR=97MW, NetOpMargin: EVE=242 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @108.5MW, LEYTE A @264MW, PGPP1 @38MW, TPC (Carmen) @30M [WEBSMS] | CVIS
11/24/2023 4:27:05 PM | Mindanao Grid-11/24/2023 16:30: LIBERTAD POWER (LPE) cut-in at 1614H. (Unplanned Outage) [WEBSMS] | CMIN
11/24/2023 4:17:06 PM | Mindanao Grid-11/24/2023 16:20: WMPC DG01 cut-out at 1615H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/24/2023 4:05:08 PM | Visayas Grid-11/24/2023 16:05: Toledo Sangi 2nd lift 34.5KV energized at 1603H. ( Unplanned Outage ) [WEBSMS] | CVIS
11/24/2023 2:36:38 PM | Visayas Grid-11/24/2023 14:36: Toledo Sangi 2nd lift 34.5KV auto tripped at 1426H. ( Unplanned Outage ) [WEBSMS] | CVIS
11/24/2023 2:36:25 PM | Mindanao Grid-11/24/2023 14:39: LIBERTAD POWER (LPE) tripped with 6MW load at 1430H. Indication: for verification. (Unplanned Outage) [WEBSMS] | CMIN
11/24/2023 2:27:05 PM | Mindanao Grid-11/24/2023 14:30: Euro Hydro (NBT) tripped with 1.5MW load at 1235H. Affected by the forced outage of NORDECO 13.8kV line. On line back at 1413H. (Unplanned Outage). [WEBSMS] | CMIN
11/24/2023 1:04:33 PM | Mindanao Grid-11/24/2023 13:07: KEGI Panaon Unit 2 cut-in at 1301H. MO dispatched (RTD). [WEBSMS] | CMIN
11/24/2023 1:02:46 PM | Mindanao Grid-11/24/2023 13:06: Agus 2 - Kibawe 138kv L2 energized at 1253H. Note: said line is energized from Agus 2 switchyard up to tower 33 only. Unplanned outage. [WEBSMS] | CMIN
11/24/2023 12:50:18 PM | [NSO Update] Luzon Grid-11/24/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15116MW, PK=11031MW, RR=432MW, NetOpMargin: PM=3653, EVE=3613 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 290MW, Ilijan A @ 360MW, Ilijan B @ 170MW [WEBSMS] | CLUZ
11/24/2023 12:48:03 PM | [NSO Update] Visayas Grid-11/24/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2687MW, PK=2268MW, RR=94MW, NetOpMargin: PM=325, EVE=261 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @108.5MW, LEYTE A @264MW, PGPP1 @38MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/24/2023 12:46:04 PM | [NSO Update] Mindanao Grid-11/24/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3358MW, PK=2276MW, RR=80MW, NetOpMargin: PM=1002, EVE=1037 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @45MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
11/24/2023 12:37:25 PM | Luzon Grid-11/24/2023 12:37: Burgos 16MVAR capacitor bank declared available at 1230H. [WEBSMS] | CLUZ
11/24/2023 12:11:49 PM | Mindanao Grid-11/24/2023 12:15: Agus 4 Unit 3 tripped with 35.1MW load at 1205H. Lowest system frequency recorded was 59.72Hz. Cause: Excitation System Fault. (Unplanned Outage) [WEBSMS] | CMIN
11/24/2023 11:00:14 AM | Mindanao Grid-11/24/2023 11:03: WMPC DG01 cut-in at 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/24/2023 10:47:23 AM | Mindanao Grid-11/24/2023 10:50: STEAG Unit 2 cut-in at 1013H (from PMS, GOMP). (Planned Outage) [WEBSMS] | CMIN
11/24/2023 10:32:03 AM | Mindanao Grid-11/24/2023 10:35: SUPREME POWER Mati (MDP) cut-in at 0900H. MO dispatched (RTD). [WEBSMS] | CMIN
11/24/2023 10:19:17 AM | Mindanao Grid-11/24/2023 10:22: Agus 4 Unit 3 cut-in at 1015H. (Unplanned Outage) [WEBSMS] | CMIN
11/24/2023 9:36:12 AM | Mindanao Grid-11/24/2023 09:39: Agus 4 Unit 3 tripped with 35.2MW load at 0912H. Lowest system recorded was 59.68Hz. No ALD. Cause: Excitation System Fault. (Unplanned Outage) [WEBSMS] | CMIN
11/24/2023 9:13:59 AM | Mindanao Grid-11/24/2023 09:17: WMPC DG04 cut-in at 0850H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/24/2023 7:28:53 AM | Mindanao Grid-11/24/2023 07:32: (Correction) Manolo Fortich 2 (MN2) Unit 4 shutdown at 0703H. Cause: Insufficient water supply (outside management control). (Unplanned Outage) [WEBSMS] | CMIN
11/24/2023 7:25:32 AM | Mindanao Grid-11/24/2023 07:28: Manolo Fortich 2 (MN2) Unit 4 shutdown at 0701H. Cause: Insufficient water supply (outside management control). (Unplanned Outage) [WEBSMS] | CMIN
11/24/2023 7:16:20 AM | Luzon Grid-11/24/2023 07:16: Sta. Rita module 30 online at 0713H (Tuning for LNG commissioning) [WEBSMS] | CLUZ
11/24/2023 5:55:03 AM | [NSO Update] Mindanao Grid-11/24/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3292MW, PK=2276MW, RR=80MW, NetOpMargin: AM=936, PM=930, EVE=867 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @110MW, AG4 @139MW, AG5 @45MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
11/24/2023 5:51:51 AM | [NSO Update] Visayas Grid-11/24/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2673MW, PK=2274MW, RR=93MW, NetOpMargin: AM=306, PM=281, EVE=251 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 268MW, PGPP1 @ 38MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
11/24/2023 5:50:21 AM | [NSO Update] Luzon Grid-11/24/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15088MW, PK=10999MW, RR=422MW, NetOpMargin: AM=3667, PM=3712, EVE=3803 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: GNPD 1 @ 550MW, Calaca 2 @ 175MW, Masinloc 3 @ 290MW, Ilijan A @ 360MW, Ilijan B @ 170MW [WEBSMS] | CLUZ
11/24/2023 5:37:48 AM | Luzon Grid-11/24/2023 05:37: Sta. Rita module 30 shutdown at 0535H (Unit tuning for LNG commissioning) [WEBSMS] | CLUZ
11/24/2023 4:58:35 AM | Luzon Grid-11/24/2023 04:58: Sta. Rita module 40 online at 0453H (Unit tuning for LNG commissioning) [WEBSMS] | CLUZ
11/24/2023 4:09:18 AM | [NSO Update] Luzon Grid-11/24/2023 04:09: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Easterlies affecting Visayas and Mindanao [WEBSMS] | CLUZ
11/24/2023 4:09:04 AM | [NSO Update] Visayas Grid-11/24/2023 04:09: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Easterlies affecting Visayas and Mindanao [WEBSMS] | CVIS
11/24/2023 4:08:52 AM | [NSO Update] Mindanao Grid-11/24/2023 04:12: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Easterlies affecting Visayas and Mindanao [WEBSMS] | CMIN
11/24/2023 3:30:19 AM | Luzon Grid-11/24/2023 03:30: Sta. Rita module 40 shutdown at 0326H (Unit Tuning for LNG commissioning) [WEBSMS] | CLUZ
11/24/2023 2:34:41 AM | Luzon Grid-11/24/2023 02:34: Sta. Rita Module 40 online at 0232H (Unit Tuning for LNG commissioning) [WEBSMS] | CLUZ
11/24/2023 1:10:55 AM | Visayas Grid-11/24/2023 01:10: Cadiz - EB Magalona (GAH) 230 KV line 2 energized at 0105H. [WEBSMS] | CVIS
11/24/2023 12:36:03 AM | Luzon Grid-11/24/2023 00:36: Sta Rita Module 40 shutdown at 0031H. (Unit Tuning for LNG commissioning) [WEBSMS] | CLUZ
11/24/2023 12:30:03 AM | Mindanao Grid-11/24/2023 00:33: Talomo 1 U1 on line at 0011H and Talomo U1 U2 on line at 0006H both from Forced Outage. (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 11:33:10 PM | Luzon Grid-11/23/2023 23:33: Lumban-Malaya 230kV line 1 was restored at 2331H. (Planned Outage) [WEBSMS] | CLUZ
11/23/2023 10:12:09 PM | Mindanao Grid-11/23/2023 22:15: Talomo 1 Unit 1 tripped with 0.1MW load at 2157H. Cause: Clogged Intake. (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 9:30:11 PM | Mindanao Grid-11/23/2023 21:33: WMPC DG04 cut-out at 2114H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/23/2023 9:07:58 PM | Mindanao Grid-11/23/2023 21:11: SUPREME POWER Mati (MDP) cut-out at 2105H. End of RTD. [WEBSMS] | CMIN
11/23/2023 8:49:37 PM | Mindanao Grid-11/23/2023 20:52: Talomo 1 Unit 2 tripped with 0.2MW load at 2023H. Cause: Insufficient Water Supply (outside management control). (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 8:17:45 PM | Luzon Grid-11/23/2023 20:17: Malaya-Lumban 230kV Line 1 de-energized at 2017H (Planned Outage) [WEBSMS] | CLUZ
11/23/2023 7:20:36 PM | Mindanao Grid-11/23/2023 19:23: NACSUR cut-out at 1904H. End of RTD. [WEBSMS] | CMIN
11/23/2023 7:20:05 PM | Mindanao Grid-11/23/2023 19:23: KEGI Maramag cut-out at 1904H. End of RTD. [WEBSMS] | CMIN
11/23/2023 6:24:43 PM | Mindanao Grid-11/23/2023 18:28: Agus 1 Unit 1 cut-in at 1821H. (Unplanned Outage). [WEBSMS] | CMIN
11/23/2023 5:45:16 PM | [NSO Update] Mindanao Grid-11/23/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3182MW, PK=2308MW, RR=80MW, NetOpMargin: EVE=793 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @35MW, AG2 @90MW, AG4 @139MW, AG5 @45MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
11/23/2023 5:44:15 PM | [NSO Update] Visayas Grid-11/23/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2664MW, PK=2312MW, RR=97MW, NetOpMargin: EVE=254 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 108.5MW, Leyte A @ 272MW, PGPP1 @ 38MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
11/23/2023 5:42:20 PM | [NSO Update] Luzon Grid-11/23/2023 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14440MW, PK=10681MW, RR=424MW, NetOpMargin: EVE=3335 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 280MW, Ilijan A @ 360MW, Ilijan B @ 170MW [WEBSMS] | CLUZ
11/23/2023 5:38:09 PM | Mindanao Grid-11/23/2023 17:41: Agus 1 Unit 2 cut-in at 1734H. (Unplanned Outage). [WEBSMS] | CMIN
11/23/2023 5:04:37 PM | Mindanao Grid-11/23/2023 17:07: NACSUR cut-in at 1700H. MO dispatched (RTD). [WEBSMS] | CMIN
11/23/2023 4:30:51 PM | Mindanao Grid-11/23/2023 16:34: WMPC DG01 cut-out at 1614H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/23/2023 4:29:33 PM | Mindanao Grid-11/23/2023 16:32: Talomo 1 Unit 2 cut-in at 1610H. Said unit tripped last 22 Nov 2023 at 2328H due to insufficient water supply (out-side management control). (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 4:07:31 PM | Mindanao Grid-11/23/2023 16:10: Therma Marine 2 (TM2) cut-out at 1603H. End of RTD. [WEBSMS] | CMIN
11/23/2023 4:06:50 PM | Mindanao Grid-11/23/2023 16:10: NACSUR cut-out at 1600H. End of RTD. [WEBSMS] | CMIN
11/23/2023 4:06:19 PM | Mindanao Grid-11/23/2023 16:09: KEGI Tandag cut-out at 1559H. End of RTD. [WEBSMS] | CMIN
11/23/2023 3:51:30 PM | Mindanao Grid-11/23/2023 15:54: KEGI Tandag cut-in at 1451H. MO dispatched (RTD). [WEBSMS] | CMIN
11/23/2023 3:36:42 PM | Luzon Grid-11/23/2023 15:36: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1533H (Planned Outage) [WEBSMS] | CLUZ
11/23/2023 3:35:51 PM | Mindanao Grid-11/23/2023 15:39: Agus 4 Unit 3 cut-in at 1534H. (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 3:25:17 PM | Mindanao Grid-11/23/2023 15:28: NACSUR cut-in at 1518H. MO dispatched (RTD). [WEBSMS] | CMIN
11/23/2023 3:24:02 PM | Mindanao Grid-11/23/2023 15:27: (Correction) NACSUR cut-out at 1500H. End of RTD. [WEBSMS] | CMIN
11/23/2023 3:21:57 PM | Mindanao Grid-11/23/2023 15:25: NACSUR cut-out at 1518H. End of RTD. [WEBSMS] | CMIN
11/23/2023 2:59:52 PM | Mindanao Grid-11/23/2023 15:03: LIBERTAD POWER (LPE) cut-in at 1341H. (Unplanned Outage). [WEBSMS] | CMIN
11/23/2023 2:49:27 PM | Mindanao Grid-11/23/2023 14:52: LIBERTAD POWER (LPE) tripped with 6MW load at 1148H. Lowest system frequency recorded was 59.91Hz. Indication: for verification. (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 2:44:41 PM | Mindanao Grid-11/23/2023 14:47: Agus 4 Unit 3 tripped with 39.6MW load at 1434H. Lowest system frequency recorded was 59.637Hz. No ALD. Indication: 86G, governor/turbine system. (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 2:02:42 PM | Mindanao Grid-11/23/2023 14:05: NACSUR cut-in at 1400H. MO dispatched (RTD). [WEBSMS] | CMIN
11/23/2023 2:00:20 PM | Mindanao Grid-11/23/2023 14:03: WMPC DG05 cut-out at 1357H. End of RTD. [WEBSMS] | CMIN
11/23/2023 1:48:21 PM | Mindanao Grid-11/23/2023 13:51: Therma Marine 2 (TM2) Unit 1 cut-in at 1340H. MO dispatched (RTD), [WEBSMS] | CMIN
11/23/2023 1:45:34 PM | Mindanao Grid-11/23/2023 13:48: WMPC DG05 cut-in at 1330H. MO dispatched (RTD). [WEBSMS] | CMIN
11/23/2023 1:44:08 PM | Mindanao Grid-11/23/2023 13:47: KEGI Maramag cut-in at 1301H. MO Dispatched (RTD). [WEBSMS] | CMIN
11/23/2023 12:47:08 PM | Luzon Grid-11/23/2023 12:47: Pagbilao EHV SS PCB 9Z-03CB08PGB restored at 1245H (Planned Outage) [WEBSMS] | CLUZ
11/23/2023 12:41:08 PM | [NSO Update] Visayas Grid-11/23/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2557MW, PK=2247MW, RR=94MW, NetOpMargin: PM=216, EVE=171 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @108.5MW, LEYTE A @272MW, PGPP1 @38MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/23/2023 12:37:19 PM | [NSO Update] Mindanao Grid-11/23/2023 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3183MW, PK=2376MW, RR=80MW, NetOpMargin: PM=727, EVE=728 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG2 @90MW, AG4 @139MW, AG5 @45MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
11/23/2023 12:34:18 PM | [NSO Update] Luzon Grid-11/23/2023 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=15029MW, PK=10938MW, RR=434MW, NetOpMargin: PM=3657, EVE=3428 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @270MW, ILIJAN A @360MW, ILIJAN B @170MW [WEBSMS] | CLUZ
11/23/2023 12:30:19 PM | Mindanao Grid-11/23/2023 12:33: Agus 1 Unit 1 (load=22.2MW) and Unit 2 (load=19.5MW) tripped at 1205H. Lowest system frequency recorded was 59.588Hz. No ALD. Cause: Trouble in its 110V DC power supply due damaged battery cells. (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 12:08:09 PM | Mindanao Grid-11/23/2023 12:11: Agus 2 - Kibawe 138kv L2 auto tripped 1148H. Note: said line is energized from Agus 2 switchyard up to tower 33 only. Unplanned outage [WEBSMS] | CMIN
11/23/2023 11:18:34 AM | Mindanao Grid-11/23/2023 11:21: MANOLO FORTICH 2 (MN2) Unit 3 cut-in at 1116H. Root-cause: Communication loss of head water level loss sensor. (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 11:08:50 AM | Mindanao Grid-11/23/2023 11:12: MANOLO FORTICH 2 (MN2) Unit 4 cut-in at 1107H. Root-cause: Communication loss of head water level loss sensor. (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 11:07:06 AM | Mindanao Grid-11/23/2023 11:10: MANOLO FORTICH 2 (MN2) Unit 2 cut-in at 1101H. Root-cause: Communication loss of head water level loss sensor. (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 11:06:36 AM | Mindanao Grid-11/23/2023 11:09: MANOLO FORTICH 2 (MN2) Unit 1 cut-in at 1055H. Root-cause: Communication loss of head water level loss sensor. (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 10:52:17 AM | Mindanao Grid-11/23/2023 10:55: WMPC DG01 cut-in at 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/23/2023 10:43:48 AM | Mindanao Grid-11/23/2023 10:47: MANOLO FORTICH 2 (MN2) Hydro Units 1, 2, 3 & 4 tripped with aggregate load of 7.8MW at 0945H. Initial cause: IWS: head water level loss (for further investigation). Lowest system frequency recorded was 59.82Hz. (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 10:24:38 AM | Mindanao Grid-11/23/2023 10:27: LAKE MAINIT Hydro Unit 2 cut-in at 0929H. (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 9:29:08 AM | Luzon Grid-11/23/2023 09:29: Pagbilao EHV SS PCB 9Z-03CB08PGB de-energized at 0920H (Planned Outage) [WEBSMS] | CLUZ
11/23/2023 9:14:43 AM | Luzon Grid-11/23/2023 09:14: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0912H (Planned Outage) [WEBSMS] | CLUZ
11/23/2023 9:03:55 AM | Mindanao Grid-11/23/2023 09:07: SUPREME POWER Mati (MDP) cut-in at 0900H. MO dispatched (RTD), [WEBSMS] | CMIN
11/23/2023 8:55:02 AM | Mindanao Grid-11/23/2023 08:58: LAKE MAINIT Hydro Unit 2 tripped with 5.9MW load at 0845H. Lowest frequency recorded was 59.79Hz. Indication: Reverse Power. (Unplanned Outage) [WEBSMS] | CMIN
11/23/2023 8:52:15 AM | Mindanao Grid-11/23/2023 08:55: WMPC DG04 cut-in at 0850H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/23/2023 8:22:38 AM | [NSO Update] Visayas Grid-11/23/2023 08:22: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2475MW, PK=2141MW, RR=93MW, NetOpMargin: AM=241, PM=171, EVE=234 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @108.5MW, LEYTE A @279MW, PGPP1 @38MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/23/2023 7:09:24 AM | Luzon Grid-11/23/2023 07:09: Bolo-Labrador 230kV Line 1 de-energized at 0708H (Planned Outage) [WEBSMS] | CLUZ
11/23/2023 5:44:00 AM | [NSO Update] Luzon Grid-11/23/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=15164MW, PK=10565MW, RR=406MW, NetOpMargin: AM=4193, PM=3719, EVE=3388 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @280MW, ILIJAN A @360MW, ILIJAN B @170MW [WEBSMS] | CLUZ
11/23/2023 5:36:53 AM | [NSO Update] Mindanao Grid-11/23/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3263MW, PK=2307MW, RR=80MW, NetOpMargin: AM=875, PM=867, EVE=907 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @90MW, AG4 @139MW, AG5 @45MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
11/23/2023 4:56:57 AM | [NSO Update] Mindanao Grid-11/23/2023 05:00: Weather Update: Shear Line affecting Southern Luzon. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CMIN
11/23/2023 4:56:42 AM | [NSO Update] Visayas Grid-11/23/2023 04:56: Weather Update: Shear Line affecting Southern Luzon. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CVIS
11/23/2023 4:56:28 AM | [NSO Update] Luzon Grid-11/23/2023 04:56: Weather Update: Shear Line affecting Southern Luzon. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CLUZ
11/23/2023 4:16:10 AM | Luzon Grid-11/23/2023 04:16: Sta. Rita module 10 online at 0411H (Unplanned Outage) [WEBSMS] | CLUZ
11/23/2023 2:11:22 AM | Luzon Grid-11/23/2023 02:11: Sta. Rita module 10 tripped at 0207H (Unplanned Outage) [WEBSMS] | CLUZ
11/23/2023 1:56:29 AM | Luzon Grid-11/23/2023 01:56: Sta. Rita Module 10 online at 0148H (Planned Outage) [WEBSMS] | CLUZ
11/22/2023 10:33:57 PM | Mindanao Grid-11/22/2023 22:37: GNPK U3 shutdown at 2230H. (Planned Outage). For reserve shutdown. [WEBSMS] | CMIN
11/22/2023 9:26:38 PM | Mindanao Grid-11/22/2023 21:29: WMPC DG04 cut-out at 2115H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/22/2023 9:24:58 PM | Mindanao Grid-11/22/2023 21:28: SUPREME POWER Mati (MDP) cut-out at 2105H. End of RTD. [WEBSMS] | CMIN
11/22/2023 9:02:39 PM | Mindanao Grid-11/22/2023 21:05: LIBERTED POWER (LPE) cut-in at 2100H. (Unplanned Outage) [WEBSMS] | CMIN
11/22/2023 8:53:37 PM | Luzon Grid-11/22/2023 20:53: Sta. Rita Module 30 online at 2047H (Planned Outage) [WEBSMS] | CLUZ
11/22/2023 8:22:15 PM | Mindanao Grid-11/22/2023 20:25: LIBERTAD POWER (LPE) tripped with 6MW load at 1945H. Indication: Earthfault Cause: affected by tripping of ZAMSURECOs feeder 2 line fault. [WEBSMS] | CMIN
11/22/2023 8:10:47 PM | Luzon Grid-11/22/2023 20:10: San Jose-Angat 115kV line 1 energized at 2004H on San Jose side (Unplanned Outage) [WEBSMS] | CLUZ
11/22/2023 7:26:42 PM | Mindanao Grid-11/22/2023 19:29: KEGI Jimenez cut-out at 1842H. End of RTD. [WEBSMS] | CMIN
11/22/2023 6:50:03 PM | Mindanao Grid-11/22/2023 18:53: KEGI Tandag cut-out at 1823H. End of RTD. [WEBSMS] | CMIN
11/22/2023 6:13:11 PM | Mindanao Grid-11/22/2023 18:16: KEGI Jimenez cut-in at 1744H. MO dispatched (RTD). [WEBSMS] | CMIN
11/22/2023 6:08:04 PM | [NSO Update] Luzon Grid-11/22/2023 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14134MW, PK=10457MW, RR=421MW, NetOpMargin: EVE=3256 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @230MW, ILIJAN A @430MW, ILIJAN B @170MW [WEBSMS] | CLUZ
11/22/2023 6:06:17 PM | [NSO Update] Mindanao Grid-11/22/2023 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3186MW, PK=2322MW, RR=80MW, NetOpMargin: EVE=783 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @50MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
11/22/2023 6:00:26 PM | [NSO Update] Visayas Grid-11/22/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2449MW, PK=2160MW, RR=97MW, NetOpMargin: EVE=192 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @108.5MW, LEYTE A @258MW, PGPP1 @38MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/22/2023 5:40:15 PM | Mindanao Grid-11/22/2023 17:43: KEGI Tandag cut-in at 1734H. MO dispatched (RTD). [WEBSMS] | CMIN
11/22/2023 4:21:12 PM | Mindanao Grid-11/22/2023 16:24: WMPC DG01 cut-out at 1614H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/22/2023 3:47:55 PM | Luzon Grid-11/22/2023 15:47: MPGC Unit 2 online at 1546H (Ongoing Testing and Commissioning) [WEBSMS] | CLUZ
11/22/2023 3:30:01 PM | Mindanao Grid-11/22/2023 15:33: Tudaya 2 Unit 2 cut-in at 1516H. (Unplanned Outage) [WEBSMS] | CMIN
11/22/2023 3:05:43 PM | Mindanao Grid-11/22/2023 15:08: GNPK Unit 2 cut-in at 1502H. (Planned Outage) [WEBSMS] | CMIN
11/22/2023 2:18:47 PM | Luzon Grid-11/22/2023 14:18: San Jose - Angat 115kV Line 1 de-energized at 1418H (Unplanned Outage) [WEBSMS] | CLUZ
11/22/2023 2:17:21 PM | Luzon Grid-11/22/2023 14:17: Pagbilao EHV SS PCB 9Z-03CB24PGB restored at 1416H (Planned Outage) [WEBSMS] | CLUZ
11/22/2023 1:19:26 PM | Mindanao Grid-11/22/2023 13:22: Tudaya 2 Unit 2 with 1.0MW load shutdown at 1305H due to insufficient water supply (outside management control). (Unplanned Outage) [WEBSMS] | CMIN
11/22/2023 12:53:56 PM | [NSO Update] Visayas Grid-11/22/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2445MW, PK=2141MW, RR=94MW, NetOpMargin: PM=209, EVE=190 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @108.5MW, LEYTE A @263MW, PGPP1 @38MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/22/2023 12:50:48 PM | [NSO Update] Mindanao Grid-11/22/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3248MW, PK=2363MW, RR=80MW, NetOpMargin: PM=804, EVE=842 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @50MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
11/22/2023 12:48:08 PM | [NSO Update] Luzon Grid-11/22/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14667MW, PK=10584MW, RR=432MW, NetOpMargin: PM=3651, EVE=3418 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @210MW, ILIJAN A @430MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/22/2023 12:22:17 PM | Mindanao Grid-11/22/2023 12:25: Kibawe SS 138kV Bus 2 energized at 1212H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
11/22/2023 12:05:46 PM | Luzon Grid-11/22/2023 12:05: Sta Rita 20 online at 1203H (Planned Outage) [WEBSMS] | CLUZ
11/22/2023 10:56:27 AM | Mindanao Grid-11/22/2023 10:59: WMPC DG01 cut-in at 1052H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/22/2023 10:53:51 AM | Mindanao Grid-11/22/2023 10:57: SUPREME POWER MATI (MDP) cut-in at 0900H. MO dispatched (RTD). [WEBSMS] | CMIN
11/22/2023 10:51:31 AM | Mindanao Grid-11/22/2023 10:54: WMPC DG04 cut-in at 0856H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/22/2023 10:47:19 AM | Luzon Grid-11/22/2023 10:47: Mexico-Quezon 230kV line restored at 1047H (Unplanned Outage) [WEBSMS] | CLUZ
11/22/2023 10:44:35 AM | Luzon Grid-11/22/2023 10:44: Mexico-Quezon 230kV line tripped at 1039H (Unplanned Outage) [WEBSMS] | CLUZ
11/22/2023 9:57:06 AM | Luzon Grid-11/22/2023 09:57: Sta Rita 40 online at 0952H (Unplanned Outage) [WEBSMS] | CLUZ
11/22/2023 8:33:38 AM | Mindanao Grid-11/22/2023 08:36: Pulangi 4 HEP Unit 2 cut-in at 0825H. (Unplanned Outage, Outside Management Control), [WEBSMS] | CMIN
11/22/2023 8:18:17 AM | Mindanao Grid-11/22/2023 08:21: Kibawe SS 138kV Bus 2 deenergized at 0812H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
11/22/2023 8:14:51 AM | Luzon Grid-11/22/2023 08:14: Sta Rita 40 emergency shutdown at 0808H. On-going tuning test of New Fuel (LNG) (Unplanned Outage) [WEBSMS] | CLUZ
11/22/2023 7:58:16 AM | Luzon Grid-11/22/2023 07:58: Sta Rita 20 shutdown at 0728H. On-going tuning test of New Fuel (LNG) (Planned Outage) [WEBSMS] | CLUZ
11/22/2023 5:57:34 AM | [NSO Update] Luzon Grid-11/22/2023 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14587MW, PK=10383MW, RR=424MW, NetOpMargin: AM=3779, PM=3275, EVE=2955 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 3 @185MW, ILIJAN A @430MW, ILIJAN B @190MW, SAN GABRIEL @330MW [WEBSMS] | CLUZ
11/22/2023 5:32:13 AM | [NSO Update] Mindanao Grid-11/22/2023 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3261MW, PK=2175MW, RR=80MW, NetOpMargin: AM=1007, PM=892, EVE=984 Highest Unit O/L: GNPK 1&3@138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @50MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
11/22/2023 5:29:04 AM | Luzon Grid-11/22/2023 05:29: Dona Imelda(Araneta) 230kV Bus 2 was energized at 0527H. (Planned Outage) [WEBSMS] | CLUZ
11/22/2023 5:27:40 AM | [NSO Update] Visayas Grid-11/22/2023 05:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2434MW, PK=2072MW, RR=93MW, NetOpMargin: AM=269, PM=194, EVE=219 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @265MW, PGPP1 @38MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/22/2023 4:16:07 AM | [NSO Update] Luzon Grid-11/22/2023 04:16: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CLUZ
11/22/2023 4:15:43 AM | [NSO Update] Mindanao Grid-11/22/2023 04:18: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CMIN
11/22/2023 4:15:12 AM | [NSO Update] Visayas Grid-11/22/2023 04:15: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CVIS
11/22/2023 2:35:49 AM | Visayas Grid-11/22/2023 02:36: CEDC Unit 1 cut in at 0232H. [WEBSMS] | CVIS
11/21/2023 11:45:06 PM | Luzon Grid-11/21/2023 23:45: Dona Imelda(Araneta) 230kV Bus 2 was de-energized at 2343H. (Planned Outage) [WEBSMS] | CLUZ
11/21/2023 11:03:43 PM | Mindanao Grid-11/21/2023 23:07: Talomo A Unit 2 (TL1 U2) Online at 2249H. From emergency shutdown due to clogged Weir Intake. [WEBSMS] | CMIN
11/21/2023 10:09:45 PM | Mindanao Grid-11/21/2023 22:13: TL 1 U1 Online at 2147H. From emergency shutdown due to clogged Weir Intake. [WEBSMS] | CMIN
11/21/2023 9:36:52 PM | Mindanao Grid-11/21/2023 21:40: MDP shutdown at 2105H. End of RTD. [WEBSMS] | CMIN
11/21/2023 9:22:31 PM | Mindanao Grid-11/21/2023 21:25: WMPC DG05 cut-out at 2114H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/21/2023 8:04:36 PM | Luzon Grid-11/21/2023 20:04: Sta Rita Module 40 shutdown at 2003H. (Planned Outage) [WEBSMS] | CLUZ
11/21/2023 7:50:53 PM | Luzon Grid-11/21/2023 19:51: San Jose-Angat 115kV line 1 - energized at 1949H on the San Jose side. (Planned Outage) [WEBSMS] | CLUZ
11/21/2023 7:46:19 PM | Visayas Grid-11/21/2023 19:46: ALD occurred at Visayas feeders=38.68Mw at 1937H due to tripping of CEDC unit #1 =83.7MW. The lowest frequency is 59.16Hz. [WEBSMS] | CVIS
11/21/2023 6:23:12 PM | Mindanao Grid-11/21/2023 18:26: Talomo 1 Unit 1 (load=0.40MW) shutdown at 1715H due to clogged weir intake due to flood (outside management control). (Unplanned Outage) [WEBSMS] | CMIN
11/21/2023 6:22:39 PM | Mindanao Grid-11/21/2023 18:26: Talomo 1 Unit 2 (load=0.38MW) shutdown at 1703H due to clogged weir intake due to flood (outside management control). (Unplanned Outage) [WEBSMS] | CMIN
11/21/2023 6:17:38 PM | Mindanao Grid-11/21/2023 18:21: Talomo 3 Unit 1 cut-in at 1728H. (Unplanned Outage) [WEBSMS] | CMIN
11/21/2023 6:17:11 PM | Mindanao Grid-11/21/2023 18:20: Talomo 3 Unit 2 cut-in at 1719H. (Unplanned Outage) [WEBSMS] | CMIN
11/21/2023 6:16:22 PM | Mindanao Grid-11/21/2023 18:19: Talomo 2B Unit 1 cut-in at 1631H. (Unplanned Outage) [WEBSMS] | CMIN
11/21/2023 6:15:54 PM | Mindanao Grid-11/21/2023 18:19: Talomo 2A Unit 2 cut-in at 1642H. (Unplanned Outage) [WEBSMS] | CMIN
11/21/2023 6:15:25 PM | Mindanao Grid-11/21/2023 18:18: Talomo 2A Unit 1 cut-in at 1637H. (Unplanned Outage) [WEBSMS] | CMIN
11/21/2023 6:14:42 PM | Mindanao Grid-11/21/2023 18:18: Talomo 2 Unit 3 cut-in at 1649H. (Unplanned Outage) [WEBSMS] | CMIN
11/21/2023 6:14:16 PM | Mindanao Grid-11/21/2023 18:17: Talomo 2 Unit 1 cut-in at 1644H. (Unplanned Outage) [WEBSMS] | CMIN
11/21/2023 6:13:46 PM | Mindanao Grid-11/21/2023 18:17: Talomo 2 Unit 2 cut-in at 1641H. (Unplanned Outage) [WEBSMS] | CMIN
11/21/2023 5:59:26 PM | [NSO Update] Luzon Grid-11/21/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13930MW, PK=10116MW, RR=406MW, NetOpMargin: EVE=3408 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 3 @170MW, ILIJAN A @430MW, ILIJAN B @190MW, STA. RITA 10 @220MW, STA. RITA 20 @220MW, STA. RITA 40 @220MW [WEBSMS] | CLUZ
11/21/2023 5:54:40 PM | Mindanao Grid-11/21/2023 17:58: WMPC DG06 cut-out at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/21/2023 5:53:02 PM | [NSO Update] Mindanao Grid-11/21/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3039MW, PK=2286MW, RR=80MW, NetOpMargin: EVE=673 Highest Unit O/L: GNPK 1&3@138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @80MW, AG4 @147MW, AG5 @50MW, AG6 @155MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/21/2023 5:44:04 PM | [NSO Update] Visayas Grid-11/21/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2449MW, PK=2075MW, RR=97MW, NetOpMargin: EVE=277 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @292MW, PGPP1 @38MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/21/2023 4:37:39 PM | Mindanao Grid-11/21/2023 16:41: (Correction) Talomo 1 Unit 2 cut-in at 1625H. (Unplanned Outage, outside management control) [WEBSMS] | CMIN
11/21/2023 4:36:00 PM | Mindanao Grid-11/21/2023 16:39: Talomo 1 Unit 2 cut-in at 1635H. (Unplanned Outage, outside management control) [WEBSMS] | CMIN
11/21/2023 4:33:41 PM | Mindanao Grid-11/21/2023 16:37: Talomo 2B Unit 1 (load=0.22MW) emergency shutdown at 1507H to facilitate hotspot correction at Lower Talomo Switchyard (HEDCOR-initiated activity). [WEBSMS] | CMIN
11/21/2023 4:32:51 PM | Mindanao Grid-11/21/2023 16:36: Talomo 2A Unit 1 (load=0.25MW), and Unit 2 (load=0.125MW) emergency shutdown at 1509H to facilitate hotspot correction at Lower Talomo Switchyard (HEDCOR-initiated activity). [WEBSMS] | CMIN
11/21/2023 4:31:38 PM | Mindanao Grid-11/21/2023 16:35: Talomo 2 Unit 1 (load=0.13MW), Unit 2 (load=0.17MW), and Unit 3 (load=0.14MW) emergency shutdown at 1507H to facilitate hotspot correction at Lower Talomo Switchyard (HEDCOR-initiated activity). [WEBSMS] | CMIN
11/21/2023 4:30:11 PM | Mindanao Grid-11/21/2023 16:33: Talomo 3 Unit 1 (load=0.75MW), and Unit 2 (load=0.61MW) emergency shutdown at 1506H to facilitate hotspot correction at Lower Talomo Switchyard (HEDCOR-initiated activity). [WEBSMS] | CMIN
11/21/2023 4:03:55 PM | Mindanao Grid-11/21/2023 16:07: WMPC DG04 declared available at 1600H. [WEBSMS] | CMIN
11/21/2023 3:17:13 PM | Luzon Grid-11/21/2023 15:17: Pagbilao EHV SS PCB 9Z-03CB04PGB energized at 1503H (Planned Outage) [WEBSMS] | CLUZ
11/21/2023 1:08:26 PM | Mindanao Grid-11/21/2023 13:11: AG5 U1 Online at 1307H. (Planned Outage). PMS(GOMP). [WEBSMS] | CMIN
11/21/2023 12:53:16 PM | [NSO Update] Mindanao Grid-11/21/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3045MW, PK=2292MW, RR=80MW, NetOpMargin: PM=673, EVE=712 Highest Unit O/L: GNPK 1&3@138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @80MW, AG4 @147MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/21/2023 12:50:33 PM | [NSO Update] Visayas Grid-11/21/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2448MW, PK=2083MW, RR=94MW, NetOpMargin: PM=270, EVE=252 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @253MW, PGPP1 @38MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/21/2023 12:46:36 PM | [NSO Update] Luzon Grid-11/21/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14472MW, PK=10514MW, RR=433MW, NetOpMargin: PM=3525, EVE=3284 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 3 @170MW, ILIJAN A @510MW, ILIJAN B @190MW, STA. RITA 10 @220MW, STA. RITA 20 @220MW, STA. RITA 40 @220MW [WEBSMS] | CLUZ
11/21/2023 11:27:15 AM | Luzon Grid-11/21/2023 11:27: Sta. Rita Module 60 online at 1125H (Unplanned Outage) [WEBSMS] | CLUZ
11/21/2023 11:12:52 AM | Luzon Grid-11/21/2023 11:13: Pagbilao EHV SS PCB 9Z-03CB04PGB de-energized at 1109H (Planned Outage) [WEBSMS] | CLUZ
11/21/2023 11:09:10 AM | Mindanao Grid-11/21/2023 11:12: SBL B U1 Online at 1048H. (Unplanned Outage). From FO. [WEBSMS] | CMIN
11/21/2023 11:06:08 AM | Mindanao Grid-11/21/2023 11:09: SBL B U1 tripped with 10.5MW load at 1038H. (Unplanned Outage). [WEBSMS] | CMIN
11/21/2023 11:04:05 AM | Mindanao Grid-11/21/2023 11:07: MDP Online at 1052H. (Unplanned Outage) from FO. [WEBSMS] | CMIN
11/21/2023 11:03:13 AM | Mindanao Grid-11/21/2023 11:06: MDP tripped with 4MW Load at 1048H. (Unplanned Outage). [WEBSMS] | CMIN
11/21/2023 10:59:25 AM | Mindanao Grid-11/21/2023 11:02: WMPC 6 Online as RPS at 1050H. For RPS. System Voltage Requirement. [WEBSMS] | CMIN
11/21/2023 10:39:27 AM | Mindanao Grid-11/21/2023 10:42: MDP (Supreme Mati) Online at 0900H. Follow RTD. [WEBSMS] | CMIN
11/21/2023 10:38:03 AM | Mindanao Grid-11/21/2023 10:41: Sibulan B U1 Online at 1032H. (Unplanned Outage). From FO. [WEBSMS] | CMIN
11/21/2023 10:36:50 AM | Mindanao Grid-11/21/2023 10:40: Sibulan B U1 tripped with 11MW load at 1022H. (Unplanned Outage) No relay indication. For further investigation. [WEBSMS] | CMIN
11/21/2023 10:17:52 AM | Mindanao Grid-11/21/2023 10:21: Sibulan AB/TU1 Online at 1016H. (Unplanned Outage). From FO. [WEBSMS] | CMIN
11/21/2023 9:14:19 AM | Mindanao Grid-11/21/2023 09:17: SIBULAN HYDRO PLANTs tripped with a load of 30MW at 0903H. (Unplanned Outage). [WEBSMS] | CMIN
11/21/2023 8:53:26 AM | Mindanao Grid-11/21/2023 08:56: WMPC DG Online as RPS at 0850H. For RPS. System Voltage Requirement. [WEBSMS] | CMIN
11/21/2023 8:39:26 AM | Mindanao Grid-11/21/2023 08:42: Jasaan SS 138KV Bus 1 deenergized at 0832H. Planned outage. [WEBSMS] | CMIN
11/21/2023 6:48:31 AM | Visayas Grid-11/21/2023 06:48: DaanBantayan SS LPC feeder isolated at 0608H and reconnected to new energized Dayhagon 10 MVA transformer at 0640H. [WEBSMS] | CVIS
11/21/2023 6:36:06 AM | Luzon Grid-11/21/2023 06:36: Las Pinas (Zapote) SS 300MVA T04 restored at 0631H (Planned Outage) [WEBSMS] | CLUZ
11/21/2023 5:58:39 AM | [NSO Update] Luzon Grid-11/21/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14304MW, PK=10476MW, RR=406MW, NetOpMargin: AM=3422, PM=3134, EVE=3033 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @170MW, ILIJAN A @430MW, ILIJAN B @190MW, SAN GABRIEL @330MW, STA. RITA 10 @220MW, STA. RITA 20 @220MW, STA. RITA 40 @220MW [WEBSMS] | CLUZ
11/21/2023 5:50:37 AM | [NSO Update] Mindanao Grid-11/21/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3018MW, PK=2209MW, RR=80MW, NetOpMargin: AM=729, PM=563, EVE=598 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @80MW, AG4 @90MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @120MW [WEBSMS] | CMIN
11/21/2023 5:49:28 AM | [NSO Update] Visayas Grid-11/21/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2417MW, PK=1975MW, RR=85MW, NetOpMargin: AM=357, PM=194, EVE=218 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @292MW, PGPP1 @38MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/21/2023 5:48:16 AM | [NSO Update] Mindanao Grid-11/21/2023 05:51: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CMIN
11/21/2023 5:48:04 AM | [NSO Update] Visayas Grid-11/21/2023 05:48: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CVIS
11/21/2023 5:47:50 AM | [NSO Update] Luzon Grid-11/21/2023 05:48: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
11/21/2023 2:25:29 AM | Luzon Grid-11/21/2023 02:25: Paco 300MVA T05 (Customer Owned) restored at 0220H (Planned Outage) [WEBSMS] | CLUZ
11/21/2023 12:21:17 AM | Luzon Grid-11/21/2023 00:21: Paco 300MVA T05 (Customer Owned) was de-energized at 0014H. (Planned Outage) [WEBSMS] | CLUZ
11/20/2023 9:15:35 PM | Mindanao Grid-11/20/2023 21:19: WMPC DG5 Shutdown as RPS at 2113H. From RPS. System Voltage Requirement. [WEBSMS] | CMIN
11/20/2023 9:07:07 PM | Mindanao Grid-11/20/2023 21:10: MDP Shutdown at 2105H. Follow RTD. [WEBSMS] | CMIN
11/20/2023 8:29:47 PM | Mindanao Grid-11/20/2023 20:33: AGC(Lake Mainit Hydro) Online at 2226H. (Unplanned Outage) From FO. [WEBSMS] | CMIN
11/20/2023 8:26:45 PM | Mindanao Grid-11/20/2023 20:30: AGC (Lake Mainit Hydro) with a load of 11.5MW tripped at 2022H. (Unplanned Outage). [WEBSMS] | CMIN
11/20/2023 8:25:56 PM | Luzon Grid-11/20/2023 20:26: Las Pinas (Zapote) SS 300MVA T04 de-energized at 2023H (Planned Outage) [WEBSMS] | CLUZ
11/20/2023 7:57:28 PM | Luzon Grid-11/20/2023 19:57: Sta. Rita Module 30 shutdown at 1953H (Planned Outage) [WEBSMS] | CLUZ
11/20/2023 7:53:16 PM | Visayas Grid-11/20/2023 19:53: Visayas Spot Peak for November 20, 2023, 2117 MW at 1800H. Highest peak for the year is 2458 MW at 1422H on May 17, 2023 [WEBSMS] | CVIS
11/20/2023 6:04:12 PM | [NSO Update] Mindanao Grid-11/20/2023 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2984MW, PK=2235MW, RR=80MW, NetOpMargin: EVE=669 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/20/2023 5:55:48 PM | [NSO Update] Visayas Grid-11/20/2023 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2361MW, PK=2083MW, RR=85MW, NetOpMargin: EVE=192 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @287MW, PGPP1 @76MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/20/2023 5:53:47 PM | [NSO Update] Luzon Grid-11/20/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13724MW, PK=10213MW, RR=372MW, NetOpMargin: EVE=3139 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @200MW, CLC2 @175MW, ILIJAN A @430MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/20/2023 4:14:44 PM | Mindanao Grid-11/20/2023 16:18: WMPC DG6 shutdown at 1613H. From RPS. System Voltage Requirement. [WEBSMS] | CMIN
11/20/2023 3:14:25 PM | Luzon Grid-11/20/2023 15:14: Masinloc U3 onlineonline at 1507H (Unplanned Outage) [WEBSMS] | CLUZ
11/20/2023 1:08:22 PM | Mindanao Grid-11/20/2023 13:11: Talomo1 U2 Shutdown at 0913H. Due to Insufficient Water Supply(IWS). Follow RTD. [WEBSMS] | CMIN
11/20/2023 12:59:24 PM | [NSO Update] Luzon Grid-11/20/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14385MW, PK=10538MW, RR=383MW, NetOpMargin: PM=3464, EVE=3314 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/20/2023 12:53:30 PM | [NSO Update] Visayas Grid-11/20/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2438MW, PK=2027MW, RR=85MW, NetOpMargin: PM=326, EVE=260 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @ 298MW, PGPP1 @ 76MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
11/20/2023 12:51:04 PM | [NSO Update] Mindanao Grid-11/20/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3024MW, PK=2337MW, RR=80MW, NetOpMargin: PM=607, EVE=661 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/20/2023 12:39:49 PM | Mindanao Grid-11/20/2023 12:43: LPE Online at 1226H. (Unplanned Outage) From FO. [WEBSMS] | CMIN
11/20/2023 10:52:29 AM | Mindanao Grid-11/20/2023 10:55: WMPC DG6 Online as RPS at 1050H. For RPS. System Voltage Requirement. [WEBSMS] | CMIN
11/20/2023 10:40:34 AM | Mindanao Grid-11/20/2023 10:43: LPE tripped with a load of 6MW. (Unplanned Outage). [WEBSMS] | CMIN
11/20/2023 10:21:53 AM | Mindanao Grid-11/20/2023 10:25: WMPC DG5 Online at 1018H. Replacement Unit. For RPS. System Voltage Requirement. [WEBSMS] | CMIN
11/20/2023 10:15:23 AM | Mindanao Grid-11/20/2023 10:18: WMPC DG4 tripped with 8.5MW load at 1012H. As RPS. System Voltage Requirement. [WEBSMS] | CMIN
11/20/2023 9:06:39 AM | Mindanao Grid-11/20/2023 09:10: MDP Online at 0859H. Follow RTD. [WEBSMS] | CMIN
11/20/2023 9:05:07 AM | Mindanao Grid-11/20/2023 09:08: Agus6 U4 Shutdown at 0902H. (Planned Outage) PMS. [WEBSMS] | CMIN
11/20/2023 8:54:28 AM | Mindanao Grid-11/20/2023 08:57: WMPC DG4 Online at 0850H. For RPS. System Voltage Requirement. [WEBSMS] | CMIN
11/20/2023 7:29:50 AM | Mindanao Grid-11/20/2023 07:33: MF2 U1 shutdown at 0705H.(Planned Outage) Follow RTD. [WEBSMS] | CMIN
11/20/2023 5:49:32 AM | [NSO Update] Mindanao Grid-11/20/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3005MW, PK=2195MW, RR=80MW, NetOpMargin: AM=730, PM=629, EVE=647 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @80MW, AG4 @139MW, AG5 @25MW, AG6 @155MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/20/2023 5:48:15 AM | [NSO Update] Visayas Grid-11/20/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2447MW, PK=2022MW, RR=85MW, NetOpMargin: AM=341, PM=170, EVE=170 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 298MW, PGPP1 @ 76MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
11/20/2023 5:47:24 AM | Mindanao Grid-11/20/2023 05:50: Lake Mainit HEPP online at 0427H. Unplanned Outage. [WEBSMS] | CMIN
11/20/2023 5:46:58 AM | [NSO Update] Luzon Grid-11/20/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13584MW, PK=9905MW, RR=377MW, NetOpMargin: AM=3302, PM=2157, EVE=2101 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/20/2023 5:40:54 AM | Luzon Grid-11/20/2023 05:41: Sual 1 online at 0538H (Planned Outage) [WEBSMS] | CLUZ
11/20/2023 5:28:19 AM | Luzon Grid-11/20/2023 05:28: San Lorenzo 50 online at 0525H (Unplanned Outage). [WEBSMS] | CLUZ
11/20/2023 4:41:21 AM | [NSO Update] Mindanao Grid-11/20/2023 04:44: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0440H with power going to Visayas. [WEBSMS] | CMIN
11/20/2023 4:41:06 AM | [NSO Update] Visayas Grid-11/20/2023 04:41: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0440H with power going to Visayas. [WEBSMS] | CVIS
11/20/2023 4:23:02 AM | Mindanao Grid-11/20/2023 04:26: Lake Mainit HEPP with 11MW gross generation tripped at 0417H. Indication Power Signal Fault. Lowest Frequency=59.94Hz. Unplanned Outage. [WEBSMS] | CMIN
11/20/2023 4:16:53 AM | [NSO Update] Mindanao Grid-11/20/2023 04:20: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CMIN
11/20/2023 4:16:33 AM | [NSO Update] Visayas Grid-11/20/2023 04:16: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CVIS
11/20/2023 4:16:07 AM | [NSO Update] Luzon Grid-11/20/2023 04:16: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
11/20/2023 4:06:00 AM | Luzon Grid-11/20/2023 04:06: San Lorenzo 50 tripped at 0358H with a load of 111MW. The lowest frequency recorded is 59.591, No ALD (Unplanned Outage) [WEBSMS] | CLUZ
11/19/2023 11:52:59 PM | Mindanao Grid-11/19/2023 23:56: Butuan - Placer 138KV Line 1 restored at 2345H. Planned Outage. [WEBSMS] | CMIN
11/19/2023 11:46:32 PM | [NSO Update] Mindanao Grid-11/19/2023 23:49: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2345H from forward power direction. [WEBSMS] | CMIN
11/19/2023 11:45:55 PM | [NSO Update] Visayas Grid-11/19/2023 23:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2345H from forward power direction. [WEBSMS] | CVIS
11/19/2023 10:02:22 PM | Luzon Grid-11/19/2023 22:02: Masinloc U3 at 75MW tripped at 2200H (Unplanned Outage) [WEBSMS] | CLUZ
11/19/2023 9:57:27 PM | Mindanao Grid-11/19/2023 22:00: Butuan SS 138KV Bus no. 2 restored at 2154H. Planned Outage. [WEBSMS] | CMIN
11/19/2023 9:08:17 PM | Mindanao Grid-11/19/2023 21:11: SUPREME POWER Mati cut-out at 2105H. End of RTD. [WEBSMS] | CMIN
11/19/2023 8:37:58 PM | Luzon Grid-11/19/2023 20:38: San Lorenzo 50 online at 2035H (Planned Outage) [WEBSMS] | CLUZ
11/19/2023 8:23:39 PM | Luzon Grid-11/19/2023 20:23: Balsik 230kV Bus 2 restored at 2022H (Planned Outage) [WEBSMS] | CLUZ
11/19/2023 6:43:26 PM | Luzon Grid-11/19/2023 18:43: Masinloc 3 online at 1839H (Unplanned Outage) [WEBSMS] | CLUZ
11/19/2023 6:06:58 PM | Mindanao Grid-11/19/2023 18:10: Butuan SS 138KB Bus 2 deenergized at 1803H. Planned Outage. [WEBSMS] | CMIN
11/19/2023 5:50:58 PM | [NSO Update] Mindanao Grid-11/19/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2980MW, PK=2011MW, RR=80MW, NetOpMargin: EVE=889 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @80MW, AG4 @139MW, AG5 @25MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/19/2023 5:49:14 PM | [NSO Update] Visayas Grid-11/19/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2418MW, PK=1877MW, RR=83MW, NetOpMargin: EVE=457 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 305MW, PGPP1 @ 76MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
11/19/2023 5:47:46 PM | [NSO Update] Luzon Grid-11/19/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12952MW, PK=8957MW, RR=356MW, NetOpMargin: EVE=3639 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 430MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/19/2023 5:25:01 PM | Luzon Grid-11/19/2023 17:25: Bolo(Kadampat)-Nagsaag 500kV line 1 restored at 1724H (Planned Outage) [WEBSMS] | CLUZ
11/19/2023 4:50:41 PM | Mindanao Grid-11/19/2023 16:54: Maramag SS 75MVA Power Transformer no. 1 restored at 1647H. Planned Outage. [WEBSMS] | CMIN
11/19/2023 4:48:42 PM | Luzon Grid-11/19/2023 16:48: San Jose 300MVA T03 energized at 1647H (Planned Outage) [WEBSMS] | CLUZ
11/19/2023 3:39:30 PM | Visayas Grid-11/19/2023 15:39: Cebu-Mandaue 138KV line 1 energized @ 1517H. Planned Outage [WEBSMS] | CVIS
11/19/2023 3:15:45 PM | Mindanao Grid-11/19/2023 15:19: LAKE MAINIT Hydro cut-in at 1512H. (Unplanned Outage) [WEBSMS] | CMIN
11/19/2023 3:14:22 PM | Mindanao Grid-11/19/2023 15:17: WMPC DG04 declared available at 1500H (from forced outage). [WEBSMS] | CMIN
11/19/2023 3:08:39 PM | Mindanao Grid-11/19/2023 15:12: LAKE MAINIT Hydro tripped with 11.2MW load at 1459H. Lowest system frequency recorded was 59.83Hz. Indication: 81OU Gen Over/Under Frequency Operated. (Unplanned Outage) [WEBSMS] | CMIN
11/19/2023 3:03:50 PM | Mindanao Grid-11/19/2023 15:07: Culaman SS 230KV Bus no. 2 restored at 1455H. Planned Outage. [WEBSMS] | CMIN
11/19/2023 1:56:08 PM | Luzon Grid-11/19/2023 13:56: Binan-Calamba 230kV line 1 and Binan-Calamba 230kV line 2 were restored at 1352H and 1354H respectively. (Planned Outage) [WEBSMS] | CLUZ
11/19/2023 1:37:59 PM | Mindanao Grid-11/19/2023 13:41: LAKE MAINIT Hydro cut-in at 1300H. (Unplanned Outage) [WEBSMS] | CMIN
11/19/2023 1:36:32 PM | Mindanao Grid-11/19/2023 13:39: LIBERTAD POWER tripped with 6MW load at 1320H. Lowest recorded system frequency was 59.96MW. Indication: Turbine Trip. (Unplanned Outage) [WEBSMS] | CMIN
11/19/2023 1:04:35 PM | [NSO Update] Visayas Grid-11/19/2023 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2466MW, PK=1687MW, RR=75MW, NetOpMargin: PM=704, EVE=446 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @334MW, PGPP1 @76MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/19/2023 1:00:16 PM | [NSO Update] Luzon Grid-11/19/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13583MW, PK=8668MW, RR=356MW, NetOpMargin: PM=4559, EVE=3592 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @430MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/19/2023 12:59:28 PM | Mindanao Grid-11/19/2023 13:02: LAKE MAINIT Hydro tripped with 11.2MW load at 1250H. Lowest system frequency recorded was 60.1Hz. Indication: Overvoltage. (Unplanned Outage) [WEBSMS] | CMIN
11/19/2023 12:30:05 PM | Mindanao Grid-11/19/2023 12:33: LAKE MAINIT Hydro cut-in at 1036H. (Unplanned Outage) [WEBSMS] | CMIN
11/19/2023 10:31:30 AM | Mindanao Grid-11/19/2023 10:34: LAKE MAINIT Hydro tripped with 11.3MW load at 1027H. Lowest system frequency recorded was 59.95Hz. Indication: Power Signal Fault. (Unplanned Outage) [WEBSMS] | CMIN
11/19/2023 10:23:44 AM | Mindanao Grid-11/19/2023 10:27: LAKE MAINIT Hydro cut-in at 1017H. (Unplanned Outage) [WEBSMS] | CMIN
11/19/2023 10:21:40 AM | Mindanao Grid-11/19/2023 10:25: LAKE MAINIT Hydro tripped with 11.2MW load at 1006H. Lowest system frequency recorded was 60.0Hz. Indication: Power Signal Fault. (Unplanned Outage) [WEBSMS] | CMIN
11/19/2023 9:18:54 AM | Mindanao Grid-11/19/2023 09:22: SUPREME POWER Mati (MDP) cut-in at 0900H. MO dispatched (RTD). [WEBSMS] | CMIN
11/19/2023 9:08:11 AM | Mindanao Grid-11/19/2023 09:11: (Correction) AGUS 2 Unit 3 shutdown at 0901H for PMS (Non-GOMP). (Planned Outage) [WEBSMS] | CMIN
11/19/2023 9:07:22 AM | Mindanao Grid-11/19/2023 09:10: AGUS 2 Unit 1 shutdown at 0901H for PMS (Non-GOMP). (Planned Outage) [WEBSMS] | CMIN
11/19/2023 8:42:52 AM | Luzon Grid-11/19/2023 08:42: Balsik 230kV Bus 2 was de-energized at 0840H. (Planned Outage) [WEBSMS] | CLUZ
11/19/2023 8:31:08 AM | [NSO Update] Mindanao Grid-11/19/2023 08:34: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0828H with power going to Visayas. [WEBSMS] | CMIN
11/19/2023 8:30:48 AM | [NSO Update] Visayas Grid-11/19/2023 08:30: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0828H with power going to Visayas. [WEBSMS] | CVIS
11/19/2023 8:12:37 AM | Luzon Grid-11/19/2023 08:12: Calamba-Binan 230kV line 1 and Calamba-Binan 230kV line 2 were de-energized at 0808H and 0810H respectively. (Planned Outage) [WEBSMS] | CLUZ
11/19/2023 8:06:49 AM | Mindanao Grid-11/19/2023 08:10: LAKE MAINIT Hydro cut-in at 0747H. (Unplanned Outage) [WEBSMS] | CMIN
11/19/2023 7:41:37 AM | Mindanao Grid-11/19/2023 07:45: LAKE MAINIT Hydro tripped with 11.2MW load at 0734H. Lowest system frequency recorded was 60.03Hz. Indication: Excitation Voltage Alarm. (Unplanned Outage) [WEBSMS] | CMIN
11/19/2023 7:13:19 AM | Visayas Grid-11/19/2023 07:13: Colon-Veco 69KV line auto tripped @0658H with load of 12MW. Unplanned Outage [WEBSMS] | CVIS
11/19/2023 6:51:10 AM | Mindanao Grid-11/19/2023 06:54: Maramag SS 75MVA Power Transformer no. 1 deenergized at 0618H. Planned Outage. [WEBSMS] | CMIN
11/19/2023 6:45:14 AM | Mindanao Grid-11/19/2023 06:48: Butuan - Placer 138KV Line 1 deenergized at 0631H. Planned Outage. [WEBSMS] | CMIN
11/19/2023 6:40:23 AM | Luzon Grid-11/19/2023 06:40: San Jose 300MVA T03 was de-energized at 0638H. (Planned Outage) [WEBSMS] | CLUZ
11/19/2023 6:31:42 AM | Visayas Grid-11/19/2023 06:31: Cebu-Mandaue 138KV line 1 manually open @0618H. Planned Outage [WEBSMS] | CVIS
11/19/2023 6:16:03 AM | Luzon Grid-11/19/2023 06:16: Bolo(Kadampat)-Nagsaag 500kV line 1 was de-energized at 0613H. (Planned Outage) [WEBSMS] | CLUZ
11/19/2023 6:05:58 AM | [NSO Update] Mindanao Grid-11/19/2023 06:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3106MW, PK=1757MW, RR=68MW, NetOpMargin: AM=1281, PM=1092, EVE=892 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @80MW, AG4 @139MW, AG5 @25MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/19/2023 6:02:02 AM | [NSO Update] Visayas Grid-11/19/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2391MW, PK=1673MW, RR=75MW, NetOpMargin: AM=643, PM=608, EVE=387 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @80.3MW, LEYTE A @334MW, PGPP1 @76MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/19/2023 5:57:12 AM | [NSO Update] Luzon Grid-11/19/2023 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13664MW, PK=8454MW, RR=355MW, NetOpMargin: AM=4855, PM=4580, EVE=3704 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 430MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/19/2023 5:16:17 AM | Mindanao Grid-11/19/2023 05:19: Culaman SS 230kV Bus No.2 deenergized at 0506H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
11/19/2023 4:35:25 AM | [NSO Update] Mindanao Grid-11/19/2023 04:38: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 465 km East of Surigao City, Surigao del Norte (9.3�N, 129.7�E). Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CMIN
11/19/2023 4:34:45 AM | [NSO Update] Visayas Grid-11/19/2023 04:34: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 465 km East of Surigao City, Surigao del Norte (9.3�N, 129.7�E). Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CVIS
11/19/2023 4:33:46 AM | [NSO Update] Luzon Grid-11/19/2023 04:33: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 465 km East of Surigao City, Surigao del Norte (9.3�N, 129.7�E). Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
11/19/2023 3:00:58 AM | [NSO Update] Visayas Grid-11/19/2023 03:01: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0257H from forward power direction. [WEBSMS] | CVIS
11/19/2023 3:00:24 AM | [NSO Update] Mindanao Grid-11/19/2023 03:03: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0257H from forward power direction. [WEBSMS] | CMIN
11/19/2023 12:55:22 AM | Mindanao Grid-11/19/2023 00:58: Lake Mainit HEPP online at 0044H. Unplanned Outage. [WEBSMS] | CMIN
11/19/2023 12:31:45 AM | Luzon Grid-11/19/2023 00:31: San Lorenzo Module 60 tripped at 0026H from a 101MW load. The lowest system frequency was 59.639Hz. (On-going Unit tuning for LNG Commissioning-Unplanned Outage) [WEBSMS] | CLUZ
11/19/2023 12:29:47 AM | Mindanao Grid-11/19/2023 00:33: Lake Mainit HEPP with 11MW gross generation tripped at 0025H. Indication: Power Signal Fault. Unplanned Outage. [WEBSMS] | CMIN
11/18/2023 10:27:01 PM | Mindanao Grid-11/18/2023 22:30: Lake Mainit HEPP online at 2224H. Unplanned Outage. [WEBSMS] | CMIN
11/18/2023 8:35:02 PM | Mindanao Grid-11/18/2023 20:38: Polanco SS Power Transformer No.1 energized at 2026H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
11/18/2023 8:33:06 PM | Mindanao Grid-11/18/2023 20:36: MCC U3 (Minergy Coal Balingasag) Online at 2024H, from Reserved Shutdown. [WEBSMS] | CMIN
11/18/2023 7:21:01 PM | Visayas Grid-11/18/2023 19:21: Cebu SS 138 kV Bus 1 energized at 1916H. (Planned Outage) [WEBSMS] | CVIS
11/18/2023 5:52:45 PM | [NSO Update] Mindanao Grid-11/18/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2984MW, PK=2067MW, RR=80MW, NetOpMargin: EVE=838 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/18/2023 5:45:19 PM | [NSO Update] Visayas Grid-11/18/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2368MW, PK=1951MW, RR=85MW, NetOpMargin: EVE=332 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @ 80.3MW, Leyte A @ 340MW, PGPP1 @ 76MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
11/18/2023 5:41:29 PM | [NSO Update] Luzon Grid-11/18/2023 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12919MW, PK=9502MW, RR=389MW, NetOpMargin: EVE=3028 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/18/2023 5:38:28 PM | Luzon Grid-11/18/2023 17:38: Bayombong-Matuno 69kV Line (Customer Owned) restored at 1737H (Planned Outage) [WEBSMS] | CLUZ
11/18/2023 4:59:24 PM | Mindanao Grid-11/18/2023 17:02: Agus 6 U3 online at 1654H. Unplanned Outage. [WEBSMS] | CMIN
11/18/2023 4:59:06 PM | Luzon Grid-11/18/2023 16:59: San Juan (Kalayaan)-Calauan 230kV Line 1 restored at 1658H (Planned Outage) [WEBSMS] | CLUZ
11/18/2023 4:24:20 PM | Mindanao Grid-11/18/2023 16:27: Agus 6 U3 with 39MW gross generation tripped at 1611H. Indication: Overspeed, 5C-Complete Shutdown. Frequency Dipped=59.6349Hz. Unplanned Outage. [WEBSMS] | CMIN
11/18/2023 4:21:33 PM | Mindanao Grid-11/18/2023 16:24: Agus 6 U3 with 39MW gross generation tripped at 1611H. Indication: Overspeed, 5C-Complete Shutdown. Frequency Dipped=59.6349Hz. Unplanned Outage. [WEBSMS] | CMIN
11/18/2023 4:10:14 PM | Luzon Grid-11/18/2023 16:10: Calaca Unit 1 online at 1608H (Planned Outage) [WEBSMS] | CLUZ
11/18/2023 3:23:42 PM | Mindanao Grid-11/18/2023 15:27: WMPC DG05 shutdown at 1513H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/18/2023 1:36:04 PM | Luzon Grid-11/18/2023 13:36: San Jose - Angat 115kV Line 3 energized at San Jose side at 1334H. (Planned Outage) [WEBSMS] | CLUZ
11/18/2023 1:00:27 PM | [NSO Update] Luzon Grid-11/18/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13425MW, PK=9911MW, RR=400MW, NetOpMargin: PM=3114, EVE=2741 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 430MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/18/2023 12:54:54 PM | [NSO Update] Mindanao Grid-11/18/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3015MW, PK=2052MW, RR=80MW, NetOpMargin: PM=883, EVE=824 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/18/2023 12:51:53 PM | [NSO Update] Visayas Grid-11/18/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2479MW, PK=1898MW, RR=85MW, NetOpMargin: PM=496, EVE=346 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @ 80.3MW, Leyte A @ 334MW, PGPP1 @ 76MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
11/18/2023 11:57:41 AM | Mindanao Grid-11/18/2023 12:01: WMPC DG05 online at 1150H, as replacement of WMPC DG04 which tripped earlier at 1142H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/18/2023 11:49:04 AM | Mindanao Grid-11/18/2023 11:52: WMPC DG04 with 8.5MW gross generation and run as RPS, tripped at 1142H. Indication: HT Low Pressure Stop. Unplanned Outage. [WEBSMS] | CMIN
11/18/2023 11:45:45 AM | Mindanao Grid-11/18/2023 11:49: Pulangi 4 U3 online at 1127H. Planned Outage. (Affected by the Planned outage of Maramag 138kV Bus #1) [WEBSMS] | CMIN
11/18/2023 11:35:33 AM | Luzon Grid-11/18/2023 11:35: Balsik-SBMA 230kV Line 1 restored at 1134H. (Planned Outage) [WEBSMS] | CLUZ
11/18/2023 11:26:37 AM | Mindanao Grid-11/18/2023 11:29: Maramag SS 138KV Bus 1 energized at 1117H. Planned Outage / Non-GOMP [WEBSMS] | CMIN
11/18/2023 11:25:59 AM | Mindanao Grid-11/18/2023 11:29: Libertad Power (Biomass) online at 0929H. Unplanned Outage. [WEBSMS] | CMIN
11/18/2023 9:53:01 AM | Mindanao Grid-11/18/2023 09:56: WMPC DG04 Online at 0950H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/18/2023 8:19:06 AM | Luzon Grid-11/18/2023 08:19: Bayombong-Matuno 69kV Line (Customer Owned) de-energized at 0815H. (Planned Outage) [WEBSMS] | CLUZ
11/18/2023 8:13:18 AM | Mindanao Grid-11/18/2023 08:16: Polanco SS Power Transformer No.1 deenergized at 0725H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
11/18/2023 7:30:16 AM | Mindanao Grid-11/18/2023 07:33: Libertad Power (Biomass) with 5MW gross generation tripped at 1717H. Indication: Main Steam Line High Temperature. Unplanned Outage. [WEBSMS] | CMIN
11/18/2023 7:07:40 AM | Luzon Grid-11/18/2023 07:07: Balsik-SBMA 230kV Line 1 de-energized at 0707H. (Planned Outage) [WEBSMS] | CLUZ
11/18/2023 6:44:27 AM | Mindanao Grid-11/18/2023 06:47: Maramag SS 138KV Bus 1 de-energized at 0614H. Planned Outage / Non-GOMP [WEBSMS] | CMIN
11/18/2023 6:42:55 AM | Mindanao Grid-11/18/2023 06:46: Euro Hydro (NBT) shutdown at 0610H. Affected by the planned outage of Nabunturan-Monkayo 69kV line. Planned Outage. [WEBSMS] | CMIN
11/18/2023 6:38:52 AM | Visayas Grid-11/18/2023 06:38: Cebu Bus 1 manually open @0617H, pre arranged maintenance. Planned Outage [WEBSMS] | CVIS
11/18/2023 6:37:37 AM | Visayas Grid-11/18/2023 06:37: TPC 1 A emergency cut-out @0626H, possible boiler tube leak. Unplanned Outage [WEBSMS] | CVIS
11/18/2023 6:17:51 AM | Luzon Grid-11/18/2023 06:17: San Juan (Kalayaan)-Calauan 230kV Line 1 de-energized at 0617H. (Planned Outage) [WEBSMS] | CLUZ
11/18/2023 6:14:50 AM | Mindanao Grid-11/18/2023 06:18: Lake Mainit HEPP online at 0601H. Unplanned Outage. [WEBSMS] | CMIN
11/18/2023 6:13:20 AM | Mindanao Grid-11/18/2023 06:16: Pulangi 4 Unit #3 shutdown at 0602H. Affected by the shutdown request of P&E at Maramag SS for decommissioning of 7-08CB04MRM. Unplanned Outage. [WEBSMS] | CMIN
11/18/2023 5:48:37 AM | Mindanao Grid-11/18/2023 05:51: LAKE MAINIT Hydro tripped with 10.7MW load at 0542H. Lowest frequency recorded was 59.94Hz. Indication: Power Signal Fault. (Unplanned Outage) [WEBSMS] | CMIN
11/18/2023 5:47:37 AM | [NSO Update] Mindanao Grid-11/18/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2991MW, PK=2002MW, RR=70MW, NetOpMargin: AM=919, PM=841, EVE=792 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @30.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @30MW [WEBSMS] | CMIN
11/18/2023 5:46:24 AM | [NSO Update] Visayas Grid-11/18/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2532MW, PK=2054MW, RR=84MW, NetOpMargin: AM=393, PM=418, EVE=264 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 80.3MW, Leyte A @ 334MW, PGPP1 @ 76MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
11/18/2023 5:44:59 AM | [NSO Update] Luzon Grid-11/18/2023 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13474MW, PK=9590MW, RR=398MW, NetOpMargin: AM=3486, PM=3027, EVE=2679 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 430MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/18/2023 4:58:20 AM | [NSO Update] Luzon Grid-11/18/2023 04:58: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 605 km East of Guiuan, Eastern Samar (10.1�N, 131.2�E). Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
11/18/2023 4:57:42 AM | [NSO Update] Mindanao Grid-11/18/2023 05:01: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 605 km East of Guiuan, Eastern Samar (10.1�N, 131.2�E). Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CMIN
11/18/2023 4:57:24 AM | [NSO Update] Visayas Grid-11/18/2023 04:57: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 605 km East of Guiuan, Eastern Samar (10.1�N, 131.2�E). Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CVIS
11/18/2023 4:46:24 AM | Mindanao Grid-11/18/2023 04:49: Minergy Coal (MCC) Unit 1 with 49.6MW load tripped at 0425H. Lowest frequency recorded was 59.76Hz, Initial Cause: tube leak. [WEBSMS] | CMIN
11/18/2023 2:47:41 AM | Mindanao Grid-11/18/2023 02:51: Therma South (DCP) Unit 2 cut-in at 0242H. (Unplanned Outage) [WEBSMS] | CMIN
11/18/2023 12:09:14 AM | Luzon Grid-11/18/2023 00:09: Masinloc 3 shutdown at 0004H (Planned Outage) [WEBSMS] | CLUZ
11/18/2023 12:08:29 AM | Visayas Grid-11/18/2023 00:08: CEDC U1 cut in at 0006H. (Planned Outage) [WEBSMS] | CVIS
11/18/2023 12:06:49 AM | Mindanao Grid-11/18/2023 00:10: STEAG Unit 2 shutdown at 0000H for PMS (GOMP). (Planned Outage) [WEBSMS] | CMIN
11/17/2023 9:28:42 PM | Mindanao Grid-11/17/2023 21:32: WMPC DG05 shutdown at 2113H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/17/2023 8:59:54 PM | Luzon Grid-11/17/2023 20:59: Binga PCB 8-01CB04BIZ closed at 2059H (Unplanned Outage) [WEBSMS] | CLUZ
11/17/2023 7:54:33 PM | Luzon Grid-11/17/2023 19:54: San Lorenzo 50 shutdown at 1951H (Planned Outage) [WEBSMS] | CLUZ
11/17/2023 7:16:52 PM | Mindanao Grid-11/17/2023 19:20: SMC Unit #1 online at 1909H. Unplanned Outage. [WEBSMS] | CMIN
11/17/2023 7:00:42 PM | Mindanao Grid-11/17/2023 19:04: TSI Unit #2 manually shutdown at 1803H, to facilitate correction of Oil Leak at Induced Draft Fan (IDF). Follow RTD. Emergency shutdown/Unplanned Outage. [WEBSMS] | CMIN
11/17/2023 6:53:30 PM | Mindanao Grid-11/17/2023 18:56: Update: SMC Unit #1 with 150MW gross generation tripped at 1614H. Indication: Induced Draft Fan Stop (IDF). Estimated re-synchronization to the grid is at 2100H today (11-17-2023). [WEBSMS] | CMIN
11/17/2023 6:39:00 PM | Luzon Grid-11/17/2023 18:39: Limay-BCCPP 230kV Line 2 restored at 1838H (Planned Outage). [WEBSMS] | CLUZ
11/17/2023 6:27:40 PM | Mindanao Grid-11/17/2023 18:31: Corrected: Pulangi Unit #1 online at 1657H. Unplanned Outage [WEBSMS] | CMIN
11/17/2023 5:55:55 PM | [NSO Update] Luzon Grid-11/17/2023 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13459MW, PK=10356MW, RR=435MW, NetOpMargin: EVE=2668 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 3 @ 175MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/17/2023 5:54:16 PM | [NSO Update] Mindanao Grid-11/17/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2880MW, PK=1907MW, RR=80MW, NetOpMargin: EVE=893 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/17/2023 5:52:48 PM | [NSO Update] Visayas Grid-11/17/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2575MW, PK=2200MW, RR=87MW, NetOpMargin: EVE=288 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 80.3MW, Leyte A @ 326MW, PGPP1 @ 76MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
11/17/2023 5:44:25 PM | Luzon Grid-11/17/2023 17:44: Binga PCB 8-01CB04BIZ open at 1739H (Unplanned Outage). [WEBSMS] | CLUZ
11/17/2023 5:42:33 PM | Mindanao Grid-11/17/2023 17:45: Lamsan Biomass (LSK) online at 1725H. Unplanned Outage. [WEBSMS] | CMIN
11/17/2023 5:41:23 PM | Mindanao Grid-11/17/2023 17:44: Lamsan Biomass (LSK) with 10MW gross generation tripped at 1716H. Indication: 67N (Earth Fault). Unplanned Outage. [WEBSMS] | CMIN
11/17/2023 5:37:14 PM | Mindanao Grid-11/17/2023 17:40: Mati Diesel (MDP) online at 1723H. Unplanned Outage. [WEBSMS] | CMIN
11/17/2023 5:35:45 PM | Mindanao Grid-11/17/2023 17:39: Mati Diesel (MDP) with 4MW gross generation tripped at 1719H. Indication: Reverse Power. Unplanned Outage. [WEBSMS] | CMIN
11/17/2023 5:32:03 PM | Mindanao Grid-11/17/2023 17:35: Pulangi Unit #3 online at 1718H. Unplanned Outage [WEBSMS] | CMIN
11/17/2023 5:30:29 PM | Mindanao Grid-11/17/2023 17:33: Pulangi Unit #1 online at 1647H. Unplanned Outage [WEBSMS] | CMIN
11/17/2023 5:17:52 PM | Mindanao Grid-11/17/2023 17:21: Baloi - Kauswagan 230kV L2 energized at 1702H. (Planned Outage) [WEBSMS] | CMIN
11/17/2023 5:10:16 PM | Visayas Grid-11/17/2023 17:10: Magdugo - Dumanjug 230 kV Line 2 energized at 1705H. (Planned Outage) [WEBSMS] | CVIS
11/17/2023 5:08:07 PM | Mindanao Grid-11/17/2023 17:11: Pulangi U1 and U3 each with 25MW gross generation tripped at 1614H. Indication to follow. Unplanned Outage [WEBSMS] | CMIN
11/17/2023 5:04:20 PM | Mindanao Grid-11/17/2023 17:07: SMC Unit #1 with 150MW Gross Generation tripped at 1614H. Details to Follow. Unplanned Outage. [WEBSMS] | CMIN
11/17/2023 4:41:11 PM | Luzon Grid-11/17/2023 16:41: Bolo-Labrador 230kV Line 1 restored at 1639H (Planned Outage) [WEBSMS] | CLUZ
11/17/2023 3:06:35 PM | Mindanao Grid-11/17/2023 15:09: Libertad Power (Biomass) online at 1459H. Unplanned Outage. [WEBSMS] | CMIN
11/17/2023 2:50:27 PM | Mindanao Grid-11/17/2023 14:53: Libertad Power (Biomass) with 6MW gross generation tripped at 1300H. Indication: Main Steam Temperature High High. Unplanned Outage. [WEBSMS] | CMIN
11/17/2023 1:08:32 PM | [NSO Update] Mindanao Grid-11/17/2023 13:11: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3179MW, PK=2172MW, RR=80MW, NetOpMargin: PM=927, EVE=870 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/17/2023 1:07:21 PM | [NSO Update] Visayas Grid-11/17/2023 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2665MW, PK=2194MW, RR=84MW, NetOpMargin: PM=387, EVE=221 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @317MW, PGPP1 @76MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/17/2023 1:06:08 PM | [NSO Update] Luzon Grid-11/17/2023 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14164MW, PK=10795MW, RR=452MW, NetOpMargin: PM=2917, EVE=2636 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @175MW, STA. RITA 30 @260MW, ILIJAN A @340MW, ILIJAN B @290MW [WEBSMS] | CLUZ
11/17/2023 12:38:52 PM | Luzon Grid-11/17/2023 12:38: Ilijan GT2-1 shutdown at 1237H. (Unplanned Outage) [WEBSMS] | CLUZ
11/17/2023 12:29:00 PM | Luzon Grid-11/17/2023 12:29: Ilijan GT2-1 online at 1226H. (Unplanned Outage) [WEBSMS] | CLUZ
11/17/2023 10:54:23 AM | Mindanao Grid-11/17/2023 10:57: WMPC DG06 online at 1050H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/17/2023 10:49:53 AM | Mindanao Grid-11/17/2023 10:53: WMPC DG05 online at 1042H as replacement of WMPC DG04 which is on forced outage. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/17/2023 10:37:18 AM | Mindanao Grid-11/17/2023 10:40: WMPC DG04 with 8.5MW gross generation and run as RPS tripped at 1032H. Indication: Oil Mist Concentration High Stop. Unplanned Outage. [WEBSMS] | CMIN
11/17/2023 8:54:24 AM | Mindanao Grid-11/17/2023 08:57: WMPC DG04 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/17/2023 8:11:09 AM | Visayas Grid-11/17/2023 08:11: Magdugo-Dumanjug 230KV Line 2 de-energized at 0805H. (Planned Outage) [WEBSMS] | CVIS
11/17/2023 8:10:55 AM | Luzon Grid-11/17/2023 08:10: Bolo-Labrador 230kV Line 1 de-energized at 0810H. (Planned Outage) [WEBSMS] | CLUZ
11/17/2023 7:36:13 AM | Mindanao Grid-11/17/2023 07:39: Baloi - Kauswagan 230kV L2 de-energized at 0715H. (Planned Outage) [WEBSMS] | CMIN
11/17/2023 7:33:09 AM | Mindanao Grid-11/17/2023 07:36: Agus 5 - Aurora 138kV line ang Agus 5 Unit 1 138kV line energized at 0708H. (Planned Outage) [WEBSMS] | CMIN
11/17/2023 7:13:24 AM | Luzon Grid-11/17/2023 07:13: Limay-BCCPP 230kV Line 2 de-energized at 0712H. (Planned Outage) [WEBSMS] | CLUZ
11/17/2023 6:46:29 AM | Mindanao Grid-11/17/2023 06:49: Agus 5 - Aurora 138kV line ang Agus 5 Unit 1 138kV line de-energized at 0642H. (Planned Outage) [WEBSMS] | CMIN
11/17/2023 5:49:25 AM | [NSO Update] Mindanao Grid-11/17/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3142MW, PK=2191MW, RR=80MW, NetOpMargin: AM=871, PM=779, EVE=855 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/17/2023 5:44:21 AM | [NSO Update] Visayas Grid-11/17/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2566MW, PK=2110MW, RR=83MW, NetOpMargin: AM=373, PM=286, EVE=246 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @334MW, PGPP1 @76MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/17/2023 5:41:12 AM | [NSO Update] Luzon Grid-11/17/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14257MW, PK=10640MW, RR=436MW, NetOpMargin: AM=3181, PM=2836, EVE=2715 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 3 @175MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/17/2023 4:32:01 AM | [NSO Update] Luzon Grid-11/17/2023 04:32: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
11/17/2023 4:29:39 AM | Luzon Grid-11/17/2023 04:29: Dona Imelda (Araneta)- Manila (Paco) 230kV L restored at 0429H (Planned Outage) [WEBSMS] | CLUZ
11/17/2023 4:29:25 AM | [NSO Update] Mindanao Grid-11/17/2023 04:32: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CMIN
11/17/2023 4:28:55 AM | [NSO Update] Visayas Grid-11/17/2023 04:28: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CVIS
11/17/2023 12:41:19 AM | Luzon Grid-11/17/2023 00:41: Bacman U3 online at 0040H (Unplanned Outage) [WEBSMS] | CLUZ
11/17/2023 12:36:46 AM | Luzon Grid-11/17/2023 00:36: Bacman U2 online at 0035H (Unplanned Outage) [WEBSMS] | CLUZ
11/17/2023 12:15:40 AM | Luzon Grid-11/17/2023 00:15: Dona Imelda (Araneta)- Manila (Paco) 230kV L de-energized at 0014H (Planned Outage) [WEBSMS] | CLUZ
11/16/2023 9:18:57 PM | Mindanao Grid-11/16/2023 21:22: WMPC DG05 shutdown at 2113H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/16/2023 8:14:14 PM | Mindanao Grid-11/16/2023 20:17: Euro Hydro (NBT) with 1.2MW gross generation isolated/tripped at 1413H. Affected by the forced outage of NORDECO 13.8kV line. Unplanned Outage. [WEBSMS] | CMIN
11/16/2023 8:10:17 PM | Mindanao Grid-11/16/2023 20:13: Euro Hydro (NBT) online at 0710H. Unplanned outage. [WEBSMS] | CMIN
11/16/2023 6:10:06 PM | [NSO Update] Mindanao Grid-11/16/2023 18:13: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3104MW, PK=2166MW, RR=80MW, NetOpMargin: EVE=858 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/16/2023 6:07:46 PM | [NSO Update] Visayas Grid-11/16/2023 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2532MW, PK=2110MW, RR=82MW, NetOpMargin: EVE=340 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @334MW, PGPP1 @76MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/16/2023 6:03:45 PM | [NSO Update] Luzon Grid-11/16/2023 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13450MW, PK=10487MW, RR=425MW, NetOpMargin: EVE=2538 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 3 @175MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/16/2023 5:47:31 PM | Luzon Grid-11/16/2023 17:47: Lumban-Gumaca 230kV Line 2 restored at 1745H (Planned Outage) [WEBSMS] | CLUZ
11/16/2023 4:46:36 PM | Mindanao Grid-11/16/2023 16:49: Baloi-Kauswagan 230kV Line 1 re-energized at 1634H. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
11/16/2023 4:18:46 PM | Mindanao Grid-11/16/2023 16:22: WMPC DG01 shutdown at 1613H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/16/2023 2:12:33 PM | Mindanao Grid-11/16/2023 14:15: Corrected: Lamsan Biomass (LSK) online at 1158H. Said plant was shutdown last Nov. 1, 2023 at 0001H due to fuel shortage. (Outside Management Control Outage) [WEBSMS] | CMIN
11/16/2023 1:55:55 PM | Mindanao Grid-11/16/2023 13:59: Manolo Fortich-Maramag 138kV L2 re-energized at 1331H. From Planned Outage (Non-GOMP) [WEBSMS] | CMIN
11/16/2023 1:02:18 PM | Mindanao Grid-11/16/2023 13:05: Corrected: Lamsan Biomass (LSK) online at 1158H since Nov. 1, 2023 due to Fuel Shortage (Outside Management Control Outage). [WEBSMS] | CMIN
11/16/2023 12:59:07 PM | [NSO Update] Mindanao Grid-11/16/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3180MW, PK=2192MW, RR=80MW, NetOpMargin: PM=908, EVE=946 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/16/2023 12:42:19 PM | [NSO Update] Visayas Grid-11/16/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2612MW, PK=2198MW, RR=79MW, NetOpMargin: PM=335, EVE=236 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @315MW, PGPP1 @38MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/16/2023 12:40:03 PM | [NSO Update] Luzon Grid-11/16/2023 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14034MW, PK=10874MW, RR=435MW, NetOpMargin: PM=2725, EVE=2413 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 3 @175MW, ILIJAN A @350MW, ILIJAN B @290MW [WEBSMS] | CLUZ
11/16/2023 12:30:46 PM | Luzon Grid-11/16/2023 12:30: SBMA-Subic Solar Power 230kV Line restored at 1229H (Planned Outage) [WEBSMS] | CLUZ
11/16/2023 12:30:43 PM | Mindanao Grid-11/16/2023 12:34: Lamsan Biomass (LSK) online at 1158H, from outside Management Control Outage/Fuel Shortage. [WEBSMS] | CMIN
11/16/2023 10:55:54 AM | Mindanao Grid-11/16/2023 10:59: WMPC DG01 online at 1050H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/16/2023 9:21:27 AM | Mindanao Grid-11/16/2023 09:24: Manolo Fortich-Maramag 138kV Line 2 de-energized at 0813H to facilitate decommissioning & dismantling of PCB 7-10CB24MRM including its associated DS & CT. P&E request under ERC Approved MSRP, Stage 1, Schedule 2. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
11/16/2023 8:56:04 AM | Mindanao Grid-11/16/2023 08:59: WMPC DG05 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/16/2023 8:01:50 AM | Luzon Grid-11/16/2023 08:01: Bacman 1 2 & 3 with total load of 120MW tripped at 0750H, The lowest frequency recorded is 59.623Hz. No ALD (Unplanned Outage) [WEBSMS] | CLUZ
11/16/2023 7:53:34 AM | Mindanao Grid-11/16/2023 07:56: Baloi-Kauswagan 230kV Line 1 de-energized at 0717H for MTD-A to conduct maintenance of M1 & M2 Protections, with ride-on TL maintenance activities. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
11/16/2023 7:06:27 AM | Luzon Grid-11/16/2023 07:06: Lumban-Gumaca 230kV Line 2 de-energized at 0705H (Planned Outage) [WEBSMS] | CLUZ
11/16/2023 6:26:32 AM | Mindanao Grid-11/16/2023 06:29: Lake Mainit (AGC) HEP online at 0604H. (Unplanned Outage). [WEBSMS] | CMIN
11/16/2023 6:24:47 AM | Mindanao Grid-11/16/2023 06:28: Lake Mainit (AGC) HEP with 10.5MW gross generation tripped at 0549H. Indication: Gen. 2 Power Signal Fault. (Unplanned Outage). [WEBSMS] | CMIN
11/16/2023 6:06:40 AM | Luzon Grid-11/16/2023 06:06: SBMA-Subic Solar Power 230kV Line de-energized at 0601H (Planned Outage) [WEBSMS] | CLUZ
11/16/2023 5:48:39 AM | [NSO Update] Mindanao Grid-11/16/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3191MW, PK=2252MW, RR=80MW, NetOpMargin: AM=859, PM=822, EVE=699 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/16/2023 5:44:39 AM | [NSO Update] Visayas Grid-11/16/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2622MW, PK=2267MW, RR=78MW, NetOpMargin: AM=277, PM=356, EVE=265 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @334MW, PGPP1 @76MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
11/16/2023 5:44:07 AM | Mindanao Grid-11/16/2023 05:47: EURO HYDRO (NBT) Tripped with 1.1MW load at 0511H. Indication: For further verification. (Unplanned Outage). [WEBSMS] | CMIN
11/16/2023 5:41:44 AM | [NSO Update] Luzon Grid-11/16/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14026MW, PK=10490MW, RR=430MW, NetOpMargin: AM=3106, PM=2722, EVE=2310 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 3 @120MW, ILIJAN A @350MW, ILIJAN B @290MW [WEBSMS] | CLUZ
11/16/2023 4:24:40 AM | [NSO Update] Visayas Grid-11/16/2023 04:24: Weather Advisory: Shear Line affecting Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CVIS
11/16/2023 4:24:21 AM | [NSO Update] Mindanao Grid-11/16/2023 04:27: Weather Advisory: Shear Line affecting Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
11/16/2023 4:24:15 AM | [NSO Update] Luzon Grid-11/16/2023 04:24: Weather Advisory: Shear Line affecting Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
11/16/2023 4:02:00 AM | Luzon Grid-11/16/2023 04:02: Correction: Ilijan GT1-1 online at 0354H (Unplanned Outage) [WEBSMS] | CLUZ
11/16/2023 3:56:06 AM | Luzon Grid-11/16/2023 03:56: Ilijan GT2-1 online at 0354H (Unplanned Outage) [WEBSMS] | CLUZ
11/16/2023 2:23:04 AM | Luzon Grid-11/16/2023 02:23: Ilijan GT2-1 tripped at 0210H with 160MW load. Lowest frequency was 59.474hz. (Unplanned Outage) [WEBSMS] | CLUZ
11/15/2023 9:07:46 PM | Mindanao Grid-11/15/2023 21:11: SPC Mati shutdown at 2105H. MO Dispatch. [WEBSMS] | CMIN
11/15/2023 9:04:28 PM | Mindanao Grid-11/15/2023 21:08: Agus 5 - Aurora 138kV line restored at 2102H. (Unplanned Outage) [WEBSMS] | CMIN
11/15/2023 8:32:22 PM | Mindanao Grid-11/15/2023 20:35: Lake Mainit HEPP cut in at 2006H. Unplanned Outage [WEBSMS] | CMIN
11/15/2023 8:01:12 PM | Mindanao Grid-11/15/2023 20:04: Lake Mainit (AGC) HEP tripped at 1957H with load of 10.5MW. Indication: Power Signal Fault. (Unplanned Outage). [WEBSMS] | CMIN
11/15/2023 7:42:32 PM | Mindanao Grid-11/15/2023 19:46: Agus 5 - Aurora 138kV line tripped at 1922H. (Unplanned Outage) [WEBSMS] | CMIN
11/15/2023 6:22:20 PM | Mindanao Grid-11/15/2023 18:25: Kauswagan - GNPK 230kV Line 2 energized at 1816H. (Planned Outage) [WEBSMS] | CMIN
11/15/2023 5:40:51 PM | [NSO Update] Mindanao Grid-11/15/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3139MW, PK=2291MW, RR=80MW, NetOpMargin: EVE=768 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/15/2023 5:37:56 PM | [NSO Update] Luzon Grid-11/15/2023 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13458MW, PK=10070MW, RR=430MW, NetOpMargin: EVE=2958 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC2 @175MW, MSLC3 @175MW, ILIJAN A @190MW, ILIJAN B @510MW [WEBSMS] | CLUZ
11/15/2023 5:33:39 PM | [NSO Update] Visayas Grid-11/15/2023 17:33: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2629MW, PK=2282MW, RR=82MW, NetOpMargin: EVE=265 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @334MW, PGPP1 @76MW, TPC (Carmen) @30MW, PDPP3-C @10MW, PDPP3-E @7MW, PDPP3-G @7MW, PDPP3-H @10MW [WEBSMS] | CVIS
11/15/2023 5:24:59 PM | Mindanao Grid-11/15/2023 17:28: WMPC DG04 Declared available at 1700H. (Unplanned Outage) [WEBSMS] | CMIN
11/15/2023 5:15:03 PM | Mindanao Grid-11/15/2023 17:18: ASIGA (ASG) HEP tripped with a load of 4.2MW at 1650H. Indication: For further investigation. (Unplanned Outage) [WEBSMS] | CMIN
11/15/2023 5:11:06 PM | Luzon Grid-11/15/2023 17:11: Lumban-Gumaca 230kV Line 1 restored at 1710H (Planned Outage) [WEBSMS] | CLUZ
11/15/2023 5:10:23 PM | Mindanao Grid-11/15/2023 17:13: Lake Mainit (AGC) HEP tripped at 1651H with load of 10.5MW. Indication: Power Signal Fault. (Unplanned Outage). [WEBSMS] | CMIN
11/15/2023 5:05:32 PM | Mindanao Grid-11/15/2023 17:09: WMPC DG01 shutdown at 1614H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/15/2023 4:41:53 PM | Luzon Grid-11/15/2023 16:42: Ilijan ST1 online at 1631H (Unplanned Outage) [WEBSMS] | CLUZ
11/15/2023 4:18:49 PM | Mindanao Grid-11/15/2023 16:22: WMPC DG01 shutdown at 1614H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/15/2023 3:20:36 PM | Luzon Grid-11/15/2023 15:20: Ilijan ST1 tripped at 1505H (Unplanned Outage) [WEBSMS] | CLUZ
11/15/2023 1:01:14 PM | [NSO Update] Mindanao Grid-11/15/2023 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3174MW, PK=2359MW, RR=80MW, NetOpMargin: PM=736, EVE=781 Highest Unit O/L: GNPD 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/15/2023 12:59:48 PM | [NSO Update] Visayas Grid-11/15/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2599MW, PK=2299MW, RR=79MW, NetOpMargin: PM=221, EVE=208 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @315MW, PGPP1 @76MW, TPC (Carmen) @30MW, PDPP3-C @10MW, PDPP3-E @7MW, PDPP3-G @7MW, PDPP3-H @10MW [WEBSMS] | CVIS
11/15/2023 12:56:37 PM | [NSO Update] Luzon Grid-11/15/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14040MW, PK=10776MW, RR=447MW, NetOpMargin: PM=2816, EVE=2717 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @175MW, ILIJAN A @340MW, ILIJAN B @350MW [WEBSMS] | CLUZ
11/15/2023 12:53:44 PM | [NSO Update] Luzon Grid-11/15/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14040MW, PK=10776MW, RR=447MW, NetOpMargin: PM=2816, EVE=2717 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: CLC2 @175MW, MSLC3 @175MW, ILIJAN A @340MW, ILIJAN B @350MW [WEBSMS] | CLUZ
11/15/2023 12:48:46 PM | Luzon Grid-11/15/2023 12:49: Ilijan GT1-1 shutdown at 1247H (Unplanned Outage) [WEBSMS] | CLUZ
11/15/2023 11:13:26 AM | Luzon Grid-11/15/2023 11:13: Ilijan GT2-1 online at 1112H (Unplanned Outage) [WEBSMS] | CLUZ
11/15/2023 11:03:22 AM | Mindanao Grid-11/15/2023 11:06: SPC Mati cut in at 1101H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
11/15/2023 9:37:18 AM | Luzon Grid-11/15/2023 09:37: Ilijan GT2-1 with a load of 14MW tripped at 0933H (Unplanned Outage) [WEBSMS] | CLUZ
11/15/2023 9:29:52 AM | Luzon Grid-11/15/2023 09:30: Ilijan GT2-1online at 0927H (Unplanned Outage). [WEBSMS] | CLUZ
11/15/2023 8:37:43 AM | Mindanao Grid-11/15/2023 08:41: NagaMin - Zamboanga 138kV Line 2 energized at 0823H. (Planned Outage) [WEBSMS] | CMIN
11/15/2023 8:09:10 AM | Luzon Grid-11/15/2023 08:09: Limay-Batangas II (BPC) 230kV Line 2 de-energized at 0807H (Planned Outage) [WEBSMS] | CLUZ
11/15/2023 7:05:57 AM | Luzon Grid-11/15/2023 07:06: Lumban-Gumaca 230kV Line 1 de-energized at 0705H (Planned Outage) [WEBSMS] | CLUZ
11/15/2023 6:22:30 AM | Mindanao Grid-11/15/2023 06:26: Nagamin-Zamboanga 138KV L2 de-energized at 0543H to facilitate hotspot corrections as requested by MD 1-SS. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
11/15/2023 5:52:57 AM | [NSO Update] Luzon Grid-11/15/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14056MW, PK=10710MW, RR=435MW, NetOpMargin: AM=2911, PM=2739, EVE=2530 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC2 @340MW, MSLC3 @120MW, ILIJAN A @510MW, ILIJAN B @190MW, STA. RITA 30 @260MW [WEBSMS] | CLUZ
11/15/2023 5:51:20 AM | [NSO Update] Mindanao Grid-11/15/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3276MW, PK=2320MW, RR=80MW, NetOpMargin: AM=876, PM=852, EVE=816 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/15/2023 5:47:21 AM | [NSO Update] Visayas Grid-11/15/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2516MW, PK=2264MW, RR=78MW, NetOpMargin: AM=174, PM=193, EVE=251 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @325MW, PGPP1 @76MW, TPC (Carmen) @30MW, PDPP3-C @10MW, PDPP3-E @7MW, PDPP3-G @7MW, PDPP3-H @10MW [WEBSMS] | CVIS
11/15/2023 5:20:35 AM | [NSO Update] Mindanao Grid-11/15/2023 05:24: Weather Update: Shear Line affecting Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
11/15/2023 5:20:23 AM | [NSO Update] Visayas Grid-11/15/2023 05:20: Weather Update: Shear Line affecting Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CVIS
11/15/2023 5:20:11 AM | [NSO Update] Luzon Grid-11/15/2023 05:20: Weather Update: Shear Line affecting Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
11/15/2023 3:45:40 AM | Mindanao Grid-11/15/2023 03:49: Lake Mainit HEPP cut in at 0341H. Unplanned Outage. [WEBSMS] | CMIN
11/15/2023 3:21:59 AM | Mindanao Grid-11/15/2023 03:25: Lake Mainit HEPP with 10.5MW gross generation tripped at 0317H. Indication: Power Signal Fault. Unplanned Outage. [WEBSMS] | CMIN
11/14/2023 5:46:34 PM | [NSO Update] Mindanao Grid-11/14/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3117MW, PK=2354MW, RR=80MW, NetOpMargin: EVE=684 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/14/2023 5:44:23 PM | [NSO Update] Visayas Grid-11/14/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2671MW, PK=2329MW, RR=97MW, NetOpMargin: EVE=245 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @334MW, PGPP1 @76MW, TPC (Carmen) @30MW, PDPP3-C @10MW, PDPP3-E @7MW, PDPP3-H @10MW [WEBSMS] | CVIS
11/14/2023 5:39:09 PM | [NSO Update] Luzon Grid-11/14/2023 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13540MW, PK=10553MW, RR=419MW, NetOpMargin: EVE=2568 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 @170MW, ILIJAN A @510MW, ILIJAN B @190MW, STA. RITA 30 @260MW [WEBSMS] | CLUZ
11/14/2023 5:37:50 PM | Visayas Grid-11/14/2023 17:38: Carcon-Sangi 34.5 kV Line 3 energized at 1734H. (Planned Outage) [WEBSMS] | CVIS
11/14/2023 4:54:55 PM | Mindanao Grid-11/14/2023 16:58: WMPC DG01 shutdown at 1614H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/14/2023 4:19:54 PM | Mindanao Grid-11/14/2023 16:23: WMPC DG01 shutdown at 1614H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/14/2023 2:59:26 PM | Luzon Grid-11/14/2023 14:59: Labo-Gumaca 230kV Line 1 restored at 1457H (Planned Outage) [WEBSMS] | CLUZ
11/14/2023 12:59:34 PM | [NSO Update] Mindanao Grid-11/14/2023 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3150MW, PK=2379MW, RR=80MW, NetOpMargin: PM=691, EVE=745 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @60MW [WEBSMS] | CMIN
11/14/2023 12:58:54 PM | [NSO Update] Visayas Grid-11/14/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2542MW, PK=2277MW, RR=93MW, NetOpMargin: PM=172, EVE=265 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @324MW, PGPP1 @76MW, TPC (Carmen) @30MW, PDPP3-C @ 10MW, PDPP3-E @ 7MW, PDPP3-G @ 7MW, PDPP3-H @ 10MW [WEBSMS] | CVIS
11/14/2023 12:51:45 PM | [NSO Update] Luzon Grid-11/14/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14038MW, PK=11055MW, RR=462MW, NetOpMargin: PM=2571, EVE=2379 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 170MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/14/2023 11:30:17 AM | Mindanao Grid-11/14/2023 11:33: Pulangi 4 HEP Unit 2 shutdown at 1117H with 25MW load due to low reservoir elevation at 283.3m.a.s.l. (Unplanned Outage). [WEBSMS] | CMIN
11/14/2023 10:27:29 AM | Mindanao Grid-11/14/2023 10:31: Zamboanga SS 138KV Busbar # 2 re-energized at 1014H after conducting decommissioning of DS 7-02DS07ZAM & removal of its drop conductor. From Planned Outage / Non-GOMP [WEBSMS] | CMIN
11/14/2023 9:20:17 AM | Mindanao Grid-11/14/2023 09:23: SPC Mati cut in at 0901H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
11/14/2023 8:53:12 AM | Mindanao Grid-11/14/2023 08:56: WMPC DG05 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/14/2023 8:16:46 AM | Visayas Grid-11/14/2023 08:17: Carcon-Sangi 34.5 kV Line 3 de-energized at 0812H. (Planned Outage) [WEBSMS] | CVIS
11/14/2023 8:05:56 AM | Luzon Grid-11/14/2023 08:06: Labo-Gumaca 230kV Line 1 de-energized at 0805H (Planned Outage) [WEBSMS] | CLUZ
11/14/2023 7:35:35 AM | Mindanao Grid-11/14/2023 07:39: Zamboanga SS 138KV Busbar # 2 de-energized at 0641H to conduct decommissioning of DS 7-02DS07ZAM & removal of its drop conductor. Planned Outage / Non-GOMP [WEBSMS] | CMIN
11/14/2023 6:03:40 AM | [NSO Update] Mindanao Grid-11/14/2023 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3190MW, PK=2308MW, RR=80MW, NetOpMargin: AM=801, PM=692, EVE=756 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @90MW [WEBSMS] | CMIN
11/14/2023 5:58:50 AM | [NSO Update] Luzon Grid-11/14/2023 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13976MW, PK=10883MW, RR=455MW, NetOpMargin: AM=2638, PM=2279, EVE=2182 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 120MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/14/2023 5:51:00 AM | [NSO Update] Visayas Grid-11/14/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2721MW, PK=2351MW, RR=93MW, NetOpMargin: AM=277, PM=281, EVE=298 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @ 80.3MW, Leyte A @ 327MW, PGPP1 @ 76MW [WEBSMS] | CVIS
11/14/2023 4:17:18 AM | [NSO Update] Mindanao Grid-11/14/2023 04:20: Weather Update: Shear Line affecting Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
11/14/2023 4:14:43 AM | [NSO Update] Visayas Grid-11/14/2023 04:14: Weather Update: Shear Line affecting Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CVIS
11/14/2023 4:14:27 AM | [NSO Update] Luzon Grid-11/14/2023 04:14: Weather Update: Shear Line affecting Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
11/14/2023 12:44:21 AM | Mindanao Grid-11/14/2023 00:47: Talomo 2 U3 with load 0.134 MW tripped at 2259H. Indication: 51G ground time OC fault. (Unplanned outage). [WEBSMS] | CMIN
11/13/2023 9:18:06 PM | Mindanao Grid-11/13/2023 21:21: WMPC DG05 shutdown at 2114H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/13/2023 6:17:43 PM | [NSO Update] Visayas Grid-11/13/2023 18:17: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2614MW, PK=2326MW, RR=97MW, NetOpMargin: EVE=191 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @ 80.3MW, Leyte A @ 328MW, PGPP1 @ 76MW, PDPP3-C @ 10MW, PDPP3-E @ 7MW, PDPP3-G @ 7MW, PDPP3-H @ 10MW [WEBSMS] | CVIS
11/13/2023 6:11:11 PM | [NSO Update] Luzon Grid-11/13/2023 18:11: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13257MW, PK=10387MW, RR=443MW, NetOpMargin: EVE=2427 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 90MW ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/13/2023 5:52:18 PM | Mindanao Grid-11/13/2023 17:55: Zamboanga - Pitogo 138KV Line 2 restored at 1747H. Planned Outage. [WEBSMS] | CMIN
11/13/2023 4:16:54 PM | Mindanao Grid-11/13/2023 16:20: WMPC DG01 shutdown at 1614H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/13/2023 1:19:32 PM | Mindanao Grid-11/13/2023 13:23: Minergy Coal U3 cut in at 1312H from FO. (Unplanned outage) [WEBSMS] | CMIN
11/13/2023 12:53:29 PM | [NSO Update] Mindanao Grid-11/13/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3204MW, PK=2432MW, RR=80MW, NetOpMargin: PM=692, EVE=733 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @144MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @130MW [WEBSMS] | CMIN
11/13/2023 12:46:30 PM | [NSO Update] Luzon Grid-11/13/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13792MW, PK=11007MW, RR=463MW, NetOpMargin: PM=2322, EVE=2198 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC3 150MW, ILIJAN A @510MW, ILIJAN B @190MW [WEBSMS] | CLUZ
11/13/2023 12:42:46 PM | [NSO Update] Visayas Grid-11/13/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2751MW, PK=2353MW, RR=94MW, NetOpMargin: PM=304, EVE=258 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @ 80.3MW, Leyte A @ 323MW, PGPP1 @ 76MW, PDPP3-C @ 10MW, PDPP3-E @ 7MW, PDPP3-G @ 7MW, PDPP3-H @ 10MW [WEBSMS] | CVIS
11/13/2023 12:16:10 PM | Mindanao Grid-11/13/2023 12:19: TUDAYA 2 U2 cut in at 1041H from FO due to insufficient Water Supply. Outside Management Control Outage. [WEBSMS] | CMIN
11/13/2023 11:21:43 AM | Mindanao Grid-11/13/2023 11:25: Minergy Coal U3 tripped with 55MW load at 1039H. Indication: Turbine main steam inlet temp high. [WEBSMS] | CMIN
11/13/2023 10:02:33 AM | Mindanao Grid-11/13/2023 10:06: STEAG U1 cut in at 0956H from PMS. (Planned Outage) [WEBSMS] | CMIN
11/13/2023 9:04:24 AM | Mindanao Grid-11/13/2023 09:07: SPC Mati cut in at 0900H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
11/13/2023 8:56:24 AM | Mindanao Grid-11/13/2023 08:59: WMPC DG05 online at 0851H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/13/2023 8:11:43 AM | Visayas Grid-11/13/2023 08:11: 2nd Lift - Sangi 34.5 kV Line de-energized at 0807H. (Planned Outage) [WEBSMS] | CVIS
11/13/2023 8:09:45 AM | Mindanao Grid-11/13/2023 08:13: Lake Mainit (AGC) cut-in at 0800H from PMS (Non-GOMP). (Planned Outage) [WEBSMS] | CMIN
11/13/2023 6:53:16 AM | Mindanao Grid-11/13/2023 06:56: Zamboanga - Pitogo 138KV Line 2 deenergized at 0651H. Planned Outage. [WEBSMS] | CMIN
11/13/2023 6:00:23 AM | [NSO Update] Luzon Grid-11/13/2023 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13976MW, PK=10568MW, RR=448MW, NetOpMargin: AM=2960, PM=1885, EVE=1592 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 335MW, Masinloc 2 @ 330MW, Masinloc 3 @ 120MW, Ilijan A @ 510MW, Ilijan B @ 190MW, Sta. Rita 30 @ 260MW [WEBSMS] | CLUZ
11/13/2023 5:57:19 AM | [NSO Update] Mindanao Grid-11/13/2023 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3160MW, PK=2233MW, RR=80MW, NetOpMargin: AM=847, PM=749, EVE=776 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @130MW [WEBSMS] | CMIN
11/13/2023 5:56:19 AM | [NSO Update] Visayas Grid-11/13/2023 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2619MW, PK=2268MW, RR=93MW, NetOpMargin: AM=257, PM=275, EVE=257 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 80.3MW, Leyte A @ 328MW, PGPP1 @ 76MW, PDPP3-C @ 10MW, PDPP3-E @ 7MW, PDPP3-G @ 7MW, PDPP3-H @ 10MW [WEBSMS] | CVIS
11/13/2023 4:12:44 AM | [NSO Update] Luzon Grid-11/13/2023 04:12: Weather Update: Shear Line affecting Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
11/13/2023 4:12:07 AM | [NSO Update] Mindanao Grid-11/13/2023 04:15: Weather Update: Shear Line affecting Southern Luzon. Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
11/13/2023 2:29:01 AM | Luzon Grid-11/13/2023 02:29: Dona Imelda 230kV Bus 2 restored at 0228H (Unplanned Outage) [WEBSMS] | CLUZ
11/12/2023 10:46:06 PM | Luzon Grid-11/12/2023 22:46: Dona Imelda 230kV Bus 2 de-energized at 2244H (Unplanned Outage) [WEBSMS] | CLUZ
11/12/2023 10:38:43 PM | Visayas Grid-11/12/2023 22:38: Cebu SS 138 kV Bus 1 energized at 2236H. (Planned Outage) [WEBSMS] | CVIS
11/12/2023 10:33:10 PM | Mindanao Grid-11/12/2023 22:36: ASIGA (ASG) HEP Tripped at 2223H with 4.5MW load. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
11/12/2023 9:35:34 PM | Mindanao Grid-11/12/2023 21:39: Mati Diesel (MDP) cut-out at 2105H. End of RTD. [WEBSMS] | CMIN
11/12/2023 8:41:45 PM | Mindanao Grid-11/12/2023 20:45: Zamboanga - Pitogo 138kV L1 energized at 2030H. (Planned Outage) [WEBSMS] | CMIN
11/12/2023 7:48:29 PM | Visayas Grid-11/12/2023 19:48: Visayas Spot Peak for November 12, 2023, 2119MW at 1806H. Highest peak for the year is 2458 MW at 1422H on May 17, 2023 [WEBSMS] | CVIS
11/12/2023 7:47:27 PM | Mindanao Grid-11/12/2023 19:50: WMPC DG05 cut-out at 1944H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/12/2023 5:59:35 PM | [NSO Update] Mindanao Grid-11/12/2023 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3111MW, PK=2092MW, RR=78MW, NetOpMargin: EVE=941 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @141MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
11/12/2023 5:59:31 PM | Mindanao Grid-11/12/2023 18:03: Zamboanga 138kV Bus no. 2 energized at 1754H. (Planned Outage) [WEBSMS] | CMIN
11/12/2023 5:58:39 PM | [NSO Update] Visayas Grid-11/12/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2407MW, PK=2119MW, RR=97MW, NetOpMargin: EVE=191 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @317MW, PGPP1 @76MW, PDPP3-C @10MW, PDPP3-E @7MW, PDPP3-G @7MW, PDPP3-H @10MW [WEBSMS] | CVIS
11/12/2023 5:58:27 PM | Mindanao Grid-11/12/2023 18:01: Nasipit Transformer no. 2 energized at 1748H. (Planned Outage) [WEBSMS] | CMIN
11/12/2023 5:52:53 PM | [NSO Update] Luzon Grid-11/12/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13201MW, PK=9764MW, RR=356MW, NetOpMargin: EVE=3080 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @325MW, MSLC2 @325MW, MSLC3 @135MW, ILIJAN A @430MW, ILIJAN B @190MW, STA. RITA 30 @260MW [WEBSMS] | CLUZ
11/12/2023 5:52:13 PM | Mindanao Grid-11/12/2023 17:55: TMI U1 cut in at 1747H, for SOC management of TMI BESS. [WEBSMS] | CMIN
11/12/2023 5:43:09 PM | Luzon Grid-11/12/2023 17:43: Botolan-Subic 230kV Line restored at 1741H (Planned Outage) [WEBSMS] | CLUZ
11/12/2023 5:32:10 PM | Mindanao Grid-11/12/2023 17:35: Matanao - Digos Solar 69kV L de-energized at 1724H. (Planned Outage) [WEBSMS] | CMIN
11/12/2023 5:26:15 PM | Luzon Grid-11/12/2023 17:26: Payocpoc PCB 8-02CB04PAY restored at 1723H (Unplanned Outage) [WEBSMS] | CLUZ
11/12/2023 5:23:27 PM | Luzon Grid-11/12/2023 17:23: Botolan 230kV Bus 1 restored at 1723H (Planned Outage) [WEBSMS] | CLUZ
11/12/2023 5:21:27 PM | Visayas Grid-11/12/2023 17:21: Magdugo - Daanlungsod 138 kV Line energized at 1719H. (Planned Outage) [WEBSMS] | CVIS
11/12/2023 5:16:37 PM | Mindanao Grid-11/12/2023 17:20: Placer Transformer No. 3 energized at 1712H. (Planned Outage) [WEBSMS] | CMIN
11/12/2023 5:14:51 PM | Mindanao Grid-11/12/2023 17:18: Placer Transformer No. 3 energized at 1712H. (Planned Outage) [WEBSMS] | CMIN
11/12/2023 5:06:33 PM | Luzon Grid-11/12/2023 17:06: Nagsaag 500kV Bus 1 restored at 1706H (Planned Outage) [WEBSMS] | CLUZ
11/12/2023 4:39:08 PM | Luzon Grid-11/12/2023 16:39: Payocpoc PCB 8-02CB04PAY de-energized at 1637H (Unplanned Outage) [WEBSMS] | CLUZ
11/12/2023 3:26:48 PM | Luzon Grid-11/12/2023 15:26: Quezon (Balintawak)-Dona Imelda (Araneta) 230kV Line restored at 1525H (Planned Outage) [WEBSMS] | CLUZ
11/12/2023 12:47:27 PM | [NSO Update] Luzon Grid-11/12/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13575MW, PK=9343MW, RR=316MW, NetOpMargin: PM=3916, EVE=2805 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @325MW, MSLC2 @325MW, MSLC3 @80MW, ILIJAN A @430MW, ILIJAN B @190MW, STA. RITA 30 @260MW [WEBSMS] | CLUZ
11/12/2023 12:37:49 PM | [NSO Update] Visayas Grid-11/12/2023 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2240MW, PK=1933MW, RR=93MW, NetOpMargin: PM=214, EVE=189 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @317MW, PGPP1 @76MW, PDPP3-C @10MW, PDPP3-E @7MW, PDPP3-G @7MW, PDPP3-H @10MW [WEBSMS] | CVIS
11/12/2023 11:19:45 AM | Luzon Grid-11/12/2023 11:19: Malolos newly replaced GCB 82YV8 energized at 1116H (Planned Outage) [WEBSMS] | CLUZ
11/12/2023 10:56:58 AM | Mindanao Grid-11/12/2023 11:00: Update: Sibulan B U2 tripped at 0911H with 6.2MW load. Indication - Governor Trip. [WEBSMS] | CMIN
11/12/2023 10:54:09 AM | Mindanao Grid-11/12/2023 10:57: Talomo 1 Unit 2 with 0.2MW load shutdown at 1020H due to insufficient water supply. (Unplanned Outage). [WEBSMS] | CMIN
11/12/2023 10:11:03 AM | Mindanao Grid-11/12/2023 10:14: Tacurong - Gensan 138kV Line 1 energized at 1006H. (Planned Outage) [WEBSMS] | CMIN
11/12/2023 9:48:14 AM | Mindanao Grid-11/12/2023 09:51: Placer Transformer no. 3 de-energized at 0837H. (Planned Outage) [WEBSMS] | CMIN
11/12/2023 9:38:01 AM | Mindanao Grid-11/12/2023 09:41: Tagoloan - Villanueva 138kV Line 2 energized at 0931H. (Planned Outage) [WEBSMS] | CMIN
11/12/2023 9:18:50 AM | Mindanao Grid-11/12/2023 09:22: Sibulan B U2 tripped at 0911H with 6.2MW load. Details to be determined. [WEBSMS] | CMIN
11/12/2023 9:07:46 AM | Mindanao Grid-11/12/2023 09:11: SPC Mati cut in at 0900H. MO Dispatch. Follow RTD. [WEBSMS] | CMIN
11/12/2023 9:03:46 AM | Mindanao Grid-11/12/2023 09:07: Tudaya 2 U1 cut in at 0855H from FO. Affected by tripping of Toril - Digos 69kV Line. (Unplanned Outage). [WEBSMS] | CMIN
11/12/2023 8:59:46 AM | Visayas Grid-11/12/2023 08:59: Mandaue - Paknaan 69 kV Line energized at 0857H. (Unplanned Outage, SIPS activated) [WEBSMS] | CVIS
11/12/2023 8:57:08 AM | Visayas Grid-11/12/2023 08:57: Cebu - Mandaue 138 kV Line 1 re-energized at 0854H. (Unplanned Outage) [WEBSMS] | CVIS
11/12/2023 8:55:32 AM | Visayas Grid-11/12/2023 08:55: Cebu - Mandaue 138 kV Line 2 SIPS activated at 0850H isolating Mandaue - Paknaan 69 kV Line with 37.8 MW load. Cebu - Mandaue Line 1 tripped at 0842H. [WEBSMS] | CVIS
11/12/2023 8:55:29 AM | Mindanao Grid-11/12/2023 08:58: Tudaya 2 U1 with 4.4MW load isolated affected by tripping of Toril - Digos 69kV Line. (Unplanned outage) [WEBSMS] | CMIN
11/12/2023 8:49:57 AM | Visayas Grid-11/12/2023 08:50: Cebu - Mandaue 138 kV Line 1 tripped (Mandaue PCB only) at 0842H. (Unplanned Outage) [WEBSMS] | CVIS
11/12/2023 7:38:59 AM | Mindanao Grid-11/12/2023 07:42: Tacurong - Gensan 138kV Line 1 de-energized at 0721H. (Planned Outage). [WEBSMS] | CMIN
11/12/2023 7:36:48 AM | Luzon Grid-11/12/2023 07:36: Nagsaag 500kV Bus 1 de-energized at 0735H (Planned Outage) [WEBSMS] | CLUZ
11/12/2023 7:03:16 AM | Visayas Grid-11/12/2023 07:03: Magdugo - Daanlungsod 138 kV Line de-energized at 0638H. (Planned Outage) [WEBSMS] | CVIS
11/12/2023 6:45:40 AM | Mindanao Grid-11/12/2023 06:49: EURO Hydro with load of 1.2 isolated by the tripping of DANECO feeder. (Unplanned Outage). [WEBSMS] | CMIN
11/12/2023 6:44:07 AM | Luzon Grid-11/12/2023 06:44: Botolan 230kV Bus 1 de-energized at 0643H (Planned Outage) [WEBSMS] | CLUZ
11/12/2023 6:41:11 AM | Luzon Grid-11/12/2023 06:41: Botolan-Subic 230kV Line de-energized at 0638H (Planned Outage) [WEBSMS] | CLUZ
11/12/2023 6:40:37 AM | Mindanao Grid-11/12/2023 06:44: Zamboanga 138kV Bus No. 2 de-energized at 0636H. (Planned Outage) [WEBSMS] | CMIN
11/12/2023 6:39:11 AM | Mindanao Grid-11/12/2023 06:42: Nasipit Transformer No. 2 de-energized at 0626H. (Planned Outage) [WEBSMS] | CMIN
11/12/2023 6:26:14 AM | Visayas Grid-11/12/2023 06:26: Daanlungsod SS 138 kV Bus 1 de-energized at 0623H. (Planned Outage) [WEBSMS] | CVIS
11/12/2023 6:13:42 AM | Visayas Grid-11/12/2023 06:13: Cebu SS 138 kV Bus 1 de-energized at 0613H. (Planned Outage) [WEBSMS] | CVIS
11/12/2023 6:01:57 AM | Mindanao Grid-11/12/2023 06:05: Tagoloan - Villanueva 138KV Line 2 deenergized at 0537H. Planned outage. [WEBSMS] | CMIN
11/12/2023 5:59:29 AM | [NSO Update] Mindanao Grid-11/12/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3150MW, PK=1788MW, RR=68MW, NetOpMargin: AM=1294, PM=1151, EVE=922 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @140MW [WEBSMS] | CMIN
11/12/2023 5:58:37 AM | [NSO Update] Visayas Grid-11/12/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2482MW, PK=1885MW, RR=93MW, NetOpMargin: AM=504, PM=377, EVE=173 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 80.3MW, Leyte A @ 323MW, PGPP1 @ 76MW, PDPP3-C @ 10MW, PDPP3-E @ 7MW, PDPP3-G @ 7MW, PDPP3-H @ 10MW [WEBSMS] | CVIS
11/12/2023 5:56:58 AM | [NSO Update] Luzon Grid-11/12/2023 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14093MW, PK=8994MW, RR=316MW, NetOpMargin: AM=4783, PM=4332, EVE=2992 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 325MW, Masinloc 2 @ 325MW, Masinloc 3 @ 290MW, Sta. Rita 30 @ 260MW, Ilijan A @ 430MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/12/2023 4:51:04 AM | Luzon Grid-11/12/2023 04:51: Hermosa-Malolos 230kV line was restored at 0450H. (Planned Outage) [WEBSMS] | CLUZ
11/12/2023 4:48:06 AM | Luzon Grid-11/12/2023 04:48: Malolos 150MVA T01 was restored at 0444H. (Planned Outage) [WEBSMS] | CLUZ
11/12/2023 4:27:12 AM | [NSO Update] Mindanao Grid-11/12/2023 04:30: Weather Update: Shear Line affecting Central Luzon. Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CMIN
11/12/2023 4:25:14 AM | [NSO Update] Visayas Grid-11/12/2023 04:25: Weather Update: Shear Line affecting Central Luzon. Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CVIS
11/12/2023 4:24:43 AM | [NSO Update] Luzon Grid-11/12/2023 04:24: Weather Update: Shear Line affecting Central Luzon. Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
11/12/2023 3:59:04 AM | Luzon Grid-11/12/2023 03:59: Malolos 150MVA T01 was de-energized at 0358H. (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 10:14:23 PM | Luzon Grid-11/11/2023 22:14: Quezon (Balintawak)-Dona Imelda (Araneta) 230kV Line de-energized at 2213H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 10:00:04 PM | Luzon Grid-11/11/2023 22:00: San Jose 115kV Bus 2 restored at 2159H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 9:39:55 PM | Luzon Grid-11/11/2023 21:40: Sta. Rita Module 20 online at 2005H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 9:16:47 PM | Luzon Grid-11/11/2023 21:16: Correction: Concepcion-UPSI Concepcion BESS 69kV Line restored at 1937H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 8:08:36 PM | Luzon Grid-11/11/2023 20:08: Sta. Rita Module 20 online at 0805H (Unplanned Outage) [WEBSMS] | CLUZ
11/11/2023 7:53:36 PM | Mindanao Grid-11/11/2023 19:57: ASIGA U2 cut in at 1718H, U1 at 1721H from FO affected by the TL maintenance of ANECO 69kV Line. [WEBSMS] | CMIN
11/11/2023 7:38:05 PM | Luzon Grid-11/11/2023 19:38: Concepcion-UPSI Concepcion BESS 69kV Line restored at 0737H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 7:31:22 PM | Luzon Grid-11/11/2023 19:31: Lal-lo-Magapit BESS 69kV Line restored at 0731H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 7:24:13 PM | Luzon Grid-11/11/2023 19:24: Lal-lo-Cagayan North Solar 69kV Line 1 restored at 1924H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 7:11:17 PM | Luzon Grid-11/11/2023 19:11: Concepcion-Concepcion 1 Solar Power Plant 69kV Line restored at 1908H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 6:03:08 PM | Luzon Grid-11/11/2023 18:03: Payocpoc-Bauang 230kV Line restored at 1802H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 6:02:37 PM | Luzon Grid-11/11/2023 18:02: Concepcion-UPSI Concepcion BESS 69kV Line de-energized at 1800H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 6:01:22 PM | Luzon Grid-11/11/2023 18:01: Concepcion-Concepcion 1 Solar Power Plant 69kV Line de-energized at 1800H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 5:59:19 PM | [NSO Update] Mindanao Grid-11/11/2023 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3107MW, PK=2233MW, RR=80MW, NetOpMargin: EVE=795 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @139MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @130MW [WEBSMS] | CMIN
11/11/2023 5:58:21 PM | [NSO Update] Visayas Grid-11/11/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2531MW, PK=2198MW, RR=97MW, NetOpMargin: EVE=236 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @333MW, PGPP1 @76MW [WEBSMS] | CVIS
11/11/2023 5:54:58 PM | Luzon Grid-11/11/2023 17:55: Balingueo-Payocpoc 230kV Line restored at 1754H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 5:53:47 PM | [NSO Update] Luzon Grid-11/11/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12676MW, PK=10277MW, RR=407MW, NetOpMargin: EVE=1992 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @175MW, GNPD 2 @550MW, MSLC1 @330MW, MSLC2 @330MW, MSLC3 @110MW, SUAL 2 @590MW, ILIJAN A @535MW, ILIJAN B @165MW, STA. RITA 30 @260MW [WEBSMS] | CLUZ
11/11/2023 4:53:25 PM | Visayas Grid-11/11/2023 16:53: Daan Lungsod-Calongcalong 138 KV Line 1 energized at 1645H. (Planned Outage) [WEBSMS] | CVIS
11/11/2023 4:43:51 PM | Mindanao Grid-11/11/2023 16:47: Pitogo SS 138KV Bus 1 restored at 1637H. Planned Outage. [WEBSMS] | CMIN
11/11/2023 3:36:17 PM | Visayas Grid-11/11/2023 15:36: Magdugo-Calatrava 230 KV Line energized at 1525H. (Planned Outage) [WEBSMS] | CVIS
11/11/2023 3:30:38 PM | Visayas Grid-11/11/2023 15:30: Magdugo 230 KV bus 2 energized at 1525H. (Planned Outage) [WEBSMS] | CVIS
11/11/2023 1:17:32 PM | [NSO Update] Visayas Grid-11/11/2023 13:17: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2413MW, PK=2064MW, RR=94MW, NetOpMargin: PM=254, EVE=184 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @330MW, PGPP1 @76MW, PDPP3-E @7MW, PDPP3-G @7MW, PDPP3-H @10MW [WEBSMS] | CVIS
11/11/2023 1:08:33 PM | [NSO Update] Mindanao Grid-11/11/2023 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3111MW, PK=2193MW, RR=80MW, NetOpMargin: PM=838, EVE=771 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @130MW [WEBSMS] | CMIN
11/11/2023 1:06:56 PM | [NSO Update] Luzon Grid-11/11/2023 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13135MW, PK=10286MW, RR=428MW, NetOpMargin: PM=2421, EVE=1851 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @175MW, GNPD 2 @550MW, MSLC1 @330MW, MSLC2 @330MW, MSLC3 @110MW, SUAL 2 @450MW, ILIJAN A @535MW, ILIJAN B @165MW, STA. RITA 30 @260MW [WEBSMS] | CLUZ
11/11/2023 9:53:13 AM | Mindanao Grid-11/11/2023 09:56: WMPC DG05 online at 0950H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/11/2023 9:34:52 AM | Mindanao Grid-11/11/2023 09:38: Aurora SS 100mva Transformer 2 restored at 0929H. Planned Outage. [WEBSMS] | CMIN
11/11/2023 8:29:42 AM | Mindanao Grid-11/11/2023 08:33: Pitogo ss 138KV Bus 1 deenergized at 0826H. Planned Outage. [WEBSMS] | CMIN
11/11/2023 7:52:14 AM | Luzon Grid-11/11/2023 07:52: Concepcion-UPSI Concepcion BESS 69kV Line restored at 0751H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 7:46:05 AM | Mindanao Grid-11/11/2023 07:49: Aurora ss 100MVA Transformer 2 deenergized at 0742H. Planned Outage. [WEBSMS] | CMIN
11/11/2023 7:39:48 AM | Luzon Grid-11/11/2023 07:39: Concepcion-Concepcion 1 Solar Power Plant 69kV Line restored at 0739H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 7:07:00 AM | Visayas Grid-11/11/2023 07:07: Daan Lungsod-Calongcalong 138 KV Line 1 de-energized at 0706H. (Planned Outage) [WEBSMS] | CVIS
11/11/2023 6:59:03 AM | Visayas Grid-11/11/2023 06:59: Magdugo 230 KV bus 2 de-energized at 0658H. (Planned Outage) [WEBSMS] | CVIS
11/11/2023 6:39:19 AM | Visayas Grid-11/11/2023 06:39: Daan Lungsod 138 KV Bus 1 de-energized at 0636H. (Planned Outage) [WEBSMS] | CVIS
11/11/2023 6:35:05 AM | Luzon Grid-11/11/2023 06:35: Balingueo-Payocpoc 230kV Line de-energized at 0632H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 6:33:47 AM | Luzon Grid-11/11/2023 06:33: Payocpoc-Bauang 230kV Line de-energized at 0628H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 6:30:43 AM | [NSO Update] Mindanao Grid-11/11/2023 06:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3120MW, PK=2085MW, RR=80MW, NetOpMargin: AM=956, PM=890, EVE=823 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @130MW [WEBSMS] | CMIN
11/11/2023 6:27:48 AM | [NSO Update] Visayas Grid-11/11/2023 06:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2378MW, PK=2117MW, RR=93MW, NetOpMargin: AM=169, PM=194, EVE=288 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @330MW, PGPP1 @76MW, PDPP3-E @7MW, PDPP3-G @7MW, PDPP3-H @10MW [WEBSMS] | CVIS
11/11/2023 6:27:27 AM | Mindanao Grid-11/11/2023 06:30: Zamboanga - Pitogo 138KV Line 1 deenergized at 0604H. Planned outage. [WEBSMS] | CMIN
11/11/2023 6:20:33 AM | [NSO Update] Luzon Grid-11/11/2023 06:20: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13489MW, PK=10433MW, RR=420MW, NetOpMargin: AM=2636, PM=2139, EVE=1970 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, MSLC2 @330MW, MSLC3 @110MW, ILIJAN A @510MW, ILIJAN B @190MW, ST. RITA 30 @260MW [WEBSMS] | CLUZ
11/11/2023 5:56:45 AM | Luzon Grid-11/11/2023 05:56: Lal-lo-Magapit BESS 69kV Line de-energized at 0555H. (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 5:49:49 AM | Luzon Grid-11/11/2023 05:49: Lal-lo-Cagayan North de-energized at 0548H. (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 5:24:09 AM | Luzon Grid-11/11/2023 05:24: Concepcion-UPSI Concepcion BESS 69kV Line de-energized at 0513H. (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 5:11:48 AM | Luzon Grid-11/11/2023 05:11: Concepcion-Concepcion 1 Solar Power Plant 69kV Line de-energized at 0511H. (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 4:52:46 AM | Luzon Grid-11/11/2023 04:52: Sta. Rita 20 shutdown at 0450H. (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 4:43:59 AM | [NSO Update] Luzon Grid-11/11/2023 04:44: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
11/11/2023 4:39:01 AM | [NSO Update] Mindanao Grid-11/11/2023 04:42: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CMIN
11/11/2023 4:38:35 AM | [NSO Update] Visayas Grid-11/11/2023 04:38: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CVIS
11/11/2023 4:18:36 AM | Luzon Grid-11/11/2023 04:18: San Jose 115kV Bus 2 de-energized at 0417H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 2:18:54 AM | Luzon Grid-11/11/2023 02:19: Dasmarinas SS PCB 9Z-01CB24DAS de-energized at 0218H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 1:59:55 AM | Luzon Grid-11/11/2023 02:00: Dasmarinas SS PCB 9Z-01CB04DAS restored at 0152H (Planned Outage) [WEBSMS] | CLUZ
11/11/2023 1:12:55 AM | Luzon Grid-11/11/2023 01:13: Malolos-Hermosa 230kV Line (including Malolos SS 230kV Bus 2) de-energized at 0106H (Planned Outage) [WEBSMS] | CLUZ
11/10/2023 11:10:53 PM | Luzon Grid-11/10/2023 23:10: Dasmarinas SS PCB 9Z-01CB04DAS de-energized at 2310H. (Planned Outage) [WEBSMS] | CLUZ
11/10/2023 9:19:07 PM | Mindanao Grid-11/10/2023 21:22: WMPC DG05 shutdown at 2114H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/10/2023 6:27:40 PM | Luzon Grid-11/10/2023 18:27: Mexico 300MVA T03 tripped at 1819H. (Unplanned Outage) [WEBSMS] | CLUZ
11/10/2023 6:08:48 PM | [NSO Update] Mindanao Grid-11/10/2023 18:12: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3072MW, PK=2330MW, RR=80MW, NetOpMargin: EVE=662 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @130MW [WEBSMS] | CMIN
11/10/2023 5:57:54 PM | [NSO Update] Visayas Grid-11/10/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2593MW, PK=2267MW, RR=97MW, NetOpMargin: EVE=229 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @328MW, PGPP1 @76MW, PDPP3-E @7MW, PDPP3-G @7MW, PDPP3-H @10MW [WEBSMS] | CVIS
11/10/2023 5:48:38 PM | [NSO Update] Luzon Grid-11/10/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13058MW, PK=10937MW, RR=430MW, NetOpMargin: EVE=1691 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @335MW, MSLC2 @335MW, MSLC3 @115MW, ILIJAN A @510MW, ILIJAN B @190MW, ST. RITA 30 @260MW [WEBSMS] | CLUZ
11/10/2023 5:37:49 PM | Luzon Grid-11/10/2023 17:37: Bolo(Kadampat) 600MVA T01 restored at 1737H. (Planned Outage) [WEBSMS] | CLUZ
11/10/2023 5:08:54 PM | Visayas Grid-11/10/2023 17:09: Daan Lungsod 138 KV Bus 1 energized at 1704H. (Planned Outage) [WEBSMS] | CVIS
11/10/2023 4:49:16 PM | Visayas Grid-11/10/2023 16:49: Daan Lungsod-Calongcalong 138 KV Line 2 energized at 1645H. (Planned Outage) [WEBSMS] | CVIS
11/10/2023 4:18:10 PM | Mindanao Grid-11/10/2023 16:21: WMPC DG01 shutdown at 1614H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/10/2023 4:13:15 PM | Mindanao Grid-11/10/2023 16:16: SEDI EEI Unit no.1 shutdown at 1607H to facilitate scheduled Plant performance test. Follow RTD. (Planned Outage) [WEBSMS] | CMIN
11/10/2023 3:48:08 PM | Mindanao Grid-11/10/2023 15:51: SEDI EEI Unit no.1 online at 1540H to facilitate scheduled Plant performance test. Follow RTD. [WEBSMS] | CMIN
11/10/2023 3:46:05 PM | Mindanao Grid-11/10/2023 15:49: SEDI EEI Unit no.3 shutdown at 1533H to facilitate scheduled Plant performance test. Follow RTD. (Planned Outage) [WEBSMS] | CMIN
11/10/2023 12:59:26 PM | [NSO Update] Luzon Grid-11/10/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13745MW, PK=11401MW, RR=461MW, NetOpMargin: PM=1883, EVE=1659 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @335MW, MSLC2 @330MW, MSLC3 @115MW, ILIJAN A @510MW, ILIJAN B @190MW, ST. RITA 30 @260MW [WEBSMS] | CLUZ
11/10/2023 12:54:47 PM | [NSO Update] Mindanao Grid-11/10/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3109MW, PK=2384MW, RR=80MW, NetOpMargin: PM=645, EVE=727 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @130MW [WEBSMS] | CMIN
11/10/2023 12:52:14 PM | [NSO Update] Visayas Grid-11/10/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2570MW, PK=2302MW, RR=94MW, NetOpMargin: PM=174, EVE=176 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @318MW, PGPP1 @76MW, PDPP3-C @10MW, PDPP3-E @10MW, PDPP3-G @7MW, PDPP3-H @10MW [WEBSMS] | CVIS
11/10/2023 11:13:42 AM | Mindanao Grid-11/10/2023 11:17: WMPC DG01 online at 1059H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/10/2023 10:59:58 AM | Mindanao Grid-11/10/2023 11:03: Sultan Kudarat-Lamsan 69kV L energized at 1041H. [WEBSMS] | CMIN
11/10/2023 10:46:09 AM | Mindanao Grid-11/10/2023 10:49: Pulangi 4 HEP Unit 3 online at 1041H from PMS (GOMP). (Planned Outage) [WEBSMS] | CMIN
11/10/2023 9:14:20 AM | Mindanao Grid-11/10/2023 09:17: SEDI EEI online at 0901H to facilitate scheduled Plant performance test. Follow RTD. [WEBSMS] | CMIN
11/10/2023 9:07:47 AM | Mindanao Grid-11/10/2023 09:11: MDP(Supreme Mati) online at 0900H. MO Dispatch - Follow RTD. [WEBSMS] | CMIN
11/10/2023 9:07:09 AM | Mindanao Grid-11/10/2023 09:10: Sultan Kudarat-Lamsan 69kV L deenergized at 0828H. Emergency shutdown requested by Lamsan Power Corporation. [WEBSMS] | CMIN
11/10/2023 8:54:30 AM | Mindanao Grid-11/10/2023 08:57: WMPC DG05 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/10/2023 7:38:55 AM | Visayas Grid-11/10/2023 07:39: Daan Lungsod-Calongcalong 138 KV Line 2 de-energized at 0738H. (Planned Outage) [WEBSMS] | CVIS
11/10/2023 7:32:08 AM | Visayas Grid-11/10/2023 07:32: Daan Lungsod 138 KV Bus 1 de-energized at 0721H. (Planned Outage) [WEBSMS] | CVIS
11/10/2023 6:47:19 AM | Luzon Grid-11/10/2023 06:47: Bolo(Kadampat) 600MVA T01 - de-energized at 0645H. (Planned Outage) [WEBSMS] | CLUZ
11/10/2023 5:53:41 AM | [NSO Update] Mindanao Grid-11/10/2023 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3078MW, PK=2282MW, RR=80MW, NetOpMargin: AM=716, PM=610, EVE=682 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @26MW, AG6 @174MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/10/2023 5:51:52 AM | [NSO Update] Visayas Grid-11/10/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2607MW, PK=2269MW, RR=93MW, NetOpMargin: AM=245, PM=266, EVE=259 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @328MW, PGPP1 @76MW, PDPP3-C @8MW, PDPP3-E @8MW, PDPP3-G @7MW, PDPP3-H @8MW [WEBSMS] | CVIS
11/10/2023 5:44:33 AM | [NSO Update] Luzon Grid-11/10/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13745MW, PK=11157MW, RR=447MW, NetOpMargin: AM=2140, PM=1680, EVE=1544 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @335MW, MSLC2 @330MW, MSLC3 @120MW, SLPGC 1 @145MW, ILIJAN A @510MW, ILIJAN B @190MW, STA. RITA 30 @260MW [WEBSMS] | CLUZ
11/10/2023 5:31:03 AM | Mindanao Grid-11/10/2023 05:34: Tudaya 2 U2 with Load of 1.1MW shutdown at 0517H due to Insufficient water supply. Unplanned Outage [WEBSMS] | CMIN
11/10/2023 5:23:00 AM | Mindanao Grid-11/10/2023 05:26: Tudaya 2 U2 cut out at 0517H with load of 1.1MW due to Insufficient Water Supply. Unplanned Outage. [WEBSMS] | CMIN
11/10/2023 5:17:54 AM | Mindanao Grid-11/10/2023 05:21: Talomo 1 Unit 2 with 0.221MW load shutdown at 0235H due to insufficient water supply. [WEBSMS] | CMIN
11/10/2023 5:01:20 AM | [NSO Update] Mindanao Grid-11/10/2023 05:04: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
11/10/2023 5:01:03 AM | [NSO Update] Visayas Grid-11/10/2023 05:01: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
11/10/2023 5:00:47 AM | [NSO Update] Luzon Grid-11/10/2023 05:00: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
11/9/2023 11:12:10 PM | Luzon Grid-11/09/2023 23:12: For info: Commissioning and energization of Lal-lo PCBs 5-02CB08LAL & 5-02CB24LAL and Stub Protections was completed at 2305H. [WEBSMS] | CLUZ
11/9/2023 9:21:47 PM | Mindanao Grid-11/09/2023 21:25: WMPC DG05 shutdown at 2113H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/9/2023 7:47:19 PM | Mindanao Grid-11/09/2023 19:50: Agus 7 Unit 1 138kV line energized at 1537H. (Planned Outage) [WEBSMS] | CMIN
11/9/2023 6:24:08 PM | Luzon Grid-11/09/2023 18:24: Hermosa-Calaguiman 69kV Line restored at 1823H (Planned Outage) [WEBSMS] | CLUZ
11/9/2023 6:11:58 PM | [NSO Update] Mindanao Grid-11/09/2023 18:15: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3042MW, PK=2300MW, RR=80MW, NetOpMargin: EVE=662 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @26MW, AG6 @174MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/9/2023 6:08:26 PM | [NSO Update] Luzon Grid-11/09/2023 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13120MW, PK=11131MW, RR=425MW, NetOpMargin: EVE=1565 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @335MW, MSLC2 @330MW, MSLC3 @120MW, SLPGC 1 @125MW, ILIJAN A @510MW, ILIJAN B @190MW, STA. RITA 30 @260MW [WEBSMS] | CLUZ
11/9/2023 6:01:50 PM | [NSO Update] Visayas Grid-11/09/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2553MW, PK=2247MW, RR=75MW, NetOpMargin: EVE=231 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @315MW, PGPP1 @76MW [WEBSMS] | CVIS
11/9/2023 5:04:13 PM | Luzon Grid-11/09/2023 17:04: Bolo (Kadampat) 600MVA T02 restored at 1703H (Planned Outage) [WEBSMS] | CLUZ
11/9/2023 4:28:48 PM | Mindanao Grid-11/09/2023 16:32: WMPC DG07 shutdown at 1622H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/9/2023 3:03:29 PM | Mindanao Grid-11/09/2023 15:06: NACSUR cut-out at 1500H. End of RTD. [WEBSMS] | CMIN
11/9/2023 2:45:46 PM | Luzon Grid-11/09/2023 14:45: Limay-Batangas II (BPC) 230kV line 1 restored at 1443H (Planned Outage) [WEBSMS] | CLUZ
11/9/2023 2:05:20 PM | Mindanao Grid-11/09/2023 14:08: NACSUR cut-in at 1400H. MO dispatched (RTD). [WEBSMS] | CMIN
11/9/2023 12:57:25 PM | [NSO Update] Luzon Grid-11/09/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13619MW, PK=11538MW, RR=452MW, NetOpMargin: PM=1629, EVE=1520 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 2 @ 330MW, Masinloc 3 @ 120MW, SLPGC 1 @ 100MW, Ilijan A @ 510MW, Ilijan B @ 190MW, Sta. Rita 30 @ 260MW [WEBSMS] | CLUZ
11/9/2023 12:46:55 PM | [NSO Update] Mindanao Grid-11/09/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3083MW, PK=2378MW, RR=80MW, NetOpMargin: PM=625, EVE=652 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @26MW, AG6 @174MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/9/2023 12:45:17 PM | [NSO Update] Visayas Grid-11/09/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2629MW, PK=2309MW, RR=75MW, NetOpMargin: PM=245, EVE=175 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @ 80.3MW, Leyte A @ 315MW, PGPP1 @ 68MW, PDPP3-C @ 10MW, PDPP3-E @ 10MW, PDPP3-G @ 10MW, PDPP3-H @ 7MW [WEBSMS] | CVIS
11/9/2023 12:26:05 PM | Luzon Grid-11/09/2023 12:26: Lal-lo-Cagayan North Solar 69kV line 1 - restored at 1223H (Planned Outage) [WEBSMS] | CLUZ
11/9/2023 10:52:10 AM | Mindanao Grid-11/09/2023 10:55: WMPC DG07 online at 1050H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/9/2023 10:08:57 AM | Mindanao Grid-11/09/2023 10:12: Agus 7 Unit 1 138kV line de-energized at 0850H. (Planned Outage) [WEBSMS] | CMIN
11/9/2023 9:37:09 AM | Luzon Grid-11/09/2023 09:37: Lal-lo-Cagayan North Solar 69kV line 1 - de-energized at 0934H. (Planned Outage) [WEBSMS] | CLUZ
11/9/2023 9:04:19 AM | Mindanao Grid-11/09/2023 09:07: SPC Mati Diesel (MDP) online at 0900H. MO dispatched. Follow RTD. [WEBSMS] | CMIN
11/9/2023 8:52:49 AM | Mindanao Grid-11/09/2023 08:56: WMPC DG05 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/9/2023 6:41:53 AM | Luzon Grid-11/09/2023 06:41: Bolo(Kadampat) 600MVA T02 was de-energized at 0640H. (Planned Outage) [WEBSMS] | CLUZ
11/9/2023 6:20:17 AM | Luzon Grid-11/09/2023 06:20: Limay-Batangas II (BPC) 230kV line 1 - de-energized at 0617H. (Planned Outage) [WEBSMS] | CLUZ
11/9/2023 5:50:21 AM | [NSO Update] Mindanao Grid-11/09/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3165MW, PK=2230MW, RR=80MW, NetOpMargin: AM=856, PM=809, EVE=752 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @27MW, AG6 @180MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/9/2023 5:48:43 AM | [NSO Update] Visayas Grid-11/09/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2546MW, PK=2212MW, RR=40MW, NetOpMargin: AM=294, PM=264, EVE=257 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 80.3MW, Leyte A @ 315MW, PGPP1 @ 76MW, PDPP3-C @ 10MW, PDPP3-E @ 10MW, PDPP3-G @ 10MW, PDPP3-H @ 7MW [WEBSMS] | CVIS
11/9/2023 5:46:20 AM | [NSO Update] Luzon Grid-11/09/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13738MW, PK=11077MW, RR=437MW, NetOpMargin: AM=2224, PM=1977, EVE=1599 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 330MW, Masinloc 2 @ 320MW, Masinloc 3 @ 145MW, SLPGC 1 @ 32MW, Ilijan A @ 510MW, Ilijan B @ 190MW, Sta. Rita 30 @ 260MW [WEBSMS] | CLUZ
11/9/2023 5:42:48 AM | Luzon Grid-11/09/2023 05:42: Hermosa-Calaguiman 69kV Line de-energized at 0541H. (Planned Outage) [WEBSMS] | CLUZ
11/9/2023 4:28:28 AM | [NSO Update] Visayas Grid-11/09/2023 04:28: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 395 km West Southwest of Puerto Princesa City, Palawan (8.7�N, 115.3�E). Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CVIS
11/9/2023 4:27:19 AM | [NSO Update] Mindanao Grid-11/09/2023 04:30: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 395 km West Southwest of Puerto Princesa City, Palawan (8.7�N, 115.3�E). Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CMIN
11/9/2023 4:26:54 AM | [NSO Update] Luzon Grid-11/09/2023 04:26: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 395 km West Southwest of Puerto Princesa City, Palawan (8.7�N, 115.3�E). Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
11/9/2023 3:20:50 AM | Mindanao Grid-11/09/2023 03:24: EURO HYDRO (NBT) online at 0314H. Unplanned Outage. [WEBSMS] | CMIN
11/9/2023 2:57:41 AM | Luzon Grid-11/09/2023 02:57: Manila (Paco) 300MVA T06 restored at 0257H (Planned Outage). [WEBSMS] | CLUZ
11/9/2023 2:30:06 AM | Mindanao Grid-11/09/2023 02:33: EURO HYDRO (NBT) with 1.5MW gross generation tripped/isolated at 0154H. Affected by the tripping of NORDECO system 13.8kV line. Unplanned Outage. [WEBSMS] | CMIN
11/9/2023 2:15:55 AM | Luzon Grid-11/09/2023 02:15: Manila (Paco) 300MVA T06 de-energized at 0215H (Planned Outage). [WEBSMS] | CLUZ
11/9/2023 2:14:00 AM | Luzon Grid-11/09/2023 02:14: Manila (Paco) 300MVA T04 restored at 0213H (Planned Outage). [WEBSMS] | CLUZ
11/9/2023 1:32:00 AM | Mindanao Grid-11/09/2023 01:35: Talomo 3 U1 & U2 online at 0035H and 0039H respectively, Unplanned Outage [WEBSMS] | CMIN
11/9/2023 1:08:01 AM | Luzon Grid-11/09/2023 01:08: Manila (Paco) 300MVA T04 de-energized at 0103H (Planned Outage) [WEBSMS] | CLUZ
11/9/2023 12:34:27 AM | Mindanao Grid-11/09/2023 00:37: Talomo 3 U1 & U2 Tripped at 2308H, Affected by forced outage of DLPC system 13.8kV line. LD=1.5MW. Unplanned Outage [WEBSMS] | CMIN
11/9/2023 12:30:12 AM | Mindanao Grid-11/09/2023 00:33: Talomo 2B U1 Online at 2333H. Unplanned Outage [WEBSMS] | CMIN
11/9/2023 12:28:58 AM | Mindanao Grid-11/09/2023 00:32: Talomo 2A U1 Online at 2338H. Unplanned Outage [WEBSMS] | CMIN
11/9/2023 12:22:59 AM | Mindanao Grid-11/09/2023 00:26: Talomo 2B U1 Tripped at 2308H. LD=0.33MW. Affected by Forced Outage of DLPC system 13.8kV line. [WEBSMS] | CMIN
11/9/2023 12:21:55 AM | Mindanao Grid-11/09/2023 00:25: Talomo 2A U1 Tripped at 2308H. LD=0.5MW. Affected by Forced Outage of DLPC system 13.8kV line. [WEBSMS] | CMIN
11/8/2023 11:35:47 PM | Mindanao Grid-11/08/2023 23:39: WMPC DG07 cut-out at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/8/2023 10:30:27 PM | Mindanao Grid-11/08/2023 22:33: ASIGA HEPP (ASG) online at 2135H. Unplanned Outage. [WEBSMS] | CMIN
11/8/2023 9:33:40 PM | Mindanao Grid-11/08/2023 21:37: Update: ASIGA HYDRO trip with 8MW load at 2111H. Indication: Reference earth fault that cause unit 2 transformer protection relay to tripped. [WEBSMS] | CMIN
11/8/2023 9:27:41 PM | Mindanao Grid-11/08/2023 21:31: Euro Hydro on-line at 1150H from FO due to clogged trash rack at desander. [WEBSMS] | CMIN
11/8/2023 9:23:23 PM | Mindanao Grid-11/08/2023 21:26: Talomo 1 Unit 2 with 0.55MW load shutdown at 2114H due to insufficient water supply. (Unplanned Outage) [WEBSMS] | CMIN
11/8/2023 9:21:46 PM | Mindanao Grid-11/08/2023 21:25: ASIGA HYDRO trip with 8MW load at 2111H. Indication to be determined. [WEBSMS] | CMIN
11/8/2023 9:17:35 PM | Mindanao Grid-11/08/2023 21:20: WMPC DG05 cut-out at 2113H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/8/2023 7:29:19 PM | Mindanao Grid-11/08/2023 19:32: Agus 2-Kibawe 138KV L2 re-energized at 1610H at Kibawe SS side (Up to str # 103) and at 1700H at Agus 2 SS side (Up to str # 33) to prevent line pilferage. From Planned Outage / GOMP. [WEBSMS] | CMIN
11/8/2023 6:34:47 PM | Luzon Grid-11/08/2023 18:34: Limay-BCCPP 230kV line 2 restored at 1834H. (Planned Outage) [WEBSMS] | CLUZ
11/8/2023 6:12:29 PM | Mindanao Grid-11/08/2023 18:15: TMI U1 cut in at 1800H, for SOC management of TMI BESS. [WEBSMS] | CMIN
11/8/2023 5:59:23 PM | [NSO Update] Mindanao Grid-11/08/2023 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3042MW, PK=2243MW, RR=80MW, NetOpMargin: EVE=3042 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @26MW, AG6 @174MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/8/2023 5:51:52 PM | [NSO Update] Visayas Grid-11/08/2023 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2457MW, PK=2161MW, RR=40MW, NetOpMargin: EVE=256 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @312MW, PGPP1 @76MW [WEBSMS] | CVIS
11/8/2023 5:43:21 PM | [NSO Update] Luzon Grid-11/08/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12951MW, PK=10608MW, RR=428MW, NetOpMargin: EVE=1915 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, MSLC2 @315MW, MSLC3 @150MW, ILIJAN A @510MW, ILIJAN B @190MW, STA. RITA 30 @260MW [WEBSMS] | CLUZ
11/8/2023 5:26:15 PM | Luzon Grid-11/08/2023 17:26: Tayabas-Naga 230kV line 2 restored at 1725H. (Planned Outage) [WEBSMS] | CLUZ
11/8/2023 4:51:01 PM | Luzon Grid-11/08/2023 16:51: San Esteban 100MVA T02 and San Esteban-Bantay 115kV line restored at 1648H and 1649H, respectively. (Planned Outage) [WEBSMS] | CLUZ
11/8/2023 3:45:34 PM | Mindanao Grid-11/08/2023 15:48: Talomo 1 U1 cut in at 1515H from unplanned shutdown due to insufficient water supply (outside management control). [WEBSMS] | CMIN
11/8/2023 1:54:39 PM | Luzon Grid-11/08/2023 13:54: Sual Unit 2 online at 1352H. (Unplanned Outage) [WEBSMS] | CLUZ
11/8/2023 1:10:58 PM | Luzon Grid-11/08/2023 13:10: SLPGC Unit 2 online at 1309H. (Unplanned Outage) [WEBSMS] | CLUZ
11/8/2023 12:45:03 PM | Luzon Grid-11/08/2023 12:45: SLPGC Unit 1 online at 1243H. (Unplanned Outage) [WEBSMS] | CLUZ
11/8/2023 12:36:55 PM | [NSO Update] Luzon Grid-11/08/2023 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12847MW, PK=11050MW, RR=449MW, NetOpMargin: PM=1348, EVE=1242 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, MSLC2 @315MW, MSLC3 @150MW, ILIJAN A @510MW, ILIJAN B @190MW, STA. RITA 30 @260MW [WEBSMS] | CLUZ
11/8/2023 12:33:34 PM | [NSO Update] Visayas Grid-11/08/2023 12:33: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2502MW, PK=2155MW, RR=40MW, NetOpMargin: PM=307, EVE=269 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @85.5MW, LEYTE A @328MW, PGPP1 @75MW [WEBSMS] | CVIS
11/8/2023 12:30:43 PM | [NSO Update] Mindanao Grid-11/08/2023 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3070MW, PK=2237MW, RR=80MW, NetOpMargin: PM=752, EVE=813 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @26MW, AG6 @174MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/8/2023 11:38:02 AM | Mindanao Grid-11/08/2023 11:41: Agus 2-Kibawe 138KV L2 de-energized at 0827H at Kibawe SS side and 0955H at Agus 2 SS side for line maintenance initiated by D3 & D2. Note: Opened loop is at str # 33 (from Agus 2 SS) & str # 103 (from Kibawe SS). Planned Outage / GOMP. [WEBSMS] | CMIN
11/8/2023 10:54:01 AM | Mindanao Grid-11/08/2023 10:57: WMPC DG07 online at 1050H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/8/2023 9:16:06 AM | Mindanao Grid-11/08/2023 09:19: WMPC DG05 online at 0901H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/8/2023 8:04:50 AM | Mindanao Grid-11/08/2023 08:08: Agus 5 U1 shutdown at 0802H. Planned outage-GOMP. [WEBSMS] | CMIN
11/8/2023 7:58:39 AM | Luzon Grid-11/08/2023 07:58: Limay-BCCPP 230kV line 2 was de-energized at 0757H. (Planned Outage) [WEBSMS] | CLUZ
11/8/2023 6:58:15 AM | Luzon Grid-11/08/2023 06:58: BPPC(Payocpoc) 100MVA T02(Sector 2), 100MVA T03(Sector 3), and 100MVA T01(Sector 1) were de-energized at 0650H, 0651H, and 0652H respectively. (Planned Outage) [WEBSMS] | CLUZ
11/8/2023 6:44:34 AM | Luzon Grid-11/08/2023 06:44: San Esteban-Bantay 115kV line and San Esteban 100MVA T02 were de-energized at 0641H and 0642H respectively. (Planned Outage) [WEBSMS] | CLUZ
11/8/2023 6:20:26 AM | Luzon Grid-11/08/2023 06:20: Tayabas-Naga 230kV line 2 was de-energized at 0619H. (Planned Outage) [WEBSMS] | CLUZ
11/8/2023 6:05:42 AM | [NSO Update] Mindanao Grid-11/08/2023 06:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3149MW, PK=2177MW, RR=80MW, NetOpMargin: AM=893, PM=739, EVE=763 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @26MW, AG6 @174MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/8/2023 6:04:19 AM | [NSO Update] Visayas Grid-11/08/2023 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2563MW, PK=2256MW, RR=40MW, NetOpMargin: AM=267, PM=270, EVE=274 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @85.5MW, LEYTE A @328MW, PGPP1 @75MW [WEBSMS] | CVIS
11/8/2023 5:59:20 AM | [NSO Update] Luzon Grid-11/08/2023 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13069MW, PK=10936MW, RR=443MW, NetOpMargin: AM=1690, PM=1210, EVE=1304 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, MSLC2 @315MW, MSLC3 @150MW, ILIJAN A @510MW, ILIJAN B @190MW, STA. RITA 30 @260MW [WEBSMS] | CLUZ
11/8/2023 5:48:13 AM | Luzon Grid-11/08/2023 05:48: Sual 2 (198MW) tripped at 0524H. Lowest system frequency is 59.682Hz. [WEBSMS] | CLUZ
11/8/2023 5:45:57 AM | Mindanao Grid-11/08/2023 05:49: Euro Hydro (NBT) with 1.1MW gross generation tripped due to clogged trash rack at desander. Unplanned Outage. [WEBSMS] | CMIN
11/8/2023 5:28:12 AM | Luzon Grid-11/08/2023 05:28: Sual 2 tripped at 0524H. (Unplanned Outage) [WEBSMS] | CLUZ
11/8/2023 5:23:32 AM | [NSO Update] Mindanao Grid-11/08/2023 05:26: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CMIN
11/8/2023 5:20:25 AM | [NSO Update] Luzon Grid-11/08/2023 05:20: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. Northeast Monsoon affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
11/8/2023 5:16:50 AM | Visayas Grid-11/08/2023 05:16: Calongcalong-CEP 69 KV line load reduced from 11.3 MW to 0.16 MW, heavy rains and thunderstorm experienced in the area. [WEBSMS] | CVIS
11/8/2023 5:13:31 AM | Visayas Grid-11/08/2023 05:13: Toledo solar isolated at 0502H with out generation. [WEBSMS] | CVIS
11/8/2023 5:11:40 AM | Visayas Grid-11/08/2023 05:11: Calongcalong 50 MVA TR1 tripped at 0502H. [WEBSMS] | CVIS
11/8/2023 4:10:27 AM | Visayas Grid-11/08/2023 04:10: Colon-Dumanjug 138 KV Line 2 tripped/restored at 0328H/0409H. (Unplanned Outage). [WEBSMS] | CVIS
11/8/2023 3:43:02 AM | Mindanao Grid-11/08/2023 03:46: Maco - Nabunturan 138kV line restored at 0337H. (Unplanned Outage) [WEBSMS] | CMIN
11/8/2023 3:38:28 AM | Mindanao Grid-11/08/2023 03:41: Mt. Apo Unit #3 online at 0334H. Unplanned Outage. [WEBSMS] | CMIN
11/8/2023 1:51:05 AM | Mindanao Grid-11/08/2023 01:54: Mt. Apo Unit #3 with 3MW gross generation tripped at 0123H. Indication: 52L Protection Unit Cumulative Trip. Unplanned Outage. [WEBSMS] | CMIN
11/8/2023 1:48:00 AM | Mindanao Grid-11/08/2023 01:51: Mt. Apo Unit #3 with 3MW gross generation tripped at 0123H. Indication: 52L Protection Unit Cumulative Trip. Unplanned Outage. [WEBSMS] | CMIN
11/8/2023 12:08:05 AM | Mindanao Grid-11/08/2023 00:11: SEC 1 (SMF1 U1) manually shutdown at 2356H. PMS (GOMP)/Planned Outage. [WEBSMS] | CMIN
11/7/2023 11:57:40 PM | Mindanao Grid-11/08/2023 00:01: Nabunturan - Maco 138kV line tripped at 2343H. (Unplanned Outage) [WEBSMS] | CMIN
11/7/2023 11:48:44 PM | Luzon Grid-11/07/2023 23:48: New Lal-Lo 100MVA T02 commissioned at 2347H (End of Commissioning) [WEBSMS] | CLUZ
11/7/2023 11:18:56 PM | Luzon Grid-11/07/2023 23:19: New Lal-Lo 100MVA T02 energized at 2317H (On-going Commissioning) [WEBSMS] | CLUZ
11/7/2023 9:27:36 PM | Mindanao Grid-11/07/2023 21:31: WMPC DG04 cut-out at 2113H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/7/2023 8:20:36 PM | Mindanao Grid-11/07/2023 20:24: ASIGA HEPP isolated with 4.5MW load at 2008H. Affected by the tripping of Butuan - Santiago 69kV line. [WEBSMS] | CMIN
11/7/2023 6:52:24 PM | Luzon Grid-11/07/2023 18:52: Paguludan-Currimao II Solar 69kV Line (CO) restored at 1851H (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 6:50:22 PM | Luzon Grid-11/07/2023 18:50: Currimao-Paguludan 69kV Line restored at 1849H (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 6:45:00 PM | Visayas Grid-11/07/2023 18:45: Magdugo SS 230 kV Bus 2 energized at 1841H. (Planned Outage) [WEBSMS] | CVIS
11/7/2023 6:23:06 PM | [NSO Update] Luzon Grid-11/07/2023 18:23: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13078MW, PK=10745MW, RR=434MW, NetOpMargin: EVE=1899 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @335MW, Masinloc 2 @300MW, Masinloc 3 @145MW, Ilijan A @510MW, Ilijan B @190MW [WEBSMS] | CLUZ
11/7/2023 6:05:44 PM | [NSO Update] Mindanao Grid-11/07/2023 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3179MW, PK=2280MW, RR=80MW, NetOpMargin: EVE=818 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @42MW, AG6 @180MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/7/2023 6:01:31 PM | [NSO Update] Visayas Grid-11/07/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2535MW, PK=2261MW, RR=40MW, NetOpMargin: EVE=234 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @78MW, LEYTE A @295MW, PGPP1 @68MW, PDPP3 C @10MW, PDPP3 E @10MW, PDPP3 H @10MW, PDPP3 G @7MW [WEBSMS] | CVIS
11/7/2023 5:58:45 PM | Luzon Grid-11/07/2023 17:58: Calaca-SLPGC 230kV Line 1 restored at 1757H (Unplanned Outage) [WEBSMS] | CLUZ
11/7/2023 5:57:42 PM | [NSO Update] Visayas Grid-11/07/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2535MW, PK=2261MW, RR=40MW, NetOpMargin: EVE=234 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @78MW, LEYTE A @295MW, PGPP1 @68MW, PDPP3 C @10WM, PDPP3 E @10WM, PDPP3 H @10WM, PDPP3 G @7WM, [WEBSMS] | CVIS
11/7/2023 5:42:57 PM | Luzon Grid-11/07/2023 17:43: Calaca 230kV Bus 2 restored at 1741H (Unplanned Outage) [WEBSMS] | CLUZ
11/7/2023 5:41:43 PM | Luzon Grid-11/07/2023 17:41: SLPGC 230kV Bus 1 restored at 1740H (Unplanned Outage) [WEBSMS] | CLUZ
11/7/2023 5:31:24 PM | Mindanao Grid-11/07/2023 17:34: Agus 2 - Kibawe 138kV Line 1 energized at 1729H. (Planned Outage) [WEBSMS] | CMIN
11/7/2023 5:17:25 PM | Luzon Grid-11/07/2023 17:17: Correction: Calaca-SLPGC 230kV Line 1, Calaca 230kV Bus 2 and SLPGC 230kV Bus 1 tripped at 1629H. SLPGC 2 (150MW) and SLPGC 1 (40MW) also tripped (Unplanned Outage) [WEBSMS] | CLUZ
11/7/2023 5:10:59 PM | Luzon Grid-11/07/2023 17:11: Tayabas-Naga 230kV Line 1 restored at 1710H (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 4:44:08 PM | Luzon Grid-11/07/2023 16:44: Calaca-SLPGC 230kV Line 1, Calaca 230kV Bus 1 and SLPGC 230kV Bus 1 tripped at 1629H. SLPGC 2 (150MW) and SLPGC 1 (40MW) also tripped (Unplanned Outage) [WEBSMS] | CLUZ
11/7/2023 4:15:32 PM | Mindanao Grid-11/07/2023 16:19: WMPC DG07 cut-out at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/7/2023 4:07:28 PM | Luzon Grid-11/07/2023 16:07: Currimao-Laoag 115kV Line restored at 1606H (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 4:06:05 PM | Luzon Grid-11/07/2023 16:06: Bantay-Currimao 115kV Line restored at 1605H (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 3:38:21 PM | Mindanao Grid-11/07/2023 15:41: Agus 6 U3 cut in at at 1536H from emergency shutdown. (Unplanned Outage) [WEBSMS] | CMIN
11/7/2023 3:23:01 PM | Mindanao Grid-11/07/2023 15:26: Agus 6 Unit no. 3 69kV line energized at 1520H. (Unplanned Outage) [WEBSMS] | CMIN
11/7/2023 2:48:05 PM | Visayas Grid-11/07/2023 14:48: Daanlungsod SS 138 kV Bus 1 energized at 1444H. (Planned Outage) [WEBSMS] | CVIS
11/7/2023 2:30:23 PM | Mindanao Grid-11/07/2023 14:33: KEGI Tandag cut out at 1415H. Follow RTD. [WEBSMS] | CMIN
11/7/2023 12:53:06 PM | [NSO Update] Visayas Grid-11/07/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2455MW, PK=2214MW, RR=40MW, NetOpMargin: PM=201, EVE=251 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @78MW, LEYTE A @292MW, PGPP1 @68MW [WEBSMS] | CVIS
11/7/2023 12:38:31 PM | [NSO Update] Luzon Grid-11/07/2023 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13763MW, PK=11143MW, RR=462MW, NetOpMargin: PM=2158, EVE=2176 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 330MW, Masinloc 2 @ 325MW, Masinloc 3 @ 130MW, SLPGC 1 @ 40MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/7/2023 12:36:55 PM | Mindanao Grid-11/07/2023 12:40: Agus 6 Unit no. 3 69kV line de-energized at 1214H. (Unplanned Outage) [WEBSMS] | CMIN
11/7/2023 12:34:03 PM | [NSO Update] Mindanao Grid-11/07/2023 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3216MW, PK=2388MW, RR=80MW, NetOpMargin: PM=748, EVE=794 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @42MW, AG6 @180MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/7/2023 12:09:40 PM | Mindanao Grid-11/07/2023 12:13: Agus 6 Unit #3 on emergency shutdown at 1204H to facilitate hotspot correction of unit associated DS. Unplanned Outage. [WEBSMS] | CMIN
11/7/2023 10:59:24 AM | Luzon Grid-11/07/2023 10:59: Gamu-UPSI Gamu BESS 69kV Line restored at 1054H. (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 10:09:01 AM | Mindanao Grid-11/07/2023 10:12: SEDI EEI online at 1001H to facilitate scheduled Plant performance test. Follow RTD. [WEBSMS] | CMIN
11/7/2023 9:53:51 AM | Visayas Grid-11/07/2023 09:54: Magdugo SS 230KV Bus 2 de-energized at 0949H. (Planned Outage). [WEBSMS] | CVIS
11/7/2023 9:31:52 AM | Luzon Grid-11/07/2023 09:32: Tayabas SS PCB 8Z-07CB08TAY de-energized at 0927H. (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 9:05:46 AM | Mindanao Grid-11/07/2023 09:09: Mati Diesel (MDP) online at 0901H. MO dispatched. Follow RPS. [WEBSMS] | CMIN
11/7/2023 8:52:30 AM | Mindanao Grid-11/07/2023 08:56: WMPC DG04 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/7/2023 8:46:32 AM | Mindanao Grid-11/07/2023 08:50: Agus 2 - Kibawe 138kV Line 1 de-energized at 0836H. (Planned Outage) [WEBSMS] | CMIN
11/7/2023 7:35:56 AM | Visayas Grid-11/07/2023 07:36: Daanglungsod SS 138KV Bus 1 de-energized at 0721H. (Planned Outage). [WEBSMS] | CVIS
11/7/2023 7:14:12 AM | Luzon Grid-11/07/2023 07:14: Correction: Lamao SS PCB 8Z-02CB24LAY restored at 0712H. (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 7:12:27 AM | Luzon Grid-11/07/2023 07:12: Lamao SS PCB 8Z-02CB24LAY de-energized at 0712H. (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 6:57:26 AM | Luzon Grid-11/07/2023 06:57: Bantay-Currimao 115kV Line de-energized at 0657H. (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 6:55:55 AM | Luzon Grid-11/07/2023 06:56: Currimao-Laoag 115kV Line de-energized at 0655H. (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 6:38:38 AM | Luzon Grid-11/07/2023 06:38: Tayabas-Naga 230kV Line 1 de-energized at 0638H. (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 6:16:20 AM | [NSO Update] Luzon Grid-11/07/2023 06:16: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13720MW, PK=11192MW, RR=449MW, NetOpMargin: AM=2079, PM=1630, EVE=1753 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 330MW, Masinloc 2 @ 150MW, Masinloc 3 @ 125MW, SLPGC 1 @ 40MW, Ilijan A @ 510MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
11/7/2023 5:52:05 AM | Luzon Grid-11/07/2023 05:52: Currimao-Paguludan 69kV Line (CO) de-energized at 0549H (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 5:49:44 AM | Luzon Grid-11/07/2023 05:49: Paguludan-Currimao II Solar 69kV Line (CO) de-energized at 0546H (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 5:48:32 AM | Luzon Grid-11/07/2023 05:48: Paguludan-Currimao Solar 69kV Line (CO) de-energized at 0547H (Planned Outage) [WEBSMS] | CLUZ
11/7/2023 5:48:25 AM | [NSO Update] Mindanao Grid-11/07/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3224MW, PK=2240MW, RR=80MW, NetOpMargin: AM=904, PM=845, EVE=910 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @70MW, AG2 @95MW, AG4 @104MW, AG5 @42MW, AG6 @180MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/7/2023 5:47:20 AM | [NSO Update] Visayas Grid-11/07/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2530MW, PK=2299MW, RR=40MW, NetOpMargin: AM=192, PM=196, EVE=254 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 77MW, Leyte A @ 328MW, PGPP1 @ 76MW [WEBSMS] | CVIS
11/7/2023 4:07:31 AM | [NSO Update] Mindanao Grid-11/07/2023 04:11: Weather Update: Easterlies affecting Palawan, Visayas, and Mindanao. [WEBSMS] | CMIN
11/7/2023 4:06:45 AM | [NSO Update] Visayas Grid-11/07/2023 04:06: Weather Update: Easterlies affecting Palawan, Visayas, and Mindanao. [WEBSMS] | CVIS
11/7/2023 4:06:32 AM | [NSO Update] Luzon Grid-11/07/2023 04:06: Weather Update: Easterlies affecting Palawan, Visayas, and Mindanao. [WEBSMS] | CLUZ
11/7/2023 1:12:20 AM | Luzon Grid-11/07/2023 01:12: Masinloc 2 online at 0106H (Unplanned Outage) [WEBSMS] | CLUZ
11/7/2023 12:34:33 AM | Mindanao Grid-11/07/2023 00:38: Kauswagan-GNPK 230KV L4 re-energized at 2337H. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
11/7/2023 12:03:46 AM | Mindanao Grid-11/07/2023 00:07: STEAG U1 shutdown at 0000H, (Planned Outage-GOMP). [WEBSMS] | CMIN
11/6/2023 10:31:30 PM | Luzon Grid-11/06/2023 22:31: Masinloc U2 tripped at 2230H (Unplanned Outage) [WEBSMS] | CLUZ
11/6/2023 10:29:21 PM | Luzon Grid-11/06/2023 22:29: Masinloc U2 online at 2226H (Unplanned Outage) [WEBSMS] | CLUZ
11/6/2023 9:15:19 PM | Mindanao Grid-11/06/2023 21:18: WMPC DG04 shutdown at 2113H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/6/2023 8:54:43 PM | Luzon Grid-11/06/2023 20:54: SLPGC 1 online at 2049H (Unplanned Outage) [WEBSMS] | CLUZ
11/6/2023 8:00:05 PM | Visayas Grid-11/06/2023 20:00: Magdugo SS 230KV Bus 1 energized at 1958H. (Planned Outage). [WEBSMS] | CVIS
11/6/2023 6:02:54 PM | [NSO Update] Mindanao Grid-11/06/2023 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3146MW, PK=2274MW, RR=80MW, NetOpMargin: EVE=792 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @65MW, AG2 @95MW, AG4 @124MW, AG5 @40MW, AG6 @180MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/6/2023 6:01:47 PM | [NSO Update] Luzon Grid-11/06/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13061MW, PK=11038MW, RR=433MW, NetOpMargin: EVE=1590 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, MSLC3 @120MW, ILIJAN B @250MW [WEBSMS] | CLUZ
11/6/2023 5:52:04 PM | Luzon Grid-11/06/2023 17:52: Masinloc 2 with a load of 26MW tripped at 1742H (Unplanned Outage) [WEBSMS] | CLUZ
11/6/2023 5:48:09 PM | [NSO Update] Visayas Grid-11/06/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2619MW, PK=2305MW, RR=97MW, NetOpMargin: EVE=217 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @77MW, LEYTE A @315MW, PGPP1 @56MW, PDPP3-C @10MW, PDPP3-E @10MW, PDPP3-G @7MW, PDPP3-H @10MW [WEBSMS] | CVIS
11/6/2023 5:40:35 PM | Luzon Grid-11/06/2023 17:40: Masinloc 2 online at 1728H (Unplanned Outage) [WEBSMS] | CLUZ
11/6/2023 4:48:29 PM | Mindanao Grid-11/06/2023 16:52: Villanueva SS 138KV 10MVA Power Transformer # 1 re-energized at 1607H. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
11/6/2023 4:20:08 PM | Mindanao Grid-11/06/2023 16:23: WMPC DG07 shutdown at 1613H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/6/2023 1:00:02 PM | [NSO Update] Visayas Grid-11/06/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2571MW, PK=2309MW, RR=93MW, NetOpMargin: PM=169, EVE=227 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @78MW, LEYTE A @315MW, PGPP1 @66MW [WEBSMS] | CVIS
11/6/2023 12:59:48 PM | Luzon Grid-11/06/2023 12:59: San Lorenzo 50 online at 1257H. (Unplanned Outage) [WEBSMS] | CLUZ
11/6/2023 12:39:36 PM | Mindanao Grid-11/06/2023 12:43: TSI Unit #2 (DCP U2) online at 1221H. Unplanned Outage. [WEBSMS] | CMIN
11/6/2023 12:37:26 PM | [NSO Update] Mindanao Grid-11/06/2023 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3181MW, PK=2342MW, RR=80MW, NetOpMargin: PM=759, EVE=808 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @65MW, AG2 @95MW, AG4 @124MW, AG5 @40MW, AG6 @180MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/6/2023 12:34:10 PM | [NSO Update] Luzon Grid-11/06/2023 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13376MW, PK=11608MW, RR=439MW, NetOpMargin: PM=1329, EVE=1161 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @330MW, MASINLOC 3 @120MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
11/6/2023 11:34:38 AM | Mindanao Grid-11/06/2023 11:38: TSI Unit #2 (DCP U2) with 36MW gross generation tripped at 1126H. Indication: To follow. Frequency Dipped=59.7073Hz. Unplanned Outage. [WEBSMS] | CMIN
11/6/2023 11:11:30 AM | Mindanao Grid-11/06/2023 11:15: TSI Unit #2 (DCP U2) online at 1106H. Unplanned Outage. [WEBSMS] | CMIN
11/6/2023 11:09:03 AM | Luzon Grid-11/06/2023 11:09: San Lorenzo 50 with 267MW load tripped at 1107H. Lowest system frequency is 59.467Hz. (Unplanned Outage) [WEBSMS] | CLUZ
11/6/2023 10:52:44 AM | Mindanao Grid-11/06/2023 10:56: WMPC DG07 online at 1050H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/6/2023 10:31:31 AM | Visayas Grid-11/06/2023 10:31: Magdugo SS 230KV Bus 1 de-energized at 1020H. (Planned Outage). [WEBSMS] | CVIS
11/6/2023 10:28:57 AM | Mindanao Grid-11/06/2023 10:32: Mt. Apo Unit #3 online at 1020H. Unplanned Outage. [WEBSMS] | CMIN
11/6/2023 10:27:15 AM | Mindanao Grid-11/06/2023 10:30: WMPC DG04 online at 1015H. Unplanned Outage. [WEBSMS] | CMIN
11/6/2023 10:19:52 AM | Mindanao Grid-11/06/2023 10:23: WMPC DG04 run as RPS tripped at 1005H. Indication: HT Low Pressure Stop. Unplanned Outage. [WEBSMS] | CMIN
11/6/2023 9:40:46 AM | Mindanao Grid-11/06/2023 09:44: Kauswagan-GNPK 230KV L4 de-energized at 0904H per request from GNPK management to conduct OFR & UFR test, and inspection of meters & transmitters of U4. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
11/6/2023 9:00:43 AM | Mindanao Grid-11/06/2023 09:04: WMPC DG04 online at 0853H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/6/2023 8:48:29 AM | Luzon Grid-11/06/2023 08:48: San Jose-Angat 115kV Line 3 de-energized at 0847H. (Planned Outage) [WEBSMS] | CLUZ
11/6/2023 8:47:47 AM | Mindanao Grid-11/06/2023 08:51: Agus 4 Unit #3 manually shutdown at 0802H. Follow RTD. Planned Outage/PMS (GOMP). [WEBSMS] | CMIN
11/6/2023 8:46:34 AM | Luzon Grid-11/06/2023 08:46: Angat HEPP 115kV Bus 1 & 2 de-energized at 0844H and 0845H, respectively. (Planned Outage) [WEBSMS] | CLUZ
11/6/2023 8:39:42 AM | Mindanao Grid-11/06/2023 08:43: Mt. Apo Unit #3 with 3.0MW gross generation tripped at 0753H. Indication: To be investigated. [WEBSMS] | CMIN
11/6/2023 8:34:40 AM | Luzon Grid-11/06/2023 08:34: MPGC 2 shutdown at 0823H. (On-going testing and commissioning) [WEBSMS] | CLUZ
11/6/2023 8:32:44 AM | Mindanao Grid-11/06/2023 08:36: TSI Unit #2 with 60MW gross generation tripped at 0820H. Indication: Furnace Pressure High High. Frequency Dipped=59.4667Hz. Unplanned Outage. [WEBSMS] | CMIN
11/6/2023 8:10:49 AM | Mindanao Grid-11/06/2023 08:14: Villanueva SS 138KV 10MVA Power Transformer # 1 de-energized at 0739H. Simulation of tripping protection & correction of Transo/Tech-MD findings. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
11/6/2023 6:35:27 AM | Mindanao Grid-11/06/2023 06:38: GN Power Unit #3 online at 0628H from reserved shutdown. Follow RTD. [WEBSMS] | CMIN
11/6/2023 5:53:29 AM | [NSO Update] Luzon Grid-11/06/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13727MW, PK=10941MW, RR=432MW, NetOpMargin: AM=2354, PM=2052, EVE=1652 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @325MW, MSLC3 @95MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
11/6/2023 5:37:06 AM | [NSO Update] Visayas Grid-11/06/2023 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2591MW, PK=2240MW, RR=93MW, NetOpMargin: AM=257, PM=254, EVE=219 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @328MW, PGPP1 @76MW [WEBSMS] | CVIS
11/6/2023 5:37:00 AM | [NSO Update] Mindanao Grid-11/06/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3332MW, PK=2211MW, RR=80MW, NetOpMargin: AM=1041, PM=975, EVE=1032 Highest Unit O/L: GNPK 1 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @65MW, AG2 @95MW, AG4 @124MW, AG5 @40MW, AG6 @180MW, AG7 @25MW, PG4 @100MW [WEBSMS] | CMIN
11/6/2023 5:18:28 AM | Mindanao Grid-11/06/2023 05:22: (Update) GNPK Unit 3 tripped with 20.7MW load at 0513H. Lowest frequency recorded was 59.75MW. Indication: Turbine Trip. (Unplanned Outage) [WEBSMS] | CMIN
11/6/2023 5:17:32 AM | Mindanao Grid-11/06/2023 05:21: GNPK Unit 3 tripped with 20.7MW load at 0513H. Lowest frequency recorded was 59.75MW. (Unplanned Outage) [WEBSMS] | CMIN
11/6/2023 4:39:35 AM | Mindanao Grid-11/06/2023 04:43: GNPK Unit 3 cut-in at 0437H. (From Reserve Shutdown) [WEBSMS] | CMIN
11/6/2023 3:59:01 AM | [NSO Update] Luzon Grid-11/06/2023 03:59: Weather Advisory: Easterlies affecting Palawan, Visayas, and Mindanao. [WEBSMS] | CLUZ
11/6/2023 3:58:56 AM | [NSO Update] Visayas Grid-11/06/2023 03:59: Weather Advisory: Easterlies affecting Palawan, Visayas, and Mindanao. [WEBSMS] | CVIS
11/6/2023 3:58:52 AM | [NSO Update] Mindanao Grid-11/06/2023 04:02: Weather Advisory: Easterlies affecting Palawan, Visayas, and Mindanao. [WEBSMS] | CMIN
11/6/2023 3:46:41 AM | Mindanao Grid-11/06/2023 03:50: Tudaya 2 Unit 1 cut-in at 0314H. (From Shutdown) [WEBSMS] | CMIN
11/6/2023 3:46:03 AM | Mindanao Grid-11/06/2023 03:49: Sibulan B Unit 1 cut-in at 0306H. (From Shutdown) [WEBSMS] | CMIN
11/6/2023 3:45:24 AM | Mindanao Grid-11/06/2023 03:48: Tudaya 2 Unit 2 cut-in at 0232H. (From Shutdown) [WEBSMS] | CMIN
11/6/2023 3:44:48 AM | Mindanao Grid-11/06/2023 03:48: Sibulan B Unit 2 cut-in at 0218H. (From Shutdown) [WEBSMS] | CMIN
11/6/2023 3:44:14 AM | Mindanao Grid-11/06/2023 03:47: Tudaya 1 Unit 1 cut-in at 0215H. (From Shutdown) [WEBSMS] | CMIN
11/6/2023 3:43:29 AM | Mindanao Grid-11/06/2023 03:47: Sibulan A Unit 2 cut-in at 0212H. (From Shutdown) [WEBSMS] | CMIN
11/6/2023 3:42:32 AM | Mindanao Grid-11/06/2023 03:46: Sibulan A Unit 1 cut-in at 0207H. (From Shutdown) [WEBSMS] | CMIN
11/6/2023 2:17:24 AM | Mindanao Grid-11/06/2023 02:20: Sibulan B Unit 1 shutdown with 11.0MW load at 0104H. Affected by normalization of load of DLPC. (Unplanned Outage) [WEBSMS] | CMIN
11/6/2023 2:16:35 AM | Mindanao Grid-11/06/2023 02:20: Sibulan B Unit 2 shutdown with 7.5MW load at 0101H. Affected by normalization of load of DLPC. (Unplanned Outage) [WEBSMS] | CMIN
11/6/2023 2:15:56 AM | Mindanao Grid-11/06/2023 02:19: Sibulan A Unit 2 shutdown with 6.0MW load at 0101H. Affected by normalization of load of DLPC. (Unplanned Outage) [WEBSMS] | CMIN
11/6/2023 2:15:07 AM | Mindanao Grid-11/06/2023 02:18: Sibulan A Unit 1 shutdown with 6.0MW load at 0059H. Affected by normalization of load of DLPC. (Unplanned Outage) [WEBSMS] | CMIN
11/6/2023 2:14:08 AM | Mindanao Grid-11/06/2023 02:17: (Correction) Tudaya 1 Unit 1 shutdown with 4.6MW load at 0056H. Affected by normalization of load of DLPC. (Unplanned Outage) [WEBSMS] | CMIN
11/6/2023 2:13:19 AM | Mindanao Grid-11/06/2023 02:16: Tudaya 2 Unit 1 shutdown with 4.3MW load at 0057H. Affected by normalization of load of DLPC. (Unplanned Outage) [WEBSMS] | CMIN
11/6/2023 2:12:28 AM | Mindanao Grid-11/06/2023 02:16: Tudaya 1 Unit 1 shutdown with 4.6MW load at 0006H. Affected by normalization of load of DLPC. (Unplanned Outage) [WEBSMS] | CMIN
11/6/2023 2:11:01 AM | Mindanao Grid-11/06/2023 02:14: Tudaya 2 Unit 2 with 1.6MW load shutdown at 0006H. Affected by normalization of load of DLPC. (Unplanned Outage) [WEBSMS] | CMIN
11/5/2023 10:52:30 PM | Mindanao Grid-11/05/2023 22:56: Tudaya 2 Unit 2 cut-in at 2035H. (Unplanned Outage). Note: Said unit tripped at 2007H with 1.15MW load. Cause: for verification. [WEBSMS] | CMIN
11/5/2023 10:51:49 PM | Mindanao Grid-11/05/2023 22:55: Tudaya 2 Unit 1 cut-in at 2042H. (Unplanned Outage). Note: Said unit tripped at 2007H with 2.86MW load. Cause: for verification. [WEBSMS] | CMIN
11/5/2023 10:50:37 PM | Mindanao Grid-11/05/2023 22:54: Talomo 3 Unit 2 cut-in at 2104H. (Unplanned Outage). Note: Said unit tripped at 1946H with 0.55MW load. Cause: Affected by the tripping of DLPC system 13.8kV line. [WEBSMS] | CMIN
11/5/2023 10:49:39 PM | Mindanao Grid-11/05/2023 22:53: Talomo 3 Unit 1 cut-in at 2055H. (Unplanned Outage). Note: Said unit tripped at 1946H with 0.77MW load. Cause: Affected by the tripping of DLPC system 13.8kV line. [WEBSMS] | CMIN
11/5/2023 10:48:42 PM | Mindanao Grid-11/05/2023 22:52: Talomo 2B Unit 1 cut-in at 2002H. (Unplanned Outage). Note: Said unit tripped at 1946H with 0.21MW load. Cause: Affected by the tripping of DLPC system 13.8kV line. [WEBSMS] | CMIN
11/5/2023 10:47:50 PM | Mindanao Grid-11/05/2023 22:51: Talomo 2A Unit 1 cut-in at 2016H. (Unplanned Outage). Note: Said unit tripped at 1946H with 1.25MW load. Cause: Affected by the tripping of DLPC system 13.8kV line. [WEBSMS] | CMIN
11/5/2023 10:18:46 PM | Mindanao Grid-11/05/2023 22:22: Mati Diesel (MDP) cut-out at 2105H. End of RTD. [WEBSMS] | CMIN
11/5/2023 9:14:28 PM | Luzon Grid-11/05/2023 21:14: MPGC 2 online at 2113H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 9:11:07 PM | Luzon Grid-11/05/2023 21:11: MPGC 2 load rejection with a load of 150MW at 2108H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 7:48:59 PM | Mindanao Grid-11/05/2023 19:52: Mt. Apo Unit #3 online at 1941H. Unplanned Outage. [WEBSMS] | CMIN
11/5/2023 7:38:54 PM | Luzon Grid-11/05/2023 19:39: San Lorenzo 60 online at 1937H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 7:27:16 PM | Visayas Grid-11/05/2023 19:27: Compostela-Medellin 69kV Line energized at 1926H. Unplanned outage [WEBSMS] | CVIS
11/5/2023 7:22:29 PM | Visayas Grid-11/05/2023 19:22: Compostela-Consolacion 69kV Line energized at 1920H. Unplanned Outage [WEBSMS] | CVIS
11/5/2023 7:20:49 PM | Visayas Grid-11/05/2023 19:20: Compostela SS 69kV Bus energized at 1919H. (Unplanned Outage) [WEBSMS] | CVIS
11/5/2023 6:21:33 PM | Luzon Grid-11/05/2023 18:21: Muntinlupa (Sucat)-Gardner 115kV Tie Line 2 restored at 1820H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 6:20:12 PM | Luzon Grid-11/05/2023 18:20: Muntinlupa (Sucat) SS 300MVA T04 restored at 1818H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 6:10:03 PM | Visayas Grid-11/05/2023 18:10: Compostela SS 69kV Bus emergency de-energized at 1803H to facilitate correction of heavy arcing at 5DS03 7XF04COM. (Unplanned Outage) [WEBSMS] | CVIS
11/5/2023 6:06:02 PM | [NSO Update] Luzon Grid-11/05/2023 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12493MW, PK=9774MW, RR=356MW, NetOpMargin: EVE=2363 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @325MW, MSLC3 @110MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
11/5/2023 6:05:01 PM | Visayas Grid-11/05/2023 18:05: Compostela-Consolacion 69kV Line de-energized at 1802H. Unplanned Outage [WEBSMS] | CVIS
11/5/2023 6:03:46 PM | Visayas Grid-11/05/2023 18:03: Compostela-Medellin 69kV Line emergency de-energized at 1802H. Unplanned outage. [WEBSMS] | CVIS
11/5/2023 5:57:56 PM | [NSO Update] Visayas Grid-11/05/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2375MW, PK=2081MW, RR=97MW, NetOpMargin: EVE=197 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @336MW, PGPP1 @76MW [WEBSMS] | CVIS
11/5/2023 5:56:33 PM | Luzon Grid-11/05/2023 17:56: Dona Imelda(Araneta)-Kamuning 115kV Line restored at 1754H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 5:32:44 PM | [NSO Update] Mindanao Grid-11/05/2023 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3274MW, PK=2129MW, RR=77MW, NetOpMargin: EVE=1069 Highest Unit O/L: GNPK 1@138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @31.5MW, MA2 @50MW, AG1 @65MW, AG2 @95MW, AG4 @123MW, AG5 @40MW, AG6 @159MW, AG7 @15MW, PG4 @140MW [WEBSMS] | CMIN
11/5/2023 5:20:55 PM | Luzon Grid-11/05/2023 17:21: Bolo-Sual 230kV Line 1 restored at 1719H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 4:52:21 PM | Visayas Grid-11/05/2023 16:52: PCB 5CB04 7XF04COM manually opened at 1639H due to heavy arcing at 5DS03 7XF04COM. Unplanned Outage [WEBSMS] | CVIS
11/5/2023 4:48:16 PM | Mindanao Grid-11/05/2023 16:51: Butuan 100MVA Power Transformer No. 2 reenergized at 1642H. Planned Outage. [WEBSMS] | CMIN
11/5/2023 4:48:10 PM | Visayas Grid-11/05/2023 16:48: Compostela 138/69KV Transformer #4 energized 1628H. Planned Outage [WEBSMS] | CVIS
11/5/2023 4:40:18 PM | Luzon Grid-11/05/2023 16:40: San Jose-San Rafael 230kV Line restored at 1638H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 4:34:24 PM | Luzon Grid-11/05/2023 16:34: Pagbilao EHV SS 500kV Bus 2 restored at 1634H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 4:16:01 PM | Luzon Grid-11/05/2023 16:16: Botolan-Labrador 230kV Line restored at 1615H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 3:54:02 PM | Visayas Grid-11/05/2023 15:54: Magdugo-Colon 138kV Line 3 energized at 1545H. Planned Outage [WEBSMS] | CVIS
11/5/2023 3:43:29 PM | Mindanao Grid-11/05/2023 15:46: Nagamin SVC restored at 1537H. Planned outage. [WEBSMS] | CMIN
11/5/2023 3:41:42 PM | Mindanao Grid-11/05/2023 15:45: Nagamin ss 138KV Bus No. 2 restored at 1535H. Planned Outage. [WEBSMS] | CMIN
11/5/2023 3:38:58 PM | Mindanao Grid-11/05/2023 15:42: Mt Apo Unit 3 (MA3) with 3.0MW gross generation tripped at 1531H. Indication: PH level very high. Unplanned Outage. [WEBSMS] | CMIN
11/5/2023 3:08:20 PM | Mindanao Grid-11/05/2023 15:11: Nagamin-Zamboanga 138KV Line 2 restored at 1448H. Planned outage. [WEBSMS] | CMIN
11/5/2023 1:46:21 PM | Mindanao Grid-11/05/2023 13:49: Bunawan-Nabunturan 138KV Line restored at 1342H. Planned Outage. [WEBSMS] | CMIN
11/5/2023 12:59:33 PM | [NSO Update] Mindanao Grid-11/05/2023 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3308MW, PK=1933MW, RR=72MW, NetOpMargin: PM=1303, EVE=1144 Highest Unit O/L: GNPK 1@138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @31.5MW, MA2 @50MW, AG1 @65MW, AG2 @95MW, AG4 @123MW, AG5 @40MW, AG6 @159MW, AG7 @15MW, PG4 @140MW [WEBSMS] | CMIN
11/5/2023 12:50:27 PM | [NSO Update] Mindanao Grid-11/05/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3283MW, PK=1933MW, RR=72MW, NetOpMargin: PM=1278, EVE=1119 Highest Unit O/L: GNPK 1@138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @31.5MW, MA2 @50MW, AG1 @65MW, AG2 @95MW, AG4 @123MW, AG5 @15MW, AG6 @159MW, AG7 @15MW, PG4 @140MW [WEBSMS] | CMIN
11/5/2023 12:48:20 PM | [NSO Update] Luzon Grid-11/05/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13407MW, PK=9526MW, RR=355MW, NetOpMargin: PM=3526, EVE=2458 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @325MW, MSLC3 @110MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
11/5/2023 12:45:32 PM | [NSO Update] Visayas Grid-11/05/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2528MW, PK=1865MW, RR=94MW, NetOpMargin: PM=569, EVE=177 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @305MW, PGPP1 @76MW [WEBSMS] | CVIS
11/5/2023 12:11:54 PM | Luzon Grid-11/05/2023 12:12: SCPC 3 online at 1210H (Unplanned Outage) [WEBSMS] | CLUZ
11/5/2023 10:08:08 AM | Luzon Grid-11/05/2023 10:08: Dona Imelda(Araneta)-Kamuning 115kV Line de-energized at 1005H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 9:12:01 AM | Mindanao Grid-11/05/2023 09:15: Mati Diesel (MDP) online at 0900H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
11/5/2023 9:08:11 AM | Mindanao Grid-11/05/2023 09:11: Agus 7 HEPP Unit #1 shutdown at 0901H. Planned Outage/PMS (GOMP). [WEBSMS] | CMIN
11/5/2023 8:56:38 AM | Visayas Grid-11/05/2023 08:56: Lapu-Lapu GIS Fdr.# 4 energized @0835H. [WEBSMS] | CVIS
11/5/2023 8:38:59 AM | Luzon Grid-11/05/2023 08:39: San Jose-San Rafael 230kV Line de-energized at 0838H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 8:30:26 AM | Luzon Grid-11/05/2023 08:30: Pagbilao EHV SS 500kV Bus 2 de-energized at 0829H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 8:29:01 AM | Mindanao Grid-11/05/2023 08:32: Polanco SS 75MVA transformer No. 2 deenergized at 0819H.Planned Outage. [WEBSMS] | CMIN
11/5/2023 8:02:22 AM | Luzon Grid-11/05/2023 08:02: Botolan-Labrador 230kV Linede-energized at 0802H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 7:43:35 AM | Mindanao Grid-11/05/2023 07:47: Bunawan-Nabunturan 138KV Line deenergized at 0702H. Planned Outage. [WEBSMS] | CMIN
11/5/2023 7:41:57 AM | Mindanao Grid-11/05/2023 07:45: Nagamin SS 138KV Bus 2 deenergized at 0647H. Planned Outage. [WEBSMS] | CMIN
11/5/2023 7:39:41 AM | Mindanao Grid-11/05/2023 07:43: Nagamin SVC deenergized at 0643H. Planned Outage. [WEBSMS] | CMIN
11/5/2023 7:33:04 AM | Mindanao Grid-11/05/2023 07:36: Butuan SS Power Transformer No. 2 deenergized at 0629H. Planned outage. [WEBSMS] | CMIN
11/5/2023 6:35:15 AM | Luzon Grid-11/05/2023 06:35: Muntinlupa (Sucat) SS 300MVA T04 de-energized at 0633H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 6:33:40 AM | Luzon Grid-11/05/2023 06:33: Muntinlupa (Sucat)-Gardner 115kV Tie Line 2 de-energized at 0632H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 6:31:34 AM | Visayas Grid-11/05/2023 06:31: Lapu-Lapu GIS Fdr.# 4 de-energized @0613H, Customers request. [WEBSMS] | CVIS
11/5/2023 6:29:44 AM | Luzon Grid-11/05/2023 06:29: San Lorenzo 60 shutdown at 0628H (Planned Outage) [WEBSMS] | CLUZ
11/5/2023 6:29:35 AM | Visayas Grid-11/05/2023 06:29: Compostela 138/69KV Transformer #4 de-energized @0625H. Planned Outage [WEBSMS] | CVIS
11/5/2023 5:58:30 AM | [NSO Update] Luzon Grid-11/05/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13548MW, PK=9327MW, RR=352MW, NetOpMargin: AM=3869, PM=3741, EVE=3053 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @325MW, MSLC3 @110MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
11/5/2023 5:52:04 AM | [NSO Update] Mindanao Grid-11/05/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3211MW, PK=1695MW, RR=68MW, NetOpMargin: AM=1447, PM=1194, EVE=1027 Highest Unit O/L: GNPK 1 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @31.5MW, MA2 @50MW, AG1 @65MW, AG2 @40MW, AG4 @123MW, AG5 @40MW, AG6 @149MW, AG7 @15MW, PG4 @100MW [WEBSMS] | CMIN
11/5/2023 5:50:11 AM | [NSO Update] Visayas Grid-11/05/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2694MW, PK=1856MW, RR=93MW, NetOpMargin: AM=745, PM=709, EVE=277 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @295MW, PGPP1 @76MW [WEBSMS] | CVIS
11/5/2023 5:34:46 AM | Mindanao Grid-11/05/2023 05:38: Kauswagan-Lala 230kV L1 energized at 2155H (Nov. 04, 2023). [WEBSMS] | CMIN
11/5/2023 5:28:30 AM | Visayas Grid-11/05/2023 05:28: Magdugo-Colon 138kV Line 3 de-energized at 0526H. Planned Outage [WEBSMS] | CVIS
11/5/2023 5:14:52 AM | [NSO Update] Mindanao Grid-11/05/2023 05:18: Weather Update: Shear Line affecting the northern section of Northern Luzon. [WEBSMS] | CMIN
11/5/2023 5:14:35 AM | [NSO Update] Visayas Grid-11/05/2023 05:14: Weather Update: Shear Line affecting the northern section of Northern Luzon. [WEBSMS] | CVIS
11/5/2023 5:14:20 AM | [NSO Update] Luzon Grid-11/05/2023 05:14: Weather Update: Shear Line affecting the northern section of Northern Luzon. [WEBSMS] | CLUZ
11/5/2023 1:51:41 AM | Luzon Grid-11/05/2023 01:51: MakBan Unit 3 (47MW) tripped at 0142H (Unplanned Outage) [WEBSMS] | CLUZ
11/5/2023 1:06:47 AM | Mindanao Grid-11/05/2023 01:10: Tudaya 2 Unit 1 and Tudaya 2 Unit 2 both cut-in at 2303H - 04 Nov 2023. (Unplanned Outage) [WEBSMS] | CMIN
11/5/2023 1:05:57 AM | Mindanao Grid-11/05/2023 01:09: Tudaya 2 Unit 1 and Tudaya 2 Unit 2 both cut-in at 2303H. (Unplanned Outage) [WEBSMS] | CMIN
11/5/2023 1:04:47 AM | Mindanao Grid-11/05/2023 01:08: Sibulan A Unit 1, Sibulan A Unit 2, Sibulan B Unit 1, Sibulan B Unit 2, and Tudaya 1 Unit 1 cut-in at 2219H, 2218H, 2247H, 2254H, and 2257H, respectively - 04 Nov 2023. (Unplanned Outage) [WEBSMS] | CMIN
11/4/2023 11:28:55 PM | Mindanao Grid-11/04/2023 23:32: Sibulan A Unit 2 shutdown at 2155H. Affected by load transfer activity of DLPC. (Unplanned Outage) [WEBSMS] | CMIN
11/4/2023 11:27:43 PM | Mindanao Grid-11/04/2023 23:31: Sibulan B Unit 1 & Unit 2 shutdown at 2152H. Affected by load transfer activity of DLPC. (Unplanned Outage) [WEBSMS] | CMIN
11/4/2023 11:26:59 PM | Mindanao Grid-11/04/2023 23:30: Tudaya 1 shutdown at 2151H. Affected by load transfer activity of DLPC. (Unplanned Outage) [WEBSMS] | CMIN
11/4/2023 11:26:16 PM | Mindanao Grid-11/04/2023 23:29: Sibulan A Unit 1 shutdown at 2151H. Affected by load transfer activity of DLPC. (Unplanned Outage) [WEBSMS] | CMIN
11/4/2023 11:25:07 PM | Mindanao Grid-11/04/2023 23:28: Tudaya 2 Unit 1 & 2 shutdown at 2147H. Affected by load transfer activity of DLPC. (Unplanned Outage) [WEBSMS] | CMIN
11/4/2023 6:19:48 PM | Mindanao Grid-11/04/2023 18:23: Nagamin SS Power Transformer No.3 /SVC energized at 1735H. Planned Outage. [WEBSMS] | CMIN
11/4/2023 6:15:30 PM | Mindanao Grid-11/04/2023 18:18: Nagamin SS Power Transformer No. 1 energized at 1727H. Planned Outage. [WEBSMS] | CMIN
11/4/2023 6:10:41 PM | Luzon Grid-11/04/2023 18:10: Nagsaag-Bolo 500kV Line 2 restored at 1810H (Planned Outage) [WEBSMS] | CLUZ
11/4/2023 5:55:31 PM | [NSO Update] Mindanao Grid-11/04/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3169MW, PK=2111MW, RR=80MW, NetOpMargin: EVE=979 Highest Unit O/L: GNPK 1 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @65MW, AG2 @95MW, AG4 @124MW, AG5 @40MW, AG6 @180MW, AG7 @35MW, PG4 @100MW [WEBSMS] | CMIN
11/4/2023 5:54:17 PM | [NSO Update] Visayas Grid-11/04/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2528MW, PK=2136MW, RR=97MW, NetOpMargin: EVE=296 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @305MW, PGPP1 @76MW [WEBSMS] | CVIS
11/4/2023 5:52:45 PM | [NSO Update] Luzon Grid-11/04/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12841MW, PK=10331MW, RR=376MW, NetOpMargin: EVE=2134 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @330MW, MSLC3 @105MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
11/4/2023 5:52:15 PM | Mindanao Grid-11/04/2023 17:55: SMC Unit 1 cut-in at 1628H from PMS (Non-GOMP). Stable load (of 30MW) attained at 1750H. [WEBSMS] | CMIN
11/4/2023 4:35:26 PM | Visayas Grid-11/04/2023 16:35: Magdugo-Colon 138kV Line 1 energized at 1632H. Planned Outage [WEBSMS] | CVIS
11/4/2023 4:07:41 PM | Luzon Grid-11/04/2023 16:07: Pagbilao EHV 500kV Bus 1 restored at 1559H (Planned Outage) [WEBSMS] | CLUZ
11/4/2023 3:44:52 PM | Mindanao Grid-11/04/2023 15:48: Baloi-Tagoloan 138kV L Auto-Tripped 15:15:51H but Auto-Reclosed. Unplanned Outage. [WEBSMS] | CMIN
11/4/2023 3:18:18 PM | Mindanao Grid-11/04/2023 15:21: WMPC DG04 cut-out at 1514H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/4/2023 12:41:25 PM | [NSO Update] Luzon Grid-11/04/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13541MW, PK=10354MW, RR=386MW, NetOpMargin: PM=2801, EVE=2485 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 330MW, Masinloc 3 @ 105MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
11/4/2023 12:39:29 PM | [NSO Update] Mindanao Grid-11/04/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3205MW, PK=2114MW, RR=80MW, NetOpMargin: PM=1012, EVE=919 Highest Unit O/L: GNPK 1 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @65MW, AG2 @95MW, AG4 @124MW, AG5 @40MW, AG6 @180MW, AG7 @35MW, PG4 @100MW [WEBSMS] | CMIN
11/4/2023 12:34:14 PM | [NSO Update] Visayas Grid-11/04/2023 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2421MW, PK=2065MW, RR=94MW, NetOpMargin: PM=262, EVE=223 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @ 250MW, PGPP1 @ 76MW, PDPP3-G @ 7MW, PDPP3-H @ 10MW [WEBSMS] | CVIS
11/4/2023 10:23:05 AM | Mindanao Grid-11/04/2023 10:26: Talomo 1 Unit 2 with 0.18MW load shutdown at 1017H due to insufficient water supply. (Unplanned Outage). [WEBSMS] | CMIN
11/4/2023 9:53:10 AM | Mindanao Grid-11/04/2023 09:56: WMPC DG04 cut-in at 0950H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
11/4/2023 9:30:23 AM | Mindanao Grid-11/04/2023 09:33: Talomo 1 Unit 2 cut-in at 0850H. (Unplanned Outage, from outage since 28 Oct 2023 2001H due to insufficient water supply; outside management control). [WEBSMS] | CMIN
11/4/2023 8:47:02 AM | Luzon Grid-11/04/2023 08:47: Pagbilao EHV 500kV Bus 1 de-energized at 0846H (Planned Outage) [WEBSMS] | CLUZ
11/4/2023 8:23:07 AM | Visayas Grid-11/04/2023 08:23: Magdugo-Colon 138kV Line 1 de-energized at 0822H. Planned Outage [WEBSMS] | CVIS
11/4/2023 8:02:33 AM | Mindanao Grid-11/04/2023 08:06: Pulangi 4 HEP Unit 3 shutdown at 0759H for PMS (GOMP). (Planned Outage) [WEBSMS] | CMIN
11/4/2023 7:12:28 AM | Mindanao Grid-11/04/2023 07:15: Nagamin SS Power Transformer No. 1 deenergized at 0706H. Planned Outage. [WEBSMS] | CMIN
11/4/2023 7:02:06 AM | Luzon Grid-11/04/2023 07:02: Nagsaag-Bolo 500kV Line 2 de-energized at 0701H (Planned Outage) [WEBSMS] | CLUZ
11/4/2023 6:20:06 AM | Luzon Grid-11/04/2023 06:20: Bolo-Sual 230kV Line 1 de-energized at 0619H (Planned Outage) [WEBSMS] | CLUZ
11/4/2023 6:20:03 AM | Mindanao Grid-11/04/2023 06:23: Nagamin SS Power Transformer No. 3/SVC deenergized at 0608H. Planned Outage. [WEBSMS] | CMIN
11/4/2023 5:48:24 AM | [NSO Update] Luzon Grid-11/04/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13596MW, PK=9873MW, RR=382MW, NetOpMargin: AM=3341, PM=3443, EVE=3014 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 330MW, Masinloc 3 @ 95MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
11/4/2023 5:46:34 AM | [NSO Update] Mindanao Grid-11/04/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3212MW, PK=1967MW, RR=80MW, NetOpMargin: AM=1165, PM=1090, EVE=965 Highest Unit O/L: GNPK 1 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @65MW, AG2 @95MW, AG4 @124MW, AG5 @40MW, AG6 @180MW, AG7 @35MW, PG4 @100MW [WEBSMS] | CMIN
11/4/2023 5:43:34 AM | [NSO Update] Visayas Grid-11/04/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2482MW, PK=2092MW, RR=93MW, NetOpMargin: AM=296, PM=380, EVE=264 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 255MW, PGPP1 @ 76MW, PDPP3-G @ 7MW, PDPP3-H @ 10MW [WEBSMS] | CVIS
11/4/2023 4:57:08 AM | Mindanao Grid-11/04/2023 05:00: Nagamin SS Power Transformer No. 2 restored at 0450H. Planned Outage. [WEBSMS] | CMIN
11/4/2023 4:27:36 AM | Mindanao Grid-11/04/2023 04:31: Nagamin SS Power Transformer No. 2 deenergized at 0422H. Planned Outage. [WEBSMS] | CMIN
11/4/2023 4:17:40 AM | [NSO Update] Mindanao Grid-11/04/2023 04:21: Weather Update: Shear Line affecting the northern section of Northern Luzon. [WEBSMS] | CMIN
11/4/2023 4:17:25 AM | [NSO Update] Visayas Grid-11/04/2023 04:17: Weather Update: Shear Line affecting the northern section of Northern Luzon. [WEBSMS] | CVIS
11/4/2023 4:17:12 AM | [NSO Update] Luzon Grid-11/04/2023 04:17: Weather Update: Shear Line affecting the northern section of Northern Luzon. [WEBSMS] | CLUZ
11/4/2023 1:35:07 AM | Visayas Grid-11/04/2023 01:35: Maasin-UBay 138KV T/L de-energized at Ubay SS at 0123H, Bohol Sub-grid isolated from the system due to Hotspot correction at Maasin ( Guadalope CTS). (Planned Outage). ECD: 0500H [WEBSMS] | CVIS
11/3/2023 11:03:42 PM | Luzon Grid-11/03/2023 23:03: Kalayaan Unit 3 tripped as pump at 2301H (Unplanned Outage). The highest frequency is 60.19Hz. [WEBSMS] | CLUZ
11/3/2023 10:14:47 PM | Luzon Grid-11/03/2023 22:14: San Juan - Calauan 230kV Line 1 restored at 2214H. (Unplanned Outage) [WEBSMS] | CLUZ
11/3/2023 9:32:30 PM | Luzon Grid-11/03/2023 21:32: San Juan - Calauan 230kV Line 2 looped at San Juan side at 2130H. (Unplanned Outage) [WEBSMS] | CLUZ
11/3/2023 9:29:53 PM | Luzon Grid-11/03/2023 21:29: Correction: San Juan - Calauan 230kV Line 1 tripped while San Juan - Calauan 230kV Line 2 tripped at San Juan side only, both at 2106H. (Unplanned Outage) [WEBSMS] | CLUZ
11/3/2023 9:25:43 PM | Mindanao Grid-11/03/2023 21:29: WMPC DG04 shutdown at 2114H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/3/2023 9:19:00 PM | Luzon Grid-11/03/2023 21:19: MPGC 2 online at 2116H. (On-going testing and commissioning) [WEBSMS] | CLUZ
11/3/2023 9:15:32 PM | Luzon Grid-11/03/2023 21:15: San Juan - Calauan 230kV Line 1 & 2 tripped at 2106H. San Juan - Calauan 230kV Line 2 successfully reclosed at Calauan side. (Unplanned Outage) [WEBSMS] | CLUZ
11/3/2023 9:09:41 PM | Luzon Grid-11/03/2023 21:09: San Juan - Calauan 230kV Line 1 & 2 tripped at 2106H. (Unplanned Outage) [WEBSMS] | CLUZ
11/3/2023 8:34:39 PM | Luzon Grid-11/03/2023 20:34: For information: MPGC Unit 2 conducted Load Rejection Test(LRT) from 90MW load at 2033H. (Plant Commissioning Test) [WEBSMS] | CLUZ
11/3/2023 7:08:15 PM | Mindanao Grid-11/03/2023 19:11: TSI Unit #2 online at 1903H. Unplanned Outage. [WEBSMS] | CMIN
11/3/2023 6:59:31 PM | Mindanao Grid-11/03/2023 19:02: WMPC DG04 run as RPS with 8.5MW gross generation, tripped at 1853H. Indication: HT Inlet High Pressure Stop. Unplanned Outage. [WEBSMS] | CMIN
11/3/2023 5:56:54 PM | [NSO Update] Luzon Grid-11/03/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12816MW, PK=10648MW, RR=356MW, NetOpMargin: EVE=1812 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 330MW, Masinloc 3 @ 325MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
11/3/2023 5:54:21 PM | [NSO Update] Mindanao Grid-11/03/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3136MW, PK=2132MW, RR=80MW, NetOpMargin: EVE=924 Highest Unit O/L: GNPK 1 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @65MW, AG2 @95MW, AG4 @123MW, AG5 @40MW, AG6 @180MW, AG7 @35MW, PG4 @200MW [WEBSMS] | CMIN
11/3/2023 5:52:35 PM | [NSO Update] Visayas Grid-11/03/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2516MW, PK=2221MW, RR=97MW, NetOpMargin: EVE=198 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 260MW, PGPP1 @ 76MW, PDPP3-C @ 10MW, PDPP3-E @ 10MW, PDPP3-H @ 10MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
11/3/2023 5:24:11 PM | Mindanao Grid-11/03/2023 17:27: WMPC DG06 shutdown at 1613H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/3/2023 5:20:31 PM | Luzon Grid-11/03/2023 17:20: Masinloc-Bolo 230kV Line 2 restored at 1719H. (Planned Outage) [WEBSMS] | CLUZ
11/3/2023 5:06:56 PM | Luzon Grid-11/03/2023 17:06: Nagsaag - Binga 230kV Line 1 tripped and reclosed successfully on both side at 1704H. (Unplanned Outage) [WEBSMS] | CLUZ
11/3/2023 4:34:09 PM | Mindanao Grid-11/03/2023 16:37: Therma South Inc. (TSI) Unit 2 with gross generation of 148.6MW tripped at 1616H. Unplanned Outage. System frequency dipped to a low of 59.11Hz. ALD of 40.465MW. [WEBSMS] | CMIN
11/3/2023 4:09:15 PM | Mindanao Grid-11/03/2023 16:12: Lake Mainit HEPP shutdown at 1601H to facilitate scheduled equipment inspection and Maintenance activity. (Non-GOMP). Planned Outage. [WEBSMS] | CMIN
11/3/2023 12:46:05 PM | [NSO Update] Mindanao Grid-11/03/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3289MW, PK=2270MW, RR=80MW, NetOpMargin: PM=938, EVE=932 Highest Unit O/L: GNPK 1 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @65MW, AG2 @95MW, AG4 @123MW, AG5 @40MW, AG6 @180MW, AG7 @35MW, PG4 @180MW [WEBSMS] | CMIN
11/3/2023 12:45:53 PM | Mindanao Grid-11/03/2023 12:49: Lake Mainit HEPP online at 1240H. Unplanned Outage. [WEBSMS] | CMIN
11/3/2023 12:43:00 PM | [NSO Update] Visayas Grid-11/03/2023 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2556MW, PK=2270MW, RR=93MW, NetOpMargin: PM=193, EVE=255 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @255MW, PGPP1 @76MW, PDPP3-C @10MW, PDPP3-E @10MW, PDPP3-H @10MW, PDPP3-G @7MW [WEBSMS] | CVIS
11/3/2023 12:34:09 PM | [NSO Update] Luzon Grid-11/03/2023 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13400MW, PK=10954MW, RR=356MW, NetOpMargin: PM=2090, EVE=2138 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @325MW, MASINLOC 3 @320MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
11/3/2023 12:29:46 PM | Mindanao Grid-11/03/2023 12:33: Lake Mainit HEPP with 10.5MW gross generation tripped at 1222H. Indication: 50BF (Breaker Failure). Frequency=60.06Hz. Unplanned Outage. [WEBSMS] | CMIN
11/3/2023 10:54:06 AM | Mindanao Grid-11/03/2023 10:57: WMPC DG06 Online at 1050H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/3/2023 10:19:53 AM | Visayas Grid-11/03/2023 10:19: Colon - VECO 69 kV Line energized at 1014H. (new connection point) [WEBSMS] | CVIS
11/3/2023 9:03:24 AM | Mindanao Grid-11/03/2023 09:06: WMPC GG04 Online at 0853H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
11/3/2023 8:45:26 AM | Mindanao Grid-11/03/2023 08:48: Kauswagan - GNPK Line 2 deenergized at 0836H. Planned outage. [WEBSMS] | CMIN
11/3/2023 8:10:31 AM | Luzon Grid-11/03/2023 08:10: Masinloc-Bolo 230kV Line 2 de-energized at 0809H (Planned Outage) [WEBSMS] | CLUZ
11/3/2023 7:56:42 AM | Mindanao Grid-11/03/2023 08:00: Agus 4 Unit #3 online at 0753H. Unplanned Outage. [WEBSMS] | CMIN
11/3/2023 7:33:02 AM | Mindanao Grid-11/03/2023 07:36: Agus 4 Unit #3 with 36.8MW gross generation tripped at 0723H. Indication: Excitation System Problem. Lowest frequency recorded=59.6847Hz. Unplanned outage. [WEBSMS] | CMIN
11/3/2023 6:15:51 AM | [NSO Update] Luzon Grid-11/03/2023 06:15: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13574MW, PK=9752MW, RR=355MW, NetOpMargin: AM=3467, PM=3243, EVE=3067 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MASINLOC 3 @325MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
11/3/2023 5:54:46 AM | [NSO Update] Mindanao Grid-11/03/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3237MW, PK=2068MW, RR=80MW, NetOpMargin: AM=1088, PM=1041, EVE=1002 Highest Unit O/L: GNPK 1 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @65MW, AG2 @40MW, AG4 @123MW, AG5 @40MW, AG6 @149MW, AG7 @35MW, PG4 @180MW [WEBSMS] | CMIN
11/3/2023 5:51:00 AM | [NSO Update] Visayas Grid-11/03/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2412MW, PK=2076MW, RR=93MW, NetOpMargin: AM=243, PM=239, EVE=279 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @260MW, PGPP1 @76MW, PDPP3-C @10MW, PDPP3-E @10MW, PDPP3-H @10MW, PDPP3-G @7MW [WEBSMS] | CVIS
11/3/2023 4:21:38 AM | [NSO Update] Luzon Grid-11/03/2023 04:21: Weather Update: Shear Line affecting the northern and eastern sections of Northern Luzon. [WEBSMS] | CLUZ
11/3/2023 4:19:40 AM | [NSO Update] Mindanao Grid-11/03/2023 04:23: Weather Update: Shear Line affecting the northern and eastern sections of Northern Luzon. [WEBSMS] | CMIN
11/3/2023 4:18:47 AM | [NSO Update] Visayas Grid-11/03/2023 04:18: Weather Update: Shear Line affecting the northern and eastern sections of Northern Luzon. [WEBSMS] | CVIS
11/2/2023 9:59:26 PM | Visayas Grid-11/02/2023 21:59: Compostela SS 150 MVA 230/138 kV TR2 energized at 2156H. (Unplanned Outage) [WEBSMS] | CVIS
11/2/2023 8:52:01 PM | Visayas Grid-11/02/2023 20:52: Daanbantayan SS 69KV Lanao fdr (CEBECO 2) tripped at 2005H restored 2017H, load 29.8MW, indication overcurrent.(Unplanned outage) [WEBSMS] | CVIS
11/2/2023 8:26:40 PM | Mindanao Grid-11/02/2023 20:30: ASIGA Hydro cut-in at 1953H. (Unplanned Outage) [WEBSMS] | CMIN
11/2/2023 8:24:32 PM | Mindanao Grid-11/02/2023 20:27: ASIGA Hydro tripped with 4.2MW load at 1939H. Lowest frequency recorded was 60.0Hz. Cause: for verification. (Unplanned Outage) [WEBSMS] | CMIN
11/2/2023 7:00:51 PM | Mindanao Grid-11/02/2023 19:04: Davao-Bunawan 138 kV L2 Auto-Tripped at 18:35:12H and Auto-Reclosed. Unplanned Outage. [WEBSMS] | CMIN
11/2/2023 5:58:15 PM | [NSO Update] Mindanao Grid-11/02/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3086MW, PK=1997MW, RR=73MW, NetOpMargin: EVE=1017 Highest Unit O/L: GNPK 1 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @31.5MW, MA2 @50MW, AG1 @65MW, AG2 @85MW, AG4 @123MW, AG5 @40MW, AG6 @119MW, AG7 @35MW, PG4 @200MW [WEBSMS] | CMIN
11/2/2023 5:54:59 PM | [NSO Update] Visayas Grid-11/02/2023 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2404MW, PK=2038MW, RR=97MW, NetOpMargin: EVE=268 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @ 290MW, PGPP1 @ 76MW, PDPP3-E @ 10MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
11/2/2023 5:44:06 PM | [NSO Update] Luzon Grid-11/02/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13120MW, PK=9096MW, RR=356MW, NetOpMargin: EVE=3668 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MASINLOC 1 @330MW, MASINLOC 3 @325MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
11/2/2023 2:31:43 PM | Luzon Grid-11/02/2023 14:31: Limay-Orion Solar 69kV line (Customer Owned) restored at 1428H (Unplanned Outage) [WEBSMS] | CLUZ
11/2/2023 12:54:14 PM | Visayas Grid-11/02/2023 12:54: Compostela SS 150 MVA 230/138 kV TR2 tripped at 1243H. (Unplanned Outage) [WEBSMS] | CVIS
11/2/2023 12:48:37 PM | [NSO Update] Mindanao Grid-11/02/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3049MW, PK=1867MW, RR=68MW, NetOpMargin: PM=1114, EVE=985 Highest Unit O/L: GNPK 1 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @31.5MW, MA2 @50MW, AG1 @65MW, AG2 @88MW, AG4 @108MW, AG5 @20MW, AG6 @98MW, AG7 @35MW, PG4 @180MW [WEBSMS] | CMIN
11/2/2023 12:46:20 PM | [NSO Update] Visayas Grid-11/02/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2386MW, PK=1882MW, RR=94MW, NetOpMargin: PM=410, EVE=294 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @290MW, PGPP1 @76MW, PDPP3-C @10MW, PDPP3-E @10MW, PDPP3-H @10MW, PDPP3-G @7MW [WEBSMS] | CVIS
11/2/2023 12:42:50 PM | [NSO Update] Luzon Grid-11/02/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13671MW, PK=8593MW, RR=356MW, NetOpMargin: PM=4723, EVE=4430 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
11/2/2023 11:47:05 AM | Luzon Grid-11/02/2023 11:47: BCCPP SS 93.5MVA T01 restored at 1146H. (Customer Owned - Unplanned Outage) [WEBSMS] | CLUZ
11/2/2023 11:20:12 AM | Luzon Grid-11/02/2023 11:20: BCCPP SS 93.5MVA T03 restored at 1118H. (Customer Owned - Unplanned Outage) [WEBSMS] | CLUZ
11/2/2023 11:06:20 AM | Luzon Grid-11/02/2023 11:06: Limay-Batangas II (BPC) 230kV Line 2 restored at 1104H. (Unplanned Outage) [WEBSMS] | CLUZ
11/2/2023 11:03:12 AM | Luzon Grid-11/02/2023 11:03: Correction: Limay-Batangas II (BPC) 230kV Line 2 tripped at 1033H. (Unplanned Outage) [WEBSMS] | CLUZ
11/2/2023 10:56:12 AM | Luzon Grid-11/02/2023 10:56: Correction: Limay-Batangas II (BPC) 230kV Line 2 tripped at 1133H (Unplanned Outage) [WEBSMS] | CLUZ
11/2/2023 10:45:58 AM | Luzon Grid-11/02/2023 10:45: BCCPP SS 93.5MVA T03 tripped at 1034H (Unplanned Outage) [WEBSMS] | CLUZ
11/2/2023 10:44:30 AM | Luzon Grid-11/02/2023 10:44: BCCPP SS 93.5MVA T01 tripped at 1033H (Unplanned Outage) [WEBSMS] | CLUZ
11/2/2023 10:37:09 AM | Luzon Grid-11/02/2023 10:37: Limay-Orion Solar 69kV line (Customer Owned) tripped at 1033H (Unplanned Outage) [WEBSMS] | CLUZ
11/2/2023 9:54:02 AM | Luzon Grid-11/02/2023 09:54: Mauban PCB 8-07CB04MBA energized at 0950H (Unplanned Outage) [WEBSMS] | CLUZ
11/2/2023 9:22:06 AM | Luzon Grid-11/02/2023 09:22: Mauban PCB 8-07CB04MBA emergency shutdown at 0921H due to critical level of SF6 gas pressure (Unplanned Outage) [WEBSMS] | CLUZ
11/2/2023 5:47:08 AM | [NSO Update] Luzon Grid-11/02/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13756MW, PK=7241MW, RR=356MW, NetOpMargin: AM=6159, PM=5991, EVE=5015 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
11/2/2023 5:45:31 AM | [NSO Update] Mindanao Grid-11/02/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3167MW, PK=1765MW, RR=64MW, NetOpMargin: AM=1338, PM=1362, EVE=1012 Highest Unit O/L: GNPK 1 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @31.5MW, MA2 @50MW, AG1 @65MW, AG2 @40MW, AG4 @123MW, AG5 @40MW, AG6 @109MW, AG7 @35MW, PG4 @140MW [WEBSMS] | CMIN
11/2/2023 5:44:26 AM | [NSO Update] Visayas Grid-11/02/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2406MW, PK=1688MW, RR=93MW, NetOpMargin: AM=625, PM=616, EVE=413 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 288MW, PGPP1 @ 76MW, PDPP3-C @ 10MW, PDPP3-E @ 10MW, PDPP3-G @ 7MW, PDPP3-H @ 8MW [WEBSMS] | CVIS
11/2/2023 4:10:16 AM | [NSO Update] Mindanao Grid-11/02/2023 04:13: Weather Update: Shear Line affecting the eastern sections of Northern Luzon and Central Luzon. Northeast Monsoon affecting the rest of Northern and Central Luzon. [WEBSMS] | CMIN
11/2/2023 4:10:04 AM | [NSO Update] Visayas Grid-11/02/2023 04:10: Weather Update: Shear Line affecting the eastern sections of Northern Luzon and Central Luzon. Northeast Monsoon affecting the rest of Northern and Central Luzon. [WEBSMS] | CVIS
11/2/2023 4:09:51 AM | [NSO Update] Luzon Grid-11/02/2023 04:09: Weather Update: Shear Line affecting the eastern sections of Northern Luzon and Central Luzon. Northeast Monsoon affecting the rest of Northern and Central Luzon. [WEBSMS] | CLUZ
11/2/2023 3:29:43 AM | Mindanao Grid-11/02/2023 03:33: Lake Mainit HEPP online at 0326H. Unplanned Outage. [WEBSMS] | CMIN
11/2/2023 2:14:25 AM | Mindanao Grid-11/02/2023 02:17: Lake Mainit HEPP with 10.5MW gross generation, tripped at 0210H. Indication: Unit #3 reverse power. Frequency recorded was 60.05Hz. Unplanned Outage. [WEBSMS] | CMIN
11/2/2023 1:56:30 AM | Mindanao Grid-11/02/2023 01:59: Lake Mainit HEPP online at 0152H. Unplanned Outage. [WEBSMS] | CMIN
11/2/2023 1:46:59 AM | Mindanao Grid-11/02/2023 01:50: Lake Mainit HEPP with 10.5MW gross generation, tripped at 0137H. Indication: Unit #3 Reverse Power. Lowest frequency recorded was 59.95Hz. Unplanned Outage. [WEBSMS] | CMIN
11/1/2023 11:23:31 PM | Luzon Grid-11/01/2023 23:23: Masinloc Unit 2 shutdownshutdown at 2319H (Unplanned Outage) [WEBSMS] | CLUZ
11/1/2023 8:39:26 PM | Luzon Grid-11/01/2023 20:39: SCPC 3 tripped at 2038H. (Unplanned Outage) [WEBSMS] | CLUZ
11/1/2023 8:13:04 PM | Luzon Grid-11/01/2023 20:13: SCPC 3 online at 2011H. (Unplanned Outage) [WEBSMS] | CLUZ
11/1/2023 6:03:30 PM | [NSO Update] Mindanao Grid-11/01/2023 18:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1802H with power going to Visayas. [WEBSMS] | CMIN
11/1/2023 6:03:16 PM | [NSO Update] Visayas Grid-11/01/2023 18:03: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1802H with power going to Visayas. [WEBSMS] | CVIS
11/1/2023 5:54:02 PM | [NSO Update] Visayas Grid-11/01/2023 17:54: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1752H from reverse power direction. [WEBSMS] | CVIS
11/1/2023 5:53:34 PM | [NSO Update] Mindanao Grid-11/01/2023 17:57: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1752H from reverse power direction. [WEBSMS] | CMIN
11/1/2023 5:51:06 PM | Mindanao Grid-11/01/2023 17:54: SMF2 Unit #2 (SEC2) online at 1740H from PMS (GOMP). Planned Outage. [WEBSMS] | CMIN
11/1/2023 5:48:53 PM | [NSO Update] Luzon Grid-11/01/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13443MW, PK=8110MW, RR=342MW, NetOpMargin: EVE=4991 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 325MW, Masinloc 2 @ 325MW, Masinloc 3 @ 315MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
11/1/2023 5:47:28 PM | [NSO Update] Mindanao Grid-11/01/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3145MW, PK=1919MW, RR=80MW, NetOpMargin: EVE=1146 Highest Unit O/L: GNPK 1 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @65MW, AG2 @40MW, AG4 @123MW, AG5 @40MW, AG6 @149MW, AG7 @35MW, PG4 @200MW [WEBSMS] | CMIN
11/1/2023 5:46:22 PM | [NSO Update] Visayas Grid-11/01/2023 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2306MW, PK=1911MW, RR=97MW, NetOpMargin: EVE=298 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 300MW, PGPP1 @ 76MW, PDPP3-C @ 10MW, PDPP3-E @ 10MW, PDPP3-G @ 7MW, PDPP3-H @ 8MW [WEBSMS] | CVIS
11/1/2023 3:01:20 PM | [NSO Update] Mindanao Grid-11/01/2023 15:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1500H with power going to Mindanao. [WEBSMS] | CMIN
11/1/2023 3:01:06 PM | [NSO Update] Visayas Grid-11/01/2023 15:01: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1500H with power going to Mindanao. [WEBSMS] | CVIS
11/1/2023 2:52:23 PM | [NSO Update] Mindanao Grid-11/01/2023 14:55: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1449H from forward power direction. [WEBSMS] | CMIN
11/1/2023 2:52:06 PM | [NSO Update] Visayas Grid-11/01/2023 14:52: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1449H from forward power direction. [WEBSMS] | CVIS
11/1/2023 1:09:38 PM | [NSO Update] Mindanao Grid-11/01/2023 13:13: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3126MW, PK=1845MW, RR=80MW, NetOpMargin: PM=1201, EVE=994 Highest Unit O/L: GNPK 1 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @65MW, AG2 @40MW, AG4 @123MW, AG5 @40MW, AG6 @159MW, AG7 @35MW, PG4 @180MW [WEBSMS] | CMIN
11/1/2023 1:06:49 PM | [NSO Update] Visayas Grid-11/01/2023 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2426MW, PK=1736MW, RR=94MW, NetOpMargin: PM=595, EVE=233 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @304MW, PGPP1 @76MW, PDPP3-C @10MW, PDPP3-E @10MW, PDPP3-G @7MW, PDPP3-H @8MW [WEBSMS] | CVIS
11/1/2023 12:59:26 PM | [NSO Update] Luzon Grid-11/01/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13940MW, PK=7777MW, RR=316MW, NetOpMargin: PM=5847, EVE=4380 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @175MW, MSLC1 @325MW, MSLC2 @325MW, MSLC3 @315MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
11/1/2023 6:07:49 AM | [NSO Update] Mindanao Grid-11/01/2023 06:11: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3094MW, PK=1640MW, RR=75MW, NetOpMargin: AM=1379, PM=1308, EVE=1088 Highest Unit O/L: GNPK 1@138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @65MW, AG2 @40MW, AG4 @123MW, AG5 @40MW, AG6 @159MW, AG7 @35MW, PG4 @140MW [WEBSMS] | CMIN
11/1/2023 6:05:51 AM | [NSO Update] Visayas Grid-11/01/2023 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2524MW, PK=1745MW, RR=93MW, NetOpMargin: AM=686, PM=520, EVE=183 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @ 304MW, PGPP1 @ 76MW, PDPP3-C @ 10MW, PDPP3-E @ 10MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
11/1/2023 6:04:08 AM | [NSO Update] Luzon Grid-11/01/2023 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14295MW, PK=8147MW, RR=316MW, NetOpMargin: AM=5832, PM=5073, EVE=4157 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC1 @325MW, MASINLOC 2 @325MW, MASINLOC 3 @315MW, ILIJAN A @510MW, ILIJAN B @230MW, [WEBSMS] | CLUZ
11/1/2023 4:16:29 AM | [NSO Update] Luzon Grid-11/01/2023 04:16: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data over the coastal waters of Caramoan, Catanduanes (14.1�N, 124.0�E). Shear Line affecting the eastern sections of Northern and Central Luzon. Northeast Monsoon affecting the rest of Northern and Central Luzon. [WEBSMS] | CLUZ
11/1/2023 4:14:49 AM | [NSO Update] Mindanao Grid-11/01/2023 04:18: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data over the coastal waters of Caramoan, Catanduanes (14.1�N, 124.0�E). Shear Line affecting the eastern sections of Northern and Central Luzon. Northeast Monsoon affecting the rest of Northern and Central Luzon. [WEBSMS] | CMIN
11/1/2023 4:14:28 AM | [NSO Update] Visayas Grid-11/01/2023 04:14: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data over the coastal waters of Caramoan, Catanduanes (14.1�N, 124.0�E). Shear Line affecting the eastern sections of Northern and Central Luzon. Northeast Monsoon affecting the rest of Northern and Central Luzon. [WEBSMS] | CVIS
11/1/2023 12:52:36 AM | Luzon Grid-11/01/2023 00:53: SCPC Unit 3 shutdown at 0051H. (Unplanned Outage) [WEBSMS] | CLUZ
11/1/2023 12:13:49 AM | Mindanao Grid-11/01/2023 00:16: LAMSAN Biomass shutdown at 0001H. Outside Management Control due to fuel shortage. [WEBSMS] | CMIN
11/1/2023 12:10:40 AM | Mindanao Grid-11/01/2023 00:13: SMC Unit 1 shutdown at 0000H for PMS (Non-GOMP). (Planned Outage) [WEBSMS] | CMIN
11/1/2023 12:03:29 AM | Luzon Grid-11/01/2023 00:03: Limay-Orion Solar 69kV line(Customer Owned) tripped at 0002H. (Unplanned Outage) [WEBSMS] | CLUZ
10/31/2023 9:17:54 PM | Mindanao Grid-10/31/2023 21:20: WMPC DG04 cut-out at 2114H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/31/2023 7:36:52 PM | Mindanao Grid-10/31/2023 19:39: LAKE MAINIT Hydro cut-in at 1933H. (Unplanned Outage) [WEBSMS] | CMIN
10/31/2023 7:18:47 PM | Mindanao Grid-10/31/2023 19:21: LAKE MAINIT Hydro tripped with 10.6MW load at 1914H. Lowest frequency recorded was 59.92Hz. Indication: Power Signal Fault. (Unplanned Outage) [WEBSMS] | CMIN
10/31/2023 5:45:47 PM | [NSO Update] Mindanao Grid-10/31/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3366MW, PK=2042MW, RR=80MW, NetOpMargin: EVE=1244 Highest Unit O/L: GNPK 1@ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @31.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @114MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @200MW [WEBSMS] | CMIN
10/31/2023 5:44:06 PM | [NSO Update] Luzon Grid-10/31/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13594MW, PK=9330MW, RR=353MW, NetOpMargin: EVE=3911 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 325MW, Masinloc 2 @ 335MW, Masinloc 3 @ 325MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/31/2023 5:43:40 PM | [NSO Update] Visayas Grid-10/31/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2537MW, PK=2123MW, RR=92MW, NetOpMargin: EVE=323 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @ 290MW, PGPP1 @ 76MW, PDPP3-C @ 10MW, PDPP3-E @ 10MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
10/31/2023 5:35:31 PM | Mindanao Grid-10/31/2023 17:38: WMPC DG01 cut-out at 1614H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/31/2023 4:47:44 PM | Luzon Grid-10/31/2023 16:48: Limay-Orion Solar 69kV line was restored at 1647H. (Unplanned Outage) [WEBSMS] | CLUZ
10/31/2023 4:19:46 PM | Mindanao Grid-10/31/2023 16:22: Agus 6 HEP Unit 1 cut-in at 1616H. (Unplanned Outage) [WEBSMS] | CMIN
10/31/2023 3:02:51 PM | Mindanao Grid-10/31/2023 15:05: NACSUR cut-out at 1500H. End of RTD. [WEBSMS] | CMIN
10/31/2023 12:47:54 PM | [NSO Update] Luzon Grid-10/31/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14415MW, PK=9894MW, RR=356MW, NetOpMargin: PM=4165, EVE=3929 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 325MW, Masinloc 2 @ 335MW, Masinloc 3 @ 325MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/31/2023 12:44:44 PM | [NSO Update] Mindanao Grid-10/31/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3371MW, PK=2046MW, RR=80MW, NetOpMargin: PM=1244, EVE=1160 Highest Unit O/L: GNPK 1 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @31.5MW, MA2 @43MW, AG1 @60MW, AG2 @99MW, AG4 @114MW, AG5 @36MW, AG6 @149MW, AG7 @25MW, PG4 @180MW [WEBSMS] | CMIN
10/31/2023 12:41:57 PM | [NSO Update] Visayas Grid-10/31/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2644MW, PK=2026MW, RR=90MW, NetOpMargin: PM=527, EVE=260 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 280MW, PGPP1 @ 76MW, PDPP3-C @ 10MW, PDPP3-E @ 8MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
10/31/2023 12:41:24 PM | Luzon Grid-10/31/2023 12:41: Limay-Orion Solar 69kV line(Customer Owned) tripped at 1233H. (Unplanned Outage) [WEBSMS] | CLUZ
10/31/2023 10:53:37 AM | Mindanao Grid-10/31/2023 10:56: WMPC DG01 cut-in at 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/31/2023 9:08:43 AM | Mindanao Grid-10/31/2023 09:11: NACSUR cut-in at 0900H. MO dispatched (RTD). [WEBSMS] | CMIN
10/31/2023 8:53:21 AM | Mindanao Grid-10/31/2023 08:56: WMPC DG04 cut-in at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/31/2023 8:34:14 AM | Luzon Grid-10/31/2023 08:34: San Jose PCB 8-05CB08SJO was closed at 0832H. (Unplanned Outage) [WEBSMS] | CLUZ
10/31/2023 7:26:40 AM | Mindanao Grid-10/31/2023 07:29: ASIGA Hydro cut-in at 0657H. (Unplanned Outage) [WEBSMS] | CMIN
10/31/2023 6:57:40 AM | Mindanao Grid-10/31/2023 07:00: LAKE MAINIT Hydro cut-in at 0639H. (Unplanned Outage) [WEBSMS] | CMIN
10/31/2023 6:49:11 AM | Mindanao Grid-10/31/2023 06:52: ASIGA Hydro tripped with 5.1MW load at 0630H. Lowest frequency recorded was 59.79H. (Unplanned Outage). To be investigated. [WEBSMS] | CMIN
10/31/2023 6:32:28 AM | Mindanao Grid-10/31/2023 06:35: LAKE MAINIT cut-in at 0559H. Unplanned Outage. Note: Indication at 0541H tripping: Excitation Current Alarm Low. [WEBSMS] | CMIN
10/31/2023 6:22:05 AM | Mindanao Grid-10/31/2023 06:24: LAKE MAINIT Hydro tripped with 10.5MW load at 0616H. Lowest frequency recorded was 59.69Hz. (Unplanned Outage). Indication: Power Signal Fault. [WEBSMS] | CMIN
10/31/2023 6:02:00 AM | [NSO Update] Luzon Grid-10/31/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14311MW, PK=9450MW, RR=356MW, NetOpMargin: AM=4505, PM=3534, EVE=3605 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 325MW, Masinloc 2 @ 335MW, Masinloc 3 @ 325MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/31/2023 5:56:41 AM | [NSO Update] Visayas Grid-10/31/2023 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2670MW, PK=2032MW, RR=91MW, NetOpMargin: AM=547, PM=607, EVE=271 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @ 282MW, PGPP1 @ 76MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
10/31/2023 5:53:50 AM | Mindanao Grid-10/31/2023 05:56: LAKE MAINIT Hydro with 10.5MW gross generation tripped at 0541H. Indication: To be investigated. Frequency=59.86Hz. (Unplanned Outage). [WEBSMS] | CMIN
10/31/2023 5:51:00 AM | [NSO Update] Mindanao Grid-10/31/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3340MW, PK=1845MW, RR=80MW, NetOpMargin: AM=1414, PM=1131, EVE=1153 Highest Unit O/L: GNPK 1 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @31.5MW, MA2 @43MW, AG1 @60MW, AG2 @99MW, AG4 @114MW, AG5 @30MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
10/31/2023 5:22:01 AM | Luzon Grid-10/31/2023 05:22: San Jose PCB 8-05CB08SJO opened at 0520H (Unplanned Outage) [WEBSMS] | CLUZ
10/31/2023 4:20:26 AM | [NSO Update] Mindanao Grid-10/31/2023 04:23: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting Northern and Central Luzon. Meanwhile, at 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 470 km East of Virac, Catanduanes (14.3�N, 128.5�E). [WEBSMS] | CMIN
10/31/2023 4:19:53 AM | [NSO Update] Visayas Grid-10/31/2023 04:20: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting Northern and Central Luzon. Meanwhile, at 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 470 km East of Virac, Catanduanes (14.3�N, 128.5�E). [WEBSMS] | CVIS
10/31/2023 4:19:25 AM | [NSO Update] Luzon Grid-10/31/2023 04:19: Weather Update: Shear Line affecting the eastern sections of Southern Luzon and Visayas. Northeast Monsoon affecting Northern and Central Luzon. Meanwhile, at 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 470 km East of Virac, Catanduanes (14.3�N, 128.5�E). [WEBSMS] | CLUZ
10/31/2023 2:11:27 AM | Mindanao Grid-10/31/2023 02:14: LAKE MAINIT Hydro online at 0204H. (Unplanned Outage). [WEBSMS] | CMIN
10/31/2023 1:49:14 AM | Mindanao Grid-10/31/2023 01:52: LAKE MAINIT Hydro with 10.5MW gross generation tripped at 0142H. Indication: Generator #3 Power Signal Fault. Frequency=60.1Hz. (Unplanned Outage). [WEBSMS] | CMIN
10/30/2023 10:17:54 PM | Mindanao Grid-10/30/2023 22:20: GN Power Unit #3 shutdown at 2151H, for reserved shutdown. [WEBSMS] | CMIN
10/30/2023 9:56:23 PM | Luzon Grid-10/30/2023 21:56: Limay Orion Solar 69kV Line restored at 2156H (Unplanned Outage) [WEBSMS] | CLUZ
10/30/2023 8:02:47 PM | Mindanao Grid-10/30/2023 20:05: Manolo Fortich 1 Unit #2 with 4.2 gross generation on emergency shutdown at 1930H, due to Clogged Intake Weir. Unplanned Outage. [WEBSMS] | CMIN
10/30/2023 6:13:04 PM | Mindanao Grid-10/30/2023 18:15: ASIGA Hydro online at 1751H, from unplanned outage. [WEBSMS] | CMIN
10/30/2023 6:11:09 PM | Mindanao Grid-10/30/2023 18:14: ASIGA Hydro with 4.2MW gross generation tripped at 1727H. Indication: To be investigated by ASIGA HEP. (Unplanned Outage). [WEBSMS] | CMIN
10/30/2023 5:55:13 PM | Mindanao Grid-10/30/2023 17:58: LAKE MAINIT Hydro online at 1737H, from unplanned outage. [WEBSMS] | CMIN
10/30/2023 5:43:49 PM | Mindanao Grid-10/30/2023 17:46: LAKE MAINIT Hydro with 10.5MW gross generation tripped at 1722H. Indication: 86GZ Generator Master Tripped Operated. Lowest frequency recorded was 59.95Hz. (Unplanned Outage). [WEBSMS] | CMIN
10/30/2023 5:38:30 PM | Mindanao Grid-10/30/2023 17:41: WMPC DG05 shutdown at 1514H, from RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/30/2023 5:34:09 PM | [NSO Update] Luzon Grid-10/30/2023 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13537MW, PK=9027MW, RR=351MW, NetOpMargin: EVE=4158 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 325MW, Masinloc 2 @ 325MW, Ilijan A @ 420MW, Ilijan B @ 180MW [WEBSMS] | CLUZ
10/30/2023 5:33:45 PM | [NSO Update] Visayas Grid-10/30/2023 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2439MW, PK=1915MW, RR=92MW, NetOpMargin: EVE=432 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @ 278MW, PGPP1 @ 38MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
10/30/2023 5:33:26 PM | [NSO Update] Mindanao Grid-10/30/2023 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3414MW, PK=1949MW, RR=76MW, NetOpMargin: EVE=1389 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @31.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @114MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @200MW [WEBSMS] | CMIN
10/30/2023 4:52:33 PM | Luzon Grid-10/30/2023 16:53: Limay Orion Solar 69kV Line tripped at 1638H (Unplanned Outage) [WEBSMS] | CLUZ
10/30/2023 3:39:54 PM | Mindanao Grid-10/30/2023 15:42: Erratum: LAKE MAINIT Hydro with 10.5MW gross generation tripped at 1210H. Indication: 50BF Circuit Breaker Failure. Lowest frequency recorded was 59.86Hz. (Unplanned Outage). [WEBSMS] | CMIN
10/30/2023 12:32:47 PM | [NSO Update] Luzon Grid-10/30/2023 12:33: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14315MW, PK=8492MW, RR=316MW, NetOpMargin: PM=5507, EVE=4285 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 325MW, Masinloc 2 @ 325MW, Ilijan A @ 420MW, Ilijan B @ 180MW [WEBSMS] | CLUZ
10/30/2023 12:32:30 PM | [NSO Update] Visayas Grid-10/30/2023 12:32: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2657MW, PK=1748MW, RR=88MW, NetOpMargin: PM=821, EVE=451 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @ 268MW, PGPP1 @ 76MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
10/30/2023 12:31:56 PM | [NSO Update] Mindanao Grid-10/30/2023 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3433MW, PK=1718MW, RR=76MW, NetOpMargin: PM=1638, EVE=1448 Highest Unit O/L: GNPK 1&3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @31.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @114MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @180MW [WEBSMS] | CMIN
10/30/2023 12:28:32 PM | Mindanao Grid-10/30/2023 12:31: LAKE MAINIT Hydro cut-in at 1225H. (Unplanned Outage) [WEBSMS] | CMIN
10/30/2023 12:18:19 PM | Mindanao Grid-10/30/2023 12:21: LAKE MAINIT Hydro tripped with 10.5MW load at 1210H. Lowest frequency recorded was 59.86Hz. (Unplanned Outage). Affected by line disturbance (tripping of San Francisco-Alegria 69kV feeder). [WEBSMS] | CMIN
10/30/2023 11:56:35 AM | Mindanao Grid-10/30/2023 11:59: LAKE MAINIT Hydro cut-in at 1154H. (Unplanned Outage) [WEBSMS] | CMIN
10/30/2023 11:45:23 AM | Mindanao Grid-10/30/2023 11:48: LAKE MAINIT Hydro tripped with 10.7MW at 1137H. Lowest frequency recorded was 59.90Hz. (Unplanned Outage) Indication: 50BF. [WEBSMS] | CMIN
10/30/2023 10:22:37 AM | Luzon Grid-10/30/2023 10:23: Pagbilao Unit 3 online at 1019H (Unplanned Outage) [WEBSMS] | CLUZ
10/30/2023 9:54:33 AM | Mindanao Grid-10/30/2023 09:57: WMPC DG05 cut-in at 0952H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/30/2023 7:15:47 AM | Luzon Grid-10/30/2023 07:16: Pagbilao Unit 3 (53MW) tripped at 0712H (Unplanned Outage) [WEBSMS] | CLUZ
10/30/2023 5:57:19 AM | [NSO Update] Mindanao Grid-10/30/2023 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3394MW, PK=1782MW, RR=72MW, NetOpMargin: AM=1540, PM=1177, EVE=1127 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @31.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @114MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
10/30/2023 5:54:02 AM | [NSO Update] Visayas Grid-10/30/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2616MW, PK=1848MW, RR=87MW, NetOpMargin: AM=681, PM=466, EVE=321 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 268MW, PGPP1 @ 38MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
10/30/2023 5:43:53 AM | [NSO Update] Luzon Grid-10/30/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14425MW, PK=9287MW, RR=316MW, NetOpMargin: AM=4822, PM=4548, EVE=3325 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 325MW, Masinloc 2 @ 325MW, Ilijan A @ 420MW, Ilijan B @ 180MW [WEBSMS] | CLUZ
10/30/2023 4:13:25 AM | [NSO Update] Mindanao Grid-10/30/2023 04:16: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Meanwhile, at 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 995 km East of Visayas (12.1�N, 134.8�E). [WEBSMS] | CMIN
10/30/2023 4:10:51 AM | [NSO Update] Visayas Grid-10/30/2023 04:11: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Meanwhile, at 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 995 km East of Visayas (12.1�N, 134.8�E). [WEBSMS] | CVIS
10/30/2023 4:09:21 AM | [NSO Update] Luzon Grid-10/30/2023 04:09: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. Meanwhile, at 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 995 km East of Visayas (12.1�N, 134.8�E). [WEBSMS] | CLUZ
10/29/2023 6:56:21 PM | Mindanao Grid-10/29/2023 18:59: Lamsan Biomass (LSK) online at 1822H, from unplanned outage. [WEBSMS] | CMIN
10/29/2023 6:53:22 PM | Mindanao Grid-10/29/2023 18:56: Lamsan Biomass (LSK) with 8MW gross generation tripped at 1812H. Indication: 67 Directional Overcurrent. Unplanned Outage. [WEBSMS] | CMIN
10/29/2023 5:42:15 PM | [NSO Update] Luzon Grid-10/29/2023 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13686MW, PK=9515MW, RR=356MW, NetOpMargin: EVE=3815 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 325MW, Masinloc 2 @ 325MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/29/2023 5:40:49 PM | [NSO Update] Mindanao Grid-10/29/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3409MW, PK=2051MW, RR=70MW, NetOpMargin: EVE=1288 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @80MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @200MW [WEBSMS] | CMIN
10/29/2023 5:39:42 PM | [NSO Update] Visayas Grid-10/29/2023 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2409MW, PK=2076MW, RR=92MW, NetOpMargin: EVE=241 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 237MW, PGPP1 @ 76MW, PDPP3-G @ 8MW [WEBSMS] | CVIS
10/29/2023 4:13:18 PM | Luzon Grid-10/29/2023 16:13: Labrador 230kV Bus 2 restored at 1613H. (Planned Outage) [WEBSMS] | CLUZ
10/29/2023 2:15:51 PM | Mindanao Grid-10/29/2023 14:18: AGUS 4 Unit 3 cut-in at 1407H. (Unplanned Outage) [WEBSMS] | CMIN
10/29/2023 12:46:31 PM | [NSO Update] Mindanao Grid-10/29/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3464MW, PK=1924MW, RR=70MW, NetOpMargin: PM=1470, EVE=1292 Highest Unit O/L: GNPK 1&3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @115MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @180MW [WEBSMS] | CMIN
10/29/2023 12:35:09 PM | [NSO Update] Luzon Grid-10/29/2023 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14423MW, PK=9265MW, RR=351MW, NetOpMargin: PM=4807, EVE=3347 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 335MW, Masinloc 2 @ 325MW, Ilijan A @ 510MW, Ilijan B @ 230MW, SCPC 2 @75MW [WEBSMS] | CLUZ
10/29/2023 12:35:03 PM | [NSO Update] Visayas Grid-10/29/2023 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2653MW, PK=1939MW, RR=88MW, NetOpMargin: PM=626, EVE=266 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @ 237MW, PGPP1 @ 76MW, PDPP3-G@5MW [WEBSMS] | CVIS
10/29/2023 10:07:38 AM | Mindanao Grid-10/29/2023 10:10: Corrected: Agus 4 Unit #3 with 33MW gross generation tripped at 0612H. Indication: Excitation Problem (86E). Frequency reached=59.97Hz. Unplanned Outage. [WEBSMS] | CMIN
10/29/2023 6:42:44 AM | Luzon Grid-10/29/2023 06:43: Labrador 230kV Bus 2 - de-energized at 0640H. (Planned Outage) [WEBSMS] | CLUZ
10/29/2023 6:31:51 AM | Mindanao Grid-10/29/2023 06:34: Agus 4 Unit #3 with 33MW gross generation tripped at 0612H. Indication: Excitation Problem (86T). Frequency reached=59.97Hz. Unplanned Outage. [WEBSMS] | CMIN
10/29/2023 5:57:08 AM | [NSO Update] Luzon Grid-10/29/2023 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14700MW, PK=9152MW, RR=346MW, NetOpMargin: AM=5202, PM=4782, EVE=3428 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 335MW, Masinloc 2 @ 325MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/29/2023 5:50:39 AM | [NSO Update] Mindanao Grid-10/29/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3492MW, PK=1810MW, RR=66MW, NetOpMargin: AM=1615, PM=1535, EVE=1352 Highest Unit O/L: GNPK 1&3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @115MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @200MW [WEBSMS] | CMIN
10/29/2023 5:46:54 AM | [NSO Update] Visayas Grid-10/29/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2712MW, PK=1874MW, RR=87MW, NetOpMargin: AM=750, PM=603, EVE=254 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @ 255MW, PGPP1 @ 76MW [WEBSMS] | CVIS
10/29/2023 4:08:24 AM | [NSO Update] Mindanao Grid-10/29/2023 04:11: Weather update: Northeast Monsoon affecting Northern Luzon and the eastern section of Central Luzon. [WEBSMS] | CMIN
10/29/2023 4:07:43 AM | [NSO Update] Visayas Grid-10/29/2023 04:08: Weather update: Northeast Monsoon affecting Northern Luzon and the eastern section of Central Luzon. [WEBSMS] | CVIS
10/29/2023 4:06:57 AM | [NSO Update] Luzon Grid-10/29/2023 04:07: Weather update: Northeast Monsoon affecting Northern Luzon and the eastern section of Central Luzon. [WEBSMS] | CLUZ
10/29/2023 12:33:46 AM | [NSO Update] Mindanao Grid-10/29/2023 00:36: Correction. MO Initiated Market Intervention is issued at 2356H of 28 October 2023 for Luzon, Visayas and Mindanao starting interval 0005H of 29 October 2023 due to Market Participant Interface (MPI) failure. [WEBSMS] | CMIN
10/29/2023 12:33:06 AM | [NSO Update] Visayas Grid-10/29/2023 00:33: Correction. MO Initiated Market Intervention is issued at 2356H of 28 October 2023 for Luzon, Visayas and Mindanao starting interval 0005H of 29 October 2023 due to Market Participant Interface (MPI) failure. [WEBSMS] | CVIS
10/29/2023 12:31:53 AM | [NSO Update] Luzon Grid-10/29/2023 00:32: Correction. MO Initiated Market Intervention is issued at 2356H of 28 October 2023 for Luzon, Visayas and Mindanao starting interval 0005H of 29 October 2023 due to Market Participant Interface (MPI) failure. [WEBSMS] | CLUZ
10/29/2023 12:14:51 AM | Mindanao Grid-10/29/2023 00:17: TU2 U2 (1.8MW load) shutdown at 0004H Insufficient Water Supply(IWS). [WEBSMS] | CMIN
10/29/2023 12:14:46 AM | [NSO Update] Mindanao Grid-10/29/2023 00:17: MO Initiated Market Intervention has been lifted today 29 October 2023 at 0006H for Luzon and Visayas and Mindanao. Market will resume starting interval 0015H. [WEBSMS] | CMIN
10/29/2023 12:14:13 AM | [NSO Update] Luzon Grid-10/29/2023 00:14: MO Initiated Market Intervention has been lifted today 29 October 2023 at 0006H for Luzon and Visayas and Mindanao. Market will resume starting interval 0015H. [WEBSMS] | CLUZ
10/29/2023 12:13:20 AM | [NSO Update] Visayas Grid-10/29/2023 00:13: MO Initiated Market Intervention has been lifted today 29 October 2023 at 0006H for Luzon and Visayas and Mindanao. Market will resume starting interval 0015H. [WEBSMS] | CVIS
10/29/2023 12:05:13 AM | [NSO Update] Mindanao Grid-10/29/2023 00:08: MO Initiated Market Intervention is issued today 29 October 2023 for Luzon, Visayas and Mindanao starting interval 0005H due to Market Participant Interface failure (MPI). [WEBSMS] | CMIN
10/29/2023 12:04:14 AM | [NSO Update] Visayas Grid-10/29/2023 00:04: MO Initiated Market Intervention is issued today 29 October 2023 for Luzon, Visayas and Mindanao starting interval 0005H due to Market Participant Interface failure (MPI). [WEBSMS] | CVIS
10/29/2023 12:03:35 AM | [NSO Update] Luzon Grid-10/29/2023 00:03: at 2356H MO Initiated Market Intervention is issued today 29 October 2023 for Luzon, Visayas and Mindanao starting interval 0005H due to Market Participant Interface failure (MPI). [WEBSMS] | CLUZ
10/28/2023 9:51:48 PM | Mindanao Grid-10/28/2023 21:54: SURALLAH (SPGI) cut-in at 2147H. (Unplanned Outage) [WEBSMS] | CMIN
10/28/2023 8:40:58 PM | Luzon Grid-10/28/2023 20:41: MPGC 2 online at 2040H (On Commissioning Test) [WEBSMS] | CLUZ
10/28/2023 8:33:02 PM | Luzon Grid-10/28/2023 20:33: MPGC 2 load reject @112.5MW (75 percent load) at 2032H (On Commissioning Test) [WEBSMS] | CLUZ
10/28/2023 6:14:58 PM | Mindanao Grid-10/28/2023 18:17: SURALLAH (SPGI) Tripped with 5.2MW load at 1802H. Cause: To be determined. (Unplanned Outage) [WEBSMS] | CMIN
10/28/2023 5:33:47 PM | [NSO Update] Luzon Grid-10/28/2023 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13603MW, PK=10125MW, RR=377MW, NetOpMargin: EVE=3101 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 335MW, Masinloc 2 @ 325MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/28/2023 5:32:14 PM | [NSO Update] Visayas Grid-10/28/2023 17:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2560MW, PK=2226MW, RR=92MW, NetOpMargin: EVE=242 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @ 255MW PGPP1 @ 38MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
10/28/2023 5:30:29 PM | [NSO Update] Mindanao Grid-10/28/2023 17:33: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3405MW, PK=2157MW, RR=80MW, NetOpMargin: EVE=1168 Highest Unit O/L: GNPK 1&3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @80MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @200MW [WEBSMS] | CMIN
10/28/2023 5:22:25 PM | Luzon Grid-10/28/2023 17:22: Labrador SS 230kV Bus 1 restored at 1722H. (Planned Outage) [WEBSMS] | CLUZ
10/28/2023 4:16:55 PM | Mindanao Grid-10/28/2023 16:19: AGUS 2 Unit 3 HEP online at 1606. (Planned Outage) [WEBSMS] | CMIN
10/28/2023 3:25:03 PM | Mindanao Grid-10/28/2023 15:27: WMPC DG04 shutdown as RPS at 1514H. From RPS. System Voltage Requirement. [WEBSMS] | CMIN
10/28/2023 12:43:55 PM | [NSO Update] Mindanao Grid-10/28/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3422MW, PK=2124MW, RR=80MW, NetOpMargin: PM=1218, EVE=1137 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @80MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @180MW [WEBSMS] | CMIN
10/28/2023 12:42:28 PM | [NSO Update] Visayas Grid-10/28/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2599MW, PK=2104MW, RR=88MW, NetOpMargin: PM=407, EVE=243 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @ 255MW PGPP1 @ 38MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
10/28/2023 12:40:02 PM | [NSO Update] Luzon Grid-10/28/2023 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14368MW, PK=10369MW, RR=375MW, NetOpMargin: PM=3624, EVE=3044 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 325MW, Masinloc 2 @ 325MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/28/2023 10:33:36 AM | Mindanao Grid-10/28/2023 10:36: MDP Online at 0900H. Follow RTD. [WEBSMS] | CMIN
10/28/2023 9:52:54 AM | Mindanao Grid-10/28/2023 09:55: WMPC DG4 Online as RPS at 0950H For RPS. System Voltage Requirement. [WEBSMS] | CMIN
10/28/2023 8:45:56 AM | Mindanao Grid-10/28/2023 08:48: Update: FDC (FMP) Unit #1 cut-in at 0231H from unplanned outage. [WEBSMS] | CMIN
10/28/2023 6:35:37 AM | Luzon Grid-10/28/2023 06:35: Labrador SS 230kV Bus 1 de-energized at 0635H. (Planned Outage) [WEBSMS] | CLUZ
10/28/2023 5:49:14 AM | [NSO Update] Luzon Grid-10/28/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14449MW, PK=10224MW, RR=386MW, NetOpMargin: AM=3839, PM=3782, EVE=3748 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 325MW, Masinloc 2 @ 325MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/28/2023 5:47:32 AM | [NSO Update] Mindanao Grid-10/28/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3385MW, PK=2031MW, RR=78MW, NetOpMargin: AM=1277, PM=1210, EVE=1167 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @80MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
10/28/2023 5:47:26 AM | Mindanao Grid-10/28/2023 05:50: Update: FDC (FMP) cut-in at 0231H. Unplanned Outage. [WEBSMS] | CMIN
10/28/2023 5:43:52 AM | [NSO Update] Visayas Grid-10/28/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2585MW, PK=2086MW, RR=87MW, NetOpMargin: AM=412, PM=279, EVE=240 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 255MW PGPP1 @ 76MW, PDPP3-G @ 5MW [WEBSMS] | CVIS
10/28/2023 4:11:50 AM | [NSO Update] Luzon Grid-10/28/2023 04:12: Weather Update: Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
10/28/2023 4:11:37 AM | [NSO Update] Visayas Grid-10/28/2023 04:11: Weather Update: Northeast Monsoon affecting Luzon. [WEBSMS] | CVIS
10/28/2023 4:11:22 AM | [NSO Update] Mindanao Grid-10/28/2023 04:14: Weather Update: Northeast Monsoon affecting Luzon. [WEBSMS] | CMIN
10/28/2023 3:34:12 AM | Visayas Grid-10/28/2023 03:34: CEDC U1 cut out at 0004H. (Planned Outage) [WEBSMS] | CVIS
10/28/2023 2:57:54 AM | Mindanao Grid-10/28/2023 03:00: FDC (FMP) Unit 1 cut-in. Unplanned Outage. [WEBSMS] | CMIN
10/28/2023 12:00:26 AM | Luzon Grid-10/28/2023 00:00: Calaca 1 shutdown at 2356H (Unplanned Outage) [WEBSMS] | CLUZ
10/27/2023 9:45:30 PM | Visayas Grid-10/27/2023 21:45: Sangi-CTD 34.5kV line tripped/restored at 2112H/2138H. Unplanned outage [WEBSMS] | CVIS
10/27/2023 9:17:14 PM | Mindanao Grid-10/27/2023 21:20: WMPC DG4 shutdown as RPS at 2114H. From RPS. System Voltage Requirement. [WEBSMS] | CMIN
10/27/2023 8:43:22 PM | Mindanao Grid-10/27/2023 20:46: FDC U1 tripped with 122.7MW load at 2026H. The lowest frequency recorded is 59.1923Hz. No ALD. (Unplanned outage) [WEBSMS] | CMIN
10/27/2023 8:36:49 PM | Mindanao Grid-10/27/2023 20:39: FDC U1 tripped with 122.7MW load at 2026H. (Unplanned Outage) [WEBSMS] | CMIN
10/27/2023 6:22:34 PM | Luzon Grid-10/27/2023 18:22: SLPGC1 shutdown at 1819H (Unplanned Outage) [WEBSMS] | CLUZ
10/27/2023 5:33:25 PM | [NSO Update] Mindanao Grid-10/27/2023 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3409MW, PK=2217MW, RR=70MW, NetOpMargin: EVE=1123 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @25.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @200MW [WEBSMS] | CMIN
10/27/2023 5:31:14 PM | [NSO Update] Visayas Grid-10/27/2023 17:31: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2617MW, PK=2265MW, RR=92MW, NetOpMargin: EVE=260 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @255MW, PGPP1 @76MW [WEBSMS] | CVIS
10/27/2023 5:28:50 PM | [NSO Update] Luzon Grid-10/27/2023 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13944MW, PK=10577MW, RR=425MW, NetOpMargin: EVE=2942 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @325MW, MASINLOC 2 @325MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/27/2023 4:53:56 PM | Luzon Grid-10/27/2023 16:54: Nagsaag-Binga 230kV L2 tripped/reclosed at 1647H (Unplanned Outage) [WEBSMS] | CLUZ
10/27/2023 4:15:54 PM | Mindanao Grid-10/27/2023 16:18: WMPC DG6 shutdown as RPS at 1613H. From RPS. System voltage requirement. [WEBSMS] | CMIN
10/27/2023 1:45:42 PM | [NSO Update] Mindanao Grid-10/27/2023 13:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3421MW, PK=2251MW, RR=70MW, NetOpMargin: PM=2251, EVE=2170 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @80MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @180MW [WEBSMS] | CMIN
10/27/2023 1:37:51 PM | [NSO Update] Visayas Grid-10/27/2023 13:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2642MW, PK=2322MW, RR=92MW, NetOpMargin: PM=228, EVE=235 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 250MW, PGPP1 @ 76MW [WEBSMS] | CVIS
10/27/2023 1:34:42 PM | [NSO Update] Luzon Grid-10/27/2023 13:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14631MW, PK=11446MW, RR=449MW, NetOpMargin: PM=2736, EVE=2678 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 325MW, Masinloc 2 @ 325MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/27/2023 12:14:17 PM | Visayas Grid-10/27/2023 12:14: Bacolod - Barotac Viejo 138 kV Line auto-tripped at 1209H, Panay on islanding operation. (Unplanned Outage) [WEBSMS] | CVIS
10/27/2023 10:52:56 AM | Mindanao Grid-10/27/2023 10:55: WMPC DG06 cut-in at 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/27/2023 9:25:25 AM | Mindanao Grid-10/27/2023 09:28: Agus 2 Unit 1 cut-in at 0903H. Unplanned Outage. [WEBSMS] | CMIN
10/27/2023 9:10:35 AM | Mindanao Grid-10/27/2023 09:13: WMPC DG04 cut-in at 0850H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/27/2023 9:06:00 AM | Mindanao Grid-10/27/2023 09:08: AGUS 2 Unit1 auto tripped with 25MW load at 0842H. Indication: Governor Oil Pressure low. (Unplanned Outage) [WEBSMS] | CMIN
10/27/2023 8:28:01 AM | Mindanao Grid-10/27/2023 08:30: AGUS 2 Unit 3 cut-out at 0815H. PMS - GOMP. (Planned Outage) [WEBSMS] | CMIN
10/27/2023 7:00:39 AM | Mindanao Grid-10/27/2023 07:03: Lake Mainit (AGC) cut-in at 0657H. (Unplanned Outage) [WEBSMS] | CMIN
10/27/2023 6:52:17 AM | Mindanao Grid-10/27/2023 06:55: Lake Mainit (AGC) HEP auto tripped with 10.5 load at 0642H. Indication: G3 Power signal fault. (Unplanned Outage) [WEBSMS] | CMIN
10/27/2023 5:48:02 AM | [NSO Update] Luzon Grid-10/27/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14764MW, PK=11157MW, RR=434MW, NetOpMargin: AM=3173, PM=2690, EVE=2314 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 325MW, Masinloc 2 @ 325MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/27/2023 5:46:06 AM | [NSO Update] Mindanao Grid-10/27/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3392MW, PK=2141MW, RR=70MW, NetOpMargin: AM=1181, PM=1157, EVE=1129 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @27.5MW, MA2 @50MW, AG1 @60MW, AG2 @80MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
10/27/2023 5:44:45 AM | [NSO Update] Visayas Grid-10/27/2023 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2683MW, PK=2277MW, RR=90MW, NetOpMargin: AM=317, PM=248, EVE=226 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 279MW, PGPP1 @ 76MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
10/27/2023 4:09:47 AM | [NSO Update] Mindanao Grid-10/27/2023 04:12: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
10/27/2023 4:08:37 AM | [NSO Update] Visayas Grid-10/27/2023 04:08: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CVIS
10/27/2023 4:08:20 AM | [NSO Update] Luzon Grid-10/27/2023 04:08: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
10/26/2023 9:17:03 PM | Mindanao Grid-10/26/2023 21:19: WMPC DG04 cut-out at 2114H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/26/2023 8:50:37 PM | Luzon Grid-10/26/2023 20:50: Binga-Nagsaag 230kV Line 1 restored at 2050H (Unplanned Outage) [WEBSMS] | CLUZ
10/26/2023 8:48:18 PM | Luzon Grid-10/26/2023 20:48: Binga-Ambuklao 230kV Line 1 restored at 2046H (Unplanned Outage) [WEBSMS] | CLUZ
10/26/2023 8:32:32 PM | Mindanao Grid-10/26/2023 20:35: TALOMO 3 Unit 2 cut-in at 1923H. (Unplanned Outage) [WEBSMS] | CMIN
10/26/2023 8:31:15 PM | Mindanao Grid-10/26/2023 20:34: TALOMO 3 Unit 2 tripped with 0.6MW load at 1725H. Indication: Very High Drive End Bearing Temperature. (Unplanned Outage) [WEBSMS] | CMIN
10/26/2023 8:24:34 PM | Luzon Grid-10/26/2023 20:24: MPGC 2 online at 2023H (On Commissioning Test) [WEBSMS] | CLUZ
10/26/2023 8:10:57 PM | Luzon Grid-10/26/2023 20:11: Binga-Binga HEPP Overhead 230kV L1 restored at 2007H (Unplanned Outage) [WEBSMS] | CLUZ
10/26/2023 7:49:11 PM | Luzon Grid-10/26/2023 19:49: Binga-Ambuklao 230kV Line 1, Binga-Nagsaag 230kV Line 1 and Binga-Binga HEPP Overhead 230kV L1 tripped at 1941H (Unplanned Outage) [WEBSMS] | CLUZ
10/26/2023 6:17:06 PM | Luzon Grid-10/26/2023 18:17: San Juan PCB 8-02CB08SJU restored at 1816H (Unplanned Outage) [WEBSMS] | CLUZ
10/26/2023 5:56:20 PM | [NSO Update] Luzon Grid-10/26/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13757MW, PK=11097MW, RR=406MW, NetOpMargin: EVE=2254 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 1 @325MW, MASINLOC 2 @325MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/26/2023 5:27:17 PM | [NSO Update] Visayas Grid-10/26/2023 17:27: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2685MW, PK=2295MW, RR=92MW, NetOpMargin: EVE=298 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: Leyte A @ 272MW, PGPP1 @ 75MW [WEBSMS] | CVIS
10/26/2023 5:25:43 PM | [NSO Update] Mindanao Grid-10/26/2023 17:28: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3422MW, PK=2126MW, RR=70MW, NetOpMargin: EVE=1226 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @25.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @200MW [WEBSMS] | CMIN
10/26/2023 4:17:59 PM | Mindanao Grid-10/26/2023 16:20: WMPC DG06 cut-out at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/26/2023 2:43:46 PM | Luzon Grid-10/26/2023 14:44: San Juan PCB 8-02CB08SJU emergency shutdown at 1441H (Unplanned Outage) [WEBSMS] | CLUZ
10/26/2023 1:08:47 PM | [NSO Update] Mindanao Grid-10/26/2023 13:11: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3457MW, PK=2179MW, RR=70MW, NetOpMargin: PM=1208, EVE=1218 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @25.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @200MW [WEBSMS] | CMIN
10/26/2023 1:03:16 PM | [NSO Update] Visayas Grid-10/26/2023 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2733MW, PK=2336MW, RR=90MW, NetOpMargin: PM=306, EVE=241 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @ 272MW, PGPP1 @ 75MW [WEBSMS] | CVIS
10/26/2023 12:58:47 PM | [NSO Update] Luzon Grid-10/26/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14616MW, PK=11261MW, RR=437MW, NetOpMargin: PM=2918, EVE=2673 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 2 @175MW, MASINLOC 2 @335MW, MASINLOC 3 @325MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/26/2023 10:52:57 AM | Mindanao Grid-10/26/2023 10:55: WMPC DG6 online at 1050H. Cut-in as RPS. System Voltage Requirement. [WEBSMS] | CMIN
10/26/2023 9:23:35 AM | Mindanao Grid-10/26/2023 09:26: ASG tripped with 5MW load at 0907H. Loss of Power/Undervoltage/Earth Fault(line protection) Trip. [WEBSMS] | CMIN
10/26/2023 9:21:53 AM | Mindanao Grid-10/26/2023 09:24: AGC tripped with 10.5W load at 0907H. Loss of Power/Undervoltage trip. [WEBSMS] | CMIN
10/26/2023 8:53:19 AM | Mindanao Grid-10/26/2023 08:56: WMPC DG4 online at 0850H. (Planned Outage) [WEBSMS] | CMIN
10/26/2023 7:29:49 AM | Mindanao Grid-10/26/2023 07:32: ASG tripped with a load of 5MW at 0645H. Relay Indication; undervoltage Trip. [WEBSMS] | CMIN
10/26/2023 6:53:08 AM | Mindanao Grid-10/26/2023 06:55: AGC tripped with 10.5MW load at 0645H. Indication: REF. [WEBSMS] | CMIN
10/26/2023 6:04:00 AM | Mindanao Grid-10/26/2023 06:06: Lake Mainit (AGC) cut in at 0550H. (Unplanned Outage) [WEBSMS] | CMIN
10/26/2023 5:58:07 AM | Mindanao Grid-10/26/2023 06:00: ASIGA (ASG) HEP tripped with 5.0MW load at 0541H. Indication: For further verification. (Unplanned Outage) [WEBSMS] | CMIN
10/26/2023 5:52:25 AM | Mindanao Grid-10/26/2023 05:55: Lake Mainit (AGC) HEP tripped with 10.5MW load at 0541H. Indication: Restricted Earth Fault. (Unplanned Outage) [WEBSMS] | CMIN
10/26/2023 5:45:32 AM | [NSO Update] Mindanao Grid-10/26/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3393MW, PK=2200MW, RR=70MW, NetOpMargin: AM=1122, PM=1022, EVE=1106 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @25.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
10/26/2023 5:42:57 AM | [NSO Update] Visayas Grid-10/26/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2706MW, PK=2224MW, RR=88MW, NetOpMargin: AM=394, PM=230, EVE=226 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: Leyte A @ 280MW, PGPP1 @ 75MW [WEBSMS] | CVIS
10/26/2023 5:40:32 AM | [NSO Update] Luzon Grid-10/26/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14658MW, PK=10990MW, RR=431MW, NetOpMargin: AM=3237, PM=2743, EVE=2632 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 2 @175MW, MASINLOC 2 @335MW, MASINLOC 3 @325MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/26/2023 4:57:52 AM | Luzon Grid-10/26/2023 04:58: Lumban-Gumaca 230kV Line 1 auto-tripped/auto-reclosed at 0454H (Unplanned Outage) [WEBSMS] | CLUZ
10/26/2023 4:08:28 AM | [NSO Update] Luzon Grid-10/26/2023 04:08: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
10/26/2023 4:08:13 AM | [NSO Update] Mindanao Grid-10/26/2023 04:10: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CMIN
10/26/2023 4:08:08 AM | [NSO Update] Visayas Grid-10/26/2023 04:08: Weather Advisory: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CVIS
10/26/2023 2:54:36 AM | Mindanao Grid-10/26/2023 02:57: Update: TUDAYA2 Unit 2 cut-in at 0134H not 1807H. (Planned Outage - GOMP) [WEBSMS] | CMIN
10/26/2023 2:40:38 AM | Mindanao Grid-10/26/2023 02:43: ASIGA (ASG) HEP cut-in at 0237H. (Unplanned Outage) [WEBSMS] | CMIN
10/26/2023 2:34:46 AM | Mindanao Grid-10/26/2023 02:37: TUDAYA2 Unit 2 cut-in at 1807H. (Planned Outage - GOMP) [WEBSMS] | CMIN
10/26/2023 2:30:19 AM | Mindanao Grid-10/26/2023 02:33: ASIGA (ASG) HEP tripped with a load of 5.0MW at 0214H. Indication: For further investigation. (Unplanned Outage) [WEBSMS] | CMIN
10/26/2023 1:14:37 AM | Mindanao Grid-10/26/2023 01:17: TUDAYA 2 Unit 2 HEP cut-out at 00:03H with load of 2.0MW. PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
10/25/2023 10:50:08 PM | Luzon Grid-10/25/2023 22:50: Ilijan ST2 online at 2248H (Unplanned Outage) [WEBSMS] | CLUZ
10/25/2023 9:39:35 PM | Luzon Grid-10/25/2023 21:39: Ilijan GT2-2 online at 2136H (Unplanned Outage) [WEBSMS] | CLUZ
10/25/2023 9:34:05 PM | Luzon Grid-10/25/2023 21:34: SCPC Unit 2 online at 2124H (Unplanned Outage) [WEBSMS] | CLUZ
10/25/2023 9:17:04 PM | Mindanao Grid-10/25/2023 21:19: WMPC DG04 cut-out at 2114H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/25/2023 6:41:19 PM | Mindanao Grid-10/25/2023 18:44: TUDAYA2 Unit 1 & Unit 2 cut-in at 1807H. (Unplanned Outage) [WEBSMS] | CMIN
10/25/2023 6:40:31 PM | Mindanao Grid-10/25/2023 18:43: TUDAYA2 Unit 1 with 4.5MW load & Unit 2 with 2.4MW load both isolated with at 1739H due to tripping of Toril-Digos 69kV feeder. (Unplanned Outage) [WEBSMS] | CMIN
10/25/2023 6:20:05 PM | Luzon Grid-10/25/2023 18:20: SCPC Unit 2 (150MW) tripped at 1814H (Unplanned Outage) [WEBSMS] | CLUZ
10/25/2023 6:19:54 PM | Mindanao Grid-10/25/2023 18:22: Pulangi 4 Unit 3 cut-in at 1814H. (Unplanned Outage) [WEBSMS] | CMIN
10/25/2023 6:19:36 PM | Luzon Grid-10/25/2023 18:19: SCPC Unit 2 (150MW) tripped at 1814H (Unplanned Outage) [WEBSMS] | CLUZ
10/25/2023 5:50:18 PM | Mindanao Grid-10/25/2023 17:53: Pulangi 4 Unit 3 tripped with 57.3MW load at 1722H. Lowest frequency recorded was 59.490Hz. (Unplanned Outage). Cause: Spiral Case Pressure Low. [WEBSMS] | CMIN
10/25/2023 5:43:23 PM | [NSO Update] Luzon Grid-10/25/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13886MW, PK=10791MW, RR=412MW, NetOpMargin: EVE=2683 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 2 @ 335MW, Masinloc 3 @ 325MW [WEBSMS] | CLUZ
10/25/2023 5:41:54 PM | [NSO Update] Mindanao Grid-10/25/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3397MW, PK=2263MW, RR=70MW, NetOpMargin: EVE=1064 Highest Unit O/L: GNPK 1 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @24.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @190MW [WEBSMS] | CMIN
10/25/2023 5:40:15 PM | [NSO Update] Visayas Grid-10/25/2023 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2669MW, PK=2302MW, RR=92MW, NetOpMargin: EVE=274 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 280MW, PGPP1 @ 76MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
10/25/2023 4:34:49 PM | Mindanao Grid-10/25/2023 16:37: WMPC DG06 cut-out at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/25/2023 4:33:52 PM | Mindanao Grid-10/25/2023 16:36: TUDAYA2 Unit 1 cut-in at 1613H. (Planned Outage) [WEBSMS] | CMIN
10/25/2023 2:14:18 PM | Mindanao Grid-10/25/2023 14:17: General Santos-Kamanga 138kV L2 energized at 1335H. From Planned Outage (SEC-2/SMF2 Coal Plant initiated PMS/GOMP). [WEBSMS] | CMIN
10/25/2023 2:09:51 PM | Mindanao Grid-10/25/2023 14:12: General Santos-Kamanga 138kV L1 energized at 1330H. From Planned Outage. (SEC-2/SMF-2 Coal Plant initiated PMS/GOMP). [WEBSMS] | CMIN
10/25/2023 1:05:06 PM | [NSO Update] Mindanao Grid-10/25/2023 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3382MW, PK=2355MW, RR=70MW, NetOpMargin: PM=957, EVE=994 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @24.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
10/25/2023 12:39:21 PM | [NSO Update] Visayas Grid-10/25/2023 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2702MW, PK=2313MW, RR=90MW, NetOpMargin: PM=299, EVE=237 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @112.5MW, LEYTE A @275MW, PGPP1 @72MW [WEBSMS] | CVIS
10/25/2023 12:36:34 PM | [NSO Update] Luzon Grid-10/25/2023 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14656MW, PK=11027MW, RR=434MW, NetOpMargin: PM=3195, EVE=2833 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 2 @335MW, MASINLOC 3 @325MW [WEBSMS] | CLUZ
10/25/2023 11:29:36 AM | Mindanao Grid-10/25/2023 11:32: Update: WMPC DG06 cut-in at 1051H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/25/2023 11:05:51 AM | Mindanao Grid-10/25/2023 11:08: GNPK Unit 4 cut-out at 1102H - reserve shutdown. [WEBSMS] | CMIN
10/25/2023 10:55:16 AM | Mindanao Grid-10/25/2023 10:57: WMPC DG06 cut-in at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/25/2023 10:16:34 AM | Mindanao Grid-10/25/2023 10:19: TUDAYA 2 Unit 1 cut-out at 10:00H with load of 3.4MW. PMS-GOMP. (Planned Outage) [WEBSMS] | CMIN
10/25/2023 8:54:50 AM | Mindanao Grid-10/25/2023 08:57: WMPC DG04 cut-in at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/25/2023 5:45:51 AM | [NSO Update] Luzon Grid-10/25/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14557MW, PK=10693MW, RR=425MW, NetOpMargin: AM=3439, PM=3274, EVE=3046 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 2 @175MW, MASINLOC 2 @335MW, MASINLOC 3 @325MW [WEBSMS] | CLUZ
10/25/2023 5:43:29 AM | [NSO Update] Mindanao Grid-10/25/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3396MW, PK=2284MW, RR=70MW, NetOpMargin: AM=1042, PM=1003, EVE=1025 Highest Unit O/L: GNPK 1, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @24.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
10/25/2023 5:43:25 AM | [NSO Update] Visayas Grid-10/25/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2611MW, PK=2242MW, RR=87MW, NetOpMargin: AM=282, PM=271, EVE=249 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @112.5MW, LEYTE A @279MW, PGPP1 @72MW [WEBSMS] | CVIS
10/25/2023 5:28:49 AM | Luzon Grid-10/25/2023 05:29: Marilao(Duhat) 115kV Bus 1 and Marilao(Duhat) 300MVA T01 were restored at 0521H and 0523H respectively. (Planned Outage - Customer Owned) [WEBSMS] | CLUZ
10/25/2023 5:11:52 AM | Mindanao Grid-10/25/2023 05:14: GNPK Unit 3 cut-in at 0457H. (Unplanned Outage) [WEBSMS] | CMIN
10/25/2023 4:03:45 AM | [NSO Update] Luzon Grid-10/25/2023 04:03: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Shear Line affecting the eastern section of Central Luzon. [WEBSMS] | CLUZ
10/25/2023 4:03:41 AM | [NSO Update] Visayas Grid-10/25/2023 04:03: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Shear Line affecting the eastern section of Central Luzon. [WEBSMS] | CVIS
10/25/2023 4:03:23 AM | [NSO Update] Mindanao Grid-10/25/2023 04:06: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Shear Line affecting the eastern section of Central Luzon. [WEBSMS] | CMIN
10/25/2023 3:00:43 AM | Mindanao Grid-10/25/2023 03:03: Surallah Power Generation Inc. (SPGI) cut-in at 0254H. (Unplanned Outage) [WEBSMS] | CMIN
10/25/2023 2:34:29 AM | Mindanao Grid-10/25/2023 02:37: (Correction) Surallah Power Generation Inc. (SPGI) isolated with 5.9MW load at 2351H due to tripping of Tacurong-Koronadal 69 kV feeder. (Unplanned Outage) [WEBSMS] | CMIN
10/25/2023 2:33:27 AM | Mindanao Grid-10/25/2023 02:36: Surallah Power Generation Inc. (SPGI) isolated with 5.9MW load at 1151H due to tripping of Tacurong-Koronadal 69 kV feeder. (Unplanned Outage) [WEBSMS] | CMIN
10/25/2023 2:03:39 AM | Luzon Grid-10/25/2023 02:03: Marilao(Duhat) 115kV Bus 1 and Marilao(Duhat) 300MVA T01 were de-energized at 0200H. (Planned Outage - Customer Owned) [WEBSMS] | CLUZ
10/24/2023 9:17:37 PM | Mindanao Grid-10/24/2023 21:20: WMPC DG04 cut-out at 2114H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/24/2023 6:00:36 PM | Mindanao Grid-10/24/2023 18:03: Kauswagan - GNPK 230kV L3 restored at 1759H. (Unplanned Outage) [WEBSMS] | CMIN
10/24/2023 5:49:43 PM | [NSO Update] Luzon Grid-10/24/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14066MW, PK=10218MW, RR=421MW, NetOpMargin: EVE=3427 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, GNPD 1 @ 650MW, Masinloc 2 @ 335MW, Ilijan A @ 570MW, Ilijan B @ 260MW [WEBSMS] | CLUZ
10/24/2023 5:44:52 PM | [NSO Update] Mindanao Grid-10/24/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3242MW, PK=2256MW, RR=70MW, NetOpMargin: EVE=916 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @25.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @190MW [WEBSMS] | CMIN
10/24/2023 5:42:40 PM | [NSO Update] Visayas Grid-10/24/2023 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2623MW, PK=2264MW, RR=90MW, NetOpMargin: EVE=269 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 278MW, PGPP1 @ 55MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
10/24/2023 5:15:51 PM | Mindanao Grid-10/24/2023 17:18: Kauswagan - GNPK 230kV L3 de-energized at 1710H. (Unplanned Outage) [WEBSMS] | CMIN
10/24/2023 4:57:41 PM | Mindanao Grid-10/24/2023 17:00: GNPK U3 cut-out at 1649H to conduct SF6 refilling of their outdoor GIS. (Unplanned Outage). [WEBSMS] | CMIN
10/24/2023 4:53:29 PM | Mindanao Grid-10/24/2023 16:56: WMPC DG06 cut-out at 1613H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/24/2023 1:55:00 PM | Mindanao Grid-10/24/2023 13:57: GNPK Unit 1 cut-in at 1352H. (Planned Outage) [WEBSMS] | CMIN
10/24/2023 12:51:12 PM | [NSO Update] Luzon Grid-10/24/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14485MW, PK=10950MW, RR=456MW, NetOpMargin: PM=3079, EVE=3028 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 2 @330MW, ILIJAN A @550MW, ILIJAN B @ 230MW, GNPD 1 @500MW [WEBSMS] | CLUZ
10/24/2023 12:46:47 PM | [NSO Update] Visayas Grid-10/24/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2670MW, PK=2288MW, RR=90MW, NetOpMargin: PM=293, EVE=219 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @278MW, PGPP1 @50MW [WEBSMS] | CVIS
10/24/2023 12:34:21 PM | [NSO Update] Mindanao Grid-10/24/2023 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3420MW, PK=2288MW, RR=70MW, NetOpMargin: PM=1063, EVE=1118 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @25.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @190MW [WEBSMS] | CMIN
10/24/2023 11:51:17 AM | Mindanao Grid-10/24/2023 11:53: WMPC DG06 cut-in at 1051H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/24/2023 11:21:36 AM | Mindanao Grid-10/24/2023 11:24: ASIGA Hydro cut-in at 1117H. (Unplanned Outage) [WEBSMS] | CMIN
10/24/2023 11:09:44 AM | Mindanao Grid-10/24/2023 11:12: LAKE MAINIT cut-in at 1108H. (Unplanned Outage) [WEBSMS] | CMIN
10/24/2023 11:02:00 AM | Mindanao Grid-10/24/2023 11:04: ASIGA Hydro tripped with 5MW load at 1048H. Lowest frequency recorded was 59.92Hz. (Unplanned Outage) Cause: Undervoltage. [WEBSMS] | CMIN
10/24/2023 11:01:26 AM | Mindanao Grid-10/24/2023 11:04: LAKE MAINIT Hydro tripped with 10.5MW load at 1048H. Lowest frequency recorded was 59.92Hz. (Unplanned Outage) Cause: Undervoltage. [WEBSMS] | CMIN
10/24/2023 10:46:58 AM | Mindanao Grid-10/24/2023 10:49: (Update/Correction) ASIGA Hydro tripped with 5.1MW load at 0900H. Lowest frequency recorded was 59.77Hz. (Unplanned Outage) Cause: Voltage-sensitive GT2 circuit breaker tripped off on under-voltage. [WEBSMS] | CMIN
10/24/2023 10:15:48 AM | Mindanao Grid-10/24/2023 10:18: ASIGA Hydro cut-in at 0927H. (Unplanned Outage) [WEBSMS] | CMIN
10/24/2023 10:15:08 AM | Mindanao Grid-10/24/2023 10:17: ASIGA Hydro tripped with 5.1MW load at 0900H. Lowest frequency recorded was 59.77Hz. (Unplanned Outage) Cause: Voltage fluctuation. [WEBSMS] | CMIN
10/24/2023 8:58:06 AM | Mindanao Grid-10/24/2023 09:00: WMPC DG04 cut-in at 0852H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/24/2023 6:06:57 AM | Luzon Grid-10/24/2023 06:07: Quezon 230kV Bus 1 was energized at 0558H, Quezon-Mexico 230kV line was looped at Quezon side at 0600H, and San Jose-Quezon 230kV line 3 was restored at 0601H. (Planned Outage) [WEBSMS] | CLUZ
10/24/2023 6:02:59 AM | [NSO Update] Visayas Grid-10/24/2023 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2555MW, PK=2236MW, RR=88.9MW, NetOpMargin: AM=230, PM=268, EVE=236 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @278MW, PGPP1 @50MW [WEBSMS] | CVIS
10/24/2023 5:59:23 AM | [NSO Update] Mindanao Grid-10/24/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3378MW, PK=2290MW, RR=70MW, NetOpMargin: AM=1018, PM=978, EVE=1120 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @25.5MW, MA2 @50MW, AG1 @60MW, AG2 @99MW, AG4 @113MW, AG5 @36MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
10/24/2023 5:47:45 AM | [NSO Update] Luzon Grid-10/24/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13987MW, PK=10365MW, RR=443MW, NetOpMargin: AM=3179, PM=3028, EVE=2895 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 2 @335MW, ILIJAN A @550MW, ILIJAN B @ 230MW [WEBSMS] | CLUZ
10/24/2023 5:13:57 AM | Luzon Grid-10/24/2023 05:14: GNPD U1 online at 0512H (Unplanned Outage) [WEBSMS] | CLUZ
10/24/2023 4:13:44 AM | [NSO Update] Luzon Grid-10/24/2023 04:13: Weather Update: Northeast Monsoon affecting Northern Luzon. Shear Line affecting the eastern sections of Central and Southern Luzon. [WEBSMS] | CLUZ
10/24/2023 4:12:21 AM | [NSO Update] Mindanao Grid-10/24/2023 04:15: Weather Update: Northeast Monsoon affecting Northern Luzon. Shear Line affecting the eastern sections of Central and Southern Luzon. [WEBSMS] | CMIN
10/24/2023 4:11:12 AM | [NSO Update] Visayas Grid-10/24/2023 04:11: Weather Update: Northeast Monsoon affecting Northern Luzon. Shear Line affecting the eastern sections of Central and Southern Luzon. [WEBSMS] | CVIS
10/24/2023 3:07:22 AM | Mindanao Grid-10/24/2023 03:10: FDC Unit 1 cut-in at 0209H. (Unplanned outage) [WEBSMS] | CMIN
10/24/2023 12:22:15 AM | Luzon Grid-10/24/2023 00:22: Quezon(Balintawak) 230kV Bus 1 - de-energized at 0019H.(Planned Outage). (Mexico-Quezon 230kV line is un-looped at Quezon side.) [WEBSMS] | CLUZ
10/24/2023 12:17:31 AM | Luzon Grid-10/24/2023 00:17: San Jose-Quezon(Balintawak) 230kV line 3 - de-energized at 0015H (Planned Outage) [WEBSMS] | CLUZ
10/23/2023 10:34:18 PM | Mindanao Grid-10/23/2023 22:36: Supreme Power Mati isolated with 4MW at 2046H due to tripping of Maco-Banaybanay 69 kV feeder. (Unplanned Outage) [WEBSMS] | CMIN
10/23/2023 10:11:22 PM | Mindanao Grid-10/23/2023 22:14: (Update) FDC Unit 1 tripped with 108.5MW load at 2151H. Lowest frequency recorded was 59.27Hz. No ALD. (Unplanned Outage). Indication: Control Oil System Disturbed. [WEBSMS] | CMIN
10/23/2023 10:01:53 PM | Mindanao Grid-10/23/2023 22:04: FDC Unit 1 tripped with 108.5MW load at 2151H. Lowest frequency recorded was 59.27Hz. No ALD. (Unplanned Outage). Indication: to be determined. [WEBSMS] | CMIN
10/23/2023 9:19:11 PM | Mindanao Grid-10/23/2023 21:21: WMPC DG05 cut-out at 2114H. End of RPS - System Voltage Requirement, [WEBSMS] | CMIN
10/23/2023 8:05:15 PM | Luzon Grid-10/23/2023 20:05: Bolo-Cayanga 230kV line 2 - looped at Cayanga side at 2001H. [WEBSMS] | CLUZ
10/23/2023 5:44:15 PM | [NSO Update] Visayas Grid-10/23/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2526MW, PK=2157MW, RR=92MW, NetOpMargin: EVE=277 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @118MW, LEYTE A @280MW, PGPP1 @37.5MW [WEBSMS] | CVIS
10/23/2023 5:41:40 PM | [NSO Update] Luzon Grid-10/23/2023 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13353MW, PK=9720MW, RR=426MW, NetOpMargin: EVE=3207 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 2 @325MW, ILIJAN A @550MW, ILIJAN B @ 230MW [WEBSMS] | CLUZ
10/23/2023 5:40:08 PM | [NSO Update] Mindanao Grid-10/23/2023 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3075MW, PK=2200MW, RR=70MW, NetOpMargin: EVE=805 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @50MW, AG1 @35MW, AG2 @99MW, AG4 @114MW, AG5 @37MW, AG6 @149MW, AG7 @32MW, PG4 @190MW [WEBSMS] | CMIN
10/23/2023 5:03:46 PM | Mindanao Grid-10/23/2023 17:06: LAKE MAINIT Hydro cut-in at 1605H. (Unplanned Outage) [WEBSMS] | CMIN
10/23/2023 4:47:08 PM | Luzon Grid-10/23/2023 16:47: System Advisory: The ALD-affected feeders of NGCP and Meralco were restored at 1639H and 1641H respectively. [WEBSMS] | CLUZ
10/23/2023 4:43:17 PM | Luzon Grid-10/23/2023 16:43: System Advisory: ALD occurred at NGCP and Meralco feeders due to the tripping of GNPD Unit 1 with a 638MW load at 1633H. The lowest system frequency is 58.84Hz. [WEBSMS] | CLUZ
10/23/2023 4:15:02 PM | Mindanao Grid-10/23/2023 16:17: WMPC DG06 cut-out at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/23/2023 1:19:48 PM | Mindanao Grid-10/23/2023 13:22: ASIGA Hydro cut-in at 1212H. (Unplanned Outage) [WEBSMS] | CMIN
10/23/2023 12:45:39 PM | [NSO Update] Mindanao Grid-10/23/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3115MW, PK=2241MW, RR=70MW, NetOpMargin: PM=804, EVE=818 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @50MW, AG1 @35MW, AG2 @99MW, AG4 @114MW, AG5 @37MW, AG6 @149MW, AG7 @32MW, PG4 @190MW [WEBSMS] | CMIN
10/23/2023 12:43:26 PM | [NSO Update] Visayas Grid-10/23/2023 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2655MW, PK=2272MW, RR=94MW, NetOpMargin: PM=289, EVE=190 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @275MW, PGPP1 @37.5MW [WEBSMS] | CVIS
10/23/2023 12:40:45 PM | [NSO Update] Luzon Grid-10/23/2023 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14345MW, PK=10405MW, RR=451MW, NetOpMargin: PM=3489, EVE=3602 Highest Unit O/L: GNPD 2@668MW Derated Plant: CALACA 2 @175MW, GNPD 1 @640MW, MASINLOC 2 @330MW, ILIJAN A @550MW, ILIJAN B @ 230MW [WEBSMS] | CLUZ
10/23/2023 11:53:25 AM | Mindanao Grid-10/23/2023 11:56: LAKE MAINIT Hydro isolated with 10.7MW load at 1129H. Lowest frequency recorded was 59.92Hz. (Unplanned Outage) Cause: Affected by tripping of Butuan-Santiago 69 kV feeder. [WEBSMS] | CMIN
10/23/2023 11:52:39 AM | Mindanao Grid-10/23/2023 11:55: ASIGA Hydro isolated with 2MW load at 1129H. Lowest frequency recorded was 59.92Hz. (Unplanned Outage) Cause: Affected by tripping of Butuan-Santiago 69 kV feeder. [WEBSMS] | CMIN
10/23/2023 10:55:02 AM | Mindanao Grid-10/23/2023 10:57: WMPC DG06 cut-in at 1051H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/23/2023 9:04:49 AM | Mindanao Grid-10/23/2023 09:07: WMPC DG05 cut-in at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/23/2023 6:04:32 AM | [NSO Update] Mindanao Grid-10/23/2023 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3093MW, PK=2169MW, RR=70MW, NetOpMargin: AM=854, PM=779, EVE=809 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @50MW, AG1 @55MW, AG2 @99MW, AG4 @114MW, AG5 @37MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
10/23/2023 5:58:35 AM | [NSO Update] Visayas Grid-10/23/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2601MW, PK=2159MW, RR=91MW, NetOpMargin: AM=351, PM=308, EVE=287 Highest Unit O/L: THVI 1 & 2 Derated Plant: TGPP @113.5MW, LEYTE A @287MW, PGPP1 @37.5MW [WEBSMS] | CVIS
10/23/2023 5:54:15 AM | [NSO Update] Luzon Grid-10/23/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14583MW, PK=10281MW, RR=433MW, NetOpMargin: AM=3869, PM=2798, EVE=2702 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: Calaca 2 @ 175MW, GNPD 1 @ 640MW, Masinloc 2 @ 325MW, Masinloc 3 @ 330MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/23/2023 4:26:52 AM | [NSO Update] Mindanao Grid-10/23/2023 04:29: Weather Update: Northeast Monsoon affecting Northern Luzon. Shear Line affecting the eastern section of Central and Southern Luzon. [WEBSMS] | CMIN
10/23/2023 4:26:20 AM | [NSO Update] Visayas Grid-10/23/2023 04:26: Weather Update: Northeast Monsoon affecting Northern Luzon. Shear Line affecting the eastern section of Central and Southern Luzon. [WEBSMS] | CVIS
10/23/2023 4:26:03 AM | [NSO Update] Luzon Grid-10/23/2023 04:26: Weather Update: Northeast Monsoon affecting Northern Luzon. Shear Line affecting the eastern section of Central and Southern Luzon. [WEBSMS] | CLUZ
10/23/2023 12:49:56 AM | Luzon Grid-10/23/2023 00:50: Labo-Gumaca 230kV Line 2 restored at 0049H (Unplanned Outage) [WEBSMS] | CLUZ
10/22/2023 9:20:38 PM | Luzon Grid-10/22/2023 21:20: For info: Alasasin-GNPD 230kV Tie Line unlooped via GNPD PCB 8CB04(9XF03GPO) at 2113H. [WEBSMS] | CLUZ
10/22/2023 9:11:26 PM | Luzon Grid-10/22/2023 21:11: For info: Main 1 Protection for Lamao-Alasasin 230kV L1 successfully commissioned at 2109H (End of Commissioning) [WEBSMS] | CLUZ
10/22/2023 8:41:09 PM | Luzon Grid-10/22/2023 20:41: Lamao-Alasasin 230kV L1 energized at 2027H via Lamao side and looped at 2037H (On Commissioning) [WEBSMS] | CLUZ
10/22/2023 8:18:00 PM | Luzon Grid-10/22/2023 20:18: MPGC Unit 2 (75MW) tripped at 2014H (On Commissioning). Lowest system frequency is 59.692Hz. [WEBSMS] | CLUZ
10/22/2023 7:31:45 PM | Luzon Grid-10/22/2023 19:31: Bolo - Cayanga 230kV Line 2 energized at Bolo side at 1929H (On Commissioning) [WEBSMS] | CLUZ
10/22/2023 6:10:59 PM | Luzon Grid-10/22/2023 18:11: San Juan (Kalayaan)-Calauan 230kV Line 1 and 2 restored at 1805H (Planned Outage) [WEBSMS] | CLUZ
10/22/2023 5:59:07 PM | Luzon Grid-10/22/2023 17:59: GNPD Unit 2 online at 1755H (Unplanned Outage) [WEBSMS] | CLUZ
10/22/2023 5:57:19 PM | Luzon Grid-10/22/2023 17:57: GNPD Unit 2 online at 1755H (Unplanned Outage) [WEBSMS] | CLUZ
10/22/2023 5:56:29 PM | Mindanao Grid-10/22/2023 17:59: Baloi - Agus 2 138kV L1 restored at 1753H. (Unplanned Outage) [WEBSMS] | CMIN
10/22/2023 5:42:05 PM | [NSO Update] Luzon Grid-10/22/2023 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13147MW, PK=9190MW, RR=316MW, NetOpMargin: EVE=3641 Highest Unit O/L: Sual 2 @ 647MW Derated Plant: Calaca 2 @ 175MW, GNPD 1 @ 640MW, Masinloc 2 @ 250MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/22/2023 5:39:46 PM | [NSO Update] Mindanao Grid-10/22/2023 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3252MW, PK=1978MW, RR=70MW, NetOpMargin: EVE=1204 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @25.5MW, MA2 @50MW, AG1 @55MW, AG2 @99MW, AG4 @114MW, AG5 @37MW, AG6 @149MW, AG7 @32MW, PG4 @190MW [WEBSMS] | CMIN
10/22/2023 5:38:38 PM | [NSO Update] Visayas Grid-10/22/2023 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2515MW, PK=2018MW, RR=83MW, NetOpMargin: EVE=414 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 113.5MW, Leyte A @ 280MW, PGPP1 @ 37.5MW [WEBSMS] | CVIS
10/22/2023 5:19:49 PM | Luzon Grid-10/22/2023 17:19: Nagsaag 230kV Bus 1 restored at 1718H (Planned Outage) [WEBSMS] | CLUZ
10/22/2023 4:38:25 PM | Mindanao Grid-10/22/2023 16:41: Maco - Nabunturan 138kV L restored at 1635H. (Planned Outage) [WEBSMS] | CMIN
10/22/2023 4:18:57 PM | Mindanao Grid-10/22/2023 16:21: Baloi - Agus 2 138kV L1 de-energized at 1605H. (Unplanned Outage) [WEBSMS] | CMIN
10/22/2023 4:03:40 PM | Luzon Grid-10/22/2023 16:03: San Jose-San Rafael(CND) 230kV line restored at 1602H (Planned Outage) [WEBSMS] | CLUZ
10/22/2023 4:00:53 PM | Mindanao Grid-10/22/2023 16:03: Baloi - Agus 2 138kV L2 restored at 1558H. (Planned Outage) [WEBSMS] | CMIN
10/22/2023 3:52:59 PM | Visayas Grid-10/22/2023 15:53: Calong-calong - Asturias 69 kV Line energized at 1546H activity completed. (Planned Outage) [WEBSMS] | CVIS
10/22/2023 3:09:38 PM | Mindanao Grid-10/22/2023 15:12: Lake Mainit HEPP online at 1457H. Unplanned Outage [WEBSMS] | CMIN
10/22/2023 3:09:06 PM | Mindanao Grid-10/22/2023 15:11: Lake Mainit HEPP with 10.5MW tripped at 1435H due to Generator Signal Power Fault. Unplanned Outage. [WEBSMS] | CMIN
10/22/2023 3:07:38 PM | Luzon Grid-10/22/2023 15:07: SCPC Unit 3 online at 1505H (Unplanned Outage) [WEBSMS] | CLUZ
10/22/2023 2:55:31 PM | Luzon Grid-10/22/2023 14:55: San Jose-Taytay 230kV Line 1 restored at 1453H (Planned Outage) [WEBSMS] | CLUZ
10/22/2023 2:54:36 PM | Luzon Grid-10/22/2023 14:54: Tayabas PCB 9-02CB04TAY restored at 1453H (Planned Outage) [WEBSMS] | CLUZ
10/22/2023 2:51:09 PM | Visayas Grid-10/22/2023 14:51: Sangi - 2nd Lift 34.5 kV line energized at 1447H, activity completed. (Planned Outage) [WEBSMS] | CVIS
10/22/2023 2:12:28 PM | [NSO Update] Mindanao Grid-10/22/2023 14:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1410H with power going to Visayas. [WEBSMS] | CMIN
10/22/2023 2:12:16 PM | [NSO Update] Visayas Grid-10/22/2023 14:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1410H with power going to Visayas. [WEBSMS] | CVIS
10/22/2023 2:10:20 PM | [NSO Update] Mindanao Grid-10/22/2023 14:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1401H from reverse power direction. [WEBSMS] | CMIN
10/22/2023 2:10:06 PM | [NSO Update] Visayas Grid-10/22/2023 14:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1401H from reverse power direction. [WEBSMS] | CVIS
10/22/2023 1:56:25 PM | Luzon Grid-10/22/2023 13:56: Sual 230kV Bus 1 - energized at 1354H. (Planned Outage) [WEBSMS] | CLUZ
10/22/2023 1:52:05 PM | Mindanao Grid-10/22/2023 13:54: Agus 2 HEPP U3 online at 1343H. Unplanned Outage. [WEBSMS] | CMIN
10/22/2023 1:40:13 PM | Visayas Grid-10/22/2023 13:40: Cebu - Colon 138 kV Line 3 energized at 1338H. (Planned Outage) [WEBSMS] | CVIS
10/22/2023 1:26:33 PM | Mindanao Grid-10/22/2023 13:29: Mati Diesel (MDP) online at 1019H. Unplanned Outage. [WEBSMS] | CMIN
10/22/2023 1:25:19 PM | Mindanao Grid-10/22/2023 13:27: Mati Diesel (MDP) with 4MW gross generation Tripped at 1013H due to Reverse Power Trip. Unplanned Outage. [WEBSMS] | CMIN
10/22/2023 12:42:30 PM | [NSO Update] Mindanao Grid-10/22/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3270MW, PK=1796MW, RR=70MW, NetOpMargin: PM=1405, EVE=1233 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @25.5MW, MA2 @50MW, AG1 @35MW, AG2 @99MW, AG4 @114MW, AG5 @37MW, AG6 @149MW, AG7 @32MW, PG4 @190MW [WEBSMS] | CMIN
10/22/2023 12:40:55 PM | [NSO Update] Visayas Grid-10/22/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2453MW, PK=1810MW, RR=88MW, NetOpMargin: PM=555, EVE=406 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 113.5MW, Leyte A @ 273MW, PGPP1 @ 37.5MW, PDPP3-G @ 7MW [WEBSMS] | CVIS
10/22/2023 12:40:14 PM | Mindanao Grid-10/22/2023 12:42: Agus 1 HEPP U1 online at 1221H. Unplanned Outage. [WEBSMS] | CMIN
10/22/2023 12:36:53 PM | Mindanao Grid-10/22/2023 12:39: Agus 2 HEPP U2 online at 1222H. Unplanned Outage. [WEBSMS] | CMIN
10/22/2023 12:34:16 PM | Mindanao Grid-10/22/2023 12:36: Agus 2 HEPP U1 online at 1210H. Unplanned Outage. [WEBSMS] | CMIN
10/22/2023 12:18:38 PM | Mindanao Grid-10/22/2023 12:21: Agus 2 HEPP U1 online at 1210H. Unplanned Outage. [WEBSMS] | CMIN
10/22/2023 12:07:06 PM | Mindanao Grid-10/22/2023 12:09: Agus 1 HEPP U2 online at 1149H. Unplanned Outage. [WEBSMS] | CMIN
10/22/2023 11:54:46 AM | Mindanao Grid-10/22/2023 11:57: Baloi - Agus 2 138kV L1 restored at 1113. (Planned Outage) [WEBSMS] | CMIN
10/22/2023 11:35:50 AM | Luzon Grid-10/22/2023 11:35: Tayabas PCB 9-02CB04TAY - de-energized at 1134H (Planned Outage) [WEBSMS] | CLUZ
10/22/2023 11:28:42 AM | Mindanao Grid-10/22/2023 11:31: Agus2-Baloi 138kV Line 2 tripped at 1013H (While Agus 2-Baloi 138kV L1 is on Planned Outage) resulted to isolation of Agus 1 HEPP and Agus 2 HEPP with total gross generation loss of 143MW. Frequency reached at 59.108Hz. ALD/UFR activated with total LD=12.23MW. Unplanned Outage. [WEBSMS] | CMIN
10/22/2023 11:06:07 AM | Luzon Grid-10/22/2023 11:06: For info: The attempt to restore Labo-Gumaca 230kV line 2 at 1101H failed with SLGF phase C relay indication. [WEBSMS] | CLUZ
10/22/2023 11:02:38 AM | Luzon Grid-10/22/2023 11:02: Labo-Gumaca 230kV line 1 - restored at 1059H.(Unplanned Outage) [WEBSMS] | CLUZ
10/22/2023 10:59:03 AM | Mindanao Grid-10/22/2023 11:01: Baloi - Agus2 138kV L2 tripped at 1013H. (Unplanned Outage) Note: Baloi - Agus 2 138kV L1 on planned outage. [WEBSMS] | CMIN
10/22/2023 10:39:25 AM | Luzon Grid-10/22/2023 10:39: SCPC Unit 3 tripped at 1033H from 112MW load. (Unplanned Outage) [WEBSMS] | CLUZ
10/22/2023 10:23:32 AM | Luzon Grid-10/22/2023 10:23: Labo-Gumaca 230kV line 1 - auto-tripped at 1016H. (Unplanned Outage) [WEBSMS] | CLUZ
10/22/2023 10:22:01 AM | Luzon Grid-10/22/2023 10:22: Labo-Gumaca 230kV line 2 - auto-tripped at 1015H (Unplanned Outage) [WEBSMS] | CLUZ
10/22/2023 9:18:52 AM | Mindanao Grid-10/22/2023 09:21: Lake Mainit HEPP online at 0603H. Unplanned Outage. [WEBSMS] | CMIN
10/22/2023 8:50:32 AM | Mindanao Grid-10/22/2023 08:53: Pulangi 4 Unit #3 online at 0830H. Planned Outage (Non-GOMP) [WEBSMS] | CMIN
10/22/2023 8:27:24 AM | Luzon Grid-10/22/2023 08:27: Pagbilao CFTPP 230kV Bus 2 - energized at 0825H (Planned Outage) [WEBSMS] | CLUZ
10/22/2023 8:14:48 AM | Mindanao Grid-10/22/2023 08:17: Maco - Nabunturan 138kV L1 de-energized at 0807H. (Planned Outage) [WEBSMS] | CMIN
10/22/2023 8:00:42 AM | Luzon Grid-10/22/2023 08:00: Nagsaag 230kV Bus 1 - de-energized at 0759H. (Planned Outage) [WEBSMS] | CLUZ
10/22/2023 7:56:14 AM | Luzon Grid-10/22/2023 07:56: Avion Unit 2 Main Transformer - de-energized at 0754H (Planned Outage) [WEBSMS] | CLUZ
10/22/2023 7:50:54 AM | Mindanao Grid-10/22/2023 07:53: Baloi - Agus2 138kV L1 de-energized at 0736H. (Planned Outage) [WEBSMS] | CMIN
10/22/2023 7:17:47 AM | Visayas Grid-10/22/2023 07:17: Sangi - 2nd Lift 34.5 kV de-energized at 0712H. (Planned Outage) [WEBSMS] | CVIS
10/22/2023 7:09:28 AM | [NSO Update] Visayas Grid-10/22/2023 07:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0708H with power going to Mindanao. [WEBSMS] | CVIS
10/22/2023 7:09:12 AM | [NSO Update] Mindanao Grid-10/22/2023 07:11: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0708H with power going to Mindanao. [WEBSMS] | CMIN
10/22/2023 7:02:32 AM | Luzon Grid-10/22/2023 07:02: Pagbilao CFTPP 230kV Bus 2 - de-energized at 0701H. (Planned Outage) [WEBSMS] | CLUZ
10/22/2023 6:49:30 AM | [NSO Update] Visayas Grid-10/22/2023 06:49: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0645H from forward power direction. [WEBSMS] | CVIS
10/22/2023 6:49:12 AM | [NSO Update] Mindanao Grid-10/22/2023 06:51: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0645H from forward power direction. [WEBSMS] | CMIN
10/22/2023 6:43:13 AM | Visayas Grid-10/22/2023 06:43: Daanbantayan - CEBECO 2 69 kV Line energized at 0641H. (Planned Outage) [WEBSMS] | CVIS
10/22/2023 6:43:02 AM | Luzon Grid-10/22/2023 06:43: San Jose-San Rafael(CND) 230kV line - de-energized at 0640H. (Planned Outage) [WEBSMS] | CLUZ
10/22/2023 6:34:27 AM | Visayas Grid-10/22/2023 06:34: Cebu - Colon 138 kV Line 3 de-energized at 0633H. (Planned Outage) [WEBSMS] | CVIS
10/22/2023 6:22:00 AM | Visayas Grid-10/22/2023 06:22: Calong-calong - Asturias 69 kV Line de-energized at 0620H. (Planned Outage) [WEBSMS] | CVIS
10/22/2023 6:15:49 AM | Visayas Grid-10/22/2023 06:15: Daanbantayan - CEBECO 2 69 kV Line de-energized at 0610H. (Planned Outage) [WEBSMS] | CVIS
10/22/2023 5:48:59 AM | Mindanao Grid-10/22/2023 05:51: LAKE MAINIT hydro tripped with 10.5MW load at 0541H. Lowest frequency recorded was 60Hz. (Unplanned Outage) Indication: Generator Reverse Power. [WEBSMS] | CMIN
10/22/2023 5:42:26 AM | [NSO Update] Mindanao Grid-10/22/2023 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3301MW, PK=1782MW, RR=67MW, NetOpMargin: AM=1452, PM=1341, EVE=1153 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @25.5MW, MA2 @50MW, AG1 @55MW, AG2 @99MW, AG4 @114MW, AG5 @37MW, AG6 @149MW, AG7 @32MW, PG4 @190MW [WEBSMS] | CMIN
10/22/2023 5:40:32 AM | [NSO Update] Visayas Grid-10/22/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2578MW, PK=1539MW, RR=90MW, NetOpMargin: AM=949, PM=836, EVE=505 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @113.5MW, LEYTE A @318MW, PGPP1 @37.5MW [WEBSMS] | CVIS
10/22/2023 5:38:02 AM | [NSO Update] Luzon Grid-10/22/2023 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14092MW, PK=8507MW, RR=316MW, NetOpMargin: AM=5269, PM=4667, EVE=3331 Highest Unit O/L: SUAL 2 @ 647MW Derated Plant: CALACA 2 @175MW, GNPD 1 @640MW, MASINLOC 2 @250MW, SLPGC 1 @120MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/22/2023 4:57:34 AM | Mindanao Grid-10/22/2023 05:00: San Francisco-Bislig 138KV line re-energized at 0416H & looped at Bislig SS at 0418H. From Planned Outage / Non-GOMP (P&E requested shutdown). [WEBSMS] | CMIN
10/22/2023 4:51:39 AM | Mindanao Grid-10/22/2023 04:54: San Francisco SS 138KV Bus 2 re-energized at 0414H. From Planned Outage / Non-GOMP (P&E requested shutdown). [WEBSMS] | CMIN
10/22/2023 4:17:16 AM | [NSO Update] Visayas Grid-10/22/2023 04:17: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Shear Line affecting Central Luzon. [WEBSMS] | CVIS
10/22/2023 4:16:48 AM | [NSO Update] Mindanao Grid-10/22/2023 04:19: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Shear Line affecting Central Luzon. [WEBSMS] | CMIN
10/22/2023 4:16:42 AM | [NSO Update] Luzon Grid-10/22/2023 04:16: Weather Advisory: Northeast Monsoon affecting Northern Luzon. Shear Line affecting Central Luzon. [WEBSMS] | CLUZ
10/22/2023 2:20:12 AM | Luzon Grid-10/22/2023 02:20: Mexico SS 230kV Bus 1 restored at 0213H (Planned Outage) [WEBSMS] | CLUZ
10/22/2023 12:08:40 AM | Mindanao Grid-10/22/2023 00:11: LAKE MAINIT Hydro cut-in at 0002H. (Unplanned Outage) [WEBSMS] | CMIN
10/22/2023 12:07:53 AM | Mindanao Grid-10/22/2023 00:10: LAKE MAINIT Hydro tripped with 10.67MW load at 2342H. Lowest frequency recorded was 59.89Hz. (Unplanned Outage) Indication: Generator Reverse Power. [WEBSMS] | CMIN
10/21/2023 11:31:37 PM | Luzon Grid-10/21/2023 23:31: Bantay - Laoag 115kV New Main Protection commissioned at 2329H. (End of commissioning) [WEBSMS] | CLUZ
10/21/2023 11:16:09 PM | Mindanao Grid-10/21/2023 23:18: Surallah Power Generation (SPG) cut-in at 2142H. (Planned Outage) [WEBSMS] | CMIN
10/21/2023 10:40:32 PM | Luzon Grid-10/21/2023 22:40: Bantay - Laoag 115kV energized at 2235H. (On-going commissioning) [WEBSMS] | CLUZ
10/21/2023 9:18:08 PM | Mindanao Grid-10/21/2023 21:20: Talomo 1 Unit 2 cut-in at 1858H. (Unplanned Outage) [WEBSMS] | CMIN
10/21/2023 9:16:24 PM | Mindanao Grid-10/21/2023 21:18: Supreme Power Mati declared available at 2004H. [WEBSMS] | CMIN
10/21/2023 9:15:26 PM | Mindanao Grid-10/21/2023 21:18: Supreme Power Mati tripped with 4MW load at 2002H. (Unplanned Outage). Indication: Reverse Power Trip. [WEBSMS] | CMIN
10/21/2023 7:18:34 PM | Luzon Grid-10/21/2023 19:18: Mexico SS 230kV Bus 1 de-energized at 1918H. (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 6:36:48 PM | Mindanao Grid-10/21/2023 18:39: ASIGA Hydro cut-in at 1817H. (Unplanned Outage affected by maintenance activity of ANECO). [WEBSMS] | CMIN
10/21/2023 6:36:17 PM | Mindanao Grid-10/21/2023 18:38: LAKE MAINIT Hydro cut-in at 1808H. (Unplanned Outage affected by maintenance activity of ANECO). [WEBSMS] | CMIN
10/21/2023 6:15:05 PM | Mindanao Grid-10/21/2023 18:17: Maco SS Power Transformer # 1 re-energized at 1756H. From APMS activities. Planned Outage / GOMP. [WEBSMS] | CMIN
10/21/2023 6:03:01 PM | Mindanao Grid-10/21/2023 18:05: Placer SS Power Transformer # 2 re-energized at 1721H. From Planned Outage / GOMP. [WEBSMS] | CMIN
10/21/2023 6:00:50 PM | [NSO Update] Luzon Grid-10/21/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13237MW, PK=9227MW, RR=403MW, NetOpMargin: EVE=3607 Highest Unit O/L: GNPD 1@668MW Derated Plant: CLC2 @175MW, MSLC2 @330MW, SLPGC 1 @100MW, SLPGC 2 @100MW, SLTEC 1 @87MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/21/2023 5:56:57 PM | Luzon Grid-10/21/2023 17:57: Gamu-UPSI Gamu BESS 69kV Line restored at 1755H. (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 5:56:25 PM | [NSO Update] Mindanao Grid-10/21/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3012MW, PK=2157MW, RR=70MW, NetOpMargin: EVE=785 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @130MW, AG5 @37MW, AG6 @149MW, AG7 @32MW, PG4 @100MW [WEBSMS] | CMIN
10/21/2023 5:51:04 PM | [NSO Update] Visayas Grid-10/21/2023 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2437MW, PK=2109MW, RR=92MW, NetOpMargin: EVE=236 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @112.5MW, LEYTE A @305MW, PGPP1 @37.5MW [WEBSMS] | CVIS
10/21/2023 5:47:15 PM | [NSO Update] Luzon Grid-10/21/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13237MW, PK=9227MW, RR=403MW, NetOpMargin: EVE=3607 Highest Unit O/L: GNPD 1@668MW Derated Plant: CLC2 @175MW, GNPD1 @510MW, MSLC2 @330MW, SLPGC 1 @100MW, SLPGC 2 @100MW, SLTEC 1 @87MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/21/2023 5:44:08 PM | Luzon Grid-10/21/2023 17:44: Bolo SS 600MVA T03 restored at 1743H. (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 4:50:21 PM | Mindanao Grid-10/21/2023 16:52: Agus 1 Unit 2 cut-in at 1646H. (Unplanned Outage) [WEBSMS] | CMIN
10/21/2023 4:30:17 PM | Mindanao Grid-10/21/2023 16:32: WMPC DG05 cut-out at 1623H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/21/2023 4:29:21 PM | Mindanao Grid-10/21/2023 16:31: WMPC DG04 cut-out at 1558H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/21/2023 4:16:01 PM | [NSO Update] Mindanao Grid-10/21/2023 16:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1610H with power going to Visayas [WEBSMS] | CMIN
10/21/2023 4:13:51 PM | [NSO Update] Mindanao Grid-10/21/2023 16:16: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1610H with power going to Visayas [WEBSMS] | CMIN
10/21/2023 4:13:44 PM | Mindanao Grid-10/21/2023 16:16: Nagamin-Zamboanga 138KV L2 re-energized at 1549H. From Planned Outage / GOMP. [WEBSMS] | CMIN
10/21/2023 4:11:32 PM | [NSO Update] Visayas Grid-10/21/2023 16:11: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1610H with power going to Visayas [WEBSMS] | CVIS
10/21/2023 3:56:18 PM | Mindanao Grid-10/21/2023 15:58: LAKE MAINIT shutdown at 0605H. (Unplanned Outage, affected by ANECO maintenance activity). [WEBSMS] | CMIN
10/21/2023 3:47:55 PM | Mindanao Grid-10/21/2023 15:50: ASIGA Hydro isolated with 4.4MW load at 0616H due to outage of 69 kV feeder. [WEBSMS] | CMIN
10/21/2023 2:49:51 PM | Luzon Grid-10/21/2023 14:49: Muntinlupa (Sucat) SS 300MVA T02 restored at 1449H. (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 2:43:56 PM | Luzon Grid-10/21/2023 14:44: Concepcion PCB 8-04CB24CON restored at 1442H. (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 2:29:10 PM | Luzon Grid-10/21/2023 14:29: Muntinlupa (Sucat) SS 230kV Bus 2 restored at 1428H. (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 2:20:27 PM | [NSO Update] Mindanao Grid-10/21/2023 14:23: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1356H from reverse power direction [WEBSMS] | CMIN
10/21/2023 2:19:48 PM | [NSO Update] Visayas Grid-10/21/2023 14:19: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1356H from reverse power direction [WEBSMS] | CVIS
10/21/2023 2:01:01 PM | Visayas Grid-10/21/2023 14:01: Colon-Cebu 138 KV Line 2 energized at 1400H. (Planned Outage) [WEBSMS] | CVIS
10/21/2023 1:07:09 PM | Luzon Grid-10/21/2023 13:07: Concepcion PCB 8-04CB24CON shutdown at 1304H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 12:56:26 PM | [NSO Update] Luzon Grid-10/21/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13372MW, PK=9573MW, RR=421MW, NetOpMargin: PM=3379, EVE=2617 Highest Unit O/L: SUAL 2 @647MW Derated Plant: CLC2 @150MW, GNPD1 @501MW, MSLC2 @330MW, SLPGC 1 @100MW, SLPGC 2 @100MW, SLTEC 1 @60MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/21/2023 12:46:04 PM | [NSO Update] Visayas Grid-10/21/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2501MW, PK=2079MW, RR=88MW, NetOpMargin: PM=334, EVE=172 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @112.5MW, LEYTE A @308MW, PGPP1 @37.5MW, PGPP2 SOG1 @19.6MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/21/2023 12:43:24 PM | [NSO Update] Mindanao Grid-10/21/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3052MW, PK=2180MW, RR=70MW, NetOpMargin: PM=802, EVE=703 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @130MW, AG5 @37MW, AG6 @149MW, AG7 @32MW, PG4 @100MW [WEBSMS] | CMIN
10/21/2023 12:42:05 PM | [NSO Update] Mindanao Grid-10/21/2023 12:44: GRID UPDATE AS OF 1:00 PM System Condition: CAP=3052MW, PK=2180MW, RR=70MW, NetOpMargin: PM=802, EVE=703 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @130MW, AG5 @37MW, AG6 @149MW, AG7 @32MW, PG4 @100MW [WEBSMS] | CMIN
10/21/2023 11:40:04 AM | Luzon Grid-10/21/2023 11:40: Mexico-Concepcion 230kV Line 1 restored at 1138H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 10:54:33 AM | Luzon Grid-10/21/2023 10:54: Correction: Muntinlupa (Sucat) SS 115kV Bus 2 de-energized at 1053H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 10:41:22 AM | [NSO Update] Mindanao Grid-10/21/2023 10:43: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1039H with power going to Mindanao [WEBSMS] | CMIN
10/21/2023 10:40:40 AM | [NSO Update] Visayas Grid-10/21/2023 10:40: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1039H with power going to Mindanao [WEBSMS] | CVIS
10/21/2023 10:31:20 AM | [NSO Update] Mindanao Grid-10/21/2023 10:33: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1018H from forward power direction. (Planned Outage) [WEBSMS] | CMIN
10/21/2023 10:31:07 AM | Luzon Grid-10/21/2023 10:31: Muntinlupa (Sucat) SS 115kV Bus 2 de-energized at 1011H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 10:23:57 AM | Mindanao Grid-10/21/2023 10:26: WMPC DG05 cut-in at 1021H. RPS - System Voltage Requirement. Time of Call: 1013H. [WEBSMS] | CMIN
10/21/2023 10:22:01 AM | [NSO Update] Visayas Grid-10/21/2023 10:22: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1018H from forward power direction. (Planned Outage) [WEBSMS] | CVIS
10/21/2023 10:10:42 AM | Mindanao Grid-10/21/2023 10:13: WMPC DG05 declared available at 1000H (from forced outage). [WEBSMS] | CMIN
10/21/2023 10:08:15 AM | Luzon Grid-10/21/2023 10:08: Muntinlupa (Sucat) SS 115kV Bus 2 restored at 1007H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 9:45:05 AM | Mindanao Grid-10/21/2023 09:47: WMPC DG05 declared as forced outage at 0917H due to leak in its turbo charger. [WEBSMS] | CMIN
10/21/2023 9:29:01 AM | Mindanao Grid-10/21/2023 09:31: WMPC DG04 cut-in at 0921H. RPS - System Voltage Requirement. DG04 was a replacement unit for WMPC DG05 (RPS), Time of Call (for DG05): 0904H. DG05 declared as forced outage at 0917H due to leak in its turbo charger. [WEBSMS] | CMIN
10/21/2023 8:55:50 AM | Mindanao Grid-10/21/2023 08:58: Nagamin-Zamboanga 138KV L2 de-energized at 0823H. TL maintenance activity. Planned Outage / GOMP. [WEBSMS] | CMIN
10/21/2023 8:08:30 AM | Luzon Grid-10/21/2023 08:08: Mexico-Concepcion 230kV Line 1 de-energized at 0807H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 7:46:24 AM | Mindanao Grid-10/21/2023 07:48: Maco SS Power Transformer # 1 de-energized at 0711H. APMS activities. Planned Outage / GOMP. [WEBSMS] | CMIN
10/21/2023 7:30:28 AM | Visayas Grid-10/21/2023 07:30: Colon-Cebu 138 KV Line 2 de-energized at 0730H. (Planned Outage) [WEBSMS] | CVIS
10/21/2023 7:17:12 AM | Mindanao Grid-10/21/2023 07:19: Placer SS Power Transformer # 2 de-energized at 0627H. APMS activities. Planned Outage / GOMP. [WEBSMS] | CMIN
10/21/2023 7:15:40 AM | Luzon Grid-10/21/2023 07:15: Sual SS 230kV Busbar 1 de-energized at 0715H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 7:15:09 AM | Luzon Grid-10/21/2023 07:15: Muntinlupa (Sucat) SS 115kV Bus 2 de-energized at 0714H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 7:08:03 AM | Luzon Grid-10/21/2023 07:08: San Jose-Taytay 230kV Line 1 de-energized at 0707H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 7:04:40 AM | Visayas Grid-10/21/2023 07:04: KSPC U2 cut in at 0657H. (Planned Outage) [WEBSMS] | CVIS
10/21/2023 7:00:56 AM | Luzon Grid-10/21/2023 07:01: Muntinlupa (Sucat) SS 300MVA T02 de-energized at 0659H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 6:10:39 AM | Luzon Grid-10/21/2023 06:10: Bolo SS 600MVA T03 de-energized at 0610H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 5:40:05 AM | Mindanao Grid-10/21/2023 05:42: San Francisco-Bislig 139kV line and San Francisco SS 138kV Bus 2 de-energized 0532H and 0533H, respectively (Planned outage). [WEBSMS] | CMIN
10/21/2023 5:36:56 AM | [NSO Update] Luzon Grid-10/21/2023 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14234MW, PK=10103MW, RR=418MW, NetOpMargin: AM=3712, PM=2934, EVE=2616 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 2 @ 330MW, Masinloc 3 @ 330MW, SLPGC 2 @ 100MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/21/2023 5:35:08 AM | [NSO Update] Mindanao Grid-10/21/2023 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3007MW, PK=2019MW, RR=70MW, NetOpMargin: AM=918, PM=802, EVE=716 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @85MW, AG4 @130MW, AG5 @37MW, AG6 @149MW, AG7 @32MW, PG4 @100MW [WEBSMS] | CMIN
10/21/2023 5:33:29 AM | [NSO Update] Visayas Grid-10/21/2023 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2620MW, PK=1984MW, RR=87MW, NetOpMargin: AM=549, PM=406, EVE=215 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 112.5MW, Leyte A @ 318MW, PGPP1 @ 37.5MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
10/21/2023 4:23:29 AM | [NSO Update] Luzon Grid-10/21/2023 04:23: Weather Update: Northeast Monsoon affecting Northern Luzon. Shear Line affecting Central Luzon. [WEBSMS] | CLUZ
10/21/2023 4:23:16 AM | [NSO Update] Visayas Grid-10/21/2023 04:23: Weather Update: Northeast Monsoon affecting Northern Luzon. Shear Line affecting Central Luzon. [WEBSMS] | CVIS
10/21/2023 4:23:03 AM | [NSO Update] Mindanao Grid-10/21/2023 04:25: Weather Update: Northeast Monsoon affecting Northern Luzon. Shear Line affecting Central Luzon. [WEBSMS] | CMIN
10/21/2023 4:02:58 AM | Luzon Grid-10/21/2023 04:03: SLTEC 1 online at 0402H (Unplanned Outage) [WEBSMS] | CLUZ
10/21/2023 12:35:20 AM | Luzon Grid-10/21/2023 00:35: SLTEC 1 shutdown at 0033H (Unplanned Outage) [WEBSMS] | CLUZ
10/21/2023 12:24:07 AM | Luzon Grid-10/21/2023 00:24: San Juan (Kalayaan)-Calauan 230kV Line 1 and 2 de-energized at 0019H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 12:22:45 AM | Luzon Grid-10/21/2023 00:22: Calauan SS 150MVA T01 and T02 de-energized at 0017H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 12:20:59 AM | Luzon Grid-10/21/2023 00:21: Calauan SS 230kV Bus 1 and 2 de-energized at 0017H (Planned Outage) [WEBSMS] | CLUZ
10/21/2023 12:18:38 AM | Luzon Grid-10/21/2023 00:18: Calauan SS 115kV Bus 1 de-energized at 0014H (Planned Outage) [WEBSMS] | CLUZ
10/20/2023 10:40:56 PM | Mindanao Grid-10/20/2023 22:43: WMPC DG05 shutdown at 2234H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/20/2023 10:06:15 PM | Mindanao Grid-10/20/2023 22:08: Nagamin-Zamboanga 138kV L1 restored/energized at 2205H. (Planned Outage) [WEBSMS] | CMIN
10/20/2023 10:02:44 PM | Luzon Grid-10/20/2023 22:02: Lamao-Alas-asin 230kV Line 1 de-energized at 2202H (Planned Outage) [WEBSMS] | CLUZ
10/20/2023 10:00:01 PM | Luzon Grid-10/20/2023 22:00: GNPD-GMEC 230kV Tie Line loop at 2258H (Planned Outage). [WEBSMS] | CLUZ
10/20/2023 9:36:24 PM | Luzon Grid-10/20/2023 21:36: Ilijan B3 online at 2134H (Unplanned Outage) [WEBSMS] | CLUZ
10/20/2023 8:29:47 PM | Luzon Grid-10/20/2023 20:29: Ilijan B2 (2-2) online at 2028H (Unplanned Outage) [WEBSMS] | CLUZ
10/20/2023 7:10:51 PM | Mindanao Grid-10/20/2023 19:13: Nagamin-Zamboanga 138kV L1 de-energized at 1906H. (Planned Outage). [WEBSMS] | CMIN
10/20/2023 6:32:01 PM | Mindanao Grid-10/20/2023 18:34: Tudaya 2 HEPP with 6.4 gross generation tripped at 1822H. Indication: Level Header Box No Signal. Unplanned Outage. [WEBSMS] | CMIN
10/20/2023 6:14:44 PM | Luzon Grid-10/20/2023 18:14: Bolo-Labrador 230kV line 1 restored at 1814H (Planned Outage) [WEBSMS] | CLUZ
10/20/2023 6:13:39 PM | Mindanao Grid-10/20/2023 18:16: Nagamin SS 138kV 1 Bus restored/energized 1810H( Planned outage) [WEBSMS] | CMIN
10/20/2023 5:55:29 PM | Mindanao Grid-10/20/2023 17:58: WMPC DG09 shutdown at 1714H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/20/2023 5:48:15 PM | [NSO Update] Luzon Grid-10/20/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12835MW, PK=10443MW, RR=430MW, NetOpMargin: EVE=1963 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @175MW, MSLC2 @325MW, MSLC3 @330MW, SLPGC 1 @100MW, ILIJAN A @300MW [WEBSMS] | CLUZ
10/20/2023 5:44:29 PM | [NSO Update] Visayas Grid-10/20/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2579MW, PK=2210MW, RR=92MW, NetOpMargin: EVE=276 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @112.5MW, LEYTE A @318MW, PGPP1 @37.5MW, PGPP2 SOG1 @19.6MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/20/2023 5:40:14 PM | [NSO Update] Mindanao Grid-10/20/2023 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3130MW, PK=2244MW, RR=70MW, NetOpMargin: EVE=816 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @120MW, AG5 @37MW, AG6 @149MW, AG7 @32MW, PG4 @100MW [WEBSMS] | CMIN
10/20/2023 5:32:41 PM | Mindanao Grid-10/20/2023 17:35: Kauswagan - GNPK 230kV L2 de-energized at 1723H (Emergency shutdown). [WEBSMS] | CMIN
10/20/2023 4:52:51 PM | Luzon Grid-10/20/2023 16:52: Cayanga Solar 47MVA T02 and T01 energized at 1628 and 1649H, respectively, as load. [WEBSMS] | CLUZ
10/20/2023 4:43:13 PM | Luzon Grid-10/20/2023 16:43: Tayabas-San Jose 500kV line 2 energized at 1641H (Planned Outage) [WEBSMS] | CLUZ
10/20/2023 4:41:39 PM | Luzon Grid-10/20/2023 16:41: Cayanga Solar 230kV Bus 2 energized at 1640H, as load. [WEBSMS] | CLUZ
10/20/2023 4:28:54 PM | Luzon Grid-10/20/2023 16:28: Cayanga Solar 230kV Bus 1 energized at 1618H, as load. [WEBSMS] | CLUZ
10/20/2023 4:25:07 PM | Mindanao Grid-10/20/2023 16:27: WMPC DG06 shutdown at 1614H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/20/2023 4:03:23 PM | Luzon Grid-10/20/2023 16:03: Ilijan A1online at 1600H (Unplanned Outage) [WEBSMS] | CLUZ
10/20/2023 2:42:26 PM | Luzon Grid-10/20/2023 14:42: Ilijan A3 online at 1437H (Unplanned Outage) [WEBSMS] | CLUZ
10/20/2023 1:42:52 PM | Mindanao Grid-10/20/2023 13:45: WMPC DG09 online at 1340H. RPS -System Voltage Requirement. [WEBSMS] | CMIN
10/20/2023 1:33:46 PM | Luzon Grid-10/20/2023 13:33: Ilijan GT1-2 online at 1326H (Unplanned Outage) [WEBSMS] | CLUZ
10/20/2023 12:58:03 PM | [NSO Update] Luzon Grid-10/20/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13180MW, PK=11028MW, RR=446MW, NetOpMargin: PM=1706, EVE=1634 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @175MW, MSLC2 @325MW, MSLC3 @330MW, SLPGC1 @100MW [WEBSMS] | CLUZ
10/20/2023 12:52:36 PM | [NSO Update] Mindanao Grid-10/20/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3150MW, PK=2310MW, RR=70MW, NetOpMargin: PM=770, EVE=781 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @120MW, AG5 @37MW, AG6 @129MW, AG7 @32MW, PG4 @100MW [WEBSMS] | CMIN
10/20/2023 12:50:28 PM | [NSO Update] Visayas Grid-10/20/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2579MW, PK=2248MW, RR=40MW, NetOpMargin: PM=291, EVE=229 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @112.5MW, LEYTE A @318MW, PGPP1 @37.5MW, PGPP2 SOG1 @19.6MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/20/2023 12:34:40 PM | Mindanao Grid-10/20/2023 12:37: WMPC DG04 run as RPS on emergency shutdown due to cooling system problem. [WEBSMS] | CMIN
10/20/2023 12:25:32 PM | Mindanao Grid-10/20/2023 12:28: WMPC DG06 online at 1216H, to replace DG04 due to cooling system problem. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/20/2023 12:01:16 PM | Mindanao Grid-10/20/2023 12:03: WMPC DG04 online at 1055H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/20/2023 11:59:03 AM | Mindanao Grid-10/20/2023 12:01: Agus 6 Unit #3 online at 1153H. Follow RTD. Planned Outage. [WEBSMS] | CMIN
10/20/2023 10:54:13 AM | Mindanao Grid-10/20/2023 10:56: Tacurong-Gensan 138kV L2 restored/energized 1051H (Planned outage) [WEBSMS] | CMIN
10/20/2023 10:44:37 AM | Mindanao Grid-10/20/2023 10:47: Agus6- AP6 69kV L3 restored/energized 1042H (Planned outage). [WEBSMS] | CMIN
10/20/2023 9:04:35 AM | Mindanao Grid-10/20/2023 09:07: Mati Diesel (MDP) online at 0900H. Follow RTD. [WEBSMS] | CMIN
10/20/2023 8:59:41 AM | Mindanao Grid-10/20/2023 09:02: WMPC DG05 online at 0854H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/20/2023 8:59:26 AM | Luzon Grid-10/20/2023 08:59: Bantay PCB 6-01CB04BAN - de-energized at 0855H (Currimao-Bantay 115kV line is on floating status as a result). (Planned Outage) [WEBSMS] | CLUZ
10/20/2023 8:27:36 AM | Mindanao Grid-10/20/2023 08:30: Agus6- AP6 69kV L3 de-energized 0822H (Planned outage). [WEBSMS] | CMIN
10/20/2023 8:26:01 AM | Luzon Grid-10/20/2023 08:26: Tayabas-San Jose 500kV line 2 - de-energized at 0824H (Planned Outage) [WEBSMS] | CLUZ
10/20/2023 8:09:09 AM | Mindanao Grid-10/20/2023 08:11: Tacurong-Gensan 138kV L2 de-energized 0807H (Planned outage). [WEBSMS] | CMIN
10/20/2023 7:54:52 AM | Mindanao Grid-10/20/2023 07:57: Agus 6 Unit #3 shutdown at 0736H. Affected by the planned activity (Hotspot Correction) at Agus 6 Switchyard. Follow RTD. Planned Outage. (Non-GOMP). [WEBSMS] | CMIN
10/20/2023 7:09:14 AM | Mindanao Grid-10/20/2023 07:11: Nagamin SS 138kV 1 Bus de-energized 0705H( Planned outage). [WEBSMS] | CMIN
10/20/2023 6:42:14 AM | Luzon Grid-10/20/2023 06:42: Bolo-Labrador 230kV line 1 - de-energized at 0638H (Planned Outage) [WEBSMS] | CLUZ
10/20/2023 5:34:58 AM | [NSO Update] Mindanao Grid-10/20/2023 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3123MW, PK=2160MW, RR=70MW, NetOpMargin: AM=892, PM=747, EVE=860 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @85MW, AG4 @120MW, AG5 @37MW, AG6 @99MW, AG7 @32MW, PG4 @100MW [WEBSMS] | CMIN
10/20/2023 5:32:53 AM | [NSO Update] Visayas Grid-10/20/2023 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2565MW, PK=2198MW, RR=91MW, NetOpMargin: AM=277, PM=183, EVE=265 Highest Unit O/L: THVI 1 &2 @ 169MW Derated Plant: LEYTE A @318MW, PGPP1 @37.5MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/20/2023 5:32:50 AM | [NSO Update] Luzon Grid-10/20/2023 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13294MW, PK=10514MW, RR=434MW, NetOpMargin: AM=2346, PM=2018, EVE=1963 Highest Unit O/L: GNPD 1@668MW Derated Plant: CALACA 2 @175MW, MASINLOC 2 @325MW, MASINLOC 3 @330MW [WEBSMS] | CLUZ
10/20/2023 4:39:10 AM | [NSO Update] Luzon Grid-10/20/2023 04:39: Weather Advisory: Shear Line affecting Central Luzon. Northeasterly Windflow affecting Northern Luzon. [WEBSMS] | CLUZ
10/20/2023 4:18:53 AM | [NSO Update] Mindanao Grid-10/20/2023 04:21: Weather Advisory: Shear Line affecting Central Luzon. Northeasterly Windflow affecting Northern Luzon. [WEBSMS] | CMIN
10/20/2023 4:18:34 AM | [NSO Update] Visayas Grid-10/20/2023 04:18: Weather Advisory: Shear Line affecting Central Luzon. Northeasterly Windflow affecting Northern Luzon. [WEBSMS] | CVIS
10/20/2023 3:51:34 AM | Mindanao Grid-10/20/2023 03:54: (Correction) New Bataan (Euro) Hydro tripped with 1.4MW load at 2300H. (Unplanned Outage). Cause: Affected by NORDECO feeder outage. [WEBSMS] | CMIN
10/20/2023 3:49:33 AM | Mindanao Grid-10/20/2023 03:52: New Bataan (Euro) Hydro cut-in at 0054H. (Unplanned Outage) [WEBSMS] | CMIN
10/20/2023 3:48:24 AM | Mindanao Grid-10/20/2023 03:50: New Bataan (Euro) Hydro tripped with 1.4MW load at 1100H. (Unplanned Outage). Cause: Affected by NORDECO feeder outage. [WEBSMS] | CMIN
10/20/2023 3:37:10 AM | Mindanao Grid-10/20/2023 03:39: WMPC DG05 cut-out at 2314H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/19/2023 11:59:49 PM | Mindanao Grid-10/20/2023 00:02: TM2 Unit 2 declared available at 2326H. (Maintenance Outage, Non-GOMP) [WEBSMS] | CMIN
10/19/2023 11:31:49 PM | Mindanao Grid-10/19/2023 23:34: Nasipit-APTM2 138kV L2 energized at 2326H. Planned Outage. [WEBSMS] | CMIN
10/19/2023 11:20:20 PM | Mindanao Grid-10/19/2023 23:22: Agus 1 Unit 2 tripped with 15MW load at 2307H. Lowest frequency recorded was 59.82Hz. (Unplanned Outage). Indication: Rotor Earth Fault. [WEBSMS] | CMIN
10/19/2023 10:51:05 PM | Mindanao Grid-10/19/2023 22:53: Nagamin-Zamboanga 138kV L1 energized at 2247H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
10/19/2023 10:45:17 PM | Mindanao Grid-10/19/2023 22:47: Nasipit-APTM2 138kV L2 deenergized at 2204H. Planned Outage. [WEBSMS] | CMIN
10/19/2023 9:47:11 PM | Mindanao Grid-10/19/2023 21:49: WMPC DG06 cut-out at 2143H. End of RPS - System Voltage Requirement, [WEBSMS] | CMIN
10/19/2023 8:47:53 PM | Mindanao Grid-10/19/2023 20:50: Agus 4 Unit 2 cut-in at 2042H. (Planned Outage) [WEBSMS] | CMIN
10/19/2023 7:46:44 PM | Mindanao Grid-10/19/2023 19:49: TUDAYA2 Unit 2 cut-in at 1942H. (Unplanned Outage) [WEBSMS] | CMIN
10/19/2023 7:22:48 PM | Mindanao Grid-10/19/2023 19:25: TUDAYA2 Unit 2 tripped with 1.5MW load at 1909H. (Unplanned Outage). Indication: Signal Failure Vibration Drive End [WEBSMS] | CMIN
10/19/2023 7:00:16 PM | Luzon Grid-10/19/2023 19:00: For info: PGBREI Orion Solar Power Plant energized as load and fully commissioned at 1843H. (End of commissioning) [WEBSMS] | CLUZ
10/19/2023 6:52:34 PM | Luzon Grid-10/19/2023 18:52: Ilijan ST-1 (87MW) tripped at 1843H while GT1-2 (98MW), GT2-2 (96MW) and ST-2 (70MW) tripped at 1844H. Lowest system frequency is 59.222Hz. (Unplanned Outage). [WEBSMS] | CLUZ
10/19/2023 6:45:21 PM | Visayas Grid-10/19/2023 18:45: Toledo SS 40 MVA 138/34.5 kV TR2 energized at 1844H. (Planned Outage) [WEBSMS] | CVIS
10/19/2023 6:43:15 PM | Luzon Grid-10/19/2023 18:43: Ilijan A GT1-1 tripped at 1840H with 110MW load. Lowest system frequency is 59.629Hz. [WEBSMS] | CLUZ
10/19/2023 6:23:27 PM | Mindanao Grid-10/19/2023 18:25: Agus 1 Unit 2 cut-in at 1819H. (Planned Outage) [WEBSMS] | CMIN
10/19/2023 6:04:32 PM | Luzon Grid-10/19/2023 18:04: Limay - Orion Solar 69kV Line energized (at Limay side) at 1757H. (On-going commissioning). [WEBSMS] | CLUZ
10/19/2023 5:32:08 PM | [NSO Update] Mindanao Grid-10/19/2023 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3108MW, PK=2250MW, RR=70MW, NetOpMargin: EVE=788 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @37MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
10/19/2023 5:30:33 PM | Mindanao Grid-10/19/2023 17:33: Baloi-IDP 138kV L energized at 1724H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
10/19/2023 5:30:07 PM | [NSO Update] Visayas Grid-10/19/2023 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2630MW, PK=2249MW, RR=40MW, NetOpMargin: EVE=341 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @112.5MW, LEYTE A @323MW, PGPP1 @37.5MW, PGPP2 SOG1 @19.6MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/19/2023 5:27:35 PM | [NSO Update] Luzon Grid-10/19/2023 17:27: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13301MW, PK=10254MW, RR=432MW, NetOpMargin: EVE=2615 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @175MW, MSLC2 @330MW, MSLC3 @330MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/19/2023 5:18:54 PM | Mindanao Grid-10/19/2023 17:21: WMPC DG06 cut-in at 1715H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/19/2023 4:32:52 PM | Mindanao Grid-10/19/2023 16:35: Maramag-Kibawe 138kV L3 energized at 1619H. Planned Outage/GOMP. [WEBSMS] | CMIN
10/19/2023 4:18:27 PM | Mindanao Grid-10/19/2023 16:20: WMPC DG06 cut-out at 1614H. End of RPS. [WEBSMS] | CMIN
10/19/2023 3:27:28 PM | Luzon Grid-10/19/2023 15:27: Kalayaan 3 online at 1522H. (Unplanned Outage) [WEBSMS] | CLUZ
10/19/2023 3:06:43 PM | Luzon Grid-10/19/2023 15:06: Kalayaan 3 tripped with 62MW load at 1502H. Lowest system frequency was 59.88Hz. (Unplanned Outage) [WEBSMS] | CLUZ
10/19/2023 3:03:51 PM | Visayas Grid-10/19/2023 15:03: Carcon - Sangi 34.5 kV Line 1 energized at 1458H. (Unplanned Outage) [WEBSMS] | CVIS
10/19/2023 1:03:24 PM | [NSO Update] Visayas Grid-10/19/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2650MW, PK=2248MW, RR=40MW, NetOpMargin: PM=362, EVE=342 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @112.5MW, LEYTE A @315MW, PGPP1 @37.5MW, PGPP2 SOG1 @19.6MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/19/2023 12:59:19 PM | [NSO Update] Luzon Grid-10/19/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13648MW, PK=10616MW, RR=446MW, NetOpMargin: PM=2586, EVE=2178 Highest Unit O/L: GNPD 1 @650MW Derated Plant: CLC2 @175MW, MSLC2 @320MW, GNPD 1 @650MW, [WEBSMS] | CLUZ
10/19/2023 12:56:30 PM | [NSO Update] Mindanao Grid-10/19/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3117MW, PK=2319MW, RR=70MW, NetOpMargin: PM=728, EVE=758 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @37MW, AG6 @149MW, AG7 @32MW, PG4 @110MW [WEBSMS] | CMIN
10/19/2023 11:56:01 AM | Luzon Grid-10/19/2023 11:56: Laoag-Pasuquin Solar 115kV line(Customer Owned) - restored at 1154H (Planned Outage) [WEBSMS] | CLUZ
10/19/2023 11:54:47 AM | Visayas Grid-10/19/2023 11:54: Carcon 34.5 KV bus 2 energized at 1153H. (Planned Outage) [WEBSMS] | CVIS
10/19/2023 10:56:42 AM | Mindanao Grid-10/19/2023 10:59: WMPC DG06 cut-in at 1049H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/19/2023 10:35:19 AM | Mindanao Grid-10/19/2023 10:37: Manolo SS 138kV Bus 1 energized at 1022H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
10/19/2023 9:20:41 AM | Visayas Grid-10/19/2023 09:20: Carcon-Sangi 34.5 KV Line 1 de-energized at 0914H. (Unplanned Outage) [WEBSMS] | CVIS
10/19/2023 8:53:00 AM | Mindanao Grid-10/19/2023 08:55: WMPC DG05 cut-in at 0850H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/19/2023 8:32:35 AM | Visayas Grid-10/19/2023 08:32: Carcon 34.5 KV bus 2 de-energized at 0824H. (Planned Outage) [WEBSMS] | CVIS
10/19/2023 8:21:33 AM | Mindanao Grid-10/19/2023 08:24: Maramag-Kibawe 138kV L3 deenergized at 0808H. Planned Outage/GOMP. [WEBSMS] | CMIN
10/19/2023 8:14:40 AM | Luzon Grid-10/19/2023 08:14: Bantay PCB 6-01CB24BAN - de-energized at 0803H (Planned Outage) [WEBSMS] | CLUZ
10/19/2023 7:47:18 AM | Mindanao Grid-10/19/2023 07:49: Manolo SS 138kV Bus 1 deenergized at 0740H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
10/19/2023 7:35:18 AM | Mindanao Grid-10/19/2023 07:37: Baloi-IDP 138kV L deenergized at 0712H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
10/19/2023 7:32:23 AM | Mindanao Grid-10/19/2023 07:34: (Correction/Update) ASIGA HEPP with 4.5MW gross generation tripped at 0526H. Indication: Undervoltage. Voltage dipped brought by fault at Lake Mainit (Transformer Restricted Earth Fault). ASIGA HEPP cut-in at 0548H. (Unplanned Outage) [WEBSMS] | CMIN
10/19/2023 7:17:52 AM | Mindanao Grid-10/19/2023 07:20: Nagamin-Zamboanga 138kV L1 deenergized at 0706H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
10/19/2023 5:59:56 AM | [NSO Update] Mindanao Grid-10/19/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3148MW, PK=2141MW, RR=70MW, NetOpMargin: AM=937, PM=783, EVE=810 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @85MW, AG4 @100MW, AG5 @38MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
10/19/2023 5:57:03 AM | [NSO Update] Luzon Grid-10/19/2023 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13825MW, PK=11134MW, RR=442MW, NetOpMargin: AM=2249, PM=1931, EVE=1948 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CALACA 2 @175MW, MASINLOC 2 @320MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/19/2023 5:55:02 AM | Mindanao Grid-10/19/2023 05:57: ASIGA HEPP online at 0548H. Unplanned Outage. [WEBSMS] | CMIN
10/19/2023 5:54:41 AM | [NSO Update] Visayas Grid-10/19/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2577MW, PK=2204MW, RR=40MW, NetOpMargin: AM=333, PM=295, EVE=311 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @ 112.5MW, Leyte A @ 323MW, PGPP1 @ 37.5MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
10/19/2023 5:51:36 AM | Mindanao Grid-10/19/2023 05:54: ASIGA HEPP with 4.5MW gross generation tripped at 0527H. Indication: To be determined. Unplanned Outage. [WEBSMS] | CMIN
10/19/2023 5:49:20 AM | Mindanao Grid-10/19/2023 05:51: Lake Mainit HEPP online at 0536H. Unplanned Outage. [WEBSMS] | CMIN
10/19/2023 5:35:52 AM | Mindanao Grid-10/19/2023 05:38: Lake Mainit HEPP with 10.7MW gross generation tripped at 0526H due to Transformer Earth Fault (REF). Frequency=60.2Hz. Unplanned Outage. [WEBSMS] | CMIN
10/19/2023 4:03:46 AM | [NSO Update] Mindanao Grid-10/19/2023 04:06: Weather Advisory: Northeasterly Windflow affecting Northern and Central Luzon. [WEBSMS] | CMIN
10/19/2023 4:02:57 AM | [NSO Update] Visayas Grid-10/19/2023 04:03: Weather Advisory: Northeasterly Windflow affecting Northern and Central Luzon. [WEBSMS] | CVIS
10/19/2023 4:02:51 AM | [NSO Update] Luzon Grid-10/19/2023 04:03: Weather Advisory: Northeasterly Windflow affecting Northern and Central Luzon. [WEBSMS] | CLUZ
10/19/2023 2:42:14 AM | Luzon Grid-10/19/2023 02:42: Taytay (Dolores) 115kV Bus 2 restored at 0239H (Planned Outage). [WEBSMS] | CLUZ
10/19/2023 12:19:19 AM | Luzon Grid-10/19/2023 00:19: Sta. Rita 40 online at 0014H (Unplanned Outage) [WEBSMS] | CLUZ
10/19/2023 12:05:40 AM | Luzon Grid-10/19/2023 00:05: Taytay (Dolores) SS 115kV Bus 2 de-energized at 0005H (Planned Outage) [WEBSMS] | CLUZ
10/18/2023 9:21:51 PM | Mindanao Grid-10/18/2023 21:24: WMPC DG05 shutdown at 2113H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/18/2023 8:47:04 PM | Mindanao Grid-10/18/2023 20:49: Sibulan HEPP and Tudaya 2 HEPP with 41.29MW total gross generation simultaneously tripped at 2028H. Frequency dip=59.596Hz. Indication to follow. Unplanned Outage. [WEBSMS] | CMIN
10/18/2023 8:45:28 PM | Mindanao Grid-10/18/2023 20:48: Kibawe-Tacurong 138kV Line 1 auto tripped 20:33:22H and auto reclosed 5 seconds after. (Unplanned outage) [WEBSMS] | CMIN
10/18/2023 7:00:29 PM | Luzon Grid-10/18/2023 19:00: Lal-lo-Magapit BESS 69kV Line restored at 1856H (Planned Outage) [WEBSMS] | CLUZ
10/18/2023 6:54:48 PM | Mindanao Grid-10/18/2023 18:57: Mt. Apo Unit #3 online at 1851H. Unplanned Outage. [WEBSMS] | CMIN
10/18/2023 6:29:20 PM | Luzon Grid-10/18/2023 18:29: Sta. Rita 20 online at 1826H (Unplanned Outage) [WEBSMS] | CLUZ
10/18/2023 5:53:41 PM | [NSO Update] Luzon Grid-10/18/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12600MW, PK=10668MW, RR=426MW, NetOpMargin: EVE=1506 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 2 @ 330MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/18/2023 5:50:11 PM | [NSO Update] Visayas Grid-10/18/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2557MW, PK=2205MW, RR=75MW, NetOpMargin: EVE=277 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @100.5MW, LEYTE A @315MW, PGPP1 @37.5MW, PGPP2 SOG1 @19.6MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/18/2023 5:32:13 PM | Luzon Grid-10/18/2023 17:32: Lumban-Malaya 230kV Line 2 restored at 1731H (Planned Outage) [WEBSMS] | CLUZ
10/18/2023 5:30:16 PM | [NSO Update] Mindanao Grid-10/18/2023 17:33: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3101MW, PK=2255MW, RR=70MW, NetOpMargin: EVE=776 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @39MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
10/18/2023 5:11:59 PM | Luzon Grid-10/18/2023 17:12: Sta. Rita 20 shutdown at 1711H (Unplanned Outage) [WEBSMS] | CLUZ
10/18/2023 4:42:47 PM | Mindanao Grid-10/18/2023 16:45: WMPC DG01 shutdown at 1613H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/18/2023 4:41:07 PM | Mindanao Grid-10/18/2023 16:43: Mt. Apo Unit #3 with 3MW gross generation tripped at 1604H. Indication: Activation of Restricted Earth Fault (REF). Unplanned Outage. [WEBSMS] | CMIN
10/18/2023 3:28:47 PM | Mindanao Grid-10/18/2023 15:31: KE Panaon U1 shutdown at 1525H. Follow RTD. [WEBSMS] | CMIN
10/18/2023 1:34:14 PM | Mindanao Grid-10/18/2023 13:37: KE Panaon U1 online at 1301H to facilitate Ancillary Reserve Test (DR and RPS). Follow RTD. [WEBSMS] | CMIN
10/18/2023 1:02:25 PM | Mindanao Grid-10/18/2023 13:05: Manolo-Maramag 138kV L1 restored 1257H (Unplanned outage) [WEBSMS] | CMIN
10/18/2023 1:01:18 PM | Mindanao Grid-10/18/2023 13:04: Manolo-Maramag 138kV L1 autotripped. (Unplanned outage). [WEBSMS] | CMIN
10/18/2023 12:57:14 PM | [NSO Update] Luzon Grid-10/18/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13329MW, PK=11369MW, RR=446MW, NetOpMargin: PM=1515, EVE=1365 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Masinloc 2 @ 330MW, Ilijan A @ 510MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/18/2023 12:53:26 PM | [NSO Update] Mindanao Grid-10/18/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3102MW, PK=2287MW, RR=70MW, NetOpMargin: PM=745, EVE=817 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @39MW, AG6 @149MW, AG7 @32MW, PG4 @110MW [WEBSMS] | CMIN
10/18/2023 12:51:51 PM | [NSO Update] Visayas Grid-10/18/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2637MW, PK=2199MW, RR=75MW, NetOpMargin: PM=363, EVE=281 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 111.5MW, Leyte A @ 315MW, PGPP1 @ 37.5MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
10/18/2023 11:55:07 AM | Mindanao Grid-10/18/2023 11:57: Baloi-IDPP 138kV line restored/energized at 1153H (Planned Outage). [WEBSMS] | CMIN
10/18/2023 11:41:16 AM | Luzon Grid-10/18/2023 11:41: Sta. Rita 20 online at 1139H. (Unplanned Outage) [WEBSMS] | CLUZ
10/18/2023 11:25:54 AM | Luzon Grid-10/18/2023 11:26: Batangas SS PCB 8-02CB24BTN restored at 1124H. (Planned Outage) [WEBSMS] | CLUZ
10/18/2023 10:59:22 AM | Mindanao Grid-10/18/2023 11:02: WMPC DG01 online at 1053H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/18/2023 10:41:01 AM | Luzon Grid-10/18/2023 10:41: Calaca 2 online at 1039H. (Unplanned Outage) [WEBSMS] | CLUZ
10/18/2023 10:19:28 AM | Luzon Grid-10/18/2023 10:19: Batangas SS PCB 8-02CB24BTN de-energized at 1019H. (Planned Outage) [WEBSMS] | CLUZ
10/18/2023 10:17:39 AM | Luzon Grid-10/18/2023 10:17: Batangas SS PCB 8-02CB08BTN restored at 1011H. (Planned Outage) [WEBSMS] | CLUZ
10/18/2023 9:15:16 AM | Mindanao Grid-10/18/2023 09:18: MDP (Mati Diesel) online at 0901H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
10/18/2023 9:13:43 AM | Mindanao Grid-10/18/2023 09:16: WMPC DG05 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/18/2023 9:10:03 AM | Luzon Grid-10/18/2023 09:10: Batangas SS PCB 8-02CB08BTN de-energized at 0910H. (Planned Outage) [WEBSMS] | CLUZ
10/18/2023 9:08:16 AM | Visayas Grid-10/18/2023 09:08: Magdugo-Dumanjug 230 KV Line 2 energized at 0904H, activity completed. (Planned Outage) [WEBSMS] | CVIS
10/18/2023 8:57:19 AM | Mindanao Grid-10/18/2023 09:00: Jasaan SS 138kV Transformer 2 restored/energized at 0855H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
10/18/2023 8:08:46 AM | Mindanao Grid-10/18/2023 08:11: Pulangi 4 HEPP Unit #3 shutdown at 0802H to facilitate replacement of unit�s generator air coolers. (Non-GOMP). Follow RTD. Planned Outage. [WEBSMS] | CMIN
10/18/2023 7:13:18 AM | Luzon Grid-10/18/2023 07:13: Lumban-Malaya 230kV Line 2 de-energized at 0712H. (Planned Outage) [WEBSMS] | CLUZ
10/18/2023 7:10:29 AM | Mindanao Grid-10/18/2023 07:13: Baloi-IDPP 138kV line de-energized at 0705H to facilitate Relay replacement program by MTD-A (Planned Outage). [WEBSMS] | CMIN
10/18/2023 7:08:45 AM | Luzon Grid-10/18/2023 07:09: Lal-lo-Magapit BESS 69kV Line de-energized at 0706H. (Planned Outage) [WEBSMS] | CLUZ
10/18/2023 6:46:39 AM | Luzon Grid-10/18/2023 06:46: Las Pinas 300MVA T05 restored at 0646H. (Unplanned Outage) [WEBSMS] | CLUZ
10/18/2023 6:17:58 AM | Mindanao Grid-10/18/2023 06:20: Jasaan SS 138kV Transformer 2 deenergized at 0603H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
10/18/2023 5:54:24 AM | Luzon Grid-10/18/2023 05:54: Quezon(Balintawak) 300MVA T02 restored at 0548H (Planned Outage) [WEBSMS] | CLUZ
10/18/2023 5:51:03 AM | [NSO Update] Visayas Grid-10/18/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2602MW, PK=2126MW, RR=75MW, NetOpMargin: AM=400, PM=237, EVE=284 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @111.5MW, LEYTE A @323MW, PGPP1 @37.5MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/18/2023 5:49:45 AM | Visayas Grid-10/18/2023 05:50: Magdugo-Dumanjug 230 KV Line 2 de-energized at 0549H. (Planned Outage) [WEBSMS] | CVIS
10/18/2023 5:49:41 AM | [NSO Update] Luzon Grid-10/18/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13215MW, PK=11231MW, RR=446MW, NetOpMargin: AM=1538, PM=1026, EVE=1208 Highest Unit O/L: GNPD 1@668MW Derated Plant: MSLC2 @320MW, MSLC3 @325MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/18/2023 5:39:38 AM | [NSO Update] Mindanao Grid-10/18/2023 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3143MW, PK=2166MW, RR=70MW, NetOpMargin: AM=907, PM=789, EVE=818 Highest Unit O/L: GNPK 3&4@ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @39MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
10/18/2023 5:12:20 AM | Luzon Grid-10/18/2023 05:12: Sta. Rita 20 emergency shutdown at 0509H due to critical water level at cooling sea water intake (Unplanned Outage) [WEBSMS] | CLUZ
10/18/2023 4:28:50 AM | [NSO Update] Visayas Grid-10/18/2023 04:29: Weather Update: Northeasterly Windflow affecting Northern Luzon. [WEBSMS] | CVIS
10/18/2023 4:27:45 AM | [NSO Update] Mindanao Grid-10/18/2023 04:30: Weather Update: Northeasterly Windflow affecting Northern Luzon. [WEBSMS] | CMIN
10/18/2023 4:24:29 AM | [NSO Update] Luzon Grid-10/18/2023 04:24: Weather Update: Northeasterly Windflow affecting Northern Luzon. [WEBSMS] | CLUZ
10/18/2023 3:44:22 AM | Luzon Grid-10/18/2023 03:44: Meralco Calauan 150MVA Bank 1 restored at 0335H (Unplanned Outage) [WEBSMS] | CLUZ
10/18/2023 2:16:23 AM | Luzon Grid-10/18/2023 02:16: Meralco Calauan 150MVA Bank 1 de-energized at 0204H (Unplanned Outage) [WEBSMS] | CLUZ
10/18/2023 1:27:09 AM | Luzon Grid-10/18/2023 01:27: San Jose 115kV Bus 2 restored at 0127H (Planned Outage) [WEBSMS] | CLUZ
10/18/2023 1:13:42 AM | Luzon Grid-10/18/2023 01:13: Currimao - Paguludan 69kV Line restored at 0113H (Unplanned Outage) [WEBSMS] | CLUZ
10/18/2023 12:16:12 AM | Luzon Grid-10/18/2023 00:16: Las Pinas 300MVA T05 de-energized at 0013H (Unplanned Outage) [WEBSMS] | CLUZ
10/17/2023 11:48:10 PM | Luzon Grid-10/17/2023 23:48: Quezon(Balintawak) 300MVA T02 de-energized at 2332H (Planned Outage) [WEBSMS] | CLUZ
10/17/2023 11:20:48 PM | Luzon Grid-10/17/2023 23:21: Quezon(Balintawak) 300MVA T03 restored at 2320H (Unplanned Outage) [WEBSMS] | CLUZ
10/17/2023 9:29:35 PM | Mindanao Grid-10/17/2023 21:32: WMPC DG05 shutdown at 2113H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/17/2023 9:07:54 PM | Luzon Grid-10/17/2023 21:08: Quezon(Balintawak) 300MVA T03 de-energized at 2107H (Unplanned Outage) [WEBSMS] | CLUZ
10/17/2023 7:58:57 PM | Luzon Grid-10/17/2023 19:59: Sta Rita 30 online at 1958H (Unplanned Outage) [WEBSMS] | CLUZ
10/17/2023 7:15:57 PM | Luzon Grid-10/17/2023 19:16: Currimao - Paguludan 69kV Line de-energized at 1915H (Unplanned Outage) [WEBSMS] | CLUZ
10/17/2023 6:55:11 PM | Mindanao Grid-10/17/2023 18:57: Mt. Apo Unit #3 online at 1852H. Unplanned Outage. [WEBSMS] | CMIN
10/17/2023 6:12:19 PM | Luzon Grid-10/17/2023 18:12: San Jose 115kV Bus 2 de-energized at 1809H (Planned Outage) [WEBSMS] | CLUZ
10/17/2023 5:59:46 PM | Luzon Grid-10/17/2023 18:00: For info: San Lorenzo-Sta Rita 230kV Busses were unlopped at 1750H while Batangas 300MVA T04 and T05 were paralleled at 1757H. (Preparation for the synchronization of Sta. Rita 30) [WEBSMS] | CLUZ
10/17/2023 5:49:06 PM | [NSO Update] Luzon Grid-10/17/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12367MW, PK=10712MW, RR=428MW, NetOpMargin: EVE=1227 Highest Unit O/L: GNPD 1@668MW Derated Plant: CALACA 1@215MW, MSLC2 @310MW, MSLC3 @320MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/17/2023 5:47:10 PM | [NSO Update] Mindanao Grid-10/17/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3157MW, PK=2263MW, RR=70MW, NetOpMargin: EVE=824 Highest Unit O/L: GNPK 3&4@ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @95MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @31MW, PG4 @170MW [WEBSMS] | CMIN
10/17/2023 5:45:35 PM | [NSO Update] Visayas Grid-10/17/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2558MW, PK=2173MW, RR=40MW, NetOpMargin: EVE=345 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @112.5MW, LEYTE A @323MW, PGPP1 @74MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/17/2023 5:37:05 PM | Mindanao Grid-10/17/2023 17:39: Nasipit 138kV Bus 1 energized at 1708H. (PO00AC / Non-GOMP) 1. P&E Request Shutdown. [WEBSMS] | CMIN
10/17/2023 5:34:57 PM | Mindanao Grid-10/17/2023 17:37: Mt. Apo Unit #3 tripped at 1714H, due to Restricted Earth Fault (REF). Unplanned Outage. [WEBSMS] | CMIN
10/17/2023 5:28:28 PM | Mindanao Grid-10/17/2023 17:31: Nasipit 138kV Bus 1 deenergized at 1611H. (PO00AC / Non-GOMP) 1. P&E Request Shutdown. [WEBSMS] | CMIN
10/17/2023 5:19:20 PM | Luzon Grid-10/17/2023 17:19: Lumban-Malaya 230kV Line 1 restored at 1719H (Planned Outage) [WEBSMS] | CLUZ
10/17/2023 5:04:29 PM | Mindanao Grid-10/17/2023 17:07: KE Jimenez U1 online at 1701H to facilitate the ANCILLARY RESERVE TEST (DR and RPS). Follow RTD. [WEBSMS] | CMIN
10/17/2023 5:01:45 PM | Luzon Grid-10/17/2023 17:01: Malaya 2 shutdown at 1700H (Planned Outage) [WEBSMS] | CLUZ
10/17/2023 4:59:05 PM | Luzon Grid-10/17/2023 16:59: BCCPP SS PCB 8-06CB08BCC restored at 1657H. (Planned Outage) [WEBSMS] | CLUZ
10/17/2023 4:17:11 PM | Mindanao Grid-10/17/2023 16:19: WMPC DG02 shutdown at 1614H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/17/2023 3:32:24 PM | Mindanao Grid-10/17/2023 15:35: KE Jimenez U2 shutdown at 1524H, from testing activity. (ANCILLARY RESERVE TEST; DR and RPS). Follow RTD. [WEBSMS] | CMIN
10/17/2023 3:31:29 PM | Luzon Grid-10/17/2023 15:31: Batangas PCB 8-02CB04BTN restored at 1530H (Planned Outage) [WEBSMS] | CLUZ
10/17/2023 2:32:22 PM | Mindanao Grid-10/17/2023 14:35: Kauswagan SS 230kV PCB 8-01CB08KSW and 8-01CB24KSW (Kauswagan-GNPK 230kV L1) energized at 1356H and 1357H respectively. To improve System Reliability. [WEBSMS] | CMIN
10/17/2023 2:01:22 PM | Mindanao Grid-10/17/2023 14:04: General Santos-Kamanga 138kV L2 deenergized at 1217H. Emergency customers request in relation to Sarangani Energy Corporation - 2 Plant GOMP Shutdown. [WEBSMS] | CMIN
10/17/2023 1:47:11 PM | Mindanao Grid-10/17/2023 13:49: General Santos-Kamanga 138kV L1 deenergized at 1212H. Emergency customers request in relation to Sarangani Energy Corporation - 2 Plant GOMP Shutdown. [WEBSMS] | CMIN
10/17/2023 1:38:39 PM | Luzon Grid-10/17/2023 13:38: Batangas SS PCB 8-02CB04BTN de-energized at 1333H. (Planned Outage) [WEBSMS] | CLUZ
10/17/2023 1:30:02 PM | Mindanao Grid-10/17/2023 13:32: KE Jimenez U2 online at 1301H to facilitate the Ancillary Reserve Test (DR and RPS). Follow RTD. [WEBSMS] | CMIN
10/17/2023 1:26:19 PM | Luzon Grid-10/17/2023 13:26: Batangas SS PCB 8-01CB24BTN restored at 1326H. (Planned Outage) [WEBSMS] | CLUZ
10/17/2023 1:21:24 PM | Mindanao Grid-10/17/2023 13:24: KE Jimenez U2 online at 1301H, to facilitate the Ancillary Reserve Test (DR and RPS). Follow RTD. [WEBSMS] | CMIN
10/17/2023 12:58:20 PM | [NSO Update] Visayas Grid-10/17/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2694MW, PK=2239MW, RR=40MW, NetOpMargin: PM=415, EVE=345 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @112MW, LEYTE A @320MW, PGPP1 @75MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/17/2023 12:50:44 PM | [NSO Update] Luzon Grid-10/17/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13316MW, PK=11377MW, RR=439MW, NetOpMargin: PM=1500, EVE=1333 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MSLC2 @200MW, MSLC3 @310MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/17/2023 12:47:15 PM | [NSO Update] Visayas Grid-10/17/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2694MW, PK=2239MW, RR=40MW, NetOpMargin: PM=415, EVE=345 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @112MW, LEYTE A @310MW, PGPP1 @75MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/17/2023 12:43:07 PM | [NSO Update] Mindanao Grid-10/17/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3143MW, PK=2282MW, RR=70MW, NetOpMargin: PM=792, EVE=819 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @128MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @105MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @31MW, PG4 @140MW [WEBSMS] | CMIN
10/17/2023 11:53:36 AM | Mindanao Grid-10/17/2023 11:56: Bunawan-Maco 138kV L tripped at 10:57:40 H. Auto-Reclosed after 3 sec. Unplanned Outage. [WEBSMS] | CMIN
10/17/2023 11:13:31 AM | Luzon Grid-10/17/2023 11:13: Batangas SS PCB 8-01CB24BTN de-energized at 1112H. (Planned Outage) [WEBSMS] | CLUZ
10/17/2023 11:03:29 AM | Mindanao Grid-10/17/2023 11:06: WMPC DG05 declared available at 1030H, from Forced Outage. [WEBSMS] | CMIN
10/17/2023 10:55:14 AM | Mindanao Grid-10/17/2023 10:58: WMPC DG05 online at 1049H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/17/2023 10:30:55 AM | Mindanao Grid-10/17/2023 10:33: MCC Unit #1 (Minergy Coal Balingasag) online at 1018H from PMS (Non GOMP). Planned Outage. Follow RTD. [WEBSMS] | CMIN
10/17/2023 10:13:34 AM | Mindanao Grid-10/17/2023 10:16: Agus 2 Unit #1 online at 1000H from PMS. Follow RTD. Planned Outage. [WEBSMS] | CMIN
10/17/2023 10:10:43 AM | Mindanao Grid-10/17/2023 10:13: WMPC DG02 online at 0945H, as replacement for WMPC DG05 which is on emergency shutdown due to Cylinder B1 High Pressure Pipe Leak. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/17/2023 10:08:26 AM | Mindanao Grid-10/17/2023 10:11: WMPC DG05 run as RPS, on emergency shutdown at 1001H, due to Cylinder B1 High Pressure Pipe Leak. Unplanned Outage. [WEBSMS] | CMIN
10/17/2023 9:08:43 AM | Mindanao Grid-10/17/2023 09:11: MDP (Mati Diesel) online at 0900H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
10/17/2023 9:00:39 AM | Mindanao Grid-10/17/2023 09:03: WMPC DG05 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/17/2023 8:03:04 AM | Luzon Grid-10/17/2023 08:03: BCCPP SS PCB 8-06CB08BCC de-energized at 0803H. (Planned Outage) [WEBSMS] | CLUZ
10/17/2023 7:10:02 AM | Luzon Grid-10/17/2023 07:10: Lumban-Malaya 230kV Line 1 de-energized at 0709H. (Planned Outage) [WEBSMS] | CLUZ
10/17/2023 6:50:35 AM | Mindanao Grid-10/17/2023 06:53: Nasipit SS 138kV Bus 1 energized at 0632H. (Planned Outage/Non-GOMP) [WEBSMS] | CMIN
10/17/2023 6:35:56 AM | Luzon Grid-10/17/2023 06:36: Lal-lo-Magapit BESS 69kV Line and Lal-lo-Cagayan North Solar 69kV Line 1 & 2 de-energized at 0626H, 0624H and 0631H respectively. (Planned Outage) [WEBSMS] | CLUZ
10/17/2023 6:03:12 AM | [NSO Update] Mindanao Grid-10/17/2023 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3159MW, PK=2161MW, RR=70MW, NetOpMargin: AM=928, PM=814, EVE=849 Highest Unit O/L: GNPK 3&4@ 138MW Derated Plant: MCC @128MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @82MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @31MW, PG4 @170MW [WEBSMS] | CMIN
10/17/2023 6:00:08 AM | [NSO Update] Visayas Grid-10/17/2023 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2537MW, PK=2099MW, RR=40MW, NetOpMargin: AM=398, PM=249, EVE=330 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @112MW, LEYTE A @310MW, PGPP1 @75MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/17/2023 5:53:36 AM | [NSO Update] Luzon Grid-10/17/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13368MW, PK=10813MW, RR=427MW, NetOpMargin: AM=2128, PM=1546, EVE=1249 Highest Unit O/L: GNPD 1@ 668MW Derated Plant: MSLC1 @300MW, MSLC2 @200MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/17/2023 5:22:49 AM | Mindanao Grid-10/17/2023 05:25: Nasipit SS 138kV Bus 1 de-energized at 0515H. (Planned Outage) [WEBSMS] | CMIN
10/17/2023 5:22:06 AM | Mindanao Grid-10/17/2023 05:24: Nasipit - TM2 138kV L2 de-energized at 0508H. (Planned Outage) [WEBSMS] | CMIN
10/17/2023 5:17:31 AM | Luzon Grid-10/17/2023 05:17: Laoag-Pasuquin Solar 115kV Line de-energized at 0517H (Planned Outage) [WEBSMS] | CLUZ
10/17/2023 4:18:19 AM | [NSO Update] Luzon Grid-10/17/2023 04:18: Weather Update: Northeasterly Surface Windflow affecting Northern Luzon. [WEBSMS] | CLUZ
10/17/2023 4:16:29 AM | [NSO Update] Mindanao Grid-10/17/2023 04:19: Weather Update: Northeasterly Surface Windflow affecting Northern Luzon. [WEBSMS] | CMIN
10/17/2023 4:12:58 AM | [NSO Update] Visayas Grid-10/17/2023 04:13: Weather Update: Northeasterly Surface Windflow affecting Northern Luzon. [WEBSMS] | CVIS
10/16/2023 9:16:19 PM | Mindanao Grid-10/16/2023 21:19: WMPC DG09 shutdown at 2113H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/16/2023 8:45:55 PM | Mindanao Grid-10/16/2023 20:48: EURO Hydro (NBT) online at 1610H. Unplanned Outage. [WEBSMS] | CMIN
10/16/2023 7:38:07 PM | Mindanao Grid-10/16/2023 19:40: Kauswagan SS 230kV Bay No. 4 energized at 1936H thru 8-04CB04KSW and 8-24CB24KSW. (Unplanned Outage) [WEBSMS] | CMIN
10/16/2023 7:10:00 PM | Visayas Grid-10/16/2023 19:10: Visayas Spot Peak for October 16, 2023, 2215 MW at 1412H. Highest peak for the year is 2458 MW at 1422H on May 17, 2023 [WEBSMS] | CVIS
10/16/2023 5:44:22 PM | [NSO Update] Luzon Grid-10/16/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12505MW, PK=10529MW, RR=432MW, NetOpMargin: EVE=1545 Highest Unit O/L: GNPD 1@ 668MW Derated Plant: MSLC2 @200MW, SLPGC 2@90MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/16/2023 5:32:17 PM | [NSO Update] Visayas Grid-10/16/2023 17:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2475MW, PK=2087MW, RR=40MW, NetOpMargin: EVE=348 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @97.5MW, LEYTE A @325MW, PGPP1 @74MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/16/2023 5:32:11 PM | [NSO Update] Mindanao Grid-10/16/2023 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3115MW, PK=2199MW, RR=70MW, NetOpMargin: EVE=846 Highest Unit O/L: GNPK 3&4@ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @65MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @170MW [WEBSMS] | CMIN
10/16/2023 5:11:05 PM | Luzon Grid-10/16/2023 17:11: MPGC 2 load reject @75MW (50 percent load) at 1710H (On Commissioning Test) [WEBSMS] | CLUZ
10/16/2023 4:16:31 PM | Mindanao Grid-10/16/2023 16:19: WMPC DG02 shutdown at 1613H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/16/2023 4:07:08 PM | Mindanao Grid-10/16/2023 16:09: Euro Hydro (NBT) with 1.4MW Gross Generation tripped at 1550H, due to NORDECO System voltage fluctuation. Unplanned Outage. [WEBSMS] | CMIN
10/16/2023 1:29:42 PM | Mindanao Grid-10/16/2023 13:32: Supreme Power Mati cut-in at 0944H. (Unplanned Outage) [WEBSMS] | CMIN
10/16/2023 1:28:51 PM | Mindanao Grid-10/16/2023 13:31: Supreme Power Mati tripped with 4MW load at 0923H. (Unplanned Outage). Indication: Reverse Power Alarm. [WEBSMS] | CMIN
10/16/2023 1:04:36 PM | Mindanao Grid-10/16/2023 13:07: WMPC DG02 cut-in at 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/16/2023 1:01:09 PM | Mindanao Grid-10/16/2023 13:03: WMPC DG05 cut-out at 1259H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/16/2023 12:58:30 PM | [NSO Update] Mindanao Grid-10/16/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3118MW, PK=2252MW, RR=70MW, NetOpMargin: PM=796, EVE=827 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @65MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
10/16/2023 12:54:49 PM | [NSO Update] Visayas Grid-10/16/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2631MW, PK=2204MW, RR=40MW, NetOpMargin: PM=386, EVE=315 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @97.5MW, LEYTE A @325MW, PGPP1 @74MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/16/2023 12:51:23 PM | [NSO Update] Luzon Grid-10/16/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13186MW, PK=10762MW, RR=446MW, NetOpMargin: PM=1978, EVE=1782 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MSLC1 @330MW, MSLC2 @200MW, ILIJAN A @510MW, ILIJAN B @230MW [WEBSMS] | CLUZ
10/16/2023 12:39:54 PM | Mindanao Grid-10/16/2023 12:42: NagaMin - Zamboanga 138kV L1 restored at 1226H. (Planned Outage) [WEBSMS] | CMIN
10/16/2023 12:08:04 PM | Mindanao Grid-10/16/2023 12:10: Agus 1 Unit 1 cut-in at 1055H. (Unplanned Outage) [WEBSMS] | CMIN
10/16/2023 11:13:18 AM | Luzon Grid-10/16/2023 11:13: Calaca 2 tripped with 171MW load at 1108H, lowest frequency recorded is 59.453Hz (Unplanned Outage). [WEBSMS] | CLUZ
10/16/2023 10:56:25 AM | Mindanao Grid-10/16/2023 10:59: SEDI (EEI) Unit 2 declared available at 1040H. [WEBSMS] | CMIN
10/16/2023 10:07:40 AM | Mindanao Grid-10/16/2023 10:10: WMPC DG09 cut-in at 0930H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/16/2023 9:45:45 AM | Mindanao Grid-10/16/2023 09:48: WMPC DG05 cut-in at 0930H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/16/2023 9:11:12 AM | Mindanao Grid-10/16/2023 09:13: SEDI (EEI) Unit 2 declared on forced outage at 0850H. Reason: Unable to synchronize Unit 2 to Unit 1 due to different electrical protection system. Troubleshooting on-going. [WEBSMS] | CMIN
10/16/2023 8:57:37 AM | Mindanao Grid-10/16/2023 09:00: WMPC DG09 cut-in at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/16/2023 7:07:03 AM | Mindanao Grid-10/16/2023 07:09: NagaMin - Zamboanga 138kV L1 de-energized at 0705H. (Planned Outage) [WEBSMS] | CMIN
10/16/2023 5:49:32 AM | [NSO Update] Mindanao Grid-10/16/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3156MW, PK=2273MW, RR=70MW, NetOpMargin: AM=813, PM=742, EVE=753 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @170MW [WEBSMS] | CMIN
10/16/2023 5:48:22 AM | [NSO Update] Visayas Grid-10/16/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2471MW, PK=2153MW, RR=40MW, NetOpMargin: AM=278, PM=308, EVE=317 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @97.5MW, LEYTE A @333MW, PGPP1 @74MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/16/2023 4:59:20 AM | [NSO Update] Mindanao Grid-10/16/2023 05:02: Weather Update: Northeasterly Surface Windflow affecting Extreme Northern Luzon. [WEBSMS] | CMIN
10/16/2023 4:59:07 AM | [NSO Update] Visayas Grid-10/16/2023 04:59: Weather Update: Northeasterly Surface Windflow affecting Extreme Northern Luzon. [WEBSMS] | CVIS
10/16/2023 4:58:51 AM | [NSO Update] Luzon Grid-10/16/2023 04:59: Weather Update: Northeasterly Surface Windflow affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
10/16/2023 4:27:46 AM | Luzon Grid-10/16/2023 04:27: Balingueo SS 230kV Bus 2 restored at 0427H (Planned Outage) [WEBSMS] | CLUZ
10/16/2023 3:24:14 AM | Luzon Grid-10/16/2023 03:24: MPGC Unit 2 online at 0321H (Unplanned Outage) [WEBSMS] | CLUZ
10/16/2023 3:21:32 AM | Luzon Grid-10/16/2023 03:21: Angat-San Jose 115kV Line 3 restored at 0319H (Planned Outage) [WEBSMS] | CLUZ
10/16/2023 2:53:24 AM | Luzon Grid-10/16/2023 02:53: Sta. Rita Module 10 online at 0248H (Planned Outage/Fuel Oil Commissioning) [WEBSMS] | CLUZ
10/16/2023 2:52:50 AM | Luzon Grid-10/16/2023 02:53: Sta. Rita Module 10 online at 0248H (Planned Outage/Fuel Oil Commissioning) [WEBSMS] | CLUZ
10/16/2023 2:11:36 AM | Luzon Grid-10/16/2023 02:11: MPGC Unit 2 (51MW) tripped at 0206H. (On Commissioning Test) [WEBSMS] | CLUZ
10/16/2023 1:11:04 AM | Luzon Grid-10/16/2023 01:11: Balingueo SS 230kV Bus 2 de-energized at 0110H (Planned Outage) [WEBSMS] | CLUZ
10/16/2023 12:42:24 AM | Mindanao Grid-10/16/2023 00:45: EEI (SEDI) shutdown at 2345H. Follow RTD. [WEBSMS] | CMIN
10/16/2023 12:38:15 AM | Mindanao Grid-10/16/2023 00:40: Nasipit-TM2 138KV L1 re-energized at 0001H & looped at TM2 side at 0003H after conducting reconnection of loop jumper at tower # 1 per request from TM2 management. From PO / Non-GOMP. [WEBSMS] | CMIN
10/16/2023 12:30:25 AM | Mindanao Grid-10/16/2023 00:33: Bunawan SS 300MVA Transformer # 1 re-energized at 2355H. From P&E shutdown request (ERC approved) under MSUP Stage 1 Schedule 1. [WEBSMS] | CMIN
10/15/2023 11:24:43 PM | Luzon Grid-10/15/2023 23:24: Balingueo SS 230kV Bus 1 restored at 2323H (Planned Outage) [WEBSMS] | CLUZ
10/15/2023 10:51:53 PM | Mindanao Grid-10/15/2023 22:54: Nasipit-TM2 138KV L1 de-energized at 2206H to conduct reconnection of loop jumper at tower # 1 per request from TM2 management. PO / Non-GOMP. [WEBSMS] | CMIN
10/15/2023 10:34:19 PM | Mindanao Grid-10/15/2023 22:37: Nasipit-TM2 138KV L1 de-energized at 2206H to conduct reconnection of loop jumper at tower # 1 per request from TM2 management. Non-GOMP. [WEBSMS] | CMIN
10/15/2023 9:53:25 PM | Mindanao Grid-10/15/2023 21:56: Mt. Apo 3 cut-in at 2149H. (Unplanned Outage) [WEBSMS] | CMIN
10/15/2023 9:35:56 PM | Luzon Grid-10/15/2023 21:36: Bolo-Cayanga 230kV Line 1 energized via Bolo side at 2123H (On Commissioning) [WEBSMS] | CLUZ
10/15/2023 9:27:39 PM | Mindanao Grid-10/15/2023 21:30: Agus 1 Unit 1 declared forced outage at 1713H due to problem with its governor unit. [WEBSMS] | CMIN
10/15/2023 9:26:45 PM | Luzon Grid-10/15/2023 21:26: Bolo-Cayanga 230kV Line 1 energized at 2123H (On Commissioning) [WEBSMS] | CLUZ
10/15/2023 8:51:07 PM | Mindanao Grid-10/15/2023 20:53: (Erratum) Mt. Apo 3 not yet cut-in (still isolated). Declared as forced outage at 1749H. Cause: repair of feed water pump. [WEBSMS] | CMIN
10/15/2023 8:08:27 PM | Luzon Grid-10/15/2023 20:08: Balingueo SS 230kV Bus 1 de-energized at 2004H (Planned Outage) [WEBSMS] | CLUZ
10/15/2023 7:50:07 PM | Luzon Grid-10/15/2023 19:50: Calaca-Malamig (Sta. Rosa) 230kV Line restored at 1948H (Planned Outage) [WEBSMS] | CLUZ
10/15/2023 7:44:48 PM | Mindanao Grid-10/15/2023 19:47: Supreme Power Mati cut-in at 1924H. (Unplanned Outage) [WEBSMS] | CMIN
10/15/2023 7:44:07 PM | Mindanao Grid-10/15/2023 19:46: Supreme Power Mati tripped with 3MW load at 1921H. (Unplanned Outage). Indication: Reverse Power Alarm. [WEBSMS] | CMIN
10/15/2023 7:02:35 PM | Mindanao Grid-10/15/2023 19:05: Mt. Apo 3 cut-in at 1749H. (Unplanned Outage) [WEBSMS] | CMIN
10/15/2023 6:59:01 PM | [NSO Update] Mindanao Grid-10/15/2023 19:01: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1857H with power going to Visayas. (Planned Outage) [WEBSMS] | CMIN
10/15/2023 6:58:09 PM | [NSO Update] Visayas Grid-10/15/2023 18:58: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1857H with power going to Visayas. (Planned Outage) [WEBSMS] | CVIS
10/15/2023 6:27:27 PM | Mindanao Grid-10/15/2023 18:30: Butuan SS Power Transformer # 2 re-energized at 1737H. From Planned Outage / GOMP... [WEBSMS] | CMIN
10/15/2023 6:14:37 PM | [NSO Update] Mindanao Grid-10/15/2023 18:17: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2949MW, PK=2010MW, RR=70MW, NetOpMargin: EVE=869 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @170MW [WEBSMS] | CMIN
10/15/2023 6:12:21 PM | Mindanao Grid-10/15/2023 18:15: Agus 2 - Agus 1 138KV tie-line re-energized at 1743H. From vegetation clearing per request from Agus 1 & 2 Plant management in preparation for 2023 Barangay Election. [WEBSMS] | CMIN
10/15/2023 6:10:19 PM | [NSO Update] Mindanao Grid-10/15/2023 18:13: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1503H from forward power direction. (Planned Outage) [WEBSMS] | CMIN
10/15/2023 6:07:46 PM | [NSO Update] Visayas Grid-10/15/2023 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2513MW, PK=1997MW, RR=40MW, NetOpMargin: EVE=476 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 97.5MW, Leyte A @ 340MW, PGPP1 @ 75MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
10/15/2023 6:04:01 PM | [NSO Update] Luzon Grid-10/15/2023 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12125MW, PK=9643MW, RR=356MW, NetOpMargin: EVE=2126 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 300MW, Masinloc 2 @ 180MW, Ilijan A @ 430MW, Ilijan B @ 190MW [WEBSMS] | CLUZ
10/15/2023 4:48:05 PM | Visayas Grid-10/15/2023 16:48: Compostela-Daanbantayan 230kV Line 2 energized at 1641HH activity completed. (Planned Outage) [WEBSMS] | CVIS
10/15/2023 4:45:16 PM | Mindanao Grid-10/15/2023 16:47: Bunawan SS 138KV busbar # 2 re-energized at 1633H. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
10/15/2023 3:22:06 PM | Mindanao Grid-10/15/2023 15:24: Bislig-Nabunturan 138KV line re-energized at 1449H & looped at Nabunturan SS at 1450H. From Planned Outage / GOMP. [WEBSMS] | CMIN
10/15/2023 3:09:24 PM | [NSO Update] Visayas Grid-10/15/2023 15:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1503H from forward power direction. (Planned Outage) [WEBSMS] | CVIS
10/15/2023 3:08:55 PM | [NSO Update] Visayas Grid-10/15/2023 15:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1503H from forward power direction. (Planned Outage) [WEBSMS] | CVIS
10/15/2023 3:06:05 PM | Luzon Grid-10/15/2023 15:06: San Jose-Taytay 230kV Line 2 restored at 1505H (Planned Outage) [WEBSMS] | CLUZ
10/15/2023 1:17:14 PM | Mindanao Grid-10/15/2023 13:19: Bunawan SS 138KV Busbar # 2 de-energized at 1305H. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
10/15/2023 1:08:44 PM | Mindanao Grid-10/15/2023 13:11: Agus 4 Unit 3 cut-in at 1306H. (Unplanned Outage) [WEBSMS] | CMIN
10/15/2023 1:00:43 PM | Luzon Grid-10/15/2023 13:00: MPGC 2 online at 1258H (On commissioning test) [WEBSMS] | CLUZ
10/15/2023 12:55:50 PM | [NSO Update] Luzon Grid-10/15/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12683MW, PK=9554MW, RR=356MW, NetOpMargin: PM=2773, EVE=1709 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Calaca 2 @ 175MW, Masinloc 1 @ 280MW, Masinloc 2 @ 130MW, Ilijan A @ 430MW, Ilijan B @ 130MW [WEBSMS] | CLUZ
10/15/2023 12:54:00 PM | [NSO Update] Mindanao Grid-10/15/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2872MW, PK=1856MW, RR=69MW, NetOpMargin: PM=947, EVE=793 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG2 @90MW, AG4 @50MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
10/15/2023 12:52:27 PM | [NSO Update] Visayas Grid-10/15/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2439MW, PK=1847MW, RR=40MW, NetOpMargin: PM=551, EVE=435 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 97.5MW, Leyte A @ 333MW, PGPP1 @ 74MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
10/15/2023 12:45:15 PM | Luzon Grid-10/15/2023 12:45: MPGC 2 load reject @37.5MW (25% load) at 1242H (On Commissioning Test) [WEBSMS] | CLUZ
10/15/2023 12:30:30 PM | Luzon Grid-10/15/2023 12:30: Correction: Gumaca - Labo 230kV L2 restored at 1226H (Unplanned Outage) [WEBSMS] | CLUZ
10/15/2023 12:29:20 PM | Luzon Grid-10/15/2023 12:29: Gumaca - Labo 230kV L2 restored at 1226H (Planned Outage) [WEBSMS] | CLUZ
10/15/2023 12:27:14 PM | Mindanao Grid-10/15/2023 12:29: Mt. Apo 3 shutdown at 1212H. (Unplanned Outage). Affected by maintenance activity at Kidapawan SS re: paralleling of Xmer U1 & U2. [WEBSMS] | CMIN
10/15/2023 11:55:44 AM | Mindanao Grid-10/15/2023 11:58: Agus 4 Unit 3 tripped with 38.6MW load at 1100H. Lowest frequency recorded was 59.65Hz. (Unplanned Outage). Cause: Turbine guide bearing temp high, broken shear pin. [WEBSMS] | CMIN
10/15/2023 11:51:07 AM | Mindanao Grid-10/15/2023 11:53: SEDI (EEI) cut-in at 1036H. (Unplanned Outage) [WEBSMS] | CMIN
10/15/2023 11:50:26 AM | Mindanao Grid-10/15/2023 11:53: SEDI (EEI) tripped with 4MW load at 1025H. (Unplanned Outage). Cause: its mechanical-type governor cannot coup with the dynamic changes of system frequency. [WEBSMS] | CMIN
10/15/2023 11:40:00 AM | Luzon Grid-10/15/2023 11:40: For info: San Lorenzo Module 60 completed the fuel changeover from oil to gas at 1136H. [WEBSMS] | CLUZ
10/15/2023 10:44:05 AM | Mindanao Grid-10/15/2023 10:46: Agus 4 Unit 3 cut-in at 1040H. (Unplanned Outage) [WEBSMS] | CMIN
10/15/2023 10:44:02 AM | Luzon Grid-10/15/2023 10:44: For information: San Lorenzo Module 50 completed the fuel changeover from oil to gas at 1038H. [WEBSMS] | CLUZ
10/15/2023 10:36:40 AM | Mindanao Grid-10/15/2023 10:39: SEDI (EEI) cut-in at 1010H. (Unplanned Outage) [WEBSMS] | CMIN
10/15/2023 10:36:02 AM | Mindanao Grid-10/15/2023 10:38: SEDI (EEI) tripped with 2.3MW load at 0955H. (Unplanned Outage). Cause: Stocked-up flowmeter of bunker. [WEBSMS] | CMIN
10/15/2023 9:06:06 AM | Mindanao Grid-10/15/2023 09:08: Agus 2 - Agus 1 138KV tie-line de-energized at 0820H to conduct vegetation clearing per request from Agus 1 & 2 Plant management in preparation for 2023 Barangay Election. [WEBSMS] | CMIN
10/15/2023 8:38:05 AM | Mindanao Grid-10/15/2023 08:40: Agus 4 Unit 3 tripped with 20W load at 0821H. Lowest frequency recorded was 59.69Hz. (Unplanned Outage). Indication: Turbine bearing high temp. [WEBSMS] | CMIN
10/15/2023 8:33:11 AM | [NSO Update] Mindanao Grid-10/15/2023 08:35: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0830H with power going to Visayas. (Planned Outage) [WEBSMS] | CMIN
10/15/2023 8:32:53 AM | [NSO Update] Visayas Grid-10/15/2023 08:33: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0830H with power going to Visayas. (Planned Outage) [WEBSMS] | CVIS
10/15/2023 8:08:14 AM | Mindanao Grid-10/15/2023 08:10: Agus 1 HEP Unit 1 shutdown at 0805H. (Unplanned Outage - Non-GOMP). To implement clearing of Agus 1 - Agus 2 138kV Tie Line. [WEBSMS] | CMIN
10/15/2023 7:14:38 AM | Mindanao Grid-10/15/2023 07:17: Bislig-Nabunturan 138KV line de-energized at 0705H. Planned Outage / GOMP. [WEBSMS] | CMIN
10/15/2023 7:11:36 AM | Luzon Grid-10/15/2023 07:11: Calaca-Malamig (Sta. Rosa) 230kV Line de-energized at 0711H (Planned Outage) [WEBSMS] | CLUZ
10/15/2023 7:04:20 AM | Luzon Grid-10/15/2023 07:04: Lamao 230kV Bus 2 restored at 0659H (Planned Outage) [WEBSMS] | CLUZ
10/15/2023 6:52:42 AM | Mindanao Grid-10/15/2023 06:55: Butuan SS Power Transformer # 2 de-energized at 0627H to conduct APMS activities. Planned Outage / GOMP... [WEBSMS] | CMIN
10/15/2023 6:21:57 AM | Visayas Grid-10/15/2023 06:22: Compostela-Daanbantayan 230kV Line 2 de-energized at 0620H. (Planned Outage) [WEBSMS] | CVIS
10/15/2023 6:17:46 AM | [NSO Update] Luzon Grid-10/15/2023 06:17: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13072MW, PK=9319MW, RR=356MW, NetOpMargin: AM=3397, PM=2766, EVE=1676 Highest Unit O/L: GNPD 1 @668MW Derated Plant: CLC2 @175MW, MSLC1 @325MW, MSLC2 @130MW, ILIJAN A @430MW, ILIJAN B @190MW [WEBSMS] | CLUZ
10/15/2023 6:12:56 AM | Luzon Grid-10/15/2023 06:13: Angat-San Jose 115kV Line 3 de-energized at 0607H (Planned Outage) [WEBSMS] | CLUZ
10/15/2023 5:44:00 AM | [NSO Update] Mindanao Grid-10/15/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3065MW, PK=1823MW, RR=66MW, NetOpMargin: AM=1177, PM=1091, EVE=736 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @170MW [WEBSMS] | CMIN
10/15/2023 5:42:15 AM | [NSO Update] Visayas Grid-10/15/2023 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2551MW, PK=1751MW, RR=40MW, NetOpMargin: AM=759, PM=604, EVE=451 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @333MW, PGPP1 @74MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/15/2023 5:40:38 AM | Mindanao Grid-10/15/2023 05:43: TSI Unit #1 online at 2031H. Unplanned Outage [WEBSMS] | CMIN
10/15/2023 4:51:20 AM | Mindanao Grid-10/15/2023 04:54: Lake Mainit HEP online at 0426H. Unplanned Outage. [WEBSMS] | CMIN
10/15/2023 4:47:23 AM | Luzon Grid-10/15/2023 04:47: For information: Sta. Rita Module 20 completed the fuel changeover from oil to gas at 0409H. [WEBSMS] | CLUZ
10/15/2023 4:46:13 AM | [NSO Update] Luzon Grid-10/15/2023 04:46: Weather Update: Northeasterly Surface Windflow affecting Northern Luzon. [WEBSMS] | CLUZ
10/15/2023 4:28:45 AM | [NSO Update] Mindanao Grid-10/15/2023 04:31: Weather Update: Northeasterly Surface Windflow affecting Northern Luzon. [WEBSMS] | CMIN
10/15/2023 4:28:32 AM | [NSO Update] Visayas Grid-10/15/2023 04:28: Weather Update: Northeasterly Surface Windflow affecting Northern Luzon. [WEBSMS] | CVIS
10/15/2023 4:25:31 AM | Luzon Grid-10/15/2023 04:25: Lamao 230kV Bus 2 de-energized at 0424H (Planned Outage) [WEBSMS] | CLUZ
10/15/2023 4:21:18 AM | Mindanao Grid-10/15/2023 04:24: Lake Mainit HEP with 10.7MW gross generation tripped at 0410H. Indication: 50BF. Unplanned Outage. [WEBSMS] | CMIN
10/15/2023 3:34:54 AM | Luzon Grid-10/15/2023 03:35: Lamao 230kV Bus 1 restored at 0330H (Planned Outage) [WEBSMS] | CLUZ
10/15/2023 3:21:52 AM | Luzon Grid-10/15/2023 03:22: Gumaca - Labo 230kV L2 tripped at 0319H (Unplanned Outage) [WEBSMS] | CLUZ
10/15/2023 3:08:56 AM | Luzon Grid-10/15/2023 03:09: SLPGC Unit 2 online at 0250H (Unplanned Outage) [WEBSMS] | CLUZ
10/15/2023 3:04:36 AM | Mindanao Grid-10/15/2023 03:07: TSI Unit #1 with 65MW Gross Generation tripped at 2001H. Indication: Instrument Air Pressure Low Low. Unplanned Outage. [WEBSMS] | CMIN
10/15/2023 12:15:03 AM | Luzon Grid-10/15/2023 00:15: Lamao 230kV Bus 1 - de-energized at 0010H. (Planned Outage) [WEBSMS] | CLUZ
10/14/2023 10:45:00 PM | Luzon Grid-10/14/2023 22:45: Ilijan GT1-1 - online at 2243H. (Unplanned Outage) [WEBSMS] | CLUZ
10/14/2023 8:52:15 PM | Luzon Grid-10/14/2023 20:52: GNPD Unit 2 with 148MW load tripped at 2047H. (Unplanned Outage). The lowest system frequency is 59.57Hz. [WEBSMS] | CLUZ
10/14/2023 7:04:16 PM | Luzon Grid-10/14/2023 19:04: Nagsaag 600MVA T01 - restored at 1902H. (Planned Outage) [WEBSMS] | CLUZ
10/14/2023 6:53:27 PM | Luzon Grid-10/14/2023 18:53: Ilijan GT2-1 with 128MW tripped at 1850H. (Unplanned Outage) [WEBSMS] | CLUZ
10/14/2023 6:46:10 PM | [NSO Update] Luzon Grid-10/14/2023 18:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12212MW, PK=10082MW, RR=406MW, NetOpMargin: EVE=1724 Highest Unit O/L: Sual 2 @ 647MW Derated Plant: Calaca 2 @ 175MW, GNPD 1 @ 640MW, GNPD 2 @ 334MW, Masinloc 1 @ 325MW, Masinloc 2 @ 300MW, Ilijan A @ 190MW, Ilijan B @ 430MW, San Gabriel @ 240MW, Sta. Rita 20 @ 235MW [WEBSMS] | CLUZ
10/14/2023 6:36:37 PM | Luzon Grid-10/14/2023 18:36: Binan 300MVA T03 was restored at 1836H. (Planned Outage) [WEBSMS] | CLUZ
10/14/2023 6:33:16 PM | Luzon Grid-10/14/2023 18:33: MPGC Unit 2 online at 1831H. (Testing and Commissioning) [WEBSMS] | CLUZ
10/14/2023 6:07:53 PM | [NSO Update] Mindanao Grid-10/14/2023 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3100MW, PK=2099MW, RR=70MW, NetOpMargin: EVE=931 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @170MW [WEBSMS] | CMIN
10/14/2023 5:59:29 PM | [NSO Update] Visayas Grid-10/14/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2487MW, PK=2076MW, RR=40MW, NetOpMargin: EVE=370 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @74MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/14/2023 5:04:22 PM | Luzon Grid-10/14/2023 17:04: MPGC Unit 2 conducted Load Rejection Test(LRT) from 38MW load at 1701H (Plant Commissioning Test) [WEBSMS] | CLUZ
10/14/2023 4:57:27 PM | Luzon Grid-10/14/2023 16:57: Sta Rita Module 30 - shutdown at 1652H (Unplanned Outage) [WEBSMS] | CLUZ
10/14/2023 4:48:57 PM | Visayas Grid-10/14/2023 16:49: Colon - Dumanjug 138 kV Line 2 energized at 1647H. (Planned Outage) [WEBSMS] | CVIS
10/14/2023 4:09:56 PM | Luzon Grid-10/14/2023 16:09: San Lorenzo Module 60 online at 1559H (Unplanned Outage) [WEBSMS] | CLUZ
10/14/2023 3:10:30 PM | Mindanao Grid-10/14/2023 15:13: WMPC DG10 shutdown at 1507H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/14/2023 2:44:39 PM | Luzon Grid-10/14/2023 14:44: Test Advisory [WEBSMS] | CLUZ
10/14/2023 1:22:26 PM | [NSO Update] Visayas Grid-10/14/2023 13:20: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2473MW, PK=2101MW, RR=40MW, NetOpMargin: PM=333, EVE=356 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 325MW, PGPP1 @ 74MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
10/14/2023 12:49:34 PM | [NSO Update] Luzon Grid-10/14/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13160MW, PK=10485MW, RR=430MW, NetOpMargin: PM=2245, EVE=1606 Highest Unit O/L: Sual 2 @ 647MW Derated Plant: Calaca 2 @ 175MW, GNPD 1 @ 630MW, GNPD 2 @ 334MW, Masinloc 1 @ 325MW, Masinloc 2 @ 325MW, Ilijan A @ 190MW, Ilijan B @ 430MW, San Gabriel @ 300MW, Sta. Rita 20 @ 235MW [WEBSMS] | CLUZ
10/14/2023 12:45:14 PM | [NSO Update] Mindanao Grid-10/14/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3103MW, PK=2004MW, RR=70MW, NetOpMargin: PM=1029, EVE=959 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
10/14/2023 11:16:47 AM | Luzon Grid-10/14/2023 11:16: MPGC 2 online at 1115H (On Commissioning Test) [WEBSMS] | CLUZ
10/14/2023 10:46:01 AM | Mindanao Grid-10/14/2023 10:48: WMPC DG10 cut-in at 0950H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/14/2023 7:58:15 AM | Luzon Grid-10/14/2023 07:58: San Jose-Taytay 230kV Line 2 de-energized at 0757H (Planned Outage) [WEBSMS] | CLUZ
10/14/2023 7:39:10 AM | Mindanao Grid-10/14/2023 07:41: Bunawan SS 300 MVA Power Transformer No. 1 de-energized at 0733H. (Planned Outage) [WEBSMS] | CMIN
10/14/2023 7:34:04 AM | Luzon Grid-10/14/2023 07:34: Binan 300MVA T03 de-energized at 0733H (Planned Outage) [WEBSMS] | CLUZ
10/14/2023 7:31:15 AM | Visayas Grid-10/14/2023 07:31: Colon - Dumanjug 138 kV Line 2 de-energized at 0730H. (Planned Outage) [WEBSMS] | CVIS
10/14/2023 6:53:42 AM | Luzon Grid-10/14/2023 06:53: Nagsaag 600MVA T01 de-energized at 0649H (Planned Outage) [WEBSMS] | CLUZ
10/14/2023 6:03:52 AM | [NSO Update] Mindanao Grid-10/14/2023 06:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0600H from forward power direction. (Planned Outage) [WEBSMS] | CMIN
10/14/2023 6:03:35 AM | [NSO Update] Visayas Grid-10/14/2023 06:03: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0600H from forward power direction. (Planned Outage) [WEBSMS] | CVIS
10/14/2023 5:39:42 AM | [NSO Update] Mindanao Grid-10/14/2023 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3136MW, PK=1991MW, RR=70MW, NetOpMargin: AM=1075, PM=1027, EVE=963 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @170MW [WEBSMS] | CMIN
10/14/2023 5:37:05 AM | [NSO Update] Visayas Grid-10/14/2023 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2513MW, PK=2021MW, RR=40MW, NetOpMargin: AM=451, PM=333, EVE=357 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @114.5MW, LEYTE A @325MW, PGPP1 @74MW, TPC (Carmen) @30MW [WEBSMS] | CVIS
10/14/2023 5:35:31 AM | [NSO Update] Luzon Grid-10/14/2023 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13301MW, PK=10430MW, RR=406MW, NetOpMargin: AM=2465, PM=1804, EVE=1521 Highest Unit O/L: SUAL 2 @647MW Derated Plant: CLC2 @175MW, GNPD 1 @580MW, GNPD 2 @334MW, MSLC1 @300MW, MSLC2 @315MW, ILIJAN A @190MW, ILIJAN B @430MW, SAN GABRIEL @320MW, STA. RITA 20 @235MW [WEBSMS] | CLUZ
10/14/2023 4:53:16 AM | [NSO Update] Mindanao Grid-10/14/2023 04:55: Weather Update: Northeasterly Surface Windflow affecting Northern Luzon. [WEBSMS] | CMIN
10/14/2023 4:52:47 AM | [NSO Update] Visayas Grid-10/14/2023 04:52: Weather Update: Northeasterly Surface Windflow affecting Northern Luzon. [WEBSMS] | CVIS
10/14/2023 4:52:27 AM | [NSO Update] Luzon Grid-10/14/2023 04:52: Weather Update: Northeasterly Surface Windflow affecting Northern Luzon. [WEBSMS] | CLUZ
10/14/2023 3:11:24 AM | Visayas Grid-10/14/2023 03:11: Mandaue-Paknaan 69 kV Feeder 5 energized at 0300H. (Planned Outage) [WEBSMS] | CVIS
10/14/2023 3:09:59 AM | Visayas Grid-10/14/2023 03:10: Mandaue NRA 69 kV Feeder 4 energized at 0259H. (Planned Outage) [WEBSMS] | CVIS
10/14/2023 3:05:24 AM | Visayas Grid-10/14/2023 03:05: Mandaue - Guizo 69 kV Feeder 2 energized at 0259H. (Planned Outage) [WEBSMS] | CVIS
10/14/2023 3:03:15 AM | Visayas Grid-10/14/2023 03:03: Mandaue NRA 69 kV Feeder 1 energized at 0258H. (Planned Outage) [WEBSMS] | CVIS
10/14/2023 2:05:30 AM | Mindanao Grid-10/14/2023 02:08: Butuan-San Francisco 138KV line re-energized at 0154H & looped at Butuan SS at 0155H. From Planned Outage / Non-GOMP... [WEBSMS] | CMIN
10/14/2023 1:54:21 AM | Mindanao Grid-10/14/2023 01:57: AGC online at 0141H. From FO. (Unplanned Outage) [WEBSMS] | CMIN
10/14/2023 1:26:42 AM | Mindanao Grid-10/14/2023 01:29: AGC tripped with 10.7MW load at 0117H. Indication: 50BF. [WEBSMS] | CMIN
10/14/2023 12:49:38 AM | Mindanao Grid-10/14/2023 00:52: GNPK U4 online at 0041H. (Unplanned Outage) [WEBSMS] | CMIN
10/14/2023 12:40:06 AM | Luzon Grid-10/14/2023 00:40: For info: Sta. Rita Module 50 completed the fuel changeover from gas to oil at 0028H due to gas supply restriction. [WEBSMS] | CLUZ
10/14/2023 12:37:08 AM | Mindanao Grid-10/14/2023 00:39: Butuan-San Francisco 138KV line de-energized at 0004H to facilitate hotspot correction of phase B loop connector at tower # 159 located inside San Francisco SS. Planned Outage / Non-GOMP... [WEBSMS] | CMIN
10/13/2023 11:59:48 PM | Luzon Grid-10/13/2023 23:59: For info: Sta. Rita Module 20 completed the fuel changeover from gas to oil at 2355H due to gas supply restriction. [WEBSMS] | CLUZ
10/13/2023 11:39:40 PM | Luzon Grid-10/13/2023 23:39: Sual Unit 1 shutdown at 2338H (Planned Outage) [WEBSMS] | CLUZ
10/13/2023 11:08:27 PM | Visayas Grid-10/13/2023 23:08: Mandaue Guizo 69 kV Feeder 2 de-energized at 2304H. (Planned Outage) [WEBSMS] | CVIS
10/13/2023 11:07:20 PM | Visayas Grid-10/13/2023 23:07: Mandaue NRA 69 kV Feeder 1 de-energized at 2303H. (Planned Outage) [WEBSMS] | CVIS
10/13/2023 9:16:01 PM | Mindanao Grid-10/13/2023 21:18: WMPC DG10 shutdown at 2113H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/13/2023 8:17:33 PM | Luzon Grid-10/13/2023 20:17: Botolan-Labrador 230kV Line 1 auto-tripped/auto-reclosed at 2012H (Unplanned Outage) [WEBSMS] | CLUZ
10/13/2023 5:53:15 PM | [NSO Update] Luzon Grid-10/13/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12809MW, PK=10704MW, RR=406MW, NetOpMargin: EVE=1699 Highest Unit O/L: SUAL 2 @647MW Derated Plant: CLC2 @175MW, GNPD 1 @400MW, GNPD 2 @334MW, MSLC1 @300MW, MSLC2 @315MW, ILIJAN A @169MW, ILIJAN B @600MW [WEBSMS] | CLUZ
10/13/2023 5:50:04 PM | Luzon Grid-10/13/2023 17:50: Nagsaag SS PCB 8Z-04CB08NGS restored at 1746H (Planned Outage) [WEBSMS] | CLUZ
10/13/2023 5:42:47 PM | [NSO Update] Mindanao Grid-10/13/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2831MW, PK=2122MW, RR=70MW, NetOpMargin: EVE=639 Highest Unit O/L: GNPK 3 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @170MW [WEBSMS] | CMIN
10/13/2023 5:39:21 PM | [NSO Update] Visayas Grid-10/13/2023 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2450MW, PK=2175MW, RR=50MW, NetOpMargin: EVE=225 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @330MW, PGPP1 @74MW, TPC-CARMEN@30MW [WEBSMS] | CVIS
10/13/2023 5:05:21 PM | Luzon Grid-10/13/2023 17:05: Nagsaag SS PCB 8Z-04CB08NGS de-energized at 1703H (Planned Outage) [WEBSMS] | CLUZ
10/13/2023 4:54:43 PM | Mindanao Grid-10/13/2023 16:57: Kibawe-Davao 138KV L2 re-energized at 1636H & looped at Davao SS at 1637H. From Planned Outage / GOMP... [WEBSMS] | CMIN
10/13/2023 4:53:36 PM | Visayas Grid-10/13/2023 16:53: Naga - CD1 TR2/CD1 TR1 138 KV lines energized at 1630H/1632H, activity completed. (Unplanned Outage) [WEBSMS] | CVIS
10/13/2023 4:49:44 PM | Mindanao Grid-10/13/2023 16:52: Villanueva SS 230KV Busbar # 2 re-energized at 1621H. From Planned Outage / Non-GOMP... [WEBSMS] | CMIN
10/13/2023 4:15:29 PM | Mindanao Grid-10/13/2023 16:18: WMPC DG07 shutdown at 1613H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/13/2023 3:55:37 PM | Luzon Grid-10/13/2023 15:55: Binga SS PCB 8-01CB04BIZ restored at 1554H (Planned Outage) [WEBSMS] | CLUZ
10/13/2023 2:12:33 PM | Luzon Grid-10/13/2023 14:12: Naga-Tiwi C 230kV Line 2 restored at 1412H (Planned Outage) [WEBSMS] | CLUZ
10/13/2023 2:08:44 PM | Luzon Grid-10/13/2023 14:08: Tiwi C SS 230kV Bus 1 restored at 1408H (Planned Outage) [WEBSMS] | CLUZ
10/13/2023 1:18:08 PM | Visayas Grid-10/13/2023 13:18: Carcon - Sangi 34.5 kV Line 3 energized at 1315H. (Planned Outage) [WEBSMS] | CVIS
10/13/2023 12:59:12 PM | [NSO Update] Mindanao Grid-10/13/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2962MW, PK=2179MW, RR=70MW, NetOpMargin: PM=713, EVE=769 Highest Unit O/L: GNPK 3@138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
10/13/2023 12:55:42 PM | [NSO Update] Visayas Grid-10/13/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2555MW, PK=2259MW, RR=50MW, NetOpMargin: PM=246, EVE=289 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @80.3MW, LEYTE A @330MW, PGPP1 @74MW, TPC-CARMEN@30MW [WEBSMS] | CVIS
10/13/2023 12:51:32 PM | [NSO Update] Luzon Grid-10/13/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13711MW, PK=11344MW, RR=436MW, NetOpMargin: PM=1931, EVE=1994 Highest Unit O/L: SUAL 2 @647MW Derated Plant: CALACA 2 @175MW, GNPD 2 @334MW, MASINLOC 1 @300MW, MASINLOC 2 @315MW, SUAL 1 @590MW, ILIJAN A @170MW [WEBSMS] | CLUZ
10/13/2023 12:47:45 PM | Mindanao Grid-10/13/2023 12:50: Kauswagan SS 230KV Busbar # 2 restored at 1128H with clearance from MTD-A. Indication: 87B. From Unplanned Outage. [WEBSMS] | CMIN
10/13/2023 11:26:15 AM | Luzon Grid-10/13/2023 11:26: Limay-Batangas II (BPC) 230kV Line 2 restored at 1126H (Planned Outage) [WEBSMS] | CLUZ
10/13/2023 11:23:57 AM | Visayas Grid-10/13/2023 11:24: Mandaue GIS 100 MVA 138/69 kV TR2 in parallel with TR1 at 1119H. (Planned Outage) [WEBSMS] | CVIS
10/13/2023 11:18:28 AM | Mindanao Grid-10/13/2023 11:21: Kauswagan SS 230KV Busbar # 2 tripped at 1028H. Indications to follow. Unplanned Outage. [WEBSMS] | CMIN
10/13/2023 11:04:15 AM | Mindanao Grid-10/13/2023 11:06: WMPC DG07 online at 1054H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/13/2023 10:51:25 AM | Mindanao Grid-10/13/2023 10:54: GN Power Unit #4 with 90MW Gross Generation Tripped at 102859H. Initial Indication: Furnace Flame not Detected. Frequency Dip=59.142Hz. No UFR/ALD actuated. Unplanned Outage. [WEBSMS] | CMIN
10/13/2023 9:43:39 AM | Mindanao Grid-10/13/2023 09:46: Villanueva SS 230KV Busbar # 2 de-energized at 0922H. Planned Outage / Non-GOMP... [WEBSMS] | CMIN
10/13/2023 9:38:31 AM | Mindanao Grid-10/13/2023 09:41: Kibawe-Davao 138KV L2 de-energized at 0908H for installation of Line Surge Arrester/s by MD5 TL personnel. Planned Outage / GOMP... [WEBSMS] | CMIN
10/13/2023 9:16:43 AM | Mindanao Grid-10/13/2023 09:19: MDP (Mati Diesel) online at 0900H. MO dispatched/Follow RTD, [WEBSMS] | CMIN
10/13/2023 9:04:49 AM | Mindanao Grid-10/13/2023 09:07: WMPC DG10 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
10/13/2023 9:00:27 AM | Visayas Grid-10/13/2023 09:00: Naga - CD1 TR1/CD1 TR2 138 KV lines de-energized at 0832H/0845H. (Unplanned Outage) [WEBSMS] | CVIS
10/13/2023 8:19:24 AM | Luzon Grid-10/13/2023 08:19: Limay-Batangas II (BPC) 230kV Line 2 de-energized at 0819H (Planned Outage) [WEBSMS] | CLUZ
10/13/2023 7:55:57 AM | Visayas Grid-10/13/2023 07:56: Carcon - Sangi 34.5 kV Line 3 de-energized at 0741H. (Planned Outage) [WEBSMS] | CVIS
10/13/2023 7:48:33 AM | Visayas Grid-10/13/2023 07:48: Calatrava SS 230 kV Bus 1 and 100 MVA 230/69 kV TR2 energized at 0725H and 0743H. (Unplanned Outage) [WEBSMS] | CVIS
10/13/2023 7:17:34 AM | Visayas Grid-10/13/2023 07:17: Toledo SS 40 MVA 138/34.5 kV TR2 de-energized at 0715H. (Planned Outage) [WEBSMS] | CVIS
10/13/2023 7:13:03 AM | Luzon Grid-10/13/2023 07:13: Pagudpud Wind Farm (NLREC) SS PCB 6-01CB04PWF de-energized at 0711H (Planned Outage) [WEBSMS] | CLUZ
10/13/2023 6:54:13 AM | Visayas Grid-10/13/2023 06:54: Magdugo - Calatrava 230 kV Line 1 energized at 0649H from Magdugo SS without load. (Magdugo Reactor 1 under observation - Unplanned Outage) [WEBSMS] | CVIS
10/13/2023 6:28:55 AM | Luzon Grid-10/13/2023 06:29: Tiwi C SS 230kV Bus 1 de-energized at 0627H (Planned Outage) [WEBSMS] | CLUZ
10/13/2023 6:26:56 AM | Luzon Grid-10/13/2023 06:27: Naga-Tiwi C 230kV Line 2 de-energized at 0624H (Planned Outage) [WEBSMS] | CLUZ
10/13/2023 5:52:39 AM | Mindanao Grid-10/13/2023 05:55: Baloi-Agus 4 138kv L1 and Baloi-Agus 6 138 kV L1 restored/energized 0550H and 0551H, respectively. (Planned outage). [WEBSMS] | CMIN
10/13/2023 5:41:35 AM | [NSO Update] Luzon Grid-10/13/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13885MW, PK=10971MW, RR=442MW, NetOpMargin: AM=2471, PM=2072, EVE=1991 Highest Unit O/L: SUAL 2 @647MW Derated Plant: CALACA 2 @175MW, GNPD 2 @334MW, MASINLOC 1 @300MW, MASINLOC 2 @315MW, SUAL 1 @590MW, ILIJAN A @170MW [WEBSMS] | CLUZ
10/13/2023 5:38:45 AM | [NSO Update] Visayas Grid-10/13/2023 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2556MW, PK=2233MW, RR=50MW, NetOpMargin: AM=273, PM=206, EVE=248 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @99.5MW, LEYTE A @330MW, PGPP1 @74MW, TPC-CARMEN@30MW [WEBSMS] | CVIS
10/13/2023 5:35:35 AM | [NSO Update] Mindanao Grid-10/13/2023 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3148MW, PK=2169MW, RR=70MW, NetOpMargin: AM=908, PM=864, EVE=963 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @29MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @170MW [WEBSMS] | CMIN
10/13/2023 5:33:34 AM | [NSO Update] Luzon Grid-10/13/2023 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13885MW, PK=10971MW, RR=442MW, NetOpMargin: AM=2471, PM=2072, EVE=1991 Highest Unit O/L: SUAL 2 @ 647MW Derated Plant: CALACA 1 @175MW, GNPD 2 @334MW, MASINLOC 1 @300MW, MASINLOC 2 @315MW, SUAL 1 @590MW, ILIJAN A @170MW [WEBSMS] | CLUZ
10/13/2023 5:32:36 AM | [NSO Update] Visayas Grid-10/13/2023 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2556MW, PK=2233MW, RR=50MW, NetOpMargin: AM=273, PM=206, EVE=248 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @99.5MW, LEYTE A @341MW, PGPP1 @74MW, TPC-CARMEN@30MW [WEBSMS] | CVIS
10/13/2023 4:03:58 AM | [NSO Update] Luzon Grid-10/13/2023 04:04: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 305 km West of Puerto Princesa City, Palawan (9.6�N, 116.0�E). [WEBSMS] | CLUZ
10/13/2023 4:03:49 AM | [NSO Update] Visayas Grid-10/13/2023 04:03: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 305 km West of Puerto Princesa City, Palawan (9.6�N, 116.0�E). [WEBSMS] | CVIS
10/13/2023 4:03:41 AM | [NSO Update] Mindanao Grid-10/13/2023 04:06: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 305 km West of Puerto Princesa City, Palawan (9.6�N, 116.0�E). [WEBSMS] | CMIN
10/13/2023 3:49:06 AM | Mindanao Grid-10/13/2023 03:51: Baloi-Agus 4 138kv L1 and Baloi-Agus 6 138 kV L1 de-energized 0341H and 0345H, respectively. (Planned outage). [WEBSMS] | CMIN
10/13/2023 12:43:30 AM | Luzon Grid-10/13/2023 00:43: GNPD Unit 1 online at 0030H (Planned Outage) [WEBSMS] | CLUZ
10/13/2023 12:34:18 AM | Luzon Grid-10/13/2023 00:34: Calaca Unit 2 on-line at 0030H (Unplanned Outage) [WEBSMS] | CLUZ
10/13/2023 12:33:26 AM | Mindanao Grid-10/13/2023 00:36: NBT tripped with 1.3MW load at 2300H Due to NORDECO system loss of power(brownout). [WEBSMS] | CMIN
10/12/2023 11:54:39 PM | Visayas Grid-10/12/2023 23:54: Naga-CD1TR2/CD1TR1 138 KV lines energized at 2352H/2350H. (Unplanned Outage) [WEBSMS] | CVIS
10/12/2023 11:07:47 PM | Mindanao Grid-10/12/2023 23:10: Bislig-San Francisco 138kV line auto tripped 22:53:34H and auto reclosed 22:53:36H. (Unplanned outage). [WEBSMS] | CMIN
10/12/2023 9:26:06 PM | Mindanao Grid-10/12/2023 21:28: WMPC DG10 shutdown at 2113H, from RPS-System Voltage Requirements. [WEBSMS] | CMIN
10/12/2023 9:10:38 PM | Luzon Grid-10/12/2023 21:10: Malaya Unit 2 shutdown at 2110H. (Planned Outage) [WEBSMS] | CLUZ
10/12/2023 6:21:48 PM | Visayas Grid-10/12/2023 18:21: Magdugo-Calatrava 230KV Line 1 & 2 tripped at 18013H. load involved Line 1 load 17.7MW. Under assessment [WEBSMS] | CVIS
10/12/2023 5:53:34 PM | [NSO Update] Luzon Grid-10/12/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12897MW, PK=10618MW, RR=429MW, NetOpMargin: EVE=1850 Highest Unit O/L: SUAL 2 @647MW Derated Plant: GNPD 2 @334MW, MSLC1 @300MW, MSLC2 @325MW, SUAL 1 @590MW, ILIJAN A @169MW [WEBSMS] | CLUZ
10/12/2023 5:48:53 PM | [NSO Update] Visayas Grid-10/12/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2615MW, PK=2233MW, RR=40MW, NetOpMargin: EVE=342 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @330MW, PGPP1 @74MW [WEBSMS] | CVIS
10/12/2023 5:46:52 PM | [NSO Update] Mindanao Grid-10/12/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3125MW, PK=2232MW, RR=70MW, NetOpMargin: EVE=824 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @170MW [WEBSMS] | CMIN
10/12/2023 4:18:40 PM | Mindanao Grid-10/12/2023 16:21: Villanueva SS 230kV Bus 1 restored/energized 1611H (planned outage) [WEBSMS] | CMIN
10/12/2023 4:16:49 PM | Mindanao Grid-10/12/2023 16:19: WMPC DG07 shutdown at 1613H, from RPS-System Voltage Requirements. [WEBSMS] | CMIN
10/12/2023 4:12:33 PM | Luzon Grid-10/12/2023 16:12: BCCPP SS PCB 8-02CB08BCC restored at 1611H. (Planned Outage) [WEBSMS] | CLUZ
10/12/2023 3:56:43 PM | Mindanao Grid-10/12/2023 15:59: Matanao SS 138kV Bus 2 restored/energized 1553H (planned outage) [WEBSMS] | CMIN
10/12/2023 3:34:19 PM | Luzon Grid-10/12/2023 15:34: San Jose - Angat 115kV Line 2 restored at 1532H. (Unplanned Outage) [WEBSMS] | CLUZ
10/12/2023 3:32:52 PM | Luzon Grid-10/12/2023 15:32: Santiago SS PCB 8-02CB04SAN restored at 1532H. (Planned Outage) [WEBSMS] | CLUZ
10/12/2023 2:50:37 PM | Luzon Grid-10/12/2023 14:50: Batangas SS PCB 8-01CB08BTN restored at 1435H (Planned Outage) [WEBSMS] | CLUZ
10/12/2023 2:06:26 PM | Luzon Grid-10/12/2023 14:06: San Jose - Angat 115kV Line 2 tripped at 1404H. (Unplanned Outage) [WEBSMS] | CLUZ
10/12/2023 2:02:33 PM | Mindanao Grid-10/12/2023 14:05: Baloi SS 230kV Transformer 2 restored/energized 1359H (planned outage). [WEBSMS] | CMIN
10/12/2023 1:31:50 PM | Visayas Grid-10/12/2023 13:31: Mandaue GIS. 100 MVA TR2 energized at 1312H. (Planned Outage) [WEBSMS] | CVIS
10/12/2023 1:23:37 PM | Mindanao Grid-10/12/2023 13:26: KET cut-in at 1301H. For Generating Unit Capability Test(GUCT). Follow RTD. [WEBSMS] | CMIN
10/12/2023 1:08:34 PM | [NSO Update] Mindanao Grid-10/12/2023 13:11: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3159MW, PK=2289MW, RR=70MW, NetOpMargin: PM=800, EVE=839 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @170MW [WEBSMS] | CMIN
10/12/2023 1:05:03 PM | [NSO Update] Visayas Grid-10/12/2023 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2600MW, PK=2260MW, RR=40MW, NetOpMargin: PM=300, EVE=308 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @81MW, LEYTE A @320MW, PGPP1 @74MW [WEBSMS] | CVIS
10/12/2023 12:59:45 PM | [NSO Update] Luzon Grid-10/12/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13641MW, PK=11189MW, RR=434MW, NetOpMargin: PM=2018, EVE=2121 Highest Unit O/L: SUAL 2 @647MW Derated Plant: GNPD 2 @334MW, MSLC1 @330MW, MSLC2 @330MW, SUAL 1 @590MW, ILIJAN A @240MW [WEBSMS] | CLUZ
10/12/2023 12:09:18 PM | Luzon Grid-10/12/2023 12:09: Batangas SS PCB 8-01CB08BTN de-energized at 1208H (Planned Outage) [WEBSMS] | CLUZ
10/12/2023 11:55:01 AM | Luzon Grid-10/12/2023 11:55: Batangas SS PCB 8-01CB04BTN restored at 1152H (Planned Outage) [WEBSMS] | CLUZ
10/12/2023 11:44:14 AM | Mindanao Grid-10/12/2023 11:46: Bislig SS Power Transformer 2 restored/energized 1142H (Planned outage) [WEBSMS] | CMIN
10/12/2023 10:59:03 AM | Mindanao Grid-10/12/2023 11:01: WMPC DG7 online as RPS at 1050H. For RPS. System Voltage Requirement. [WEBSMS] | CMIN
10/12/2023 10:02:11 AM | Mindanao Grid-10/12/2023 10:04: Bislig SS Power Transformer 2 de-energized 0957H (Planned outage). [WEBSMS] | CMIN
10/12/2023 9:34:21 AM | Mindanao Grid-10/12/2023 09:36: AGC online at 0923H. (Unplanned Outage) [WEBSMS] | CMIN
10/12/2023 9:30:13 AM | Luzon Grid-10/12/2023 09:30: Batangas SS PCB 8-01CB04BTN de-energized at 0930H (Planned Outage) [WEBSMS] | CLUZ
10/12/2023 9:19:58 AM | Mindanao Grid-10/12/2023 09:22: AGC tripped with 10.7MW load at 0909H. Indication: 50LBB / 50BF. (Unplanned Outage). [WEBSMS] | CMIN
10/12/2023 9:05:27 AM | Mindanao Grid-10/12/2023 09:08: Matanao SS 138kV Bus 2 de-energized 0902H (planned outage). [WEBSMS] | CMIN
10/12/2023 9:00:09 AM | Mindanao Grid-10/12/2023 09:02: Villanueva SS 230kV Bus 1 de-energized 0845H (planned outage). [WEBSMS] | CMIN
10/12/2023 8:52:57 AM | Mindanao Grid-10/12/2023 08:55: WMPC DG10 Online as RPS at 0850H. For RPS. System Voltage Requirement. [WEBSMS] | CMIN
10/12/2023 8:42:11 AM | Mindanao Grid-10/12/2023 08:44: Baloi SS 230kV Transformer 2 de-energized 0832H (planned ouatge). [WEBSMS] | CMIN
10/12/2023 8:18:46 AM | Luzon Grid-10/12/2023 08:18: BCCPP SS PCB 8-02CB08BCC de-energized at 0816H (Planned Outage) [WEBSMS] | CLUZ
10/12/2023 8:12:41 AM | Luzon Grid-10/12/2023 08:12: Santiago SS PCB 8-02CB04SAN de-energized at 0810H (Planned Outage) [WEBSMS] | CLUZ
10/12/2023 8:07:38 AM | Mindanao Grid-10/12/2023 08:10: Kauswagan - GNPK 230kV L1 de-energized at 0803H (Planned outage). [WEBSMS] | CMIN
10/12/2023 8:00:07 AM | Mindanao Grid-10/12/2023 08:02: MA3 tripped with 3.2MW load at 0747H. Affected by the tripping of 5LI1KID-BGN. (Unplanned Outage). [WEBSMS] | CMIN
10/12/2023 6:38:02 AM | Mindanao Grid-10/12/2023 06:40: Nasipit-APTM2 138 kV L1 restored/energized 1633H at Nasipit SS side only. (Planned outage) [WEBSMS] | CMIN
10/12/2023 6:14:24 AM | Luzon Grid-10/12/2023 06:14: Balsik PCB 9-01CB08BIK - de-energized at 0613H (Planned Outage) [WEBSMS] | CLUZ
10/12/2023 6:04:23 AM | Mindanao Grid-10/12/2023 06:06: Davao SS 138kV Transformer No. 3 energized at 0557H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
10/12/2023 6:02:02 AM | [NSO Update] Luzon Grid-10/12/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13770MW, PK=11093MW, RR=434MW, NetOpMargin: AM=2242, PM=1662, EVE=1844 Highest Unit O/L: SUAL 2 @647MW Derated Plant: GNPD 2 @334MW, MSLC1 @330MW, MSLC2 @330MW, SLPGC 1 @110MW, SUAL 1 @590MW, ILIJAN A @240MW, ILIJAN B @510MW [WEBSMS] | CLUZ
10/12/2023 5:45:18 AM | [NSO Update] Mindanao Grid-10/12/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3273MW, PK=2125MW, RR=70MW, NetOpMargin: AM=1079, PM=993, EVE=1029 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @170MW [WEBSMS] | CMIN
10/12/2023 5:43:43 AM | [NSO Update] Visayas Grid-10/12/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2712MW, PK=2164MW, RR=40MW, NetOpMargin: AM=507, PM=261, EVE=326 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @99.5MW, LEYTE A @341MW, PGPP1 @74MW [WEBSMS] | CVIS
10/12/2023 5:17:41 AM | Mindanao Grid-10/12/2023 05:20: Nasipit-APTM2 138 kV L1 deenergized at 0440H. GOMP shutdown requested by TM2. [WEBSMS] | CMIN
10/12/2023 5:05:11 AM | Mindanao Grid-10/12/2023 05:07: Davao SS 138kV Transformer No. 3 deenergized at 0431H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
10/12/2023 4:43:41 AM | [NSO Update] Mindanao Grid-10/12/2023 04:46: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 860 km East of Eastern Visayas (11.9 N, 133.6 E). Meanwhile, another LPA was estimated based on all available at 135 km West of Coron, Palawan (11.8 N, 119.0 E). [WEBSMS] | CMIN
10/12/2023 4:43:22 AM | [NSO Update] Visayas Grid-10/12/2023 04:43: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 860 km East of Eastern Visayas (11.9 N, 133.6 E). Meanwhile, another LPA was estimated based on all available at 135 km West of Coron, Palawan (11.8 N, 119.0 E). [WEBSMS] | CVIS
10/12/2023 4:43:06 AM | [NSO Update] Luzon Grid-10/12/2023 04:43: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 860 km East of Eastern Visayas (11.9 N, 133.6 E). Meanwhile, another LPA was estimated based on all available at 135 km West of Coron, Palawan (11.8 N, 119.0 E). [WEBSMS] | CLUZ
10/12/2023 2:41:53 AM | Luzon Grid-10/12/2023 02:41: Amadeo 300MVA T3(Customer Owned) was energized at 0227H (Planned Outage) [WEBSMS] | CLUZ
10/12/2023 12:51:18 AM | Luzon Grid-10/12/2023 00:51: Amadeo 300MVA T3(Customer Owned) was de-energized at 0044H (Planned Outage) [WEBSMS] | CLUZ
10/12/2023 12:02:58 AM | Mindanao Grid-10/12/2023 00:05: SEC U2 shutdown at 2359H, to facilitate PMS. Planned Outage. [WEBSMS] | CMIN
10/11/2023 9:16:10 PM | Mindanao Grid-10/11/2023 21:18: WMPC DG10 shutdown as RPS at 2113H. From RPS. System Voltage Requirement. [WEBSMS] | CMIN
10/11/2023 8:03:03 PM | Mindanao Grid-10/11/2023 20:05: AGC U3 tripped with 5.5MW load at 1955H. Indication: Emergency Relay KT1 Trip. [WEBSMS] | CMIN
10/11/2023 7:33:02 PM | Mindanao Grid-10/11/2023 19:35: AGC synchronized back at 1929H. From FO. [WEBSMS] | CMIN
10/11/2023 7:25:16 PM | Mindanao Grid-10/11/2023 19:27: ASG tripped with a load of 7.5MW at 1914H. Due to voltage fluctuation. [WEBSMS] | CMIN
10/11/2023 7:18:40 PM | Mindanao Grid-10/11/2023 19:21: AGC tripped with 10.7MW load at 1914H. Indication: Undervoltage trip. [WEBSMS] | CMIN
10/11/2023 5:57:47 PM | [NSO Update] Mindanao Grid-10/11/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3257MW, PK=2136MW, RR=70MW, NetOpMargin: EVE=1051 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @170MW [WEBSMS] | CMIN
10/11/2023 5:50:26 PM | [NSO Update] Visayas Grid-10/11/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2477MW, PK=2112MW, RR=40MW, NetOpMargin: EVE=325 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @102.5MW, LEYTE A @325MW, PGPP1 @74MW [WEBSMS] | CVIS
10/11/2023 5:48:58 PM | [NSO Update] Luzon Grid-10/11/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12907MW, PK=10772MW, RR=406MW, NetOpMargin: EVE=1729 Highest Unit O/L: SUAL 2 @647MW Derated Plant: GNPD 2 @334MW, MSLC1 @330MW, MSLC2 @330MW, SLPGC 1 @70MW, SLTEC 1 @118MW, SUAL 1 @590MW, ILIJAN A @300MW, ILIJAN B @430MW [WEBSMS] | CLUZ
10/11/2023 5:20:43 PM | Luzon Grid-10/11/2023 17:20: Santiago PCB 8-02CB24SAN - energized at 1719H. (Planned Outage) [WEBSMS] | CLUZ
10/11/2023 4:16:14 PM | Mindanao Grid-10/11/2023 16:18: WMPC DG7 shutdown as RPS at 1614H. From RPS. System Voltage Requirement. [WEBSMS] | CMIN
10/11/2023 3:47:43 PM | Mindanao Grid-10/11/2023 15:50: Baloi-Villanueva 230 kV Line 2 energized at 1540H, Planned Outage/GOMP. [WEBSMS] | CMIN
10/11/2023 2:38:36 PM | Luzon Grid-10/11/2023 14:38: Ilijan GT2-1 online at 1436H (Unplanned Outage) [WEBSMS] | CLUZ
10/11/2023 2:22:05 PM | Luzon Grid-10/11/2023 14:22: BCCPP S/S PCB 8-02CB24BCC energized at 1421H (Planned Outage) [WEBSMS] | CLUZ
10/11/2023 1:32:26 PM | Luzon Grid-10/11/2023 13:32: Bay S/S PCB 8-06CB24BYZ energized at 1331H (Planned Outage) [WEBSMS] | CLUZ
10/11/2023 1:03:41 PM | Mindanao Grid-10/11/2023 13:06: KE Tandag Online at 1301H. For Generating Unit Capability Test(GUCT). Follow RTD. [WEBSMS] | CMIN
10/11/2023 12:54:12 PM | [NSO Update] Mindanao Grid-10/11/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3239MW, PK=2186MW, RR=70MW, NetOpMargin: PM=983, EVE=1011 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @26MW, AG6 @149MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
10/11/2023 12:51:13 PM | [NSO Update] Visayas Grid-10/11/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2651MW, PK=2155MW, RR=40MW, NetOpMargin: PM=456, EVE=350 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @ 102.5MW, Leyte A @ 330MW, PGPP1 @ 74MW [WEBSMS] | CVIS
10/11/2023 12:50:28 PM | Luzon Grid-10/11/2023 12:50: Gamu PCB 8-03CB04GAM and PCB 8-03CB24GAM restored at 1247H & 1248H, respectively. (Planned Outage) [WEBSMS] | CLUZ
10/11/2023 12:48:50 PM | [NSO Update] Luzon Grid-10/11/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13400MW, PK=11454MW, RR=446MW, NetOpMargin: PM=1501, EVE=1665 Highest Unit O/L: SUAL 2@647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 1 @ 330MW, Masinloc 2 @ 330MW, SLTEC 1 @ 118MW, Sual 1 @ 590MW, SLPGC 1@70MW, ILIJAN A @290MW, ILIJAN B @295MW [WEBSMS] | CLUZ
10/11/2023 11:51:22 AM | Luzon Grid-10/11/2023 11:51: Concepcion SS PCB 8-04CB04CON restored at 1150H (Planned Outage) [WEBSMS] | CLUZ
10/11/2023 11:44:06 AM | Luzon Grid-10/11/2023 11:44: Ilijan ST1 online at 1140H (Unplanned Outage) [WEBSMS] | CLUZ
10/11/2023 11:03:10 AM | Mindanao Grid-10/11/2023 11:05: TSI U1 Online at 1100H. (Planned Outage) [WEBSMS] | CMIN
10/11/2023 10:52:21 AM | Mindanao Grid-10/11/2023 10:54: WMPC DG7 Online as RPS at 1050H. For RPS. System Voltage Requirement. [WEBSMS] | CMIN
10/11/2023 10:48:08 AM | Visayas Grid-10/11/2023 10:48: Naga-CD1TR1/CD1TR2 138 KV line de-energized at 1021H/1031H. (Unplanned Outage) [WEBSMS] | CVIS
10/11/2023 10:43:41 AM | Luzon Grid-10/11/2023 10:43: Correction: lijan GT1-2 online at 1039H (Unplanned Outage) [WEBSMS] | CLUZ
10/11/2023 10:41:30 AM | Luzon Grid-10/11/2023 10:41: Ilijan GT1-2 online at 0850H (Unplanned Outage) [WEBSMS] | CLUZ
10/11/2023 9:58:19 AM | Luzon Grid-10/11/2023 09:58: Bay SS PCB 8-06CB24BYZ de-energized at 0956H (Planned Outage) [WEBSMS] | CLUZ
10/11/2023 9:17:20 AM | Mindanao Grid-10/11/2023 09:19: MDP(Supreme Mati) online at 0900H. Follow RTD. [WEBSMS] | CMIN
10/11/2023 8:54:46 AM | Luzon Grid-10/11/2023 08:54: Concepcion SS PCB 8-04CB04CON de-energized at 0852H (Planned Outage) [WEBSMS] | CLUZ
10/11/2023 8:53:24 AM | Luzon Grid-10/11/2023 08:53: Ilijan ST2 online at 0850H (Unplanned Outage) [WEBSMS] | CLUZ
10/11/2023 8:52:27 AM | Mindanao Grid-10/11/2023 08:55: WMPC DG10 Online as RPS at 0850H. For RPS. System Voltage Requirement. [WEBSMS] | CMIN
10/11/2023 8:33:02 AM | Luzon Grid-10/11/2023 08:33: BCCPP SS PCB 8-02CB24BCC de-energized at 0831H (Planned Outage) [WEBSMS] | CLUZ
10/11/2023 8:23:40 AM | Mindanao Grid-10/11/2023 08:26: Baloi-Villanueva 230 kV Line 2 deenergized at 0806H, Planned Outage/GOMP. [WEBSMS] | CMIN
10/11/2023 8:19:22 AM | Mindanao Grid-10/11/2023 08:21: Talomo1 U1 cut-out at 0803H. For PMS. Follow RTD. [WEBSMS] | CMIN
10/11/2023 8:13:47 AM | Luzon Grid-10/11/2023 08:13: Gamu PCB 8-03CB04GAM and PCB 8-03CB24GAM de-energized at 0811H and 0812H, respectively. (Planned Outage) [WEBSMS] | CLUZ
10/11/2023 8:03:48 AM | Luzon Grid-10/11/2023 08:03: Santiago PCB 8-02CB24SAN de-energized at 0802H (Planned Outage) [WEBSMS] | CLUZ
10/11/2023 7:39:45 AM | Luzon Grid-10/11/2023 07:39: Ilijan GT2-2 online at 0739H (Unplanned Outage) [WEBSMS] | CLUZ
10/11/2023 6:44:42 AM | Visayas Grid-10/11/2023 06:44: Colon-Magdugo 138 KV Line 1 at Colon substation CB energized at 0643H. (Unplanned Outage) [WEBSMS] | CVIS
10/11/2023 6:36:39 AM | Visayas Grid-10/11/2023 06:36: Colon-Magdugo 138 KV Line 1 at Colon substation CB tripped at 0625H. (Unplanned Outage) [WEBSMS] | CVIS
10/11/2023 5:47:32 AM | [NSO Update] Luzon Grid-10/11/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13154MW, PK=11557MW, RR=446MW, NetOpMargin: AM=1151, PM=1014, EVE=1161 Highest Unit O/L: Sual 2 @ 647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 1 @ 330MW, Masinloc 2 @ 330MW, SLTEC 1 @ 118MW, Sual 1 @ 580MW [WEBSMS] | CLUZ
10/11/2023 5:43:23 AM | [NSO Update] Mindanao Grid-10/11/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3300MW, PK=2170MW, RR=70MW, NetOpMargin: AM=1060, PM=972, EVE=932 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @45MW, AG6 @149MW, AG7 @34MW, PG4 @170MW [WEBSMS] | CMIN
10/11/2023 5:41:37 AM | [NSO Update] Visayas Grid-10/11/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2722MW, PK=2052MW, RR=40MW, NetOpMargin: AM=630, PM=305, EVE=295 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TGPP @ 102.5MW, Leyte A @ 332MW, PGPP1 @ 74MW [WEBSMS] | CVIS
10/11/2023 4:18:05 AM | [NSO Update] Luzon Grid-10/11/2023 04:18: Weather Update: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 750 km East of Guiuan, Eastern Samar (9.8�N, 132.5�E). [WEBSMS] | CLUZ
10/11/2023 4:16:35 AM | [NSO Update] Mindanao Grid-10/11/2023 04:19: Weather Update: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 750 km East of Guiuan, Eastern Samar (9.8�N, 132.5�E). [WEBSMS] | CMIN
10/11/2023 4:16:13 AM | [NSO Update] Visayas Grid-10/11/2023 04:16: Weather Update: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 750 km East of Guiuan, Eastern Samar (9.8�N, 132.5�E). [WEBSMS] | CVIS
10/11/2023 3:48:07 AM | Luzon Grid-10/11/2023 03:48: Taytay (Dolores) SS 300MVA T03 energized at 0347H (Planned Outage) [WEBSMS] | CLUZ
10/11/2023 3:37:55 AM | Mindanao Grid-10/11/2023 03:40: Agusan Lake Mainit Hydro cut-in at 0331H. (Unplanned Outage) [WEBSMS] | CMIN
10/11/2023 3:22:21 AM | Mindanao Grid-10/11/2023 03:25: Agusan Lake Mainit Hydro tripped with 10.5MW load at 0316H. Indication: Power Signal Fault (Unplanned Outage) [WEBSMS] | CMIN
10/11/2023 1:08:15 AM | Luzon Grid-10/11/2023 01:08: Ilijan B G2-2 shutdown at 0103H (Unplanned Outage) [WEBSMS] | CLUZ
10/11/2023 12:56:06 AM | Luzon Grid-10/11/2023 00:56: Ilijan B ST-1 shutdown at 0054H (Unplanned Outage) [WEBSMS] | CLUZ
10/11/2023 12:53:56 AM | Luzon Grid-10/11/2023 00:54: Ilijan Ilijan ST A1 and GT A1-2 shutdown at 0024H and 0035H , respectively (Unplanned Outage) [WEBSMS] | CLUZ
10/10/2023 11:25:36 PM | Luzon Grid-10/10/2023 23:25: Nagsaag - San Manuel 230kV Line 1 restored at 2319H (Planned Outage) [WEBSMS] | CLUZ
10/10/2023 10:57:25 PM | Mindanao Grid-10/10/2023 23:00: GN Power (GKP) Unit 2 cut-out at 2253H - reserve shutdown. [WEBSMS] | CMIN
10/10/2023 9:22:44 PM | Luzon Grid-10/10/2023 21:22: Taytay (Dolores) SS 300MVA T03 at 2122H (Planned Outage) [WEBSMS] | CLUZ
10/10/2023 9:16:02 PM | Mindanao Grid-10/10/2023 21:18: WMPC DG10 shutdown as RPS at 2114H. From RPS. System voltage Requirement. [WEBSMS] | CMIN
10/10/2023 9:15:14 PM | Luzon Grid-10/10/2023 21:15: Nagsaag-San Manuel 230kV Line 1 de-energized at 2115H (Planned Outage) [WEBSMS] | CLUZ
10/10/2023 5:55:52 PM | [NSO Update] Mindanao Grid-10/10/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3086MW, PK=2139MW, RR=70MW, NetOpMargin: EVE=877 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @45MW, AG6 @149MW, AG7 @34MW, PG4 @150MW [WEBSMS] | CMIN
10/10/2023 5:50:18 PM | [NSO Update] Visayas Grid-10/10/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2519MW, PK=2054MW, RR=40MW, NetOpMargin: EVE=426 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @105.5MW, LEYTE A @335MW, PGPP1 @73.5MW [WEBSMS] | CVIS
10/10/2023 5:46:30 PM | [NSO Update] Luzon Grid-10/10/2023 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12396MW, PK=10840MW, RR=406MW, NetOpMargin: EVE=1151 Highest Unit O/L: Sual 2 @647MW Derated Plant: GNPD2 @334MW, MSLC2 @325MW, SLPGC 1 @145MW, SLTEC 1 @115MW, SUAL 1 @580MW, ILIJAN A @169MW, ILIJAN B @165MW [WEBSMS] | CLUZ
10/10/2023 4:48:39 PM | Mindanao Grid-10/10/2023 16:51: Correction/Additional Info: NBT(Euro Hydro) tripped with a load of 1.3MW at 1140H due to NORDECO system voltage fluctuation. (Unplanned Outage) [WEBSMS] | CMIN
10/10/2023 3:29:21 PM | Luzon Grid-10/10/2023 15:29: Bay PCB 8-07CB24BYZ energized at 1529H (Planned Outage). [WEBSMS] | CLUZ
10/10/2023 3:27:25 PM | Mindanao Grid-10/10/2023 15:30: AG5 U1 online at 1519H. (Planned Outage) [WEBSMS] | CMIN
10/10/2023 3:23:14 PM | Luzon Grid-10/10/2023 15:23: BCCPP PCB 8-04CB04BCC energized at 1523H (Planned Outage) [WEBSMS] | CLUZ
10/10/2023 2:51:05 PM | Luzon Grid-10/10/2023 14:51: Gamu PCBs 8-03CB04GAM and 8-03CB24GAM(No line/equipment involved) were energized at 1450H (Planned Outage) [WEBSMS] | CLUZ
10/10/2023 2:45:14 PM | Visayas Grid-10/10/2023 14:45: Colon-KSPC 138kV Line 2 energized at 1442H. (Planned Outage) [WEBSMS] | CVIS
10/10/2023 2:03:55 PM | Mindanao Grid-10/10/2023 14:06: ASG online at 1345H. From FO. [WEBSMS] | CMIN
10/10/2023 1:46:54 PM | Mindanao Grid-10/10/2023 13:49: AGC online at 1340H. From FO. Follow RTD. [WEBSMS] | CMIN
10/10/2023 1:28:27 PM | Luzon Grid-10/10/2023 13:28: Dasmarinas-Ilijan 500KV line was restored at 1328H. (Unplanned Outage) [WEBSMS] | CLUZ
10/10/2023 12:57:57 PM | Luzon Grid-10/10/2023 12:58: Dasmarinas-Ilijan 500kV line - tripped at 1252H. (Unplanned Outage) [WEBSMS] | CLUZ
10/10/2023 12:55:33 PM | [NSO Update] Luzon Grid-10/10/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13397MW, PK=11418MW, RR=446MW, NetOpMargin: PM=1533, EVE=1520 Highest Unit O/L: Sual 2 @647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 2 @ 325MW, SLPGC 1 @ 140MW, SLTEC 1 @115MW, Sual 1 @ 580MW, Ilijan A @ 169MW, Ilijan B @ 165MW, Calaca 1 @ 162MW [WEBSMS] | CLUZ
10/10/2023 12:35:35 PM | Mindanao Grid-10/10/2023 12:38: NBT tripped with a load of 1.3MW at 1140H. Unplanned outage. [WEBSMS] | CMIN
10/10/2023 12:34:55 PM | [NSO Update] Visayas Grid-10/10/2023 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2707MW, PK=2249MW, RR=40MW, NetOpMargin: PM=418, EVE=377 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @105.5MW, LEYTE A @329MW, PGPP1 @73.5MW [WEBSMS] | CVIS
10/10/2023 12:34:44 PM | Mindanao Grid-10/10/2023 12:37: ASG tripped with a load of 6MW at 1227H. Affected/Isolated after the tripping of 5LI1BUT-SNT. [WEBSMS] | CMIN
10/10/2023 12:34:03 PM | Mindanao Grid-10/10/2023 12:36: AGC Tripped with a load of 10.5MW at 1227H. Affected/Isolated after the tripping of 5LI1BUT-SNT. [WEBSMS] | CMIN
10/10/2023 12:32:50 PM | [NSO Update] Mindanao Grid-10/10/2023 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3094MW, PK=2242MW, RR=70MW, NetOpMargin: PM=782, EVE=790 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @26MW, AG6 @149MW, AG7 @34MW, PG4 @150MW [WEBSMS] | CMIN
10/10/2023 12:05:53 PM | Luzon Grid-10/10/2023 12:06: Bay PCB 8-07CB24BYZ - de-energized at 1204H (Planned Outage) [WEBSMS] | CLUZ
10/10/2023 12:02:20 PM | Luzon Grid-10/10/2023 12:02: Bay PCB 8-07CB08BYZ - energized at 1200H. (Planned Outage) [WEBSMS] | CLUZ
10/10/2023 10:52:46 AM | Mindanao Grid-10/10/2023 10:55: Davao-Bunawan 138kV Line 2 restored/energized 1050H (Planned outage). [WEBSMS] | CMIN
10/10/2023 10:52:33 AM | Mindanao Grid-10/10/2023 10:55: WMPC DG7 online as RPS at 1050H. For RPS. System Voltage Requirement. [WEBSMS] | CMIN
10/10/2023 10:43:33 AM | Luzon Grid-10/10/2023 10:43: Concepcion PCB 8-03CB24CON - de-energized at 1042H. (Planned Outage) [WEBSMS] | CLUZ
10/10/2023 10:33:23 AM | Luzon Grid-10/10/2023 10:33: Concepcion PCB 8-03CB04CON - re-energized at 1032H (Planned Outage) [WEBSMS] | CLUZ
10/10/2023 10:21:22 AM | Mindanao Grid-10/10/2023 10:24: EEI/SEDI/MAGDBNK Online at 1006H For Load Testing. Follow RTD. [WEBSMS] | CMIN
10/10/2023 9:53:27 AM | Mindanao Grid-10/10/2023 09:56: AG5 U1 Shutdown at 0803H. For PMS (Unplanned Outage). [WEBSMS] | CMIN
10/10/2023 9:50:27 AM | Luzon Grid-10/10/2023 09:50: Bay PCB 8-07CB08BYZ was de-energized at 0949H. (Planned Outage) [WEBSMS] | CLUZ
10/10/2023 9:34:33 AM | Mindanao Grid-10/10/2023 09:37: MF1 U2 Online at 0818H Follow RTD. [WEBSMS] | CMIN
10/10/2023 8:53:45 AM | Mindanao Grid-10/10/2023 08:56: WMPC DG10 online as RPS at 0851H. For RPS. System Voltage Requirement. [WEBSMS] | CMIN
10/10/2023 8:51:33 AM | Luzon Grid-10/10/2023 08:51: Concepcion PCB 8-03CB04CON was de-energized at 0850H. (Planned Outage) [WEBSMS] | CLUZ
10/10/2023 8:38:42 AM | Luzon Grid-10/10/2023 08:38: Gamu PCBs 8-03CB04GAM and 8-03CB24GAM(No line/equipment involved) were de-energized at 0836H.(Planned Outage) [WEBSMS] | CLUZ
10/10/2023 8:05:43 AM | Mindanao Grid-10/10/2023 08:08: Davao-Bunawan 138kV Line 2 de-energized 0801H. Planned outage [WEBSMS] | CMIN
10/10/2023 8:05:03 AM | Luzon Grid-10/10/2023 08:05: BCCPP PCB 8-04CB04BCC was de-energized at 0802H. (Planned Outage) [WEBSMS] | CLUZ
10/10/2023 6:46:31 AM | Luzon Grid-10/10/2023 06:46: San Jose 115kV Bus 1 - energized at 0645H (Planned Outage) [WEBSMS] | CLUZ
10/10/2023 6:14:46 AM | Luzon Grid-10/10/2023 06:15: Pagbilao Unit 3 online at 0612H. (Unplanned Outage) [WEBSMS] | CLUZ
10/10/2023 5:55:39 AM | [NSO Update] Mindanao Grid-10/10/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3103MW, PK=2213MW, RR=70MW, NetOpMargin: AM=820, PM=640, EVE=738 Highest Unit O/L: GNPK 2, 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @26MW, AG6 @149MW, AG7 @34MW, PG4 @150MW [WEBSMS] | CMIN
10/10/2023 5:50:40 AM | [NSO Update] Visayas Grid-10/10/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2765MW, PK=2234MW, RR=40MW, NetOpMargin: AM=491, PM=368, EVE=265 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @ 105.5MW, Leyte A @ 329MW, PGPP1 @ 73.5MW [WEBSMS] | CVIS
10/10/2023 5:45:24 AM | [NSO Update] Luzon Grid-10/10/2023 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13187MW, PK=11170MW, RR=446MW, NetOpMargin: AM=1571, PM=1089, EVE=1029 Highest Unit O/L: Sual 2 @647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 2 @ 325MW, SLPGC 1 @ 120MW, SLTEC 1 @115MW, Sual 1 @ 580MW, Ilijan A @ 169MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
10/10/2023 4:19:41 AM | [NSO Update] Mindanao Grid-10/10/2023 04:22: Weather Update: Trough of a Low Pressure Area (LPA) affecting Visayas and Mindanao. [WEBSMS] | CMIN
10/10/2023 4:18:36 AM | [NSO Update] Visayas Grid-10/10/2023 04:18: Weather Update: Trough of a Low Pressure Area (LPA) affecting Visayas and Mindanao. [WEBSMS] | CVIS
10/10/2023 4:17:03 AM | [NSO Update] Luzon Grid-10/10/2023 04:17: at 0400H Weather Update: Trough of a Low Pressure Area (LPA) affecting Visayas and Mindanao. [WEBSMS] | CLUZ
10/10/2023 1:07:46 AM | Mindanao Grid-10/10/2023 01:10: GN Power Unit #2 online at 0105H from reserved shutdown. Follow RTD. [WEBSMS] | CMIN
10/9/2023 9:19:37 PM | Mindanao Grid-10/09/2023 21:22: WMPC DG10 Shutdown as RPS at 2114H. From RPS. System Voltage Requirement. [WEBSMS] | CMIN
10/9/2023 9:10:28 PM | Mindanao Grid-10/09/2023 21:13: MDP (Supreme Power Mati) tripped with 5.3MW load at 2014H. Isolated due to tripping of Pintatagan Switching Station(Pintatagan Section of 5LI1MAC-BNY). [WEBSMS] | CMIN
10/9/2023 6:30:36 PM | Mindanao Grid-10/09/2023 18:33: MN1 U1 online at 1721H. (Unplanned Outage) [WEBSMS] | CMIN
10/9/2023 6:29:15 PM | Mindanao Grid-10/09/2023 18:32: MN1 U2 tripped with 6.2MW load at 1644H due to heavy flood and clog-up trash rack.. (Unplanned Outage) [WEBSMS] | CMIN
10/9/2023 6:28:16 PM | Mindanao Grid-10/09/2023 18:31: MN1 U1 tripped with 6.2MW load at 1644H due to heavy flood and clog-up trash rack.. (Unplanned Outage) [WEBSMS] | CMIN
10/9/2023 6:06:24 PM | Luzon Grid-10/09/2023 18:06: San Jose SS 115kV Bus 1 de-energized at 1806H. (Planned Outage) [WEBSMS] | CLUZ
10/9/2023 6:05:30 PM | Mindanao Grid-10/09/2023 18:08: Lugait 138/69/13.8 kV T2 (75MVA) energized at 1757H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
10/9/2023 5:50:04 PM | [NSO Update] Mindanao Grid-10/09/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2952MW, PK=2265MW, RR=70MW, NetOpMargin: EVE=617 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @35MW, PG4 @145MW [WEBSMS] | CMIN
10/9/2023 5:45:17 PM | [NSO Update] Luzon Grid-10/09/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11978MW, PK=10860MW, RR=440MW, NetOpMargin: EVE=678 Highest Unit O/L: Sual 2 @647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 2 @ 325MW, Masinloc 3 @ 310MW, Sual 1 @ 550MW, Ilijan A @ 169MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
10/9/2023 4:19:13 PM | Mindanao Grid-10/09/2023 16:22: NSD Shutdown at 1600H Follow RTD. [WEBSMS] | CMIN
10/9/2023 4:18:01 PM | Mindanao Grid-10/09/2023 16:20: WMPC DG8 as RPS Shutdown at 1614H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/9/2023 2:38:45 PM | Mindanao Grid-10/09/2023 14:41: PSF U2 Shutdown at 1437H. Follow RTD. [WEBSMS] | CMIN
10/9/2023 2:27:55 PM | Mindanao Grid-10/09/2023 14:30: PSF U2 Online at 1424H. Follow RTD. [WEBSMS] | CMIN
10/9/2023 1:10:36 PM | [NSO Update] Luzon Grid-10/09/2023 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12924MW, PK=11664MW, RR=446MW, NetOpMargin: PM=814, EVE=926 Highest Unit O/L: Sual 2 @ 647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 2 @ 325MW, Masinloc 3 @ 310MW, Sual 1 @ 550MW, Ilijan A @ 165MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
10/9/2023 12:59:49 PM | [NSO Update] Mindanao Grid-10/09/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2985MW, PK=2331MW, RR=70MW, NetOpMargin: PM=584, EVE=646 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: DCP @135.16MW, MCC @100MW, MCO @270MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @96MW, AG5 @40MW, AG6 @149MW, AG7 @35MW, PG4 @145MW [WEBSMS] | CMIN
10/9/2023 12:23:02 PM | Luzon Grid-10/09/2023 12:23: For info: Bay PCB 8-03CB24BYZ was de-energized at 1128H and was re-energized at 1214H. (Planned Outage) [WEBSMS] | CLUZ
10/9/2023 12:20:56 PM | Luzon Grid-10/09/2023 12:21: For info: San Jose PCB 8-08CB08SJO was de-energized at 1058H and was re-energized at 1141H. (Planned Outage) [WEBSMS] | CLUZ
10/9/2023 12:18:23 PM | Luzon Grid-10/09/2023 12:18: For info: Bay PCB 8-02CB08BYZ was energized at 1123H (Planned Outage) [WEBSMS] | CLUZ
10/9/2023 12:02:36 PM | Luzon Grid-10/09/2023 12:02: Sual Unit 2 online at 1159H. (Unplanned Outage) [WEBSMS] | CLUZ
10/9/2023 11:51:43 AM | Mindanao Grid-10/09/2023 11:54: WMPC DG08 Online as RPS at 1050H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/9/2023 11:50:16 AM | Mindanao Grid-10/09/2023 11:53: (Correction): WMPC DG10 Online as RPS at 0851H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/9/2023 11:07:11 AM | Luzon Grid-10/09/2023 11:07: Ilijan GT1-1 - shutdown at 1102H (Unplanned Outage). [WEBSMS] | CLUZ
10/9/2023 11:04:07 AM | Visayas Grid-10/09/2023 11:04: Colon 100MVA Transformer de-energized/restored ( 0443H-1009H ). (Planned Outage) [WEBSMS] | CVIS
10/9/2023 9:39:41 AM | Luzon Grid-10/09/2023 09:39: Bay PCB 8-02CB08BYZ de-energized at 0925H (Planned Outage) [WEBSMS] | CLUZ
10/9/2023 9:39:07 AM | Mindanao Grid-10/09/2023 09:41: WMPC DG10 Shutdown as RPS at 0851H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/9/2023 8:58:46 AM | Mindanao Grid-10/09/2023 09:01: SEDI Unit 3 declared unavailable starting 0801H - Preventive Maintenance Schedule. ETC Nov. 12, 2023. (Planned Outage) [WEBSMS] | CMIN
10/9/2023 7:48:18 AM | Mindanao Grid-10/09/2023 07:51: (Correction) Lugait 138/69/13.8 kV T2 (75MVA) deenergized 0704H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
10/9/2023 7:21:51 AM | Mindanao Grid-10/09/2023 07:24: Lugait 138/69/13.8 kV T1 (50MVA) deenergized at 0704H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
10/9/2023 6:04:27 AM | Luzon Grid-10/09/2023 06:04: Malaya Unit 2 online at 0601H. [WEBSMS] | CLUZ
10/9/2023 5:46:58 AM | Mindanao Grid-10/09/2023 05:49: TU2 U2 Online at 0525H. (Unplanned Outage) [WEBSMS] | CMIN
10/9/2023 5:41:56 AM | [NSO Update] Mindanao Grid-10/09/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2994MW, PK=2217MW, RR=70MW, NetOpMargin: AM=707, PM=607, EVE=683 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @35MW, PG4 @145MW [WEBSMS] | CMIN
10/9/2023 5:41:45 AM | [NSO Update] Luzon Grid-10/09/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12676MW, PK=10737MW, RR=434MW, NetOpMargin: AM=1506, PM=662, EVE=839 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GNPD 2 @334MW, MSLC2 @320MW, MSLC3 @310MW, ILIJAN A @490MW, ILIJAN B @280MW [WEBSMS] | CLUZ
10/9/2023 4:46:07 AM | [NSO Update] Mindanao Grid-10/09/2023 04:48: Weather Update: Trough of a Low Pressure Area (LPA) affecting the eastern section of Mindanao. [WEBSMS] | CMIN
10/9/2023 4:45:49 AM | [NSO Update] Visayas Grid-10/09/2023 04:46: Weather Update: Trough of a Low Pressure Area (LPA) affecting the eastern section of Mindanao. [WEBSMS] | CVIS
10/9/2023 4:45:35 AM | [NSO Update] Luzon Grid-10/09/2023 04:45: Weather Update: Trough of a Low Pressure Area (LPA) affecting the eastern section of Mindanao. [WEBSMS] | CLUZ
10/9/2023 4:14:43 AM | Mindanao Grid-10/09/2023 04:17: TU2 U2 with a load of 0.5MW tripped at 0351H. Indication: Quick shutdown - Mechanical and for further investigation. [WEBSMS] | CMIN
10/8/2023 11:09:16 PM | Mindanao Grid-10/08/2023 23:12: NBT Online at 2120H. (Unplanned Outage) [WEBSMS] | CMIN
10/8/2023 11:07:24 PM | Mindanao Grid-10/08/2023 23:10: NBT tripped with 1.7MW load at 2259H. Affected by NORDECO line voltage fluctuation. [WEBSMS] | CMIN
10/8/2023 10:12:57 PM | Luzon Grid-10/08/2023 22:13: Mexico SS 230kV Bus 2 restored at 2211H (Planned Outage) [WEBSMS] | CLUZ
10/8/2023 7:34:04 PM | Luzon Grid-10/08/2023 19:34: Binan SS 300MVA T02 restored at 1933H (Planned Outage) [WEBSMS] | CLUZ
10/8/2023 7:30:12 PM | Luzon Grid-10/08/2023 19:30: Binan SS 230kV Bus 2 restored at 1930H (Planned Outage) [WEBSMS] | CLUZ
10/8/2023 5:47:15 PM | [NSO Update] Mindanao Grid-10/08/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2942MW, PK=2005MW, RR=67MW, NetOpMargin: EVE=870 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @25MW, PG4 @145MW [WEBSMS] | CMIN
10/8/2023 5:44:43 PM | [NSO Update] Luzon Grid-10/08/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11766MW, PK=9722MW, RR=356MW, NetOpMargin: EVE=1689 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GNPD 2 @334MW, MSLC2 @335MW, MSLC3 @230MW, ILIJAN A @490MW, ILIJAN B @280MW [WEBSMS] | CLUZ
10/8/2023 5:37:58 PM | Luzon Grid-10/08/2023 17:38: San Jose-Taytay 230kV Line 1 restored at 1737H (Planned Outage) [WEBSMS] | CLUZ
10/8/2023 5:27:26 PM | Mindanao Grid-10/08/2023 17:30: Toril - Matanao 230kV L2 restored at 1721H. (Planned Outage) [WEBSMS] | CMIN
10/8/2023 5:27:10 PM | Visayas Grid-10/08/2023 17:27: Compostela SS 50 MVA 138/69 kV TR3 energized at 1726H. (Planned Outage) [WEBSMS] | CVIS
10/8/2023 5:17:48 PM | Luzon Grid-10/08/2023 17:17: Dasmarinas-MEC-Rosario 115kV Line restored at 1717H (Planned Outage) [WEBSMS] | CLUZ
10/8/2023 5:07:38 PM | Luzon Grid-10/08/2023 17:07: Bolo SS 230kV Bus 2 commisioned at 1706H (Planned Outage). [WEBSMS] | CLUZ
10/8/2023 4:35:11 PM | Luzon Grid-10/08/2023 16:35: Bolo SS 230kV Bus 2 energized at 1632H, on-going commissioning test. [WEBSMS] | CLUZ
10/8/2023 4:03:48 PM | Luzon Grid-10/08/2023 16:03: San Jose-Angat 115kV Line 1 restored at 1603H (Planned Outage) [WEBSMS] | CLUZ
10/8/2023 3:58:50 PM | Mindanao Grid-10/08/2023 16:01: Tacurong Transformer No. 4 restored at 1553H. (Planned Outage) [WEBSMS] | CMIN
10/8/2023 3:35:57 PM | Luzon Grid-10/08/2023 15:36: SLTEC 1 online at 1534H (Unplanned Outage) [WEBSMS] | CLUZ
10/8/2023 3:35:40 PM | Visayas Grid-10/08/2023 15:35: Compostela - Consolacion 69 kV Line energized at 1534H. (Planned Outage) [WEBSMS] | CVIS
10/8/2023 2:45:45 PM | Mindanao Grid-10/08/2023 14:48: Lake Mainit (AGC) HEP cut-in at 1434H. (Unplanned Outage). [WEBSMS] | CMIN
10/8/2023 2:29:34 PM | Mindanao Grid-10/08/2023 14:32: Lake Mainit (AGC) HEP cut-in at 1117H. (Unplanned Outage). [WEBSMS] | CMIN
10/8/2023 2:26:12 PM | Mindanao Grid-10/08/2023 14:28: Nasipit - Butuan 138kV L1 restored at 1418H. (Planned Outage) [WEBSMS] | CMIN
10/8/2023 2:24:49 PM | Mindanao Grid-10/08/2023 14:27: Lake Mainit (AGC) HEP tripped with 10.5MW load at 1419H. Indication: G3 Power Signal Fault. Unplanned Outage. [WEBSMS] | CMIN
10/8/2023 12:49:33 PM | [NSO Update] Luzon Grid-10/08/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12252MW, PK=9351MW, RR=356MW, NetOpMargin: PM=2545, EVE=1460 Highest Unit O/L: Sual 1 @ 647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 2 @ 335MW, Masinloc 3 @ 120MW, Pagbilao 1 @ 300MW, Ilijan A @ 490MW, Ilijan B @ 280MW [WEBSMS] | CLUZ
10/8/2023 12:47:52 PM | [NSO Update] Mindanao Grid-10/08/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2992MW, PK=1876MW, RR=67MW, NetOpMargin: PM=1049, EVE=836 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @40MW, PG4 @145MW [WEBSMS] | CMIN
10/8/2023 11:13:24 AM | Mindanao Grid-10/08/2023 11:16: Lake Mainit (AGC) HEP tripped with 10.5MW load at 1108H. Indication: G3 Power Signal Fault. Unplanned Outage. [WEBSMS] | CMIN
10/8/2023 10:26:27 AM | Mindanao Grid-10/08/2023 10:29: STEAG U1 online at 1000H. (Unplanned Outage) [WEBSMS] | CMIN
10/8/2023 8:48:41 AM | Mindanao Grid-10/08/2023 08:51: Toril - Matanao 230 kV L2 de-energized at 0834H. (Planned Outage) [WEBSMS] | CMIN
10/8/2023 8:40:18 AM | Luzon Grid-10/08/2023 08:40: Mexico SS 230kV Bus 2 de-energized at 0839H. (Planned Outage) [WEBSMS] | CLUZ
10/8/2023 8:04:10 AM | Mindanao Grid-10/08/2023 08:06: Tacurong SS Transformer No. 4 de-energized at 0801H. (Planned Outage) [WEBSMS] | CMIN
10/8/2023 7:19:56 AM | Mindanao Grid-10/08/2023 07:22: Nasipit - Butuan 138kV L1 de-energized at 0704H. (Planned Outage) [WEBSMS] | CMIN
10/8/2023 7:06:25 AM | Luzon Grid-10/08/2023 07:06: Binan SS 230kV Bus 2 de-energized at 0706H. (Planned Outage) [WEBSMS] | CLUZ
10/8/2023 7:04:40 AM | Luzon Grid-10/08/2023 07:04: Binan SS 300MVA T02 de-energized at 0704H. (Planned Outage) [WEBSMS] | CLUZ
10/8/2023 7:02:25 AM | Visayas Grid-10/08/2023 07:02: Compostela SS 50MVA TR3 de-energized at 0646H (Planned Outage). ECD: 1800H [WEBSMS] | CVIS
10/8/2023 6:40:21 AM | Luzon Grid-10/08/2023 06:40: San Jose-Angat 115kV Line 1 de-energized at 0640H. (Planned Outage) [WEBSMS] | CLUZ
10/8/2023 6:15:00 AM | [NSO Update] Luzon Grid-10/08/2023 06:12: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12436MW, PK=8679MW, RR=356MW, NetOpMargin: AM=3401, PM=2835, EVE=1475 Highest Unit O/L: Sual 1 @ 647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 2 @ 335MW, Masinloc 3 @ 120MW, Pagbilao 1 @ 300MW, Ilijan A @ 490MW, Ilijan B @ 280MW [WEBSMS] | CLUZ
10/8/2023 6:08:27 AM | Luzon Grid-10/08/2023 06:08: Dasmarinas-MEC-Rosario 115kV Line de-energized at 0608H. (Planned Outage) [WEBSMS] | CLUZ
10/8/2023 5:50:50 AM | [NSO Update] Mindanao Grid-10/08/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2900MW, PK=1721MW, RR=64MW, NetOpMargin: AM=1114, PM=1028, EVE=829 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @40MW, AG6 @149MW, AG7 @40MW, PG4 @145MW [WEBSMS] | CMIN
10/8/2023 5:50:36 AM | Visayas Grid-10/08/2023 05:50: Compostela-Consolacion 69KV line de-energized at 0545H. (Planned Outage) [WEBSMS] | CVIS
10/8/2023 4:45:20 AM | [NSO Update] Luzon Grid-10/08/2023 04:45: Weather Update: Southwest Monsoon affecting the western section of Northern and Central Luzon. [WEBSMS] | CLUZ
10/8/2023 4:44:35 AM | [NSO Update] Mindanao Grid-10/08/2023 04:47: Weather Update: Southwest Monsoon affecting the western section of Northern and Central Luzon. [WEBSMS] | CMIN
10/8/2023 4:43:29 AM | [NSO Update] Visayas Grid-10/08/2023 04:43: Weather Update: Southwest Monsoon affecting the western section of Northern and Central Luzon. [WEBSMS] | CVIS
10/8/2023 4:41:26 AM | Mindanao Grid-10/08/2023 04:44: AGC(U2 and U3) Online at 0434H (Unplanned Outage). [WEBSMS] | CMIN
10/8/2023 4:20:59 AM | Mindanao Grid-10/08/2023 04:23: AGC (U2 and U3) with a load of 10.5MW tripped at 0413H. (Unplanned Outage). [WEBSMS] | CMIN
10/7/2023 6:34:36 PM | Mindanao Grid-10/07/2023 18:37: Lake Mainit (AGC) HEP with 10.5MW load tripped at 1827H. Indication: Generator Trip Power Signal Fault. (Unplanned Outage). [WEBSMS] | CMIN
10/7/2023 5:58:36 PM | [NSO Update] Mindanao Grid-10/07/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2837MW, PK=2071MW, RR=70MW, NetOpMargin: EVE=696 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @42MW, AG6 @149MW, AG7 @37MW, PG4 @125MW [WEBSMS] | CMIN
10/7/2023 5:53:22 PM | [NSO Update] Luzon Grid-10/07/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10948MW, PK=9844MW, RR=404MW, NetOpMargin: EVE=700 Highest Unit O/L: Sual 1 @ 647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 2 @ 335MW, Masinloc 3 @ 100MW, Pagbilao 1 @ 300MW, Ilijan A @ 500MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
10/7/2023 5:18:28 PM | [NSO Update] Mindanao Grid-10/07/2023 17:21: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1716H with power going to Visayas. [WEBSMS] | CMIN
10/7/2023 5:17:22 PM | [NSO Update] Visayas Grid-10/07/2023 17:17: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1716H with power going to Visayas. [WEBSMS] | CVIS
10/7/2023 5:12:01 PM | Mindanao Grid-10/07/2023 17:14: MCC U3 Online at 1648H. (Unplanned Outage). [WEBSMS] | CMIN
10/7/2023 5:08:34 PM | Mindanao Grid-10/07/2023 17:11: Toril-Matanao 230KV L1 re-energized at 1654H & looped at Matanao SS at 1655H. From Planned Outage / GOMP. [WEBSMS] | CMIN
10/7/2023 4:41:25 PM | Luzon Grid-10/07/2023 16:41: Sual 2 shutdown at 1641H (Unplanned Outage) [WEBSMS] | CLUZ
10/7/2023 4:12:03 PM | Mindanao Grid-10/07/2023 16:14: Baloi-Agus 2 138KV L2 re-energized at 1549H & looped at Agus 2 SY at 1550H. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
10/7/2023 4:12:01 PM | Luzon Grid-10/07/2023 16:12: Mexico-San Rafael 230kV Line 1 restored at 1611H (Planned Outage) [WEBSMS] | CLUZ
10/7/2023 3:45:12 PM | Mindanao Grid-10/07/2023 15:47: Talomo A (TL1) unit 2 HEP cut-in at 1525H. (Unplanned Outage) [WEBSMS] | CMIN
10/7/2023 3:42:24 PM | Visayas Grid-10/07/2023 15:42: Visayas Grid experienced high system frequency of 61.017 hz at 1425H due to tripping of Colon-Sibonga 69 kv line with Ormoc HVDC at 29 MW reverse power flow. [WEBSMS] | CVIS
10/7/2023 3:26:00 PM | Visayas Grid-10/07/2023 15:26: Cebu-Compostela 138KV Line 1 energized 1524H (Planned Outage) [WEBSMS] | CVIS
10/7/2023 3:17:55 PM | Mindanao Grid-10/07/2023 15:20: WMPC DG10 Shutdown as RPS at 1514H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/7/2023 3:11:26 PM | Luzon Grid-10/07/2023 15:11: System Advisory: Affected ALD feeders of NGCP and MERALCO restored at 1505H and 1508H, respectively. [WEBSMS] | CLUZ
10/7/2023 3:08:03 PM | Luzon Grid-10/07/2023 15:08: System Advisory: ALD occurred at NGCP and MERALCO feeders at 1501H due to tripping of Pagbilao 3 at 421MW. Lowest Frequency=59.01Hz [WEBSMS] | CLUZ
10/7/2023 2:35:42 PM | Visayas Grid-10/07/2023 14:35: Colon-Sibonga 69 KV Line energized at 1432H. (Unplanned Outage). [WEBSMS] | CVIS
10/7/2023 2:28:00 PM | Visayas Grid-10/07/2023 14:28: Colon-Sibonga 69 KV Line tripped at 1425H. (Unplanned Outage). [WEBSMS] | CVIS
10/7/2023 1:35:33 PM | Mindanao Grid-10/07/2023 13:38: Baloi-Agus 2 138KV L2 de-energized at 1304H for installation of TL surge arresters at Tower # 33-DA. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
10/7/2023 12:45:54 PM | [NSO Update] Luzon Grid-10/07/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12496MW, PK=10421MW, RR=427MW, NetOpMargin: PM=1648, EVE=1462 Highest Unit O/L: Sual 1 @ 647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 1 @ 330MW, Masinloc 2 @ 335MW, Masinloc 3 @ 160MW, Pagbilao 1 @ 300MW, Sual 2 @ 550MW, Ilijan A @ 480MW, Ilijan B @ 230MW [WEBSMS] | CLUZ
10/7/2023 12:43:55 PM | [NSO Update] Mindanao Grid-10/07/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2794MW, PK=2048MW, RR=70MW, NetOpMargin: PM=676, EVE=615 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @42MW, AG6 @149MW, AG7 @25MW, PG4 @160MW [WEBSMS] | CMIN
10/7/2023 12:29:28 PM | Mindanao Grid-10/07/2023 12:32: MCC U2 Online at 1226H. (Unplanned Outage). [WEBSMS] | CMIN
10/7/2023 12:23:27 PM | Mindanao Grid-10/07/2023 12:26: AG7 U2 Online at 1213H. (Planned Outage) [WEBSMS] | CMIN
10/7/2023 11:56:25 AM | Mindanao Grid-10/07/2023 11:59: Baloi-Agus 2 138KV L1 re-energized at 1136H & looped at Agus 2 SY at 1137H. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
10/7/2023 11:53:57 AM | Luzon Grid-10/07/2023 11:54: Angat HEPP Main Transformer A restored at 1153H. (Planned Outage) [WEBSMS] | CLUZ
10/7/2023 11:50:42 AM | Mindanao Grid-10/07/2023 11:53: STE U2 Online at 1149H. (Unplanned Outage). [WEBSMS] | CMIN
10/7/2023 11:30:28 AM | Mindanao Grid-10/07/2023 11:33: Update: Embedded Generator MCC U2(38.98MW) and U3(40.87MW) tripped at 0834H due to under voltage affected by the outage of Tagoloan-Natumulan 69kV Feeder. (Unplanned Outage) [WEBSMS] | CMIN
10/7/2023 11:29:25 AM | Luzon Grid-10/07/2023 11:29: Ilijan ST-2 online at 1127H. (Unplanned Outage) [WEBSMS] | CLUZ
10/7/2023 10:57:39 AM | Mindanao Grid-10/07/2023 11:00: MA3 Online at 1054H. (Unplanned Outage) [WEBSMS] | CMIN
10/7/2023 10:13:19 AM | Luzon Grid-10/07/2023 10:13: Ilijan GT 2-2 online at 1012H. (Unplanned Outage) [WEBSMS] | CLUZ
10/7/2023 10:03:02 AM | Mindanao Grid-10/07/2023 10:05: WMPC DG10 Online at 0954H. Follow RTD. [WEBSMS] | CMIN
10/7/2023 9:44:46 AM | Mindanao Grid-10/07/2023 09:47: MDP with a load of 6MW tripped at 0905H. (Unplanned Outage). [WEBSMS] | CMIN
10/7/2023 9:22:36 AM | Mindanao Grid-10/07/2023 09:25: MA3 with a load of 3.2MW tripped at 0914H. (Unplanned Outage). [WEBSMS] | CMIN
10/7/2023 9:21:12 AM | Mindanao Grid-10/07/2023 09:23: MCC U2 and U2 both Trip at 0851H Details to follow. [WEBSMS] | CMIN
10/7/2023 9:01:29 AM | [NSO Update] Mindanao Grid-10/07/2023 09:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0900H from forward power direction. (Planned outage) [WEBSMS] | CMIN
10/7/2023 9:01:10 AM | [NSO Update] Visayas Grid-10/07/2023 09:01: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0900H from forward power direction. (Planned outage) [WEBSMS] | CVIS
10/7/2023 8:47:15 AM | Mindanao Grid-10/07/2023 08:49: Baloi-Agus 2 138KV L1 de-energized at 0833H for installation of TL surge arresters at Tower # 32. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
10/7/2023 8:27:30 AM | Mindanao Grid-10/07/2023 08:30: Toril-Matanao 230KV L1 de-energized at 0805H. APMS of said line. Planned Outage / GOMP. [WEBSMS] | CMIN
10/7/2023 8:13:45 AM | Visayas Grid-10/07/2023 08:13: Cebu-Compostela 138KV Line 1 de-energized 0807H (Planned Outage). ECD: 1800H. [WEBSMS] | CVIS
10/7/2023 8:06:07 AM | Luzon Grid-10/07/2023 08:06: Angat HEPP Main Transformer A de-energized at 0805H. (Planned Outage) [WEBSMS] | CLUZ
10/7/2023 7:39:01 AM | Luzon Grid-10/07/2023 07:39: San Jose-Taytay 230kV Line 1 de-energized at 0738H. (Planned Outage) [WEBSMS] | CLUZ
10/7/2023 7:11:12 AM | Luzon Grid-10/07/2023 07:11: Dona Imelda (Araneta) 300MVA T03 restored at 0710H. (Planned Outage) [WEBSMS] | CLUZ
10/7/2023 7:05:42 AM | Luzon Grid-10/07/2023 07:05: For info: Sta. Rita - San Lorenzo 230kV Bus A and Bus B looped at 0703H and 0704H respectively. [WEBSMS] | CLUZ
10/7/2023 6:51:00 AM | Luzon Grid-10/07/2023 06:51: Ilijan GT 1-1 online at 0650H. (Unplanned Outage) [WEBSMS] | CLUZ
10/7/2023 6:47:50 AM | Luzon Grid-10/07/2023 06:47: Bolo SS 230kV Bus 2 de-energized at 0647H. (Planned Outage) [WEBSMS] | CLUZ
10/7/2023 6:14:25 AM | Luzon Grid-10/07/2023 06:14: Mexico-San Rafael 230kV Line 1 de-energized at 0613H. (Planned Outage) [WEBSMS] | CLUZ
10/7/2023 5:49:20 AM | [NSO Update] Luzon Grid-10/07/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12045MW, PK=9816MW, RR=406MW, NetOpMargin: AM=1822, PM=1237, EVE=999 Highest Unit O/L: SUAL 1@647 Derated Plant: GNPD 2 @334MW, MASINLOC 2 @335MW, PAGBILAO 1 @300MW, SUAL 2 @550MW, [WEBSMS] | CLUZ
10/7/2023 5:36:26 AM | [NSO Update] Mindanao Grid-10/07/2023 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2751MW, PK=2030MW, RR=70MW, NetOpMargin: AM=651, PM=601, EVE=523 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @42MW, AG6 @149MW, AG7 @25MW, PG4 @105MW [WEBSMS] | CMIN
10/7/2023 5:36:12 AM | Luzon Grid-10/07/2023 05:36: Ilijan ST1 online at 0533H (Unplanned Outage) [WEBSMS] | CLUZ
10/7/2023 4:20:44 AM | [NSO Update] Luzon Grid-10/07/2023 04:20: Weather Advisory: Southwest Monsoon affecting the western section of Northern and Central Luzon. [WEBSMS] | CLUZ
10/7/2023 4:20:18 AM | [NSO Update] Mindanao Grid-10/07/2023 04:23: Weather Advisory: Southwest Monsoon affecting the western section of Northern and Central Luzon. [WEBSMS] | CMIN
10/7/2023 4:20:00 AM | [NSO Update] Visayas Grid-10/07/2023 04:20: Weather Advisory: Southwest Monsoon affecting the western section of Northern and Central Luzon. [WEBSMS] | CVIS
10/7/2023 4:12:57 AM | Luzon Grid-10/07/2023 04:13: Ilijan GT1-2 online at 0410H (Unplanned Outage) [WEBSMS] | CLUZ
10/7/2023 2:06:53 AM | Luzon Grid-10/07/2023 02:06: Masinloc 3 online at 0203H (Unplanned Outage) [WEBSMS] | CLUZ
10/7/2023 1:21:36 AM | Luzon Grid-10/07/2023 01:21: Masinloc 3 @74MW load tripped at 0110H. Lowest System Frequency is 59.78Hz (Unplanned Outage) [WEBSMS] | CLUZ
10/7/2023 12:50:31 AM | Luzon Grid-10/07/2023 00:50: Sta Rita 40 shutdown at 0048H (Planned Outage) [WEBSMS] | CLUZ
10/6/2023 11:52:47 PM | Luzon Grid-10/06/2023 23:52: Dona Imelda (Araneta) 300MVA T03 de-energized at 2350H (Planned Outage) [WEBSMS] | CLUZ
10/6/2023 11:43:24 PM | Luzon Grid-10/06/2023 23:43: Sta Rita 10 shutdown at 2338H (Planned Outage) [WEBSMS] | CLUZ
10/6/2023 11:14:58 PM | Luzon Grid-10/06/2023 23:15: Masinloc 3 online at 2310H (Unplanned Outage) [WEBSMS] | CLUZ
10/6/2023 11:05:41 PM | Luzon Grid-10/06/2023 23:05: San Gabriel online at 2302H (Unplanned Outage) [WEBSMS] | CLUZ
10/6/2023 9:17:36 PM | Mindanao Grid-10/06/2023 21:20: WMPC DG10 Shutdown as RPS at 2114H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/6/2023 7:23:43 PM | Mindanao Grid-10/06/2023 19:26: WMPC DG1 Shutdown at 1917H. Follow RTD. [WEBSMS] | CMIN
10/6/2023 7:22:47 PM | Mindanao Grid-10/06/2023 19:25: WMPC DG8 Shutdown at 1916H. Follow RTD. [WEBSMS] | CMIN
10/6/2023 6:47:05 PM | Mindanao Grid-10/06/2023 18:49: Lugait SS Transformer No. 1 restored at 1841H. (Planned Outage) [WEBSMS] | CMIN
10/6/2023 6:30:51 PM | Mindanao Grid-10/06/2023 18:33: WMPC DG8 Online at 1759H. Follow RTD. [WEBSMS] | CMIN
10/6/2023 6:30:04 PM | Mindanao Grid-10/06/2023 18:32: wmpc DG1 Online at 1757H Follow RTD. [WEBSMS] | CMIN
10/6/2023 5:59:19 PM | Luzon Grid-10/06/2023 17:59: Ilijan A (480MW) & B (290MW) tripped at 1754H. Lowest Frequency is 59.06Hz (Unplanned Outage) [WEBSMS] | CLUZ
10/6/2023 5:46:21 PM | [NSO Update] Mindanao Grid-10/06/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2857MW, PK=2251MW, RR=70MW, NetOpMargin: EVE=536 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @42MW, AG6 @149MW, AG7 @25MW, PG4 @125MW [WEBSMS] | CMIN
10/6/2023 5:37:51 PM | [NSO Update] Luzon Grid-10/06/2023 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11893MW, PK=10160MW, RR=426MW, NetOpMargin: EVE=1307 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GNPD 2 @ 334MW, Sual 2 @ 550MW, Masinloc 1 @ 335MW, Masinloc 2 @ 335MW, Pagbilao 1 @ 300MW, Ilijan A @ 480MW, Ilijan B @ 290MW [WEBSMS] | CLUZ
10/6/2023 4:18:19 PM | Mindanao Grid-10/06/2023 16:21: WMPC DG1 Shutdown at 1617H. Follow RTD. [WEBSMS] | CMIN
10/6/2023 4:16:18 PM | Mindanao Grid-10/06/2023 16:19: WMPC DG8 Shutdown as RPS at 1614H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/6/2023 3:43:41 PM | Mindanao Grid-10/06/2023 15:46: Bunawan SS Transformer no. 1 restored at 1538H. (Planned Outage) [WEBSMS] | CMIN
10/6/2023 3:15:38 PM | [NSO Update] Visayas Grid-10/06/2023 15:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1511H with power going to Visayas. [WEBSMS] | CVIS
10/6/2023 3:15:30 PM | [NSO Update] Mindanao Grid-10/06/2023 15:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1511H with power going to Visayas. [WEBSMS] | CMIN
10/6/2023 3:05:38 PM | [NSO Update] Visayas Grid-10/06/2023 15:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1503H from reverse power direction. [WEBSMS] | CVIS
10/6/2023 3:05:29 PM | [NSO Update] Mindanao Grid-10/06/2023 15:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1503H from reverse power direction. [WEBSMS] | CMIN
10/6/2023 3:00:48 PM | Mindanao Grid-10/06/2023 15:03: Tagoloan - Manolo 138kV L1 restored at 1452H. (Planned Outage) [WEBSMS] | CMIN
10/6/2023 1:53:43 PM | Mindanao Grid-10/06/2023 13:56: WMPC DG05 cut-out at 1325H. MO Dispatch. [WEBSMS] | CMIN
10/6/2023 1:30:29 PM | Mindanao Grid-10/06/2023 13:33: WMPC DG05 online at 1317H. (Unplanned Outage). [WEBSMS] | CMIN
10/6/2023 1:29:13 PM | Mindanao Grid-10/06/2023 13:31: WMPC DG05 tripped with 10.2MW load at 1307H. Indication: Turbo Charger B-Bank vibration alarm. (Unplanned Outage). [WEBSMS] | CMIN
10/6/2023 1:25:52 PM | Mindanao Grid-10/06/2023 13:28: Pulangi 4 Unit 1 online at 1308H. from PMS GOMP. (Planned Outage) [WEBSMS] | CMIN
10/6/2023 1:23:23 PM | Mindanao Grid-10/06/2023 13:26: WMPC DG01 AND DG05 cut-in at 1300H, MO Dispatched. [WEBSMS] | CMIN
10/6/2023 12:54:52 PM | [NSO Update] Luzon Grid-10/06/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12384MW, PK=10768MW, RR=446MW, NetOpMargin: PM=1169, EVE=1259 Highest Unit O/L: Sual 1 @ 647MW Derated Plant: GNPD 2 @ 334MW, Sual 2 @ 550MW, Masinloc 2 @ 330MW, Pagbilao 1 @ 300MW, Ilijan A @ 480MW, Ilijan B @ 290MW [WEBSMS] | CLUZ
10/6/2023 12:53:06 PM | [NSO Update] Visayas Grid-10/06/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2743MW, PK=2365MW, RR=40MW, NetOpMargin: PM=337, EVE=283 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 317MW, PGPP1 @ 75MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
10/6/2023 12:52:41 PM | [NSO Update] Mindanao Grid-10/06/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2979MW, PK=2394MW, RR=70MW, NetOpMargin: PM=515, EVE=515 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @96MW, AG5 @42MW, AG6 @149MW, AG7 @25MW, PG4 @125MW [WEBSMS] | CMIN
10/6/2023 12:03:22 PM | Mindanao Grid-10/06/2023 12:06: Agus 2 HEP U1 138kV Tie-line restored at 1201H. (Unplanned Outage) [WEBSMS] | CMIN
10/6/2023 11:19:29 AM | [NSO Update] Mindanao Grid-10/06/2023 11:22: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1116H with power going to Mindanao. [WEBSMS] | CMIN
10/6/2023 11:19:12 AM | [NSO Update] Visayas Grid-10/06/2023 11:19: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1116H with power going to Mindanao. [WEBSMS] | CVIS
10/6/2023 10:55:49 AM | Mindanao Grid-10/06/2023 10:58: Zamboanga - Pitogo 138kV L1 restored at 1051H. (Planned Outage) [WEBSMS] | CMIN
10/6/2023 10:34:58 AM | [NSO Update] Visayas Grid-10/06/2023 10:35: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1032H from forward power direction. [WEBSMS] | CVIS
10/6/2023 10:34:56 AM | [NSO Update] Mindanao Grid-10/06/2023 10:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1032H from forward power direction. [WEBSMS] | CMIN
10/6/2023 9:23:39 AM | Mindanao Grid-10/06/2023 09:26: WMPC DG10 Online as RPS at 0851H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/6/2023 8:42:36 AM | Mindanao Grid-10/06/2023 08:45: Bunawan SS Transformer no. 1 de-energized at 0834H. (Planned Outage) [WEBSMS] | CMIN
10/6/2023 8:19:23 AM | Mindanao Grid-10/06/2023 08:22: Tagoloan - Manolo 138kV L1 de-energized at 0814H. (Planned Outage) [WEBSMS] | CMIN
10/6/2023 7:33:34 AM | Mindanao Grid-10/06/2023 07:36: Lugait SS Transformer No. 1 de-energized at 0731H. (Planned Outage) [WEBSMS] | CMIN
10/6/2023 7:06:09 AM | Mindanao Grid-10/06/2023 07:08: Zamboanga - Pitogo 138kV L1 de-energized at 0703H. (Planned Outage) [WEBSMS] | CMIN
10/6/2023 5:44:24 AM | [NSO Update] Mindanao Grid-10/06/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2883MW, PK=2256MW, RR=70MW, NetOpMargin: AM=556, PM=529, EVE=660 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @42MW, AG6 @149MW, AG7 @25MW, PG4 @105MW [WEBSMS] | CMIN
10/6/2023 5:43:01 AM | [NSO Update] Luzon Grid-10/06/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12402MW, PK=10148MW, RR=446MW, NetOpMargin: AM=1808, PM=1345, EVE=1312 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GNPD 2 @334MW, MSLC1 @335MW, MSLC2 @330MW, PBL1 @300MW, SUAL 2 @550MW, ILIJAN A @480MW, ILIJAN B @290MW [WEBSMS] | CLUZ
10/6/2023 4:58:30 AM | [NSO Update] Mindanao Grid-10/06/2023 05:01: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CMIN
10/6/2023 4:56:22 AM | [NSO Update] Luzon Grid-10/06/2023 04:56: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CLUZ
10/6/2023 3:27:06 AM | Luzon Grid-10/06/2023 03:27: Dasmarinas PCB 9-02CB24DAS energized at 0325H (Unplanned Outage) [WEBSMS] | CLUZ
10/6/2023 1:39:19 AM | Luzon Grid-10/06/2023 01:39: San Lorenzo Module 50 changeover from oil to gas completed at 0133H (Unplanned Outage) [WEBSMS] | CLUZ
10/6/2023 1:19:29 AM | Luzon Grid-10/06/2023 01:19: Dasmarinas PCB 9-02CB24DAS de-energized at 0118H (Unplanned Outage) [WEBSMS] | CLUZ
10/6/2023 1:16:28 AM | Luzon Grid-10/06/2023 01:16: Dasmarinas PCB 9-02CB04DAS restored at 0115H (Unplanned Outage) [WEBSMS] | CLUZ
10/5/2023 10:47:22 PM | Luzon Grid-10/05/2023 22:47: Dasmarinas PCB 9-02CB04DAS de-energized at 2246H (Unplanned Outage) [WEBSMS] | CLUZ
10/5/2023 8:06:34 PM | Luzon Grid-10/05/2023 20:06: Masinloc Unit 3 (293MW) tripped at 1957H. Lowest system frequency is 59.382Hz. [WEBSMS] | CLUZ
10/5/2023 8:01:55 PM | Luzon Grid-10/05/2023 20:01: Masinloc Unit 3 (293MW) tripped at 1957H. Lowest system frequency is 59.382H. [WEBSMS] | CLUZ
10/5/2023 6:35:57 PM | [NSO Update] Visayas Grid-10/05/2023 18:36: Lala CS - Dumanjug CS 350kV HVDC (Mindanao-Visayas) de-blocked at 1755H with power going to Visayas. [WEBSMS] | CVIS
10/5/2023 6:35:42 PM | [NSO Update] Mindanao Grid-10/05/2023 18:38: Lala CS - Dumanjug CS 350kV HVDC (Mindanao-Visayas) de-blocked at 1755H with power going to Visayas. [WEBSMS] | CMIN
10/5/2023 6:32:31 PM | [NSO Update] Luzon Grid-10/05/2023 18:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12283MW, PK=10152MW, RR=426MW, NetOpMargin: EVE=1705 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GNPD 2 @334MW, MASINLOC 1 @335MW, MASINLOC 2 @330MW, PAGBILAO 1 @300MW, SUAL 2 @550MW, ILIJAN A @480MW, ILIJAN B @ 290MW [WEBSMS] | CLUZ
10/5/2023 6:00:33 PM | [NSO Update] Mindanao Grid-10/05/2023 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2881MW, PK=2303MW, RR=70MW, NetOpMargin: EVE=508 Highest Unit O/L: GNPK 3&4 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @42MW, AG6 @149MW, AG7 @25MW, PG4 @125MW [WEBSMS] | CMIN
10/5/2023 5:25:58 PM | [NSO Update] Visayas Grid-10/05/2023 17:26: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1713H from reverse power direction. [WEBSMS] | CVIS
10/5/2023 5:25:32 PM | [NSO Update] Mindanao Grid-10/05/2023 17:28: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1713H from reverse power direction. [WEBSMS] | CMIN
10/5/2023 5:18:09 PM | [NSO Update] Luzon Grid-10/05/2023 17:18: Weather Disturbance Alert Notice (WDAN) has been lifted today, October 05, 2023 at 1700H. Typhoon �JENNY" is now outside the Philippine Area of Responsibility (PAR). The center of the eye was estimated based on all available data 275 km West Northwest of Itbayat, Batanes (OUTSIDE PAR) (22.1 N, 119.6 E). [WEBSMS] | CLUZ
10/5/2023 5:18:03 PM | [NSO Update] Visayas Grid-10/05/2023 17:18: Weather Disturbance Alert Notice (WDAN) has been lifted today, October 05, 2023 at 1700H. Typhoon �JENNY" is now outside the Philippine Area of Responsibility (PAR). The center of the eye was estimated based on all available data 275 km West Northwest of Itbayat, Batanes (OUTSIDE PAR) (22.1 N, 119.6 E). [WEBSMS] | CVIS
10/5/2023 5:17:57 PM | [NSO Update] Mindanao Grid-10/05/2023 17:20: Weather Disturbance Alert Notice (WDAN) has been lifted today, October 05, 2023 at 1700H. Typhoon �JENNY" is now outside the Philippine Area of Responsibility (PAR). The center of the eye was estimated based on all available data 275 km West Northwest of Itbayat, Batanes (OUTSIDE PAR) (22.1 N, 119.6 E). [WEBSMS] | CMIN
10/5/2023 5:07:32 PM | Mindanao Grid-10/05/2023 17:10: Kibawe SS 138KV Busbar # 2 re-energized at 1655H. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
10/5/2023 5:04:39 PM | Luzon Grid-10/05/2023 17:04: Tayabas-San Jose 500kV line 2 energized via Tayabas side at 1655H (Planned Outage) [WEBSMS] | CLUZ
10/5/2023 4:40:22 PM | Luzon Grid-10/05/2023 16:40: Bayombong - Matuno 69kV Line restored at 1639H (Planned Outage) [WEBSMS] | CLUZ
10/5/2023 4:28:40 PM | [NSO Update] Mindanao Grid-10/05/2023 16:31: Weather Update: At 3:00 PM today, the center of the eye of Typhoon JENNY was estimated based on all available data at 240 km Northwest of Itbayat, Batanes (22.0 N, 119.9 E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CMIN
10/5/2023 4:28:33 PM | [NSO Update] Visayas Grid-10/05/2023 16:28: Weather Update: At 3:00 PM today, the center of the eye of Typhoon JENNY was estimated based on all available data at 240 km Northwest of Itbayat, Batanes (22.0 N, 119.9 E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CVIS
10/5/2023 4:28:21 PM | [NSO Update] Luzon Grid-10/05/2023 16:28: Weather Update: At 3:00 PM today, the center of the eye of Typhoon JENNY was estimated based on all available data at 240 km Northwest of Itbayat, Batanes (22.0 N, 119.9 E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CLUZ
10/5/2023 4:20:10 PM | Mindanao Grid-10/05/2023 16:22: WMPC DG07 shutdown at 1614H - End of RPS System Voltage Requirement [WEBSMS] | CMIN
10/5/2023 4:13:46 PM | Mindanao Grid-10/05/2023 16:16: Tudaya 2 Unit 2 cut-in at 1545H. (Unplanned Outage) [WEBSMS] | CMIN
10/5/2023 3:58:44 PM | Luzon Grid-10/05/2023 15:58: Bayombong - Matuno 69kV Line de-energized at 1556H (Planned Outage) [WEBSMS] | CLUZ
10/5/2023 2:46:19 PM | Luzon Grid-10/05/2023 14:46: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1443H (Planned Outage) [WEBSMS] | CLUZ
10/5/2023 1:30:06 PM | Mindanao Grid-10/05/2023 13:32: Correction: Kauswagan-Lala 230 kV L1 de-energized at 1111H to undertake stringing works for conversion from double conductors to bundle of four (4) conductors. P&E emergency shutdown request. Non-GOMP. [WEBSMS] | CMIN
10/5/2023 1:18:12 PM | [NSO Update] Mindanao Grid-10/05/2023 13:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1223H with power going to Mindanao. [WEBSMS] | CMIN
10/5/2023 1:18:00 PM | [NSO Update] Visayas Grid-10/05/2023 13:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1223H with power going to Mindanao. [WEBSMS] | CVIS
10/5/2023 1:03:58 PM | Mindanao Grid-10/05/2023 13:06: WMPC DG1 Online at 1300H. Follow RTD. [WEBSMS] | CMIN
10/5/2023 12:58:29 PM | [NSO Update] Mindanao Grid-10/05/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2935MW, PK=2397MW, RR=70MW, NetOpMargin: PM=468, EVE=511 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @96MW, AG5 @42MW, AG6 @149MW, AG7 @25MW, PG4 @125MW [WEBSMS] | CMIN
10/5/2023 12:50:58 PM | [NSO Update] Luzon Grid-10/05/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12658MW, PK=11360MW, RR=446MW, NetOpMargin: PM=852, EVE=1226 Highest Unit O/L: SUAL 1 @647MW Derated Plant: CALACA 1 @220MW, GNPD 2 @334MW, MASINLOC 1 @335MW, MASINLOC 2 @330MW, PAGBILAO 1 @300MW, SUAL 2 @550MW, ILIJAN A @480MW, ILIJAN B @ 290MW [WEBSMS] | CLUZ
10/5/2023 12:34:26 PM | Mindanao Grid-10/05/2023 12:37: Kibawe SS 138KV Busbar # 2 de-energized at 0836H. Planned Outage Non-GOMP. [WEBSMS] | CMIN
10/5/2023 11:52:18 AM | Mindanao Grid-10/05/2023 11:54: Kauswagan-Lala 230 kV L1 de-energized at 1111H to undertake stringing works for conversion from single to bundle of four (4) conductor. P&E emergency shutdown request. Non-GOMP. [WEBSMS] | CMIN
10/5/2023 11:33:31 AM | Luzon Grid-10/05/2023 11:33: Correction: San Jose SS 750MVA T01 restored at 1129H. (Planned Outage) [WEBSMS] | CLUZ
10/5/2023 11:29:27 AM | Luzon Grid-10/05/2023 11:29: San Jose SS 750MVA T01 de-energized at 1129H. (Planned Outage) [WEBSMS] | CLUZ
10/5/2023 11:04:25 AM | Mindanao Grid-10/05/2023 11:07: WMPC DG7 Online as RPS at 1050H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/5/2023 10:50:06 AM | [NSO Update] Mindanao Grid-10/05/2023 10:52: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1049H from forward power direction. [WEBSMS] | CMIN
10/5/2023 10:50:00 AM | [NSO Update] Visayas Grid-10/05/2023 10:50: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1049H from forward power direction. [WEBSMS] | CVIS
10/5/2023 9:06:42 AM | Luzon Grid-10/05/2023 09:06: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0906H. (Planned Outage) [WEBSMS] | CLUZ
10/5/2023 8:53:58 AM | Mindanao Grid-10/05/2023 08:56: WMPC DG5 Online as RPS at 0851H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/5/2023 8:01:53 AM | Luzon Grid-10/05/2023 08:01: For information: San Lorenzo 60 changeover from oil to gas at 0753H. [WEBSMS] | CLUZ
10/5/2023 7:19:05 AM | Luzon Grid-10/05/2023 07:19: Correction: Bayombong - Matuno 69kV Line restored at 0637H. (Planned Outage) [WEBSMS] | CLUZ
10/5/2023 6:38:16 AM | Luzon Grid-10/05/2023 06:38: Bayombong - Matuno 69kV Line de-energized at 0637H. (Planned Outage) [WEBSMS] | CLUZ
10/5/2023 6:22:17 AM | Luzon Grid-10/05/2023 06:22: Tayabas-San Jose 500kV line 2 de-energized at 0621H. (Planned Outage) [WEBSMS] | CLUZ
10/5/2023 6:17:07 AM | [NSO Update] Mindanao Grid-10/05/2023 06:19: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2879MW, PK=2181MW, RR=70MW, NetOpMargin: AM=628, PM=538, EVE=591 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @42MW, AG6 @149MW, AG7 @25MW, PG4 @105MW [WEBSMS] | CMIN
10/5/2023 6:07:17 AM | Luzon Grid-10/05/2023 06:07: Bayombong - Matuno 69kV Line de-energized at 0606H. (Planned Outage) [WEBSMS] | CLUZ
10/5/2023 5:58:49 AM | [NSO Update] Luzon Grid-10/05/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12948MW, PK=10909MW, RR=446MW, NetOpMargin: AM=1593, PM=714, EVE=1351 Highest Unit O/L: SUAL 1 @647MW Derated Plant: CALACA 1 @220MW, GNPD 2 @334MW, MASINLOC 1 @335MW, MASINLOC 2 @330MW, PAGBILAO 1 @300MW, SUAL 2 @550MW, ILIJAN A @480MW, ILIJAN B @ 290MW [WEBSMS] | CLUZ
10/5/2023 4:23:00 AM | [NSO Update] Luzon Grid-10/05/2023 04:23: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "JENNY" {KOINU} was estimated based on all available data at 130 km North Northwest of Itbayat, Batanes (21.8�N, 121.2�E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving Westward at 10 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CLUZ
10/5/2023 4:22:07 AM | [NSO Update] Visayas Grid-10/05/2023 04:22: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "JENNY" {KOINU} was estimated based on all available data at 130 km North Northwest of Itbayat, Batanes (21.8�N, 121.2�E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving Westward at 10 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CVIS
10/5/2023 4:21:47 AM | Visayas Grid-10/05/2023 04:21: CEDC U-3 cut-in to the system at 0253H, initial load 8MW. [WEBSMS] | CVIS
10/5/2023 4:21:26 AM | [NSO Update] Mindanao Grid-10/05/2023 04:24: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "JENNY" {KOINU} was estimated based on all available data at 130 km North Northwest of Itbayat, Batanes (21.8�N, 121.2�E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving Westward at 10 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CMIN
10/5/2023 3:50:53 AM | Mindanao Grid-10/05/2023 03:53: Lake Mainit Hydro (APC) synchronized at 0343H from FO. (Unplanned Outage) [WEBSMS] | CMIN
10/5/2023 3:33:19 AM | Mindanao Grid-10/05/2023 03:35: LAKE Mainit Hydro (APC) tripped with 10.5MW load at 0328H. Relay indication: G3 Power Signal Fault. (Unplanned Outage) [WEBSMS] | CMIN
10/5/2023 12:35:28 AM | Luzon Grid-10/05/2023 00:35: Sta. Rita Module 20 changeover from oil to gas at 0033H (Unplanned Outage) [WEBSMS] | CLUZ
10/5/2023 12:31:43 AM | Visayas Grid-10/05/2023 00:31: Quiot 100MVA Transformer TR2 energized at 0023H per customer request activity completed. [WEBSMS] | CVIS
10/4/2023 9:59:11 PM | Luzon Grid-10/04/2023 21:59: Sta. Rita Module 40 completed the fuel changeover from oil to gas at 2154H (Planned Outage) [WEBSMS] | CLUZ
10/4/2023 9:48:38 PM | Visayas Grid-10/04/2023 21:48: Quiot 100MVA Transformer manually open/close (2123H-2141H), customers request. ( Unplanned ) [WEBSMS] | CVIS
10/4/2023 9:41:40 PM | Mindanao Grid-10/04/2023 21:44: WMPC DG07 cut-out at 2114H. End of RPS - System Voltage Requirement [WEBSMS] | CMIN
10/4/2023 8:00:42 PM | Luzon Grid-10/04/2023 20:00: Balsik-Olongapo 230kV Line restored at 1959H (Planned Outage) [WEBSMS] | CLUZ
10/4/2023 7:42:51 PM | Mindanao Grid-10/04/2023 19:45: Supreme Mati (MDP) tripped with 4.5MW load at 1924H. Indication: Reverse Power Trip. (Unplanned Outage). [WEBSMS] | CMIN
10/4/2023 7:35:09 PM | Luzon Grid-10/04/2023 19:35: Balsik-Olongapo 230kV Line de-energized at 1932H (Planned Outage) [WEBSMS] | CLUZ
10/4/2023 6:38:33 PM | Luzon Grid-10/04/2023 18:38: For info: Sta. Rita Module 10 completed the fuel changeover from oil to gas at 1836H [WEBSMS] | CLUZ
10/4/2023 6:03:17 PM | [NSO Update] Luzon Grid-10/04/2023 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12311MW, PK=10459MW, RR=435MW, NetOpMargin: EVE=1417 Highest Unit O/L: SUAL 1 @647MW Derated Plant: CALACA 1 @230MW, GNPD 2 @334MW, MASINLOC 2 @335MW, MASINLOC 3 @315MW, PAGBILAO 1 @300MW, SUAL 2 @550MW, ILIJAN A @480MW, ILIJAN B @ 290MW, STA. RITA 10 @200MW, STA. RITA 20 @235MW [WEBSMS] | CLUZ
10/4/2023 5:48:39 PM | [NSO Update] Mindanao Grid-10/04/2023 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2854MW, PK=2255MW, RR=30MW, NetOpMargin: EVE=569 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @42MW, AG6 @149MW, AG7 @25MW, PG4 @105MW [WEBSMS] | CMIN
10/4/2023 5:29:52 PM | Mindanao Grid-10/04/2023 17:32: WMPC DG05 cut-out at 1613H. End of RPS - System Voltage Requirement [WEBSMS] | CMIN
10/4/2023 5:22:57 PM | Mindanao Grid-10/04/2023 17:25: Kibawe SS 138kV Bus 1 restored/energized 1718H (Planned outage). [WEBSMS] | CMIN
10/4/2023 4:35:57 PM | [NSO Update] Mindanao Grid-10/04/2023 16:38: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "JENNY" {KOINU} was estimated based on all available data at 165 km North Northeast of Itbayat, Batanes (22.1�N, 122.6�E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CMIN
10/4/2023 4:34:14 PM | [NSO Update] Luzon Grid-10/04/2023 16:34: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "JENNY" {KOINU} was estimated based on all available data at 165 km North Northeast of Itbayat, Batanes (22.1�N, 122.6�E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CLUZ
10/4/2023 4:33:29 PM | [NSO Update] Visayas Grid-10/04/2023 16:33: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "JENNY" {KOINU} was estimated based on all available data at 165 km North Northeast of Itbayat, Batanes (22.1�N, 122.6�E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CVIS
10/4/2023 4:31:46 PM | [NSO Update] Luzon Grid-10/04/2023 16:31: at 1500H Weather Update: At 3:00 PM today, the center of the eye of Typhoon "JENNY" {KOINU} was estimated based on all available data at 165 km North Northeast of Itbayat, Batanes (22.1�N, 122.6�E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CLUZ
10/4/2023 2:46:16 PM | Mindanao Grid-10/04/2023 14:48: WMPC DG05 cut-in at 1420H, as replacement for WMPC DG10. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/4/2023 2:42:58 PM | Mindanao Grid-10/04/2023 14:45: WMPC DG10 cut-out at 1434H. replaced by WMPC DG05 due to found out exhaust gas leak, for further verification. RPS - System Voltage Requirement, [WEBSMS] | CMIN
10/4/2023 1:39:42 PM | Mindanao Grid-10/04/2023 13:42: Peak Power San Francisco cut in at 1305H. MOT raised by 5 MW. [WEBSMS] | CMIN
10/4/2023 12:54:35 PM | [NSO Update] Mindanao Grid-10/04/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2371MW, RR=30MW, NetOpMargin: PM=489, EVE=581 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @96MW, AG5 @42MW, AG6 @149MW, AG7 @25MW, PG4 @105MW [WEBSMS] | CMIN
10/4/2023 12:47:19 PM | [NSO Update] Luzon Grid-10/04/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11163MW, RR=446MW, NetOpMargin: PM=1112, EVE=1380 Highest Unit O/L: SUAL 1 @647MW Derated Plant: CALACA 1 @230MW, GNPD 2 @334MW, MASINLOC 2 @335MW, MASINLOC 3 @320MW, PAGBILAO 1 @300MW, SUAL 2 @550MW, ILIJAN A @480MW, ILIJAN B @ 290MW, STA. RITA 10 @200MW, STA. RITA 20 @235MW [WEBSMS] | CLUZ
10/4/2023 12:42:05 PM | Mindanao Grid-10/04/2023 12:44: Davao-Toril 138kV Line 1 restored/energized at 1238H. (Planned Outage) [WEBSMS] | CMIN
10/4/2023 11:21:56 AM | Mindanao Grid-10/04/2023 11:24: Peak Power San Francisco cut it at 1111H. MOT raised by 5MW. [WEBSMS] | CMIN
10/4/2023 10:56:17 AM | Mindanao Grid-10/04/2023 10:58: WMPC DG07 cut in at 1051H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/4/2023 10:14:58 AM | Mindanao Grid-10/04/2023 10:17: NACSUR cut in at 1012H. MO dispatch RTD. [WEBSMS] | CMIN
10/4/2023 10:13:55 AM | Mindanao Grid-10/04/2023 10:16: TM2 Unit 2 cut in at 1000H. Ancillary Reserve Testing [WEBSMS] | CMIN
10/4/2023 9:06:28 AM | Mindanao Grid-10/04/2023 09:09: SPC Mati Diesel cut in at 0900H. [WEBSMS] | CMIN
10/4/2023 8:53:45 AM | Mindanao Grid-10/04/2023 08:56: WMPC DG10 cut in at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/4/2023 8:35:22 AM | Mindanao Grid-10/04/2023 08:38: Kibawe SS 138kV Bus 1 de-energized 0832H (Planned outage). [WEBSMS] | CMIN
10/4/2023 8:29:02 AM | Mindanao Grid-10/04/2023 08:31: NBT Euro Hydro tripped with load of 1.5 MW, affected by the tripping of NORDECO line. Restored at 0438H. [WEBSMS] | CMIN
10/4/2023 6:41:57 AM | Luzon Grid-10/04/2023 06:41: Quezon(Balintawak)-San Jose 230kV Line 2 restored at 0641H (Planned Outage) [WEBSMS] | CLUZ
10/4/2023 5:59:04 AM | [NSO Update] Mindanao Grid-10/04/2023 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2904MW, PK=2253MW, RR=30MW, NetOpMargin: AM=621, PM=604, EVE=619 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @100MW, AG5 @42MW, AG6 @149MW, AG7 @25MW, PG4 @105MW [WEBSMS] | CMIN
10/4/2023 5:55:47 AM | [NSO Update] Luzon Grid-10/04/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12915MW, PK=11116MW, RR=444MW, NetOpMargin: AM=1355, PM=976, EVE=1311 Highest Unit O/L: SUAL 1 @647MW Derated Plant: CLC1 @230MW, DINGININ 2 @334MW, MSLC2 @335MW, MSLC3 @315MW, PBL1 @300MW, SUAL 2 @550MW, ILIJAN A @480MW, ILIJAN B @ 290MW, STA. RITA 10 @200MW, STA. RITA 20 @235MW [WEBSMS] | CLUZ
10/4/2023 5:23:46 AM | [NSO Update] Mindanao Grid-10/04/2023 05:26: Weather Update: At 3:00 AM today, the center of the eye of Typhoon JENNY was estimated based on all available data at 275 km East Northeast of Itbayat, Batanes (21.9 N, 124.2 E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CMIN
10/4/2023 5:23:28 AM | [NSO Update] Visayas Grid-10/04/2023 05:23: Weather Update: At 3:00 AM today, the center of the eye of Typhoon JENNY was estimated based on all available data at 275 km East Northeast of Itbayat, Batanes (21.9 N, 124.2 E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CVIS
10/4/2023 5:23:13 AM | [NSO Update] Luzon Grid-10/04/2023 05:23: Weather Update: At 3:00 AM today, the center of the eye of Typhoon JENNY was estimated based on all available data at 275 km East Northeast of Itbayat, Batanes (21.9 N, 124.2 E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CLUZ
10/4/2023 3:40:14 AM | Visayas Grid-10/04/2023 03:40: CEDC U2 synchronized at 0335H. (Planned Outage) [WEBSMS] | CVIS
10/3/2023 9:58:22 PM | Visayas Grid-10/03/2023 21:58: Cebu SS 300MVA 230KV/138KV/13.8KV TR1 energized at 2152H for soaking (Under test & Commissioning). [WEBSMS] | CVIS
10/3/2023 9:47:36 PM | Mindanao Grid-10/03/2023 21:50: EURO HYDRO (NBT) tripped with 1.5MW load at 2128H affected by the NORDECO line outage. [WEBSMS] | CMIN
10/3/2023 9:19:58 PM | Mindanao Grid-10/03/2023 21:23: WMPC DG10 cut-out at 2113H. End of RPS - System Voltage Requirement [WEBSMS] | CMIN
10/3/2023 9:06:54 PM | Luzon Grid-10/03/2023 21:07: Quezon(Balintawak)-San Jose 230kV Line 2 de-energized at 2107H (Planned Outage) [WEBSMS] | CLUZ
10/3/2023 8:30:15 PM | Luzon Grid-10/03/2023 20:30: Labrador 230kV Bus 1 New Main Protection commissioned at 2025H. (End of Commissioning) [WEBSMS] | CLUZ
10/3/2023 8:29:01 PM | Luzon Grid-10/03/2023 20:29: Correction: Labrador 230kV Bus 1 energized at 1941H (On Commissioning) [WEBSMS] | CLUZ
10/3/2023 7:44:00 PM | Luzon Grid-10/03/2023 19:44: Labrador 230kV Line 1 energized at 1941H (On Commissioning) [WEBSMS] | CLUZ
10/3/2023 7:35:22 PM | Mindanao Grid-10/03/2023 19:38: TM1 unit 1 cut out at 1926H. End of market RTD. [WEBSMS] | CMIN
10/3/2023 7:30:00 PM | Mindanao Grid-10/03/2023 19:33: SPC Mati cut in at 1745H. Follow market RTD. [WEBSMS] | CMIN
10/3/2023 7:29:08 PM | Mindanao Grid-10/03/2023 19:32: SPC Mati tripped with 4.0MW load at 1757H due to reverse power indication. [WEBSMS] | CMIN
10/3/2023 7:28:33 PM | Mindanao Grid-10/03/2023 19:31: SPC Mati tripped with 4.3MW load at 1741H due to reverse power indication. [WEBSMS] | CMIN
10/3/2023 7:26:02 PM | Mindanao Grid-10/03/2023 19:29: SPC Mati cut in from FO affected from FO of Maco - Bananaybany 69kV Line. [WEBSMS] | CMIN
10/3/2023 6:56:07 PM | Mindanao Grid-10/03/2023 18:59: TM2 Unit 2 cut out at 1852H. Follow Market RTD [WEBSMS] | CMIN
10/3/2023 6:42:55 PM | Mindanao Grid-10/03/2023 18:46: WMPC DG07 cut out at 1840H. Follow Market RTD [WEBSMS] | CMIN
10/3/2023 6:41:50 PM | Mindanao Grid-10/03/2023 18:44: WMPC DG05 cut out at 1838H. Follow Market RTD [WEBSMS] | CMIN
10/3/2023 6:35:49 PM | Mindanao Grid-10/03/2023 18:38: Tudaya 1 Unit 1 cut in at 1726H. (Planned outage GOMP) [WEBSMS] | CMIN
10/3/2023 6:32:56 PM | Mindanao Grid-10/03/2023 18:36: WMPC DG01 cut out at 1832H. Follow Market RTD. [WEBSMS] | CMIN
10/3/2023 6:22:49 PM | [NSO Update] Mindanao Grid-10/03/2023 18:25: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2867MW, PK=2183MW, RR=30MW, NetOpMargin: EVE=655 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @96MW, AG5 @44MW, AG6 @149MW, AG7 @25MW, PG4 @125MW [WEBSMS] | CMIN
10/3/2023 6:16:47 PM | [NSO Update] Luzon Grid-10/03/2023 18:17: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12230MW, PK=10415MW, RR=406MW, NetOpMargin: EVE=1408 Highest Unit O/L: Sual 1 @647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 280MW, Sual 2 @ 550MW, Sta. Rita 10 @ 200MW, Sta. Rita 20 @ 235MW, Ilijan A @ 480MW, Ilijan B @ 290MW [WEBSMS] | CLUZ
10/3/2023 6:14:49 PM | [NSO Update] Mindanao Grid-10/03/2023 18:17: Weather Update: At 3:00 PM today, the center of the eye of Typhoon JENNY was estimated based on all available data at 325 km East of Itbayat, Batanes (21.3 N, 124.9 E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving North Northwestward at 10 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CMIN
10/3/2023 6:14:28 PM | [NSO Update] Visayas Grid-10/03/2023 18:14: Weather Update: At 3:00 PM today, the center of the eye of Typhoon JENNY was estimated based on all available data at 325 km East of Itbayat, Batanes (21.3 N, 124.9 E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving North Northwestward at 10 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CVIS
10/3/2023 6:14:11 PM | [NSO Update] Luzon Grid-10/03/2023 18:14: Weather Update: At 3:00 PM today, the center of the eye of Typhoon JENNY was estimated based on all available data at 325 km East of Itbayat, Batanes (21.3 N, 124.9 E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving North Northwestward at 10 km/h. Southwest Monsoon affecting Central Luzon, Southern Luzon, and Visayas. [WEBSMS] | CLUZ
10/3/2023 6:12:10 PM | Mindanao Grid-10/03/2023 18:15: WMPC DG01 cut in at 1802H. Follow Market RTD. [WEBSMS] | CMIN
10/3/2023 6:04:20 PM | Mindanao Grid-10/03/2023 18:07: TM1 U1 cut in at 1758H. MOT raised by 50MW. [WEBSMS] | CMIN
10/3/2023 6:03:55 PM | Mindanao Grid-10/03/2023 18:07: TM2 U2 cut in at 1757H. MOT raised by 50MW. [WEBSMS] | CMIN
10/3/2023 5:51:43 PM | Mindanao Grid-10/03/2023 17:54: WMPC DG07 cut in at 1750H. MOT raised by 10MW [WEBSMS] | CMIN
10/3/2023 5:50:38 PM | Mindanao Grid-10/03/2023 17:53: WMPC DG05 cut in at 1748H. MOT raised by 10MW. [WEBSMS] | CMIN
10/3/2023 5:05:28 PM | Mindanao Grid-10/03/2023 17:08: Villanueva SS 138kV Bus 1 energized at 1649H. Planned outage/Non-GOMP. [WEBSMS] | CMIN
10/3/2023 4:28:07 PM | Mindanao Grid-10/03/2023 16:31: SPC Mati Forced outage with 6.26 MW load at 1537H affected by the tripping of Maco - Banaybanay 69kV Line. [WEBSMS] | CMIN
10/3/2023 4:25:21 PM | Mindanao Grid-10/03/2023 16:28: TM2 U1 cut-out at 1622H. End of Ancillary testing. [WEBSMS] | CMIN
10/3/2023 4:21:42 PM | Mindanao Grid-10/03/2023 16:24: WMPC DG07 cut-out at 1613H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/3/2023 3:52:39 PM | [NSO Update] Visayas Grid-10/03/2023 15:53: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1547H with power going to Visayas. [WEBSMS] | CVIS
10/3/2023 2:21:23 PM | Mindanao Grid-10/03/2023 14:24: NACSUR (NSD) cut-in at 1420H, as energy. MO RTD dispatched. [WEBSMS] | CMIN
10/3/2023 2:02:15 PM | Mindanao Grid-10/03/2023 14:05: NACSUR cut out at 1400H. Follow RTD. [WEBSMS] | CMIN
10/3/2023 1:07:28 PM | [NSO Update] Mindanao Grid-10/03/2023 13:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1304H from forward power direction. [WEBSMS] | CMIN
10/3/2023 1:07:24 PM | [NSO Update] Visayas Grid-10/03/2023 13:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1304H from forward power direction. [WEBSMS] | CVIS
10/3/2023 1:01:19 PM | [NSO Update] Luzon Grid-10/03/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12714MW, PK=11204MW, RR=446MW, NetOpMargin: PM=1064, EVE=1344 Highest Unit O/L: Sual 1@647MW Derated Plant: Calaca 1 @ 180MW, GNPD 2 @ 334MW, Masinloc 2 @ 330MW, Masinloc 3 @ 315MW, SLPGC 1 @ 147MW, Sual 2 @ 550MW, Sta. Rita 20 @ 235MW, Ilijan A @ 480MW, Ilijan B @ 290MW [WEBSMS] | CLUZ
10/3/2023 12:47:51 PM | Luzon Grid-10/03/2023 12:48: San Gabriel shutdown at 1244H due to gas restriction (Unplanned Outage) [WEBSMS] | CLUZ
10/3/2023 12:45:48 PM | Mindanao Grid-10/03/2023 12:48: Peak Power Socsargen U 4 & U5 cut in at 1235H. MOT raised by 12MW. [WEBSMS] | CMIN
10/3/2023 12:45:39 PM | [NSO Update] Mindanao Grid-10/03/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2906MW, PK=2330MW, RR=30MW, NetOpMargin: PM=545, EVE=569 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @96MW, AG5 @44MW, AG6 @149MW, AG7 @25MW, PG4 @125MW [WEBSMS] | CMIN
10/3/2023 12:39:50 PM | Mindanao Grid-10/03/2023 12:42: Peak Power San Francisco cut in at 1228H. MOT raised by 5MW. [WEBSMS] | CMIN
10/3/2023 12:38:25 PM | Mindanao Grid-10/03/2023 12:41: Peak Power Bukidnon cut in at 1230H. MOT raised. [WEBSMS] | CMIN
10/3/2023 12:05:09 PM | Visayas Grid-10/03/2023 12:05: Magdugo - Dumanjug 230 kV Line 2 energized at 1201H. (Unplanned Outage) [WEBSMS] | CVIS
10/3/2023 11:23:45 AM | Luzon Grid-10/03/2023 11:24: Correction: For info: San Jose PCB 9-08CB04SJO and 9-01CB04SJO closed at 1121H (Planned Outage) [WEBSMS] | CLUZ
10/3/2023 11:21:56 AM | Luzon Grid-10/03/2023 11:22: For info: San Jose PCB 9-08CB04SJO and 9-01CB04SJO closed at 1040H (Planned Outage) [WEBSMS] | CLUZ
10/3/2023 10:38:20 AM | Luzon Grid-10/03/2023 10:38: Sta Rita 10 online at 1035H (Unplanned Outage) [WEBSMS] | CLUZ
10/3/2023 10:25:14 AM | Mindanao Grid-10/03/2023 10:28: TM2 unit 1 synchronized at 1011H via CB04(7LINAS-TM2)TM2 . Black Start Testing. [WEBSMS] | CMIN
10/3/2023 9:34:07 AM | Mindanao Grid-10/03/2023 09:37: NACSUR (NSD) cut-in at 0926H, as energy. MO RTD dispatched. [WEBSMS] | CMIN
10/3/2023 9:24:35 AM | Mindanao Grid-10/03/2023 09:27: Villanueva SS 138kV Bus 1 de-energized 0854H. Planned outage/Non-GOMP. [WEBSMS] | CMIN
10/3/2023 9:13:25 AM | Luzon Grid-10/03/2023 09:13: Sta Rita 10 with 166MW load tripped at 0909H. Lowest Frequency is 59.58Hz(Unplanned Outage) [WEBSMS] | CLUZ
10/3/2023 9:02:10 AM | Mindanao Grid-10/03/2023 09:05: SUPREME MATI DIESEL (MDP) cut in at 0900H. Follow RTD. [WEBSMS] | CMIN
10/3/2023 8:54:29 AM | Mindanao Grid-10/03/2023 08:57: WMPC DG10 cut-in at 0852H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/3/2023 6:03:07 AM | [NSO Update] Luzon Grid-10/03/2023 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13252MW, PK=11355MW, RR=444MW, NetOpMargin: AM=1453, PM=1028, EVE=1556 Highest Unit O/L: Sual 1 @ 647MW Derated Plant: Calaca 1 @ 220MW, GNPD 2 @ 334MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 280MW, SLPGC 1 @ 147MW, Sual 2 @ 550MW, Sta. Rita 20 @ 235MW, Ilijan A @ 480MW, Ilijan B @ 290MW [WEBSMS] | CLUZ
10/3/2023 6:00:50 AM | [NSO Update] Mindanao Grid-10/03/2023 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2953MW, PK=2226MW, RR=30MW, NetOpMargin: AM=697, PM=615, EVE=579 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @90MW, AG4 @96MW, AG5 @44MW, AG6 @149MW, AG7 @25MW, PG4 @125MW [WEBSMS] | CMIN
10/3/2023 5:26:06 AM | Mindanao Grid-10/03/2023 05:29: Baloi-Agus4 138 kV L1 restored/energized 0524H (Planned outage). [WEBSMS] | CMIN
10/3/2023 4:15:18 AM | [NSO Update] Luzon Grid-10/03/2023 04:15: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "JENNY" {KOINU} was estimated based on all available data at 360 km East of Basco, Batanes (20.2�N, 125.4�E) with maximum sustained winds of 165 km/h near the center and gustiness of up to 205 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Southern Luzon, Visayas and Mindanao. [WEBSMS] | CLUZ
10/3/2023 4:15:01 AM | [NSO Update] Mindanao Grid-10/03/2023 04:18: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "JENNY" {KOINU} was estimated based on all available data at 360 km East of Basco, Batanes (20.2�N, 125.4�E) with maximum sustained winds of 165 km/h near the center and gustiness of up to 205 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Southern Luzon, Visayas and Mindanao. [WEBSMS] | CMIN
10/3/2023 4:14:45 AM | [NSO Update] Visayas Grid-10/03/2023 04:15: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "JENNY" {KOINU} was estimated based on all available data at 360 km East of Basco, Batanes (20.2�N, 125.4�E) with maximum sustained winds of 165 km/h near the center and gustiness of up to 205 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Southern Luzon, Visayas and Mindanao. [WEBSMS] | CVIS
10/3/2023 3:46:45 AM | Mindanao Grid-10/03/2023 03:49: Lake Mainit (AGC) HEP cut-in at 0343H. (Unplanned Outage) [WEBSMS] | CMIN
10/3/2023 3:30:51 AM | Mindanao Grid-10/03/2023 03:33: Lake Mainit (AGC) HEP tripped with 10.5MW at 0325H, indication: Power Signal Fault. (Unplanned Outage) [WEBSMS] | CMIN
10/3/2023 3:14:14 AM | Mindanao Grid-10/03/2023 03:17: Baloi-Agus4 138 kV L1 de-energized 0312H (Planned outage). [WEBSMS] | CMIN
10/2/2023 11:48:24 PM | Luzon Grid-10/02/2023 23:48: For info: San Lorenzo Module 50 fuel changeover from gas to oil was completed at 2344H. (Gas supply restriction) [WEBSMS] | CLUZ
10/2/2023 11:30:54 PM | Luzon Grid-10/02/2023 23:31: For info: Sta Rita Module 40 completed the fuel changeover from gas to oil at 2257H. (Gas supply restriction) [WEBSMS] | CLUZ
10/2/2023 11:13:34 PM | Visayas Grid-10/02/2023 23:14: Carcon-Sangi 34.5kV Line 3 restored at 2307H. (Unplanned outage) [WEBSMS] | CVIS
10/2/2023 10:18:38 PM | Visayas Grid-10/02/2023 22:19: Carcon-Sangi 34.5kV Line 3 tripped at 2209H. (Unplanned outage) [WEBSMS] | CVIS
10/2/2023 9:56:31 PM | Mindanao Grid-10/02/2023 21:59: FDC U3 cut-in at 2130H (generator protection relay problem rectified). (Unplanned Outage). [WEBSMS] | CMIN
10/2/2023 9:35:24 PM | Mindanao Grid-10/02/2023 21:38: WMPC DG06 cut-out at 2113H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/2/2023 9:28:32 PM | Luzon Grid-10/02/2023 21:28: For info: Sta Rita Module 20 completed the fuel changeover from gas to oil at 2038H due to gas restriction. [WEBSMS] | CLUZ
10/2/2023 8:43:04 PM | [NSO Update] Mindanao Grid-10/02/2023 20:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 2040H with power going to Visayas. [WEBSMS] | CMIN
10/2/2023 8:42:49 PM | [NSO Update] Visayas Grid-10/02/2023 20:43: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 2040H with power going to Visayas. [WEBSMS] | CVIS
10/2/2023 7:57:43 PM | Visayas Grid-10/02/2023 19:58: Calongcalong-Magdugo 138 KV Line 2 energized at 1940H. Line 1 energized at 1955H, activity completed. (Planned Outage). [WEBSMS] | CVIS
10/2/2023 6:46:04 PM | Mindanao Grid-10/02/2023 18:49: SUPREME Power Mati (MDP) cut-in at 1741H. (Unplanned Outage) [WEBSMS] | CMIN
10/2/2023 6:33:32 PM | Mindanao Grid-10/02/2023 18:36: SUPREME Power Mati (MDP) with 4.4MW load tripped at 1721H, due to reverse power. (Unplanned Outage) [WEBSMS] | CMIN
10/2/2023 6:22:25 PM | Luzon Grid-10/02/2023 18:22: Nagsaag PCB 9-02CB24NGS restored at 1821H (Unplanned Outage) [WEBSMS] | CLUZ
10/2/2023 6:18:49 PM | Mindanao Grid-10/02/2023 18:21: Supreme Power Mati cut-in at 1310H. (Unplanned Outage) [WEBSMS] | CMIN
10/2/2023 6:17:51 PM | Mindanao Grid-10/02/2023 18:20: Supreme Power Mati tripped with 6MW load at 1304H. Frequency=59.44Hz. Indication: Reverse Power Trip (Unplanned Outage) [WEBSMS] | CMIN
10/2/2023 6:15:29 PM | [NSO Update] Mindanao Grid-10/02/2023 18:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2779MW, PK=2172MW, RR=20MW, NetOpMargin: EVE=587 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @90MW, AG4 @96MW, AG5 @41MW, AG6 @149MW, AG7 @25MW, PG4 @125MW [WEBSMS] | CMIN
10/2/2023 6:14:02 PM | [NSO Update] Luzon Grid-10/02/2023 18:14: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12415MW, PK=10532MW, RR=446MW, NetOpMargin: EVE=1437 Highest Unit O/L: SUAL 1&2 @647MW Derated Plant: GNPD 2 @334MW, MSLC1 @320MW, MSLC2 @320MW, MSLC3 @310MW, ILIJAN A @480MW, ILIJAN B @290MW, CLC 1 @230MW [WEBSMS] | CLUZ
10/2/2023 6:11:26 PM | Mindanao Grid-10/02/2023 18:14: Supreme Power Mati cut-in at 1246H. (Unplanned Outage) [WEBSMS] | CMIN
10/2/2023 6:10:48 PM | Mindanao Grid-10/02/2023 18:13: Supreme Power Mati tripped with 4MW load at 1226H. Frequency=59.4Hz. Indication: Reverse Power Trip. (Unplanned Outage) [WEBSMS] | CMIN
10/2/2023 6:10:40 PM | Mindanao Grid-10/02/2023 18:13: FDC Unit 3 cut-in 17:21:07H from PMS, but tripped at 17:21:12H, details to follow. Unplanned Outage [WEBSMS] | CMIN
10/2/2023 5:41:00 PM | Luzon Grid-10/02/2023 17:41: Pagbilao Unit 3 online at 1739H. (Unplanned Outage) [WEBSMS] | CLUZ
10/2/2023 5:23:06 PM | [NSO Update] Mindanao Grid-10/02/2023 17:26: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1720H from reverse power direction. [WEBSMS] | CMIN
10/2/2023 5:22:46 PM | [NSO Update] Visayas Grid-10/02/2023 17:23: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1720H from reverse power direction. [WEBSMS] | CVIS
10/2/2023 5:01:35 PM | Luzon Grid-10/02/2023 17:02: Nagsaag PCB 9-02CB24NGS was de-energized at 1659H to facilitate immediate repair of hydraulic pump. (Unplanned Outage) [WEBSMS] | CLUZ
10/2/2023 4:43:49 PM | Mindanao Grid-10/02/2023 16:46: WMPC DG06 cut-out at 1614H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/2/2023 3:32:33 PM | Mindanao Grid-10/02/2023 15:35: Supreme Power Mati cut-in at 1126H. (Unplanned Outage) [WEBSMS] | CMIN
10/2/2023 3:30:11 PM | Mindanao Grid-10/02/2023 15:33: Supreme Power Mati tripped with 4MW load at 1059H. Frequency=59.4Hz. Indication: Reverse Power Trip (Unplanned Outage) [WEBSMS] | CMIN
10/2/2023 2:54:38 PM | Luzon Grid-10/02/2023 14:55: SLPGC 230kV Bus 2 and Calaca-SLPGC 230kV line 2 were restored at 1452H.(Customer Owned)(Unplanned Outage) [WEBSMS] | CLUZ
10/2/2023 1:56:17 PM | Mindanao Grid-10/02/2023 13:59: (Correction) Sibulan A Hydro emergency shutdown at 1100H to facilitate turbine inspection. [WEBSMS] | CMIN
10/2/2023 1:50:41 PM | Mindanao Grid-10/02/2023 13:53: Sibulan A Hydro emergency shutdown at 1134H to facilitate turbine inspection. [WEBSMS] | CMIN
10/2/2023 1:10:08 PM | [NSO Update] Mindanao Grid-10/02/2023 13:13: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1301H with power going to Mindanao. [WEBSMS] | CMIN
10/2/2023 1:10:03 PM | [NSO Update] Visayas Grid-10/02/2023 13:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1301H with power going to Mindanao. [WEBSMS] | CVIS
10/2/2023 1:06:57 PM | [NSO Update] Mindanao Grid-10/02/2023 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2796MW, PK=2291MW, RR=20MW, NetOpMargin: PM=485, EVE=527 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @90MW, AG4 @96MW, AG5 @41MW, AG6 @149MW, AG7 @25MW, PG4 @105MW [WEBSMS] | CMIN
10/2/2023 12:59:35 PM | [NSO Update] Luzon Grid-10/02/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13009MW, PK=11482MW, RR=446MW, NetOpMargin: PM=1081, EVE=1364 Highest Unit O/L: SUAL 1&2 @647MW Derated Plant: GNPD 2 @334MW, MSLC1 @320MW, MSLC2 @320MW, MSLC3 @310MW, ILIJAN A @480MW, ILIJAN B @290MW [WEBSMS] | CLUZ
10/2/2023 11:47:14 AM | Visayas Grid-10/02/2023 11:47: Calongcalong-Magdugo 138 KV Line 1 de-energized at 1147H. (Planned Outage) [WEBSMS] | CVIS
10/2/2023 11:15:27 AM | Mindanao Grid-10/02/2023 11:18: STEAG Unit 1 emergency shutdown at 1110H due to boiler fouling. (Unplanned Outage) [WEBSMS] | CMIN
10/2/2023 11:06:21 AM | [NSO Update] Mindanao Grid-10/02/2023 11:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1104H from forward power direction. [WEBSMS] | CMIN
10/2/2023 11:06:17 AM | [NSO Update] Visayas Grid-10/02/2023 11:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1104H from forward power direction. [WEBSMS] | CVIS
10/2/2023 11:05:48 AM | Visayas Grid-10/02/2023 11:06: Toledo-Calongcalong 138 KV Line energized at 1104H. (Planned Outage) [WEBSMS] | CVIS
10/2/2023 11:02:28 AM | Luzon Grid-10/02/2023 11:02: Pagbilao Unit 1 online at 1100H (Unplanned Outage) [WEBSMS] | CLUZ
10/2/2023 10:53:00 AM | Mindanao Grid-10/02/2023 10:56: WMPC DG06 cut-in at 1051H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/2/2023 9:06:15 AM | Mindanao Grid-10/02/2023 09:09: Agus 2 HEP Unit 1 shutdown at 0905H. (Planned Outage) [WEBSMS] | CMIN
10/2/2023 9:02:32 AM | Mindanao Grid-10/02/2023 09:05: (Correction) Agus 7 HEP Unit 2 shutdown at 0901H. (Planned Outage) [WEBSMS] | CMIN
10/2/2023 9:01:49 AM | Mindanao Grid-10/02/2023 09:04: Agus 7 HEP Unit 2 shutdown at 0808H. (Planned Outage) [WEBSMS] | CMIN
10/2/2023 8:54:43 AM | Mindanao Grid-10/02/2023 08:57: WMPC DG10 cut-in at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
10/2/2023 8:37:54 AM | Mindanao Grid-10/02/2023 08:40: Villanueva SS 138kV Bus 2 de-energized 0830H (Planned outage). [WEBSMS] | CMIN
10/2/2023 8:08:45 AM | Mindanao Grid-10/02/2023 08:11: Agus 4 HEP Unit 2 shutdown at 0808H. (Planned Outage) [WEBSMS] | CMIN
10/2/2023 6:34:50 AM | Luzon Grid-10/02/2023 06:35: Quezon(Balintawak)-Dona Imelda(Araneta) 230kV Line restored at 0634H (Planned Outage) [WEBSMS] | CLUZ
10/2/2023 6:20:17 AM | Luzon Grid-10/02/2023 06:20: Labrador 230kV Bus 1 de-energized at 0608H (Planned Outage) [WEBSMS] | CLUZ
10/2/2023 5:49:10 AM | [NSO Update] Mindanao Grid-10/02/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2898MW, PK=2173MW, RR=20MW, NetOpMargin: AM=705, PM=596, EVE=691 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @90MW, AG4 @96MW, AG5 @41MW, AG6 @149MW, AG7 @25MW, PG4 @105MW [WEBSMS] | CMIN
10/2/2023 5:40:45 AM | Mindanao Grid-10/02/2023 05:43: Davao SS 138kV Transformer no. 3 restored at 0538H. (Planned Outage) [WEBSMS] | CMIN
10/2/2023 5:40:19 AM | [NSO Update] Luzon Grid-10/02/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12782MW, PK=11020MW, RR=446MW, NetOpMargin: AM=1316, PM=1105, EVE=1195 Highest Unit O/L: SUAL 1&2 @647MW Derated Plant: GNPD 2 @334MW, MSLC1 @320MW, MSLC2 @320MW, MSLC3 @310MW, ILIJAN A @480MW, ILIJAN B @290MW [WEBSMS] | CLUZ
10/2/2023 4:43:45 AM | [NSO Update] Mindanao Grid-10/02/2023 04:46: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "JENNY" {KOINU} was estimated based on all available data at 675 km East of Aparri, Cagayan (18.8�N, 128.0�E) with maximum sustained winds of 120 km/h near the center and gustiness of up to 150 km/h. It is moving Northwestward at 10 km/h. Southwest Monsoon affecting Southern Luzon, Visayas and Mindanao. [WEBSMS] | CMIN
10/2/2023 4:42:32 AM | [NSO Update] Visayas Grid-10/02/2023 04:42: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "JENNY" {KOINU} was estimated based on all available data at 675 km East of Aparri, Cagayan (18.8�N, 128.0�E) with maximum sustained winds of 120 km/h near the center and gustiness of up to 150 km/h. It is moving Northwestward at 10 km/h. Southwest Monsoon affecting Southern Luzon, Visayas and Mindanao. [WEBSMS] | CVIS
10/2/2023 4:39:50 AM | [NSO Update] Luzon Grid-10/02/2023 04:40: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "JENNY" {KOINU} was estimated based on all available data at 675 km East of Aparri, Cagayan (18.8�N, 128.0�E) with maximum sustained winds of 120 km/h near the center and gustiness of up to 150 km/h. It is moving Northwestward at 10 km/h. Southwest Monsoon affecting Southern Luzon, Visayas and Mindanao. [WEBSMS] | CLUZ
10/2/2023 4:14:33 AM | Mindanao Grid-10/02/2023 04:17: Davao SS 138kV Transformer no. 3 de-energized at 0406H. (Planned Outage) [WEBSMS] | CMIN
10/2/2023 1:13:50 AM | Mindanao Grid-10/02/2023 01:16: SPGI Biomass shutdown at 1220H. PMS (GOMP). Etc October 21, 2023. [WEBSMS] | CMIN
10/2/2023 12:27:48 AM | Luzon Grid-10/02/2023 00:28: SBPL online at 0026H. (Unplanned Outage) [WEBSMS] | CLUZ
10/2/2023 12:18:25 AM | Luzon Grid-10/02/2023 00:18: Bolo 230kV Bus 1 New Main Protection fully commissioned at 0016H. (End of commissioning) [WEBSMS] | CLUZ
10/1/2023 10:51:36 PM | Luzon Grid-10/01/2023 22:47: Bolo SS 230kV Bus 1 energized at 2244H. (On-going Commissioning) [WEBSMS] | CLUZ
10/1/2023 10:21:05 PM | Luzon Grid-10/01/2023 22:21: QPPL online at 2218H. (Unplanned Outage) [WEBSMS] | CLUZ
10/1/2023 10:08:16 PM | Luzon Grid-10/01/2023 22:08: Quezon(Balintawak)-Dona Imelda(Araneta) 230kV Line de-energized at 2207H. (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 8:55:38 PM | Luzon Grid-10/01/2023 20:56: San Lorenzo 60 online at 2054H. (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 8:53:16 PM | Mindanao Grid-10/01/2023 20:56: Update: STEAG U2 not Unit 1, emergency shutdown at 20:40:10H due to Boiler Fouling, with load of 100MW. (Unplanned Outage). [WEBSMS] | CMIN
10/1/2023 8:51:00 PM | Mindanao Grid-10/01/2023 20:54: STEAG U1 emergency shutdown at 20:40:10H due to Boiler Fouling, with load of 100MW. (Unplanned Outage). [WEBSMS] | CMIN
10/1/2023 7:53:10 PM | [NSO Update] Luzon Grid-10/01/2023 19:53: SO-initiated Market Intervention for the Luzon Grid has been lifted today, 01 October 2023 at 1940H. Market will resume starting interval 1945H. [WEBSMS] | CLUZ
10/1/2023 7:39:15 PM | Luzon Grid-10/01/2023 19:39: ALD affected feeders of NGCP and Meralco were restored at 1933H. [WEBSMS] | CLUZ
10/1/2023 7:24:18 PM | Luzon Grid-10/01/2023 19:24: San Jose - Nagsaag 500kV Line 2 restored at 1924H. (Unplanned Outage) [WEBSMS] | CLUZ
10/1/2023 7:24:07 PM | [NSO Update] Luzon Grid-10/01/2023 19:24: SO-initiated Market Intervention is issued today, 01 October 2023, for the Luzon Grid starting interval 1915H due to unimplementable RTD schedule brought about by multiple tripping incidents. [WEBSMS] | CLUZ
10/1/2023 6:58:29 PM | Luzon Grid-10/01/2023 18:58: San Jose - Nagsaag 500kV Line 2 tripped at 1845H. (Unplanned Outage) [WEBSMS] | CLUZ
10/1/2023 6:57:23 PM | Luzon Grid-10/01/2023 18:57: ALD occurred at NGCP and Meralco feeders due to the tripping of Pagbilao 1 (352MW), Pagbilao 3 (411MW), QPPL (239MW) and SBPL (300MW) at 1845H. The lowest system frequency was 58.649Hz. [WEBSMS] | CLUZ
10/1/2023 6:47:51 PM | Mindanao Grid-10/01/2023 18:50: NBT cut-in at 1816H. (Unplanned Outage) [WEBSMS] | CMIN
10/1/2023 6:42:46 PM | Mindanao Grid-10/01/2023 18:45: NBT with a load of 1.7MW trip at 1758H. Affected by voltage fluctuation at NORDECO system. (Unplanned Outage). [WEBSMS] | CMIN
10/1/2023 6:13:41 PM | [NSO Update] Mindanao Grid-10/01/2023 18:16: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2881MW, PK=1990MW, RR=20MW, NetOpMargin: EVE=871 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @125MW [WEBSMS] | CMIN
10/1/2023 5:55:25 PM | [NSO Update] Luzon Grid-10/01/2023 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12700MW, PK=9874MW, RR=356MW, NetOpMargin: EVE=2470 Highest Unit O/L: SUAL 1&2 @647MW Derated Plant: GNPD 2 @334MW, MSLC1 @330MW, MSLC2 @320MW, MSLC3 @320MW, SCPC 3 @100MW, ILIJAN A @480MW, ILIJAN B @290MW [WEBSMS] | CLUZ
10/1/2023 5:45:37 PM | Luzon Grid-10/01/2023 17:46: San Jose - Taytay 230kV Line 2 restored at 1745H. (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 5:01:38 PM | Luzon Grid-10/01/2023 17:02: Balsik 500kV Bus 2 restored at 1701H. (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 4:58:22 PM | Luzon Grid-10/01/2023 16:58: La Trinidad - Binga 230kV Line 2 auto-tripped/auto-reclosed at 1656H.(Unplanned Outage) [WEBSMS] | CLUZ
10/1/2023 4:48:50 PM | Luzon Grid-10/01/2023 16:49: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1648H. (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 4:14:30 PM | [NSO Update] Visayas Grid-10/01/2023 16:14: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm JENNY was estimated based on all available data at 770 km East of Northern Luzon (18.1 N, 128.9 E) with maximum sustained winds of 100 km/h near the center and gustiness of up to 125 km/h. It is moving Northwestward at 15 km/h. Southwest Monsoon affecting Southern Luzon, Visayas and Mindanao. [WEBSMS] | CVIS
10/1/2023 4:14:10 PM | [NSO Update] Mindanao Grid-10/01/2023 16:17: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm JENNY was estimated based on all available data at 770 km East of Northern Luzon (18.1 N, 128.9 E) with maximum sustained winds of 100 km/h near the center and gustiness of up to 125 km/h. It is moving Northwestward at 15 km/h. Southwest Monsoon affecting Southern Luzon, Visayas and Mindanao. [WEBSMS] | CMIN
10/1/2023 4:13:45 PM | [NSO Update] Luzon Grid-10/01/2023 16:14: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm JENNY was estimated based on all available data at 770 km East of Northern Luzon (18.1 N, 128.9 E) with maximum sustained winds of 100 km/h near the center and gustiness of up to 125 km/h. It is moving Northwestward at 15 km/h. Southwest Monsoon affecting Southern Luzon, Visayas and Mindanao. [WEBSMS] | CLUZ
10/1/2023 3:10:35 PM | Mindanao Grid-10/01/2023 15:13: Talomo A (TL1) HEP cut-in at 1437H. (Unplanned Outage) [WEBSMS] | CMIN
10/1/2023 3:05:00 PM | Visayas Grid-10/01/2023 15:05: Dumanjug-Magdugo 230kV Line 2 tripped at 1501H. (Unplanned Outage) [WEBSMS] | CVIS
10/1/2023 2:33:20 PM | Mindanao Grid-10/01/2023 14:36: Talomo A (TL1) Unit 1 tripped with 0.5MW load at 1342H. Relay indication: DECS 250 alarm activated, for HEDCORs further investigation. (Unplanned Outage). [WEBSMS] | CMIN
10/1/2023 2:32:48 PM | Luzon Grid-10/01/2023 14:33: Tuguegarao SS 230kV Bus 1 restored at 1432H. (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 2:29:46 PM | Mindanao Grid-10/01/2023 14:32: Tacurong SS 50MVA Power Transformer 2 restored/energized 1426H (Planned outage) [WEBSMS] | CMIN
10/1/2023 2:04:49 PM | Mindanao Grid-10/01/2023 14:07: TUDAYA 2 U2 HEP cut-in at 1200H. Affected by the planned maintenance activity of DLPC. (Planned Outage). [WEBSMS] | CMIN
10/1/2023 2:00:10 PM | Mindanao Grid-10/01/2023 14:03: UPDATE: Lake Mainit (AGC) auto tripped with 10.5MW load at 1127H. Relay indication: Power Signal Fault- Unit 3. Unplanned Outage. [WEBSMS] | CMIN
10/1/2023 1:37:29 PM | Luzon Grid-10/01/2023 13:37: San Jose SS 750MVA T01 de-energized at 1336H (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 1:09:55 PM | [NSO Update] Mindanao Grid-10/01/2023 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2896MW, PK=1776MW, RR=20MW, NetOpMargin: PM=1100, EVE=910 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @105MW [WEBSMS] | CMIN
10/1/2023 1:09:29 PM | Luzon Grid-10/01/2023 13:09: San Jose-Balsik 500kV Line restored at 1309H (Extended Outage) [WEBSMS] | CLUZ
10/1/2023 1:00:21 PM | [NSO Update] Luzon Grid-10/01/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13342MW, PK=9604MW, RR=356MW, NetOpMargin: PM=3383, EVE=2387 Highest Unit O/L: SUAL 1&2 @647MW Derated Plant: GNPD 2 @334MW, MSLC1 @320MW, MSLC2 @320MW, MSLC3 @320MW, ILIJAN A @480MW, ILIJAN B @290MW [WEBSMS] | CLUZ
10/1/2023 12:23:53 PM | Luzon Grid-10/01/2023 12:24: SCPC Unit 3 online at 1211H (Maintenance Outage) [WEBSMS] | CLUZ
10/1/2023 12:01:07 PM | Luzon Grid-10/01/2023 12:01: Lamao-SCPC 230kV Tie Line 3 restored at 1200H (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 11:46:53 AM | Mindanao Grid-10/01/2023 11:49: Lake Mainit (AGC) HEP cut-in at 1142H. Unplanned Outage. [WEBSMS] | CMIN
10/1/2023 11:32:23 AM | Mindanao Grid-10/01/2023 11:35: Lake Mainit (AGC) auto tripped with 10.5MW load at 1127H. Unplanned Outage. [WEBSMS] | CMIN
10/1/2023 11:11:08 AM | Mindanao Grid-10/01/2023 11:14: TUDAYA 2 U1 HEP cut-in at 0925H. Affected by the planned maintenance activity of DLPC. (Planned Outage). [WEBSMS] | CMIN
10/1/2023 10:59:00 AM | Mindanao Grid-10/01/2023 11:02: SIBULAN B HEP online at 0914H respectively. Affected by the Planned outage of DLPC. (PLANNED OUTAGE). [WEBSMS] | CMIN
10/1/2023 10:51:42 AM | Luzon Grid-10/01/2023 10:40: For info: Sta. Rita Module 40 completed the fuel changeover from oil to gas at 1038H. [WEBSMS] | CLUZ
10/1/2023 10:36:28 AM | Luzon Grid-10/01/2023 10:36: Balsik-Olongapo 230kV Line energized via Balsik side at 1035H (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 10:14:21 AM | Luzon Grid-10/01/2023 10:14: San Jose-Angat 115kV Line 3 restored at 1013H (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 9:18:27 AM | Mindanao Grid-10/01/2023 09:21: TUDAYA 1 U1 HEP cut-in at 0830H. Affected by the planned maintenance activity of DLPC. (Planned Outage). [WEBSMS] | CMIN
10/1/2023 9:16:09 AM | Mindanao Grid-10/01/2023 09:19: SIBULAN A U1 and U2 online at 0830H and 0834H respectively. Affected by the Planned outage of DLPC. (PLANNED OUTAGE) [WEBSMS] | CMIN
10/1/2023 9:11:49 AM | Luzon Grid-10/01/2023 09:12: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0906H (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 9:09:52 AM | Luzon Grid-10/01/2023 09:10: Balsik 500kV Bus 2 de-energized at 0906H (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 8:31:07 AM | Luzon Grid-10/01/2023 08:31: Lamao-SCPC 230kV Tie Line 3 de-energized at 0828H (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 8:18:42 AM | Luzon Grid-10/01/2023 08:19: Balsik-Olongapo 230kV Line de-energized at 0818H (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 8:14:13 AM | Mindanao Grid-10/01/2023 08:17: Pulangi 4 Unit 1 HEP shutdown at 0809H. PMS (GOMP). (Planned Outage) [WEBSMS] | CMIN
10/1/2023 8:10:38 AM | Mindanao Grid-10/01/2023 08:13: Maco-MSS 69kV line de-energized 0806H (Planned outage). [WEBSMS] | CMIN
10/1/2023 7:34:12 AM | Luzon Grid-10/01/2023 07:34: Tuguegarao SS 230kV Bus 1 de-energized at 0734H (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 7:09:36 AM | Luzon Grid-10/01/2023 07:09: San Jose-Angat 115kV Line 3 de-energized at 0709H (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 6:26:32 AM | Luzon Grid-10/01/2023 06:26: Quezon(Balintawak) 300MVA T03 restored at 0624H (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 6:20:40 AM | Mindanao Grid-10/01/2023 06:23: Tacurong SS 50MVA Power Transformer 2 de-energized 0617H (Planned outage). [WEBSMS] | CMIN
10/1/2023 6:07:57 AM | [NSO Update] Mindanao Grid-10/01/2023 06:11: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2926MW, PK=1702MW, RR=20MW, NetOpMargin: AM=1204, PM=1069, EVE=875 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @125MW [WEBSMS] | CMIN
10/1/2023 5:53:39 AM | [NSO Update] Luzon Grid-10/01/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13568MW, PK=9160MW, RR=356MW, NetOpMargin: AM=4051, PM=3534, EVE=2390 Highest Unit O/L: Sual 1 @ 647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 320MW, SLPGC 1 @ 110MW, Ilijan A @ 480MW, Ilijan B @ 290MW [WEBSMS] | CLUZ
10/1/2023 4:49:36 AM | [NSO Update] Mindanao Grid-10/01/2023 04:52: Weather Update: At 3:00 AM today, the center of Tropical Storm "JENNY" {KOINU} was estimated based on all available data at 845 km East of Central Luzon (17.2�N, 130.0�E) with maximum sustained winds of 85 km/h near the center and gustiness of up to 105 km/h. It is moving Northwestward at 20 km/h. Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
10/1/2023 4:23:50 AM | [NSO Update] Visayas Grid-10/01/2023 04:24: Weather Update: At 3:00 AM today, the center of Tropical Storm "JENNY" {KOINU} was estimated based on all available data at 845 km East of Central Luzon (17.2�N, 130.0�E) with maximum sustained winds of 85 km/h near the center and gustiness of up to 105 km/h. It is moving Northwestward at 20 km/h. Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
10/1/2023 4:21:55 AM | [NSO Update] Luzon Grid-10/01/2023 04:22: Weather Update: At 3:00 AM today, the center of Tropical Storm "JENNY" {KOINU} was estimated based on all available data at 845 km East of Central Luzon (17.2�N, 130.0�E) with maximum sustained winds of 85 km/h near the center and gustiness of up to 105 km/h. It is moving Northwestward at 20 km/h. Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
10/1/2023 1:14:52 AM | Luzon Grid-10/01/2023 01:15: SCPC Unit 3 shutdown at 0113H. (Maintenance outage) [WEBSMS] | CLUZ
10/1/2023 1:00:11 AM | Luzon Grid-10/01/2023 01:00: Quezon(Balintawak) 300MVA T03 - de-energized at 0058H (Planned Outage) [WEBSMS] | CLUZ
10/1/2023 12:33:15 AM | Mindanao Grid-10/01/2023 00:36: Sibulan Hydro shutdown at 0000H. Affected by maintenance activity of DLPC (pole erection). Outside management control, [WEBSMS] | CMIN
10/1/2023 12:32:40 AM | Mindanao Grid-10/01/2023 00:35: Tudaya1 shutdown at 2357H. Affected by maintenance activity of DLPC (pole erection). Outside management control, [WEBSMS] | CMIN
10/1/2023 12:31:33 AM | Mindanao Grid-10/01/2023 00:34: Tudaya2 shutdown at 2353H. Affected by maintenance activity of DLPC (pole erection). Outside management control, [WEBSMS] | CMIN
9/30/2023 10:50:25 PM | Luzon Grid-09/30/2023 22:46: Sual Unit 2 - online at 2233H (Planned Outage) [WEBSMS] | CLUZ
9/30/2023 9:49:34 PM | Mindanao Grid-09/30/2023 21:52: Villanueva BESS 138kV L1 restored at 2147H. (Planned Outage) [WEBSMS] | CMIN
9/30/2023 9:40:04 PM | Luzon Grid-09/30/2023 21:40: Correction of outage classification: San Jose 750MVA T05 - restored at 2122H (Planned Outage) [WEBSMS] | CLUZ
9/30/2023 9:23:33 PM | Luzon Grid-09/30/2023 21:23: San Jose 750MVA T05 - restored at 2122H (From an extended outage) [WEBSMS] | CLUZ
9/30/2023 5:49:20 PM | [NSO Update] Luzon Grid-09/30/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11905MW, PK=10358MW, RR=404MW, NetOpMargin: EVE=1143 Highest Unit O/L: Sual 1 @ 647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 310MW, SCPC 3 @ 110MW, SLPGC 1 @ 120MW, Ilijan A @ 480MW, Ilijan B @ 290MW [WEBSMS] | CLUZ
9/30/2023 5:44:55 PM | [NSO Update] Mindanao Grid-09/30/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3100MW, PK=2116MW, RR=25MW, NetOpMargin: EVE=959 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @190MW [WEBSMS] | CMIN
9/30/2023 5:04:43 PM | Luzon Grid-09/30/2023 17:05: LImay-Limay BESS 69kV line restored at 1703H (Planned Outage) [WEBSMS] | CLUZ
9/30/2023 4:59:43 PM | Mindanao Grid-09/30/2023 17:02: Matanao SS 138KV Bus 2 restored at 1649H. (Planned Outage) [WEBSMS] | CMIN
9/30/2023 4:48:50 PM | Luzon Grid-09/30/2023 16:49: Santiago SS 230kV Bus 2 restored at 1648H (Planned Outage) [WEBSMS] | CLUZ
9/30/2023 4:18:53 PM | [NSO Update] Visayas Grid-09/30/2023 16:19: Weather Update: At 3:00 PM today, the center of Tropical Storm "JENNY" {KOINU} was estimated based on all available data at 995 km East of Central Luzon (15.8�N, 130.9�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving Northwestward at 10 km/h. Southwest Monsoon affecting Southern Luzon and Visayas. [WEBSMS] | CVIS
9/30/2023 4:18:15 PM | [NSO Update] Mindanao Grid-09/30/2023 16:21: Weather Update: At 3:00 PM today, the center of Tropical Storm "JENNY" {KOINU} was estimated based on all available data at 995 km East of Central Luzon (15.8�N, 130.9�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving Northwestward at 10 km/h. Southwest Monsoon affecting Southern Luzon and Visayas. [WEBSMS] | CMIN
9/30/2023 4:16:26 PM | [NSO Update] Luzon Grid-09/30/2023 16:16: Weather Update: At 3:00 PM today, the center of Tropical Storm "JENNY" {KOINU} was estimated based on all available data at 995 km East of Central Luzon (15.8�N, 130.9�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving Northwestward at 10 km/h. Southwest Monsoon affecting Southern Luzon and Visayas. [WEBSMS] | CLUZ
9/30/2023 3:51:02 PM | Luzon Grid-09/30/2023 15:51: Santiago SS 230kV Bus 2 de-energized at 1548H (Planned Outage) [WEBSMS] | CLUZ
9/30/2023 3:16:08 PM | Mindanao Grid-09/30/2023 15:19: WMPC DG10 cut-out at 1513H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/30/2023 1:12:37 PM | Visayas Grid-09/30/2023 13:12: Dumanjug-Magdugo 230 KV Line 2 energized at 1312H. (Unplanned Outage) [WEBSMS] | CVIS
9/30/2023 12:52:36 PM | [NSO Update] Luzon Grid-09/30/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12579MW, PK=10531MW, RR=356MW, NetOpMargin: PM=1692, EVE=1354 Highest Unit O/L: Sual 1 @ 647MW Derated Plant: GNPD 2 @ 334MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 310MW, SCPC 3 @ 110MW, SLPGC 1 @ 80MW, Ilijan A @ 480MW, Ilijan B @ 290MW [WEBSMS] | CLUZ
9/30/2023 12:49:36 PM | [NSO Update] Mindanao Grid-09/30/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3105MW, PK=2057MW, RR=25MW, NetOpMargin: PM=1023, EVE=994 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @170MW [WEBSMS] | CMIN
9/30/2023 10:13:56 AM | Mindanao Grid-09/30/2023 10:16: WMPC DG10 cut-in at 0951H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/30/2023 8:33:51 AM | Luzon Grid-09/30/2023 08:34: Santiago SS 230kV Bus 2 restored at 0833H (Planned Outage) [WEBSMS] | CLUZ
9/30/2023 8:31:25 AM | Visayas Grid-09/30/2023 08:31: Dumanjug-Magdugo 230 KV Line 2 emergency de-energized at 0828H, hotspot correction. (Unplanned Outage) [WEBSMS] | CVIS
9/30/2023 8:19:53 AM | Mindanao Grid-09/30/2023 08:22: Matanao SS 138KV Bus 2 deenergized at 0815H. (Planned Outage) [WEBSMS] | CMIN
9/30/2023 8:05:09 AM | Luzon Grid-09/30/2023 08:05: Binga-La Trinidad 230kV Line 1 restored at 0804H (Planned Outage) [WEBSMS] | CLUZ
9/30/2023 7:36:38 AM | Luzon Grid-09/30/2023 07:36: Santiago SS 230kV Bus 2 de-energized at 0736H (Planned Outage) [WEBSMS] | CLUZ
9/30/2023 7:29:55 AM | Visayas Grid-09/30/2023 07:30: Calongcalong-Toledo Line de-energized at 0728H.(Planned Outage) [WEBSMS] | CVIS
9/30/2023 7:25:59 AM | Mindanao Grid-09/30/2023 07:29: New Bataan (Euro) Hydro cut-in at 0714H. (Unplanned Outage) [WEBSMS] | CMIN
9/30/2023 7:24:37 AM | Mindanao Grid-09/30/2023 07:27: New Bataan (Euro) Hydro tripped with 1.7MW load at 0710H. Frequency dip is 59.65Hz (with load variation of steel mill). (Unplanned Outage) [WEBSMS] | CMIN
9/30/2023 6:39:45 AM | Luzon Grid-09/30/2023 06:40: Bolo SS 230kV Bus 1 de-energized at 0639H (Planned Outage) [WEBSMS] | CLUZ
9/30/2023 6:31:54 AM | Luzon Grid-09/30/2023 06:32: San Jose-Balsik 500kV Line de-energized at 0632H (Planned Outage) [WEBSMS] | CLUZ
9/30/2023 6:29:20 AM | Luzon Grid-09/30/2023 06:29: San Jose 750MVA T05 de-energized at 0629H (Planned Outage) [WEBSMS] | CLUZ
9/30/2023 6:03:33 AM | [NSO Update] Mindanao Grid-09/30/2023 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3137MW, PK=1975MW, RR=25MW, NetOpMargin: AM=1137, PM=1101, EVE=1025 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @190MW [WEBSMS] | CMIN
9/30/2023 5:59:35 AM | [NSO Update] Luzon Grid-09/30/2023 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12832MW, PK=10405MW, RR=350MW, NetOpMargin: AM=2077, PM=1748, EVE=1396 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GNPD 2 @334MW, MSLC1 @320MW, MSLC2 @320MW, MSLC3 @310MW, SCPC 3 @110MW, SLPGC 1 @80MW, ILIJAN A @480MW, ILIJAN B @290MW [WEBSMS] | CLUZ
9/30/2023 5:41:55 AM | Luzon Grid-09/30/2023 05:42: Binga-La Trinidad 230kV Line 1 de-energized at 0541H (Planned Outage) [WEBSMS] | CLUZ
9/30/2023 5:36:13 AM | Luzon Grid-09/30/2023 05:36: LImay-Limay BESS 69kV line de-energized at 0535H (Planned Outage) [WEBSMS] | CLUZ
9/30/2023 5:05:01 AM | Luzon Grid-09/30/2023 05:05: Calaca Unit 2 (101MW) tripped at 0501H. Lowest system frequency is 59.650Hz. [WEBSMS] | CLUZ
9/30/2023 5:00:41 AM | [NSO Update] Mindanao Grid-09/30/2023 05:03: Weather Update: At 3:00 AM today, the center of Tropical Storm JENNY was estimated based on all available data at 1,155 km East of Central Luzon (15.7 N, 132.9 E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Southern Luzon and Visayas. [WEBSMS] | CMIN
9/30/2023 5:00:27 AM | [NSO Update] Visayas Grid-09/30/2023 05:00: Weather Update: At 3:00 AM today, the center of Tropical Storm JENNY was estimated based on all available data at 1,155 km East of Central Luzon (15.7 N, 132.9 E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Southern Luzon and Visayas. [WEBSMS] | CVIS
9/30/2023 5:00:08 AM | [NSO Update] Luzon Grid-09/30/2023 05:00: Weather Update: At 3:00 AM today, the center of Tropical Storm JENNY was estimated based on all available data at 1,155 km East of Central Luzon (15.7 N, 132.9 E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Southern Luzon and Visayas. [WEBSMS] | CLUZ
9/30/2023 1:56:49 AM | Luzon Grid-09/30/2023 01:57: For info: Sta. Rita Module 20 completed the fuel changeover from oil to gas at 0154H. [WEBSMS] | CLUZ
9/29/2023 11:27:36 PM | Luzon Grid-09/29/2023 23:27: San Lorenzo Module 60 shutdown at 2325H (Planned Outage) [WEBSMS] | CLUZ
9/29/2023 9:19:02 PM | Mindanao Grid-09/29/2023 21:22: WMPC DG10 Shutdown as RPS at 2114H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/29/2023 7:50:44 PM | Mindanao Grid-09/29/2023 19:53: MA3 Online at 1945H. (Unplanned Outage). [WEBSMS] | CMIN
9/29/2023 6:58:28 PM | [NSO Update] Visayas Grid-09/29/2023 18:58: Weather Disturbance Alert Notice (WDAN) issued at 1700H. The Low-Pressure Area East of Central Luzon has entered the Philippine Area of Responsibility (PAR) and developed into Tropical Depression JENNY. The center was estimated based on all available data at 1400 km East of Southeastern Luzon (15.2�N, 134.7�E) with maximum sustained winds of 45km/h near the center & gustiness of up to 55 km/h. [WEBSMS] | CVIS
9/29/2023 6:57:42 PM | [NSO Update] Mindanao Grid-09/29/2023 19:00: Weather Disturbance Alert Notice (WDAN) issued at 1700H. The Low-Pressure Area East of Central Luzon has entered the Philippine Area of Responsibility (PAR) and developed into Tropical Depression JENNY. The center was estimated based on all available data at 1400 km East of Southeastern Luzon (15.2�N, 134.7�E) with maximum sustained winds of 45km/h near the center & gustiness of up to 55 km/h. [WEBSMS] | CMIN
9/29/2023 6:56:00 PM | [NSO Update] Luzon Grid-09/29/2023 18:56: Weather Disturbance Alert Notice (WDAN) issued at 1700H. The Low-Pressure Area East of Central Luzon has entered the Philippine Area of Responsibility (PAR) and developed into Tropical Depression �JENNY�. The center was estimated based on all available data at 1400 km East of Southeastern Luzon (15.2�N, 134.7�E) with maximum sustained winds of 45km/h near the center & gustiness of up to 55 km/h. [WEBSMS] | CLUZ
9/29/2023 6:28:38 PM | Mindanao Grid-09/29/2023 18:31: PSF U2 Online at 1826H. (Unplanned Outage). [WEBSMS] | CMIN
9/29/2023 6:27:42 PM | Mindanao Grid-09/29/2023 18:30: PSF U2 Tripped at 1822H. (Unplanned Outage). [WEBSMS] | CMIN
9/29/2023 6:27:30 PM | Luzon Grid-09/29/2023 18:27: San Jose - Taytay 230kV Line 2 de-energized at 1825H (Planned Outage) [WEBSMS] | CLUZ
9/29/2023 6:18:15 PM | Visayas Grid-09/29/2023 18:18: CEDC U3 emergency cut-out at 1816H, possible boiler tube leak. (Unplanned Outage) [WEBSMS] | CVIS
9/29/2023 5:58:18 PM | [NSO Update] Mindanao Grid-09/29/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3089MW, PK=2127MW, RR=25MW, NetOpMargin: EVE=937 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @190MW [WEBSMS] | CMIN
9/29/2023 5:52:19 PM | [NSO Update] Luzon Grid-09/29/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12151MW, PK=10484MW, RR=408MW, NetOpMargin: EVE=1259 Highest Unit O/L: Sual 1 @647MW Derated Plant: Calaca 2 @ 174MW, GNPD 2 @ 334MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 310MW, SCPC 3 @ 110MW, SLPGC 1 @ 70MW, Sta. Rita 20 @ 235MW, Ilijan A @ 355MW, Ilijan B @175MW [WEBSMS] | CLUZ
9/29/2023 5:32:16 PM | Visayas Grid-09/29/2023 17:32: Magdugo - Dumanjug 230 kV Line 2 energized with load at 1727H. (Test and Commissioning) [WEBSMS] | CVIS
9/29/2023 4:15:30 PM | Mindanao Grid-09/29/2023 16:18: WMPC DG6 as RPS shutdown at 1613H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/29/2023 3:47:15 PM | Luzon Grid-09/29/2023 15:47: La Trinidad S/S PCB 8-01CB04LTR closed at 1546H (Unplanned Outage) [WEBSMS] | CLUZ
9/29/2023 2:25:46 PM | Mindanao Grid-09/29/2023 14:28: NBT cut-in at 1330H. (Unplanned Outage). [WEBSMS] | CMIN
9/29/2023 2:24:34 PM | Mindanao Grid-09/29/2023 14:27: NBT with a load of 1.7MW trip at 1325H. Affected by voltage fluctuation at NORDECO system. [WEBSMS] | CMIN
9/29/2023 2:22:16 PM | Visayas Grid-09/29/2023 14:22: Magdugo - Dumanjug 230 kV Line 2 energized without load from Magdugo SS at 1412H. (Test and Commissioning) [WEBSMS] | CVIS
9/29/2023 12:45:24 PM | [NSO Update] Luzon Grid-09/29/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13160MW, PK=11355MW, RR=436MW, NetOpMargin: PM=1369, EVE=1737 Highest Unit O/L: Sual 1 @ 647MW Derated Plant: Calaca 2 @ 174MW, GNPD 2 @ 334MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 310MW, SCPC 3 @ 110MW, SLPGC 1 @ 70MW, Ilijan B @ 255MW, Sta. Rita 20 @ 235MW [WEBSMS] | CLUZ
9/29/2023 12:40:10 PM | [NSO Update] Mindanao Grid-09/29/2023 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3125MW, PK=2217MW, RR=25MW, NetOpMargin: PM=882, EVE=908 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @190MW [WEBSMS] | CMIN
9/29/2023 10:54:20 AM | Mindanao Grid-09/29/2023 10:57: WMPC DG6 Online as RPS at 1051H. For RPS - System System Voltage Requirement. [WEBSMS] | CMIN
9/29/2023 8:54:43 AM | Mindanao Grid-09/29/2023 08:57: WMPC DG10 Online as RPS at 0851H For RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/29/2023 7:58:05 AM | Luzon Grid-09/29/2023 07:58: SLTEC 1 shutdown at 0755H (Unplanned Outage) [WEBSMS] | CLUZ
9/29/2023 5:44:09 AM | [NSO Update] Mindanao Grid-09/29/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3132MW, PK=2100MW, RR=25MW, NetOpMargin: AM=1007, PM=930, EVE=915 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @190MW [WEBSMS] | CMIN
9/29/2023 5:40:42 AM | [NSO Update] Luzon Grid-09/29/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13433MW, PK=10929MW, RR=430MW, NetOpMargin: AM=2074, PM=1275, EVE=1532 Highest Unit O/L: SUAL 1 @647MW Derated Plant: CLC2 @174MW, GNPD 2 @334MW, MSLC1 @320MW, MSLC2 @320MW, MSLC3 @310MW, SCPC 3 @110MW, SLTEC 1 @45MW, ILIJAN B @255MW, STA. RITA 20 @235MW [WEBSMS] | CLUZ
9/29/2023 4:27:09 AM | [NSO Update] Mindanao Grid-09/29/2023 04:30: Weather Update: Trough of a Low Pressure Area (LPA) affecting the eastern sections of Visayas and Mindanao. Southwest Monsoon affects the western sections of Southern Luzon and Visayas. [WEBSMS] | CMIN
9/29/2023 4:26:56 AM | [NSO Update] Visayas Grid-09/29/2023 04:27: Weather Update: Trough of a Low Pressure Area (LPA) affecting the eastern sections of Visayas and Mindanao. Southwest Monsoon affects the western sections of Southern Luzon and Visayas. [WEBSMS] | CVIS
9/29/2023 4:26:40 AM | [NSO Update] Luzon Grid-09/29/2023 04:26: Weather Update: Trough of a Low Pressure Area (LPA) affecting the eastern sections of Visayas and Mindanao. Southwest Monsoon affects the western sections of Southern Luzon and Visayas. [WEBSMS] | CLUZ
9/29/2023 2:40:31 AM | Mindanao Grid-09/29/2023 02:43: Agusan Lake Mainit Hydro tripped with 10.5MW load at 0233H. Indication: Power Signal Failure (Unplanned Outage). [WEBSMS] | CMIN
9/29/2023 1:06:06 AM | Mindanao Grid-09/29/2023 01:09: Agus 6 HEP Unit 1 emergency shutdown at 0101H due to governor overheating. (Unplanned Outage) [WEBSMS] | CMIN
9/29/2023 12:40:28 AM | Luzon Grid-09/29/2023 00:40: Calamba 300MVA T02 - de-energized at 0034H. (Customer owned - Planned Outage) [WEBSMS] | CLUZ
9/29/2023 12:19:19 AM | Luzon Grid-09/29/2023 00:19: Las Pinas(Zapote)-CBP1A 115kV line - de-energized at 0017H. (Customer Owned and Maintained line - Planned Outage) [WEBSMS] | CLUZ
9/28/2023 11:08:24 PM | Mindanao Grid-09/28/2023 23:11: Agus 6 HEP Unit 1 cut-in at 2305H. Repair of governor oil pump. (Unplanned Outage) [WEBSMS] | CMIN
9/28/2023 9:30:08 PM | Luzon Grid-09/28/2023 21:30: Sual Unit 2 - shutdown at 2128H (Planned Outage) [WEBSMS] | CLUZ
9/28/2023 9:19:36 PM | Mindanao Grid-09/28/2023 21:22: WMPC DG10 shutdown as RPS at 2114H. from RPS. System Voltage Requirement. [WEBSMS] | CMIN
9/28/2023 7:01:27 PM | Luzon Grid-09/28/2023 19:01: SLPGC Unit 1 - online at 1854H. (Unplanned Outage) [WEBSMS] | CLUZ
9/28/2023 5:54:38 PM | [NSO Update] Mindanao Grid-09/28/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3058MW, PK=2126MW, RR=65MW, NetOpMargin: EVE=866 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @170MW [WEBSMS] | CMIN
9/28/2023 5:41:36 PM | [NSO Update] Luzon Grid-09/28/2023 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13223MW, PK=10630MW, RR=405MW, NetOpMargin: EVE=2188 Highest Unit O/L: Sual 1 @ 647MW Derated Plant: GNPD 2 @ 334MW, Calaca 2 @ 174MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 310MW, SCPC 3 @ 110MW, Sual 2 @ 620MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
9/28/2023 5:39:07 PM | Mindanao Grid-09/28/2023 17:42: AGC Lake Mainit U2 tripped with 5.2MW load AT 1607H due reversed Power. Unplanned Outage [WEBSMS] | CMIN
9/28/2023 5:39:00 PM | Luzon Grid-09/28/2023 17:39: La Trinidad S/S PCB 8-01CB04LTR de-energized at 1738H. (Unplanned Outage) [WEBSMS] | CLUZ
9/28/2023 5:26:18 PM | Mindanao Grid-09/28/2023 17:29: AGC Lake Mainit U2 cut in at 1724H. Unplanned Outage. [WEBSMS] | CMIN
9/28/2023 4:19:24 PM | Mindanao Grid-09/28/2023 16:22: AGC Lake Mainit U2 tripped with 5.2MW load AT 1607H. Unplanned Outage. [WEBSMS] | CMIN
9/28/2023 4:16:24 PM | Mindanao Grid-09/28/2023 16:19: WMPC DG06 shutdown as RPS at 1614H. from RPS. System Voltage Requirement. [WEBSMS] | CMIN
9/28/2023 4:12:53 PM | Mindanao Grid-09/28/2023 16:15: AGC Lake Mainit U2 tripped with 5.2MW load. Unplanned Outage. [WEBSMS] | CMIN
9/28/2023 3:08:43 PM | Mindanao Grid-09/28/2023 15:11: NACSUR cut out at 1500H, Follow RTD. [WEBSMS] | CMIN
9/28/2023 12:46:05 PM | Luzon Grid-09/28/2023 12:46: Malaya - Ingrid 230kV Line 2 restored at 1245H. (Unplanned Outage) [WEBSMS] | CLUZ
9/28/2023 12:36:46 PM | [NSO Update] Luzon Grid-09/28/2023 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13702MW, PK=11659MW, RR=436MW, NetOpMargin: PM=1607, EVE=1754 Highest Unit O/L: Sual 1 @ 647MW Derated Plant: GNPD 2 @ 334MW, Calaca 2 @ 174MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 320MW, SCPC 3 @ 110MW, Sual 2 @ 620MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
9/28/2023 12:34:51 PM | [NSO Update] Mindanao Grid-09/28/2023 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3094MW, PK=2197MW, RR=65MW, NetOpMargin: PM=832, EVE=826 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @170MW [WEBSMS] | CMIN
9/28/2023 11:58:25 AM | Mindanao Grid-09/28/2023 12:01: MSS (Maco BESS) tripped with load of -20MW at 1153H. Regulating Reserve (AGC). [WEBSMS] | CMIN
9/28/2023 11:43:16 AM | Luzon Grid-09/28/2023 11:43: For info: Sta. Rita Module 20 completed the fuel changeover from gas to oil at 1137H. [WEBSMS] | CLUZ
9/28/2023 10:54:37 AM | Mindanao Grid-09/28/2023 10:57: WMPC DG6 Online as RPS at 1051H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/28/2023 10:36:42 AM | Mindanao Grid-09/28/2023 10:39: Villanueva-BESS 138kV L1 de-energized at 1004H. (Planned Outage) [WEBSMS] | CMIN
9/28/2023 10:32:02 AM | Luzon Grid-09/28/2023 10:32: Malaya - Lumban 230kV Line 1 restored at 1031H. (Unplanned Outage) [WEBSMS] | CLUZ
9/28/2023 10:07:40 AM | Luzon Grid-09/28/2023 10:07: Malaya - Ingrid 230kV Line 2 tripped at 0954H. (Unplanned Outage) [WEBSMS] | CLUZ
9/28/2023 9:59:39 AM | Luzon Grid-09/28/2023 09:59: Malaya - Lumban 230kV Line 1 tripped at 0953H. (Unplanned Outage) [WEBSMS] | CLUZ
9/28/2023 8:51:44 AM | Mindanao Grid-09/28/2023 08:54: WMPC DG10 Online as RPS at 0849H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/28/2023 5:40:13 AM | [NSO Update] Mindanao Grid-09/28/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3105MW, PK=2145MW, RR=65MW, NetOpMargin: AM=895, PM=877, EVE=863 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @170MW [WEBSMS] | CMIN
9/28/2023 5:40:05 AM | [NSO Update] Luzon Grid-09/28/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14188MW, PK=10860MW, RR=430MW, NetOpMargin: AM=2899, PM=2431, EVE=2892 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: CALACA 2 @150MW, MASINLOC 1 @320MW, MASINLOC 2 @320MW, MASINLOC 3 @320MW, SCPC 3 @110MW, SUAL 2 @620MW, ILIJAN A @575MW, ILIJAN B @225MW [WEBSMS] | CLUZ
9/28/2023 5:26:28 AM | Luzon Grid-09/28/2023 05:26: Calamba SS 300MVA T01 energized at 0523H (Planned Outage) [WEBSMS] | CLUZ
9/28/2023 4:53:03 AM | Luzon Grid-09/28/2023 04:53: Dona Imelda(Araneta) - Kamuning-Valencia 115kV Line restored at 0452H (Planned Outage) [WEBSMS] | CLUZ
9/28/2023 4:18:57 AM | [NSO Update] Mindanao Grid-09/28/2023 04:21: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 800 km East of Extreme Northern Luzon (21.7�N, 129.5�E). [WEBSMS] | CMIN
9/28/2023 4:18:41 AM | [NSO Update] Visayas Grid-09/28/2023 04:18: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 800 km East of Extreme Northern Luzon (21.7�N, 129.5�E). [WEBSMS] | CVIS
9/28/2023 4:18:21 AM | [NSO Update] Luzon Grid-09/28/2023 04:18: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 800 km East of Extreme Northern Luzon (21.7�N, 129.5�E). [WEBSMS] | CLUZ
9/28/2023 3:44:06 AM | Luzon Grid-09/28/2023 03:44: Dona Imelda(Araneta) - Kamuning-Valencia 115kV Line de-energized at 0344H (Planned Outage) [WEBSMS] | CLUZ
9/28/2023 1:27:47 AM | [NSO Update] Visayas Grid-09/28/2023 01:28: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0126H with power going to Visayas. [WEBSMS] | CVIS
9/28/2023 1:27:41 AM | [NSO Update] Mindanao Grid-09/28/2023 01:30: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0126H with power going to Visayas. [WEBSMS] | CMIN
9/28/2023 12:45:29 AM | Mindanao Grid-09/28/2023 00:48: Minergy Balingasag Coal Unit 1 cut-out at 0010H. (Planned Outage) [WEBSMS] | CMIN
9/28/2023 12:42:58 AM | Luzon Grid-09/28/2023 00:43: Calamba SS 300MVA T01 de-energized at 0041H (Planned Outage) [WEBSMS] | CLUZ
9/27/2023 9:22:47 PM | Mindanao Grid-09/27/2023 21:22: WMPC DG10 shutdown as RPS at 2114H. from RPS. System Voltage Requirement. [WEBSMS] | CMIN
9/27/2023 8:08:03 PM | Mindanao Grid-09/27/2023 20:08: MSS Online at 2001H. APFC Operation. [WEBSMS] | CMIN
9/27/2023 8:01:17 PM | [NSO Update] Mindanao Grid-09/27/2023 20:01: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1954H from forward power direction. [WEBSMS] | CMIN
9/27/2023 7:58:54 PM | [NSO Update] Visayas Grid-09/27/2023 19:58: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1954H from forward power direction. [WEBSMS] | CVIS
9/27/2023 5:59:34 PM | "[NSO Update] Mindanao Grid-09/27/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3114MW, PK=2084MW, RR=65MW, NetOpMargin: EVE=965 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @190MW [WEBSMS]" | CMIN
9/27/2023 5:47:56 PM | "[NSO Update] Luzon Grid-09/27/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12685MW, PK=10706MW, RR=408MW, NetOpMargin: EVE=1571 Highest Unit O/L: SUAL 1 @ 647MW Derated Plant: CALACA 2 @150MW, MSLC1 @320MW, MSLC2 @320MW, MSLC3 @320MW, SCPC 3 @110MW, SUAL 2 @620MW, ILIJAN B @245MW [WEBSMS]" | CLUZ
9/27/2023 5:30:21 PM | Luzon Grid-09/27/2023 17:30: Gumaca-Labo 230kV line 1 - restored at 1729H (Planned Outage) [WEBSMS] | CLUZ
9/27/2023 5:21:31 PM | Luzon Grid-09/27/2023 17:21: GNPD Unit 2 - online at 1718H. (Unplanned Outage) [WEBSMS] | CLUZ
9/27/2023 2:50:39 PM | Visayas Grid-09/27/2023 14:50: Daanlungsod SS 138KV Bus 1 energized at 1449H. (Planned Outage). [WEBSMS] | CVIS
9/27/2023 1:35:53 PM | Mindanao Grid-09/27/2023 13:35: MA3 U1 tripped with load of 3.2MW at 1325H. (Unplanned Outage). [WEBSMS] | CMIN
9/27/2023 1:02:31 PM | "[NSO Update] Luzon Grid-09/27/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13341MW, PK=11583MW, RR=436MW, NetOpMargin: PM=1322, EVE=1591 Highest Unit O/L: Sual 1 @647MW Derated Plant: CLC2 @150MW, MSLC1 @320MW, MSLC2 @320MW, MSLC3 @320MW, SCPC 3 @110MW, SUAL 2 @620MW [WEBSMS]" | CLUZ
9/27/2023 12:54:31 PM | "[NSO Update] Mindanao Grid-09/27/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3133MW, PK=2120MW, RR=65MW, NetOpMargin: PM=948, EVE=928 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @170MW [WEBSMS]" | CMIN
9/27/2023 12:50:44 PM | Luzon Grid-09/27/2023 12:50: Balsik-SBMA 230kV Line restored at 1246H (Planned Outage) [WEBSMS] | CLUZ
9/27/2023 11:58:53 AM | Luzon Grid-09/27/2023 11:59: Binan PCB 8-07CB04BIN energized at 1145H (Planned Outage) [WEBSMS] | CLUZ
9/27/2023 11:50:38 AM | Luzon Grid-09/27/2023 11:50: For info: Calaca-SLPGC 230kV line 2 - auto-tripped on 0949H at Calaca side while on unlooped status at SLPGC side. (Customer owned and maintained line)(Unplanned Outage) [WEBSMS] | CLUZ
9/27/2023 10:53:32 AM | Visayas Grid-09/27/2023 10:53: Daanbantayan- Tabango 230KV Line 2 energized at 1052H hot-spot correction at Tabango SS side phase B terminal connector (bolt). (8Z-XR04TAB) activity completed. [WEBSMS] | CVIS
9/27/2023 10:53:13 AM | Mindanao Grid-09/27/2023 10:56: WMPC DG10 Online as RPS at 1051H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/27/2023 10:15:54 AM | Luzon Grid-09/27/2023 10:16: System Advisory: ALD affected feeders of NGCP and Meralco were restored at 1007H. [WEBSMS] | CLUZ
9/27/2023 10:13:15 AM | Luzon Grid-09/27/2023 10:13: System Advisory: (Correction of time): ALD occurred at NGCP and Meralco feeders due to the tripping of GNPD Unit 2 at 0958H from 662MW load. The lowest system frequency was 58.866Hz. [WEBSMS] | CLUZ
9/27/2023 10:06:28 AM | Luzon Grid-09/27/2023 10:06: System Advisory: ALD occurred at NGCP and Meralco feeders due to the tripping of GNPD Unit 2 at 0959H from 662MW load. The lowest system frequency was 58.866Hz. [WEBSMS] | CLUZ
9/27/2023 9:29:30 AM | Mindanao Grid-09/27/2023 09:32: WMPC DG6 Online at 0922H. For RPS - System Voltage Requirement. Replacement Unit. [WEBSMS] | CMIN
9/27/2023 9:23:21 AM | Luzon Grid-09/27/2023 09:23: Binan PCB 8-07CB04BIN de-energized at 0920H (Planned Outage) [WEBSMS] | CLUZ
9/27/2023 9:18:27 AM | Mindanao Grid-09/27/2023 09:21: WMPC DG10 trip with 8.5MW load at 0910H. (Unplanned Outage). [WEBSMS] | CMIN
9/27/2023 9:08:43 AM | Visayas Grid-09/27/2023 09:08: Daanbantayan- Tabango 230KV Line 2 de-energized at 0859H to facilitate hot-spot correction at Tabango SS side phase B terminal connector (bolt). (8Z-XR04TAB) activity duration 3hrs (Unplanned Outage ). [WEBSMS] | CVIS
9/27/2023 9:05:20 AM | Mindanao Grid-09/27/2023 09:08: PG4 U3 Online at 0901H. (Unplanned Outage). [WEBSMS] | CMIN
9/27/2023 8:52:03 AM | Mindanao Grid-09/27/2023 08:55: WMPC DG10 Online at 0848H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/27/2023 7:47:42 AM | Visayas Grid-09/27/2023 07:47: Daanlungsod SS 138KV Bus 1 de-energized at 0724. ECD: 1800H (planned Outage). [WEBSMS] | CVIS
9/27/2023 6:19:42 AM | Luzon Grid-09/27/2023 06:19: Labo-Gumaca 230kV line 1 - de-energized at 0619H. (Planned Outage) [WEBSMS] | CLUZ
9/27/2023 5:56:39 AM | [NSO Update] Mindanao Grid-09/27/2023 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2968MW, PK=2048MW, RR=25MW, NetOpMargin: AM=895, PM=743, EVE=707 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @30MW, AG2 @110MW, AG4 @126MW, AG5 @41MW, AG6 @149MW, AG7 @35MW, PG4 @130MW [WEBSMS] | CMIN
9/27/2023 5:54:31 AM | Luzon Grid-09/27/2023 05:54: Muntinlupa (Sucat)-Binan 230kV Line 3 restored at 0553H (Planned Outage) [WEBSMS] | CLUZ
9/27/2023 5:43:17 AM | [NSO Update] Luzon Grid-09/27/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14186MW, PK=11084MW, RR=430MW, NetOpMargin: AM=2672, PM=2141, EVE=2191 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CALACA 2 @ 174MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 320MW, SCPC 3 @ 110MW, Sual 2 @ 620MW, Ilijan A @ 575MW, Ilijan B @ 225MW [WEBSMS] | CLUZ
9/27/2023 4:50:58 AM | [NSO Update] Luzon Grid-09/27/2023 04:51: Weather Advisory: Trough of a Low Pressure Area (LPA) affecting Visayas and Mindanao. [WEBSMS] | CLUZ
9/27/2023 4:42:28 AM | Visayas Grid-09/27/2023 04:42: Mandaue GIS 100 MVA Transformer # 1 restored/energized 0329H. ( Unplanned Outage) [WEBSMS] | CVIS
9/27/2023 4:25:27 AM | [NSO Update] Mindanao Grid-09/27/2023 04:28: Weather Advisory: Trough of a Low Pressure Area (LPA) affecting Visayas and Mindanao. [WEBSMS] | CMIN
9/27/2023 4:25:07 AM | [NSO Update] Visayas Grid-09/27/2023 04:25: Weather Advisory: Trough of a Low Pressure Area (LPA) affecting Visayas and Mindanao. [WEBSMS] | CVIS
9/27/2023 4:17:32 AM | [NSO Update] Mindanao Grid-09/27/2023 04:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0415H with power going to Visayas. [WEBSMS] | CMIN
9/27/2023 4:17:21 AM | [NSO Update] Visayas Grid-09/27/2023 04:17: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0415H with power going to Visayas. [WEBSMS] | CVIS
9/27/2023 3:25:12 AM | Luzon Grid-09/27/2023 03:25: Muntinlupa (Sucat) SS 230kV Bus 2 restored at 0322H (Planned Outage) [WEBSMS] | CLUZ
9/27/2023 3:14:57 AM | Visayas Grid-09/27/2023 03:15: Mandaue GIS 100 MVA Transformer # 1 emergency shutdown at 0204H correction of Voltage transformer termination. (Unplanned Outage) [WEBSMS] | CVIS
9/27/2023 2:04:00 AM | Mindanao Grid-09/27/2023 02:06: Agus 6 Unit 5 cut in at 0202H. Unplanned Outage. [WEBSMS] | CMIN
9/27/2023 1:40:02 AM | Mindanao Grid-09/27/2023 01:42: Agus 6 Unit 5 tripped at 0116H with 40MW load. Unplanned Outage. [WEBSMS] | CMIN
9/27/2023 1:38:43 AM | Mindanao Grid-09/27/2023 01:41: Pulangi IV Unit 3 tripped at 0116H with 40MW load. Unplanned Outage. [WEBSMS] | CMIN
9/27/2023 1:24:10 AM | [NSO Update] Mindanao Grid-09/27/2023 01:27: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was auto-blocked at 0116H with power going to Visayas. [WEBSMS] | CMIN
9/27/2023 1:23:41 AM | [NSO Update] Visayas Grid-09/27/2023 01:23: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was auto-blocked at 0116H with power going to Visayas. [WEBSMS] | CVIS
9/27/2023 12:31:22 AM | Luzon Grid-09/27/2023 00:31: Muntinlupa (Sucat) SS 230kV Bus 2 de-energized at 0030H (Planned Outage) [WEBSMS] | CLUZ
9/27/2023 12:11:13 AM | Luzon Grid-09/27/2023 00:11: Muntinlupa (Sucat)-Binan 230kV Line 3 de-energized at 0010H (Planned Outage) [WEBSMS] | CLUZ
9/26/2023 9:25:28 PM | Mindanao Grid-09/26/2023 21:28: WMPC DG10 cut-out at 2114H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/26/2023 6:07:12 PM | Luzon Grid-09/26/2023 18:07: Tayabas-San Jose 500kV line 2 energized at 1802H in Tayabas side (Unplanned Outage) [WEBSMS] | CLUZ
9/26/2023 5:53:31 PM | [NSO Update] Luzon Grid-09/26/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13521MW, PK=11314MW, RR=408MW, NetOpMargin: EVE=1799 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CALACA 2 @ 150MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 310MW, SCPC 3 @ 110MW, Sual 2 @ 620MW, Ilijan A @ 575MW, Ilijan B @ 225MW [WEBSMS] | CLUZ
9/26/2023 5:47:12 PM | [NSO Update] Mindanao Grid-09/26/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2949MW, PK=2082MW, RR=65MW, NetOpMargin: EVE=802 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MCO @270MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @30MW, AG2 @105MW, AG4 @121MW, AG5 @39MW, AG6 @145MW, AG7 @34MW, PG4 @165MW [WEBSMS] | CMIN
9/26/2023 5:36:55 PM | Luzon Grid-09/26/2023 17:37: Concepcion-Clark 230kV line 1 - auto-tripped/auto-reclosed at 1726H.(Unplanned Outage) [WEBSMS] | CLUZ
9/26/2023 4:51:52 PM | Luzon Grid-09/26/2023 16:52: Tayabas-San Jose 500kV line 2 was de-energized at 1651H. (Unplanned Outage) [WEBSMS] | CLUZ
9/26/2023 4:31:26 PM | Luzon Grid-09/26/2023 16:31: SLPGC Unit 2 Main Transformer was de-energized at 1615H, SLPGC 230kV Bus 2 was de-energized at 1617H, and Calaca-SLPGC 230kV line 2 was unlooped at SLPGC side at 1617H.(Unplanned Outage requested by SLPGC) [WEBSMS] | CLUZ
9/26/2023 4:17:00 PM | Mindanao Grid-09/26/2023 16:19: WMPC DG06 cut-out at 1615H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/26/2023 3:22:08 PM | Luzon Grid-09/26/2023 15:22: Balsik PCB 9-02CB24BIK - energized at 1520H (Planned Outage) [WEBSMS] | CLUZ
9/26/2023 2:51:39 PM | [NSO Update] Mindanao Grid-09/26/2023 14:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2981MW, PK=2133MW, RR=65MW, NetOpMargin: PM=783, EVE=793 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MCO @270MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @30MW, AG2 @105MW, AG4 @121MW, AG5 @39MW, AG6 @145MW, AG7 @34MW, PG4 @165MW [WEBSMS] | CMIN
9/26/2023 2:38:01 PM | [NSO Update] Luzon Grid-09/26/2023 14:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14065MW, PK=11265MW, RR=436MW, NetOpMargin: PM=2364, EVE=2320 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CLC 2 @ 174MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 310MW, SCPC 3 @ 110MW, Sual 2 @ 620MW, Ilijan A @ 575MW, Ilijan B @ 225MW [WEBSMS] | CLUZ
9/26/2023 2:15:42 PM | Luzon Grid-09/26/2023 14:15: Bantay PCB 6-01CB04BAN - energized at 1413H (Planned Outage) [WEBSMS] | CLUZ
9/26/2023 2:07:45 PM | [NSO Update] Mindanao Grid-09/26/2023 14:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1403H with power going to Visayas. [WEBSMS] | CMIN
9/26/2023 2:06:16 PM | [NSO Update] Visayas Grid-09/26/2023 14:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1403H with power going to Visayas. [WEBSMS] | CVIS
9/26/2023 12:51:53 PM | [NSO Update] Mindanao Grid-09/26/2023 12:54: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was auto-blocked at 1239H with power going to Visayas. [WEBSMS] | CMIN
9/26/2023 12:50:55 PM | [NSO Update] Visayas Grid-09/26/2023 12:51: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was auto-blocked at 1239H with power going to Visayas. [WEBSMS] | CVIS
9/26/2023 11:37:42 AM | Luzon Grid-09/26/2023 11:37: Lumban-Malaya 230kV line 1 auto-tripped/auto-reclosed at 1129H. (Unplanned Outage) [WEBSMS] | CLUZ
9/26/2023 11:31:40 AM | Visayas Grid-09/26/2023 11:31: Visayas frequency reaches 61.089Hz due to tripping of Sta. Barbara-Miag-ao 69kV Feeder with 46.95MW load at 1124H. [WEBSMS] | CVIS
9/26/2023 11:13:41 AM | Luzon Grid-09/26/2023 11:13: Mexico PCB 8-05CB04MEX - energized at 1111H. (Planned Outage) [WEBSMS] | CLUZ
9/26/2023 10:47:02 AM | Mindanao Grid-09/26/2023 10:49: WMPC DG10 cut-in at 0854H. RPS - System Voltage Requirement [WEBSMS] | CMIN
9/26/2023 9:11:25 AM | Luzon Grid-09/26/2023 09:11: Lumban-Gumaca 230kV line 1 was restored at 0910H. (Unplanned Outage) [WEBSMS] | CLUZ
9/26/2023 9:00:14 AM | Luzon Grid-09/26/2023 09:00: Mexico PCB 8-05CB04MEX - de-energized at 0859H (Planned Outage) [WEBSMS] | CLUZ
9/26/2023 8:34:39 AM | Luzon Grid-09/26/2023 08:34: Balsik PCB 9-02CB24BIK - de-energized at 0832H (Planned Outage) [WEBSMS] | CLUZ
9/26/2023 7:36:44 AM | Luzon Grid-09/26/2023 07:36: Taytay(Dolores) 300MVA T02 - restored at 0735H. (Planned Outage) [WEBSMS] | CLUZ
9/26/2023 7:34:44 AM | Luzon Grid-09/26/2023 07:34: Taytay(Dolores) 115kV Bus 2 - energized at 0733H (Planned Outage) [WEBSMS] | CLUZ
9/26/2023 6:11:53 AM | Luzon Grid-09/26/2023 06:12: Bantay PCB 6-01CB04BAN - de-energized at 0609H. (Planned Outage) [WEBSMS] | CLUZ
9/26/2023 6:09:33 AM | [NSO Update] Mindanao Grid-09/26/2023 06:12: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2995MW, PK=2194MW, RR=65MW, NetOpMargin: AM=736, PM=748, EVE=761 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @32MW, AG1 @30MW, AG2 @105MW, AG4 @121MW, AG5 @39MW, AG6 @145MW, AG7 @34MW, PG4 @165MW [WEBSMS] | CMIN
9/26/2023 5:59:49 AM | [NSO Update] Luzon Grid-09/26/2023 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14176MW, PK=11053MW, RR=430MW, NetOpMargin: AM=2692, PM=2589, EVE=2662 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CLC 2 @ 174MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 310MW, SCPC 3 @ 110MW, Sual 2 @ 620MW, Ilijan A @ 575MW, Ilijan B @ 225MW [WEBSMS] | CLUZ
9/26/2023 5:59:01 AM | Mindanao Grid-09/26/2023 06:01: Lake Mainit Hydro tripped with 10.5MW load at 0553H. (Unplanned Outage). Indication: 50BF. [WEBSMS] | CMIN
9/26/2023 4:11:02 AM | Luzon Grid-09/26/2023 04:11: Lumban - Gumaca 230kV Line 1 tripped at 0407H. (Unplanned Outage) [WEBSMS] | CLUZ
9/26/2023 4:01:56 AM | [NSO Update] Mindanao Grid-09/26/2023 04:04: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CMIN
9/26/2023 4:01:49 AM | [NSO Update] Luzon Grid-09/26/2023 04:02: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CLUZ
9/26/2023 4:01:43 AM | [NSO Update] Visayas Grid-09/26/2023 04:01: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CVIS
9/26/2023 1:30:34 AM | Luzon Grid-09/26/2023 01:30: Taytay (Dolores) - Teresa 115kV Line, Taytay (Dolores) 300MVA T02 and Taytay (Dolores) 115kV Bus 2 de-energized at 0112H, 0115H and 0120H, respectively (Planned Outage) [WEBSMS] | CLUZ
9/26/2023 12:21:57 AM | Luzon Grid-09/26/2023 00:22: Muntinlupa (Sucat) - Binan 230kV Line 4 restored at 0016H (Planned Outage) [WEBSMS] | CLUZ
9/25/2023 11:22:33 PM | Mindanao Grid-09/25/2023 23:25: GNPK Unit 2 cut-out at 2315H on reserved shutdown. [WEBSMS] | CMIN
9/25/2023 10:42:03 PM | Mindanao Grid-09/25/2023 22:44: Mt. Apo 3 cut-in at 2231H. (Unplanned Outage) [WEBSMS] | CMIN
9/25/2023 10:14:36 PM | Luzon Grid-09/25/2023 22:14: Muntinlupa(Sucat)-Binan 230kV Line 4 de-energized at 2214H. (Planned Outage) [WEBSMS] | CLUZ
9/25/2023 7:19:13 PM | Mindanao Grid-09/25/2023 19:22: Kauswagan-Lala 230kV Line 2 successfully energized/restored at 1909H. From emergency shutdown. [WEBSMS] | CMIN
9/25/2023 6:20:33 PM | [NSO Update] Luzon Grid-09/25/2023 18:20: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13513MW, PK=10321MW, RR=426MW, NetOpMargin: EVE=2766 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: Calaca 2 @ 140MW, Masinloc 1 @ 325MW, Masinloc 2 @ 310MW, Masinloc 3 @ 305MW, QPPL @ 275MW, SCPC 3 @ 110MW, Sual 2 @ 620MW, Ilijan A @ 575MW, Ilijan B @ 225MW [WEBSMS] | CLUZ
9/25/2023 6:18:59 PM | [NSO Update] Mindanao Grid-09/25/2023 18:21: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2974MW, PK=2156MW, RR=65MW, NetOpMargin: EVE=753 Highest Unit O/L: GNPK 2, 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @117MW, AG5 @38MW, AG6 @171MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
9/25/2023 4:24:52 PM | Mindanao Grid-09/25/2023 16:27: WMPC DG01 cut-out at 1615H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/25/2023 3:39:42 PM | Luzon Grid-09/25/2023 15:39: Balsik PCB 9-01CB04BIK restored at 1539H (Planned Outage) [WEBSMS] | CLUZ
9/25/2023 3:29:36 PM | Luzon Grid-09/25/2023 15:29: Santiago PCB 8-04CB24SAN restored at 1528H (Unplanned Outage) [WEBSMS] | CLUZ
9/25/2023 3:00:29 PM | Luzon Grid-09/25/2023 15:00: Santiago PCB 8-04CB24SAN de-energized at 1458H (Unplanned Outage) [WEBSMS] | CLUZ
9/25/2023 2:04:28 PM | Mindanao Grid-09/25/2023 14:07: STEAG Unit 2 cut-in at 1403H. (Unplanned Outage) [WEBSMS] | CMIN
9/25/2023 1:18:25 PM | Luzon Grid-09/25/2023 13:18: QPPL online at 1316H (Unplanned Outage) [WEBSMS] | CLUZ
9/25/2023 12:53:28 PM | [NSO Update] Mindanao Grid-09/25/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2910MW, PK=2273MW, RR=65MW, NetOpMargin: PM=572, EVE=596 Highest Unit O/L: GNPK 2,3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @117MW, AG5 @38MW, AG6 @171MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
9/25/2023 12:43:28 PM | [NSO Update] Luzon Grid-09/25/2023 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13879MW, PK=11167MW, RR=474MW, NetOpMargin: PM=2238, EVE=2350 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CLC2 @140MW, MSLC1 @325MW, MSLC2 @310MW, MSLC3 @305MW, SCPC 3 @110MW, SUAL 2 @620MW, ILIJAN A @575MW, ILIJAN B @225MW [WEBSMS] | CLUZ
9/25/2023 12:30:33 PM | Mindanao Grid-09/25/2023 12:33: Supreme Power Mati cut-in at 1159H. (Unplanned Outage) [WEBSMS] | CMIN
9/25/2023 11:46:43 AM | Mindanao Grid-09/25/2023 11:49: WMPC DG01cut-in at 1049H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/25/2023 11:21:27 AM | Mindanao Grid-09/25/2023 11:24: Supreme Power Mati tripped with 3.1MW load at 1000H. Indication: Overvoltage. (Unplanned Outage) [WEBSMS] | CMIN
9/25/2023 11:20:44 AM | Mindanao Grid-09/25/2023 11:23: Supreme Power Mati cut-in at 0946H. (Unplanned Outage) [WEBSMS] | CMIN
9/25/2023 11:19:50 AM | Mindanao Grid-09/25/2023 11:22: Supreme Power Mati tripped with 3.1MW load at 0938H. Indication: Overvoltage. [WEBSMS] | CMIN
9/25/2023 11:16:17 AM | Mindanao Grid-09/25/2023 11:19: Supreme Power Mati cut-in at 0924H. (Unplanned Outage) [WEBSMS] | CMIN
9/25/2023 11:14:02 AM | Mindanao Grid-09/25/2023 11:16: Supreme Power Mati tripped with 3.0MW load at 0911H. Note: frequency was 60.969Hz due to autoblocking of HVDC. Indication: Reverse Power. No ALD (Unplanned Outage) [WEBSMS] | CMIN
9/25/2023 10:57:22 AM | Mindanao Grid-09/25/2023 11:00: Maco BESS tripped with +19.7MW load at 1030H. (Unplanned Outage). [WEBSMS] | CMIN
9/25/2023 10:43:54 AM | [NSO Update] Mindanao Grid-09/25/2023 10:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1041H with power going to Visayas. [WEBSMS] | CMIN
9/25/2023 10:43:09 AM | [NSO Update] Visayas Grid-09/25/2023 10:43: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1041H with power going to Visayas. [WEBSMS] | CVIS
9/25/2023 9:52:44 AM | Mindanao Grid-09/25/2023 09:55: WMPC DG10 cut-in at 0856H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/25/2023 9:19:48 AM | Visayas Grid-09/25/2023 09:19: Dumanjug SS 150 MVA 230/138 kV TR2 energized at 0911H. (Unplanned Outage) [WEBSMS] | CVIS
9/25/2023 9:17:35 AM | [NSO Update] Mindanao Grid-09/25/2023 09:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was auto-blocked at 0912H with power going to Visayas. [WEBSMS] | CMIN
9/25/2023 9:17:22 AM | [NSO Update] Visayas Grid-09/25/2023 09:17: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was auto-blocked at 0912H with power going to Visayas. [WEBSMS] | CVIS
9/25/2023 8:54:48 AM | Luzon Grid-09/25/2023 08:54: Balsik PCB 9-01CB04BIK de-energized at 0847H (Planned Outage) [WEBSMS] | CLUZ
9/25/2023 7:03:28 AM | Mindanao Grid-09/25/2023 07:06: GNPK Unit 4 cut-in at 0608H. (Unplanned Outage) [WEBSMS] | CMIN
9/25/2023 6:27:27 AM | Luzon Grid-09/25/2023 06:27: Dona Imelda(Araneta)-Quezon(Balintawak) 230kV line restored at 0627H (Planned Outage) [WEBSMS] | CLUZ
9/25/2023 5:57:27 AM | [NSO Update] Mindanao Grid-09/25/2023 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2806MW, PK=2062MW, RR=65MW, NetOpMargin: AM=679, PM=593, EVE=561 Highest Unit O/L: GNPK 2&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @135MW, AG5 @44MW, AG6 @164MW, AG7 @38MW, PG4 @165MW [WEBSMS] | CMIN
9/25/2023 5:46:13 AM | [NSO Update] Luzon Grid-09/25/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14017MW, PK=11137MW, RR=435MW, NetOpMargin: AM=2446, PM=1848, EVE=2045 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CLC2 @140MW, MSLC1 @325MW, MSLC2 @310MW, MSLC3 @305MW, SCPC 3 @110MW, SUAL 2 @620MW, ILIJAN A @575MW, ILIJAN B @225MW [WEBSMS] | CLUZ
9/25/2023 5:19:50 AM | [NSO Update] Mindanao Grid-09/25/2023 05:22: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CMIN
9/25/2023 5:19:21 AM | [NSO Update] Visayas Grid-09/25/2023 05:19: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CVIS
9/25/2023 5:19:07 AM | [NSO Update] Luzon Grid-09/25/2023 05:19: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon and Visayas. [WEBSMS] | CLUZ
9/25/2023 1:44:20 AM | Luzon Grid-09/25/2023 01:44: Mexico 230kV Bus 2 restored at 0132H (Planned Outage) [WEBSMS] | CLUZ
9/25/2023 12:37:38 AM | Luzon Grid-09/25/2023 00:37: For info: Labrador 230kV Bus 2 New Main Protections commissioning and energization was completed at 0035H. [WEBSMS] | CLUZ
9/24/2023 11:59:27 PM | Luzon Grid-09/24/2023 23:59: Labrador 230kV Bus 2 energized at 2357H (On-going commissioning and energization of new Main Protections) [WEBSMS] | CLUZ
9/24/2023 9:06:02 PM | Luzon Grid-09/24/2023 21:06: Dona Imelda(Araneta)-Quezon(Balintawak) 230kV line - de-energized at 2105H.(Planned Outage) [WEBSMS] | CLUZ
9/24/2023 8:10:59 PM | Luzon Grid-09/24/2023 20:11: San Gabriel online at 2009H. (Unplanned Outage) [WEBSMS] | CLUZ
9/24/2023 8:03:34 PM | Mindanao Grid-09/24/2023 20:06: Jasaan - Butuan 138KV line restored at 1956H. (Planned outage) [WEBSMS] | CMIN
9/24/2023 7:39:59 PM | Luzon Grid-09/24/2023 19:40: Batangas 300MVA T04 and T05 were paralleled at 1933H. (After the unlooping the Busses of Sta Rita and San Lorenzo in preparation for the synchronization of San Gabriel CCPP). [WEBSMS] | CLUZ
9/24/2023 7:26:55 PM | Luzon Grid-09/24/2023 19:27: For info: Sta Rita-San Lorenzo 230kV Busses A and Busses B were unlooped at 1923H and 1924H respectively. (Preparation for the start-up of San Gabriel CCPP) [WEBSMS] | CLUZ
9/24/2023 6:28:41 PM | Luzon Grid-09/24/2023 18:28: Binga PCB 8-01CB24BIZ energized at 1827H (Unplanned Outage) [WEBSMS] | CLUZ
9/24/2023 6:23:00 PM | Luzon Grid-09/24/2023 18:23: Sta Rita Module 20 online at 1820H (Unplanned Outage). [WEBSMS] | CLUZ
9/24/2023 5:55:10 PM | Luzon Grid-09/24/2023 17:55: San Jose-Taytay 230kV Line 1 restored at 1754H. (Planned Outage) [WEBSMS] | CLUZ
9/24/2023 5:45:31 PM | [NSO Update] Mindanao Grid-09/24/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2738MW, PK=1954MW, RR=63MW, NetOpMargin: EVE=721 Highest Unit O/L: GNPK 2&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @117MW, AG5 @38MW, AG6 @171MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
9/24/2023 5:41:03 PM | [NSO Update] Luzon Grid-09/24/2023 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12472MW, PK=9559MW, RR=315MW, NetOpMargin: EVE=2598 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CLC2 @140MW, MSLC1 @330MW, MSLC2 @315MW, MSLC3 @330MW, SCPC 3 @110MW, SUAL 2 @620MW, ILIJAN A @575MW, ILIJAN B @225MW [WEBSMS] | CLUZ
9/24/2023 5:32:21 PM | Luzon Grid-09/24/2023 17:32: Sta. Rita 20 tripped with 152MW load at 1730H. Lowest system frequency is 59.532Hz. (Unplanned Outage) [WEBSMS] | CLUZ
9/24/2023 5:22:22 PM | Visayas Grid-09/24/2023 17:22: Daan-Bantayan 100MVA Transformer # 1restored/energized at 1638H. (Planned Outage) [WEBSMS] | CVIS
9/24/2023 4:58:13 PM | Mindanao Grid-09/24/2023 17:01: Erratum: Jasaan SS 138KV Bus 1 restored at 1643H. (Planned Outage). [WEBSMS] | CMIN
9/24/2023 4:48:34 PM | Mindanao Grid-09/24/2023 16:51: Jasaan SS 138KV Bus 1 restored at 1645H. Planned Outage. [WEBSMS] | CMIN
9/24/2023 4:22:14 PM | Luzon Grid-09/24/2023 16:22: Bay-Calamba 230kV Line 2 restored at 1621H. (Planned Outage) [WEBSMS] | CLUZ
9/24/2023 3:19:21 PM | Mindanao Grid-09/24/2023 15:22: Kauswagan_GNPK 230KV Line 4 restored at 1511H. (Unplanned Outage) [WEBSMS] | CMIN
9/24/2023 3:18:41 PM | Luzon Grid-09/24/2023 15:18: QPPL tripped with 180MW load at 1516H. Lowest system frequency is 59.552Hz. (Unplanned Outage) [WEBSMS] | CLUZ
9/24/2023 2:39:13 PM | Luzon Grid-09/24/2023 14:39: For info: San Lorenzo 50 completed fuel changeover from oil to natural gas at 1437H [WEBSMS] | CLUZ
9/24/2023 1:04:47 PM | Luzon Grid-09/24/2023 13:04: Binga-Ambuklao 230kV Line 1 restored at 1304H. (Planned Outage) [WEBSMS] | CLUZ
9/24/2023 1:04:42 PM | Visayas Grid-09/24/2023 13:04: Mandaue GIS 69 kV Feeder 1 and Feeder 2 energized at 1303H. (Planned Outage) [WEBSMS] | CVIS
9/24/2023 12:50:07 PM | [NSO Update] Mindanao Grid-09/24/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2770MW, PK=1809MW, RR=65MW, NetOpMargin: PM=896, EVE=704 Highest Unit O/L: GNPK 2&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @117MW, AG5 @38MW, AG6 @171MW, AG7 @30MW, PG4 @165MW [WEBSMS] | CMIN
9/24/2023 12:40:23 PM | [NSO Update] Luzon Grid-09/24/2023 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13810MW, PK=9003MW, RR=346MW, NetOpMargin: PM=4460, EVE=3280 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CALACA 2 @140MW, MASINLOC 1 @330MW, MASINLOC 2 @315MW, MASINLOC 3 @310MW, SCPC 3 @110MW, ILIJAN A @575MW, ILIJAN B @225MW, SUAL 2 @620MW, STA. RITA 20 @235MW, STA. RITA 30 @200MW [WEBSMS] | CLUZ
9/24/2023 11:32:39 AM | Luzon Grid-09/24/2023 11:32: For info: Sta Rita Module 30 completed fuel changeover from oil to nat gas at 1130H [WEBSMS] | CLUZ
9/24/2023 11:04:21 AM | Luzon Grid-09/24/2023 11:04: For info: Avion 1 completed the fuel changeover from oil to natural gas at 1001H. [WEBSMS] | CLUZ
9/24/2023 10:40:47 AM | Luzon Grid-09/24/2023 10:40: Las Pinas (Zapote) SS 300MVA T02 restored at 1039H (Planned Outage) [WEBSMS] | CLUZ
9/24/2023 9:19:19 AM | Luzon Grid-09/24/2023 09:19: For info: San Lorenzo 60 completed the fuel changeover from oil to nat gas at 0917H [WEBSMS] | CLUZ
9/24/2023 8:59:45 AM | Luzon Grid-09/24/2023 08:59: Mexico SS 230kV Bus 2 de-energized at 0859H. (Planned Outage) [WEBSMS] | CLUZ
9/24/2023 8:48:10 AM | Visayas Grid-09/24/2023 08:48: Magdugo - Colon 138 kV Line 2 energized at 0846H. (Planned outage) [WEBSMS] | CVIS
9/24/2023 8:40:33 AM | Luzon Grid-09/24/2023 08:40: For info: Sta Rita Module 10 completed the fuel changeover from oil to nat gas at 0829H [WEBSMS] | CLUZ
9/24/2023 8:19:03 AM | Mindanao Grid-09/24/2023 08:21: Malita BESS 69KV Line restored/energized at 0817H. (Planned Outage) [WEBSMS] | CMIN
9/24/2023 8:16:23 AM | Visayas Grid-09/24/2023 08:16: Mandaue GIS 69 kV Feeder 4 and Feeder 5 de-energized at 0810H and 0811H. (Planned Outage) [WEBSMS] | CVIS
9/24/2023 8:11:00 AM | Mindanao Grid-09/24/2023 08:13: Jasaan SS 138kV Bus 1 de-energized 0808H. Planned outage / N-GOMP. [WEBSMS] | CMIN
9/24/2023 8:07:30 AM | Luzon Grid-09/24/2023 08:07: Avion 2 completed changeover from fuel oil to gas at 0802H. [WEBSMS] | CLUZ
9/24/2023 7:42:26 AM | Luzon Grid-09/24/2023 07:42: BCCPP 230kV Bus 2 restored at 0741H. (Planned Outage) [WEBSMS] | CLUZ
9/24/2023 7:39:58 AM | Luzon Grid-09/24/2023 07:40: Las Pinas (Zapote) SS 300MVA T02 de-energized at 0739H. (Planned Outage) [WEBSMS] | CLUZ
9/24/2023 7:13:37 AM | Luzon Grid-09/24/2023 07:13: Bay-Calamba 230kV Line 2 de-energized at 0713H. (Planned Outage) [WEBSMS] | CLUZ
9/24/2023 6:14:18 AM | Visayas Grid-09/24/2023 06:14: Daanbantayan SS 100 MVA 230/69 kV TR de-energized at 0610H. (Planned Outage) [WEBSMS] | CVIS
9/24/2023 6:12:46 AM | Visayas Grid-09/24/2023 06:12: Daanbantayan - Lanao 69 kV Line de-energized at 0607H. (Planned Outage) [WEBSMS] | CVIS
9/24/2023 6:05:47 AM | Mindanao Grid-09/24/2023 06:08: Jasaan - Butuan 138kV L de-energized at 0605. (Planned Outage) [WEBSMS] | CMIN
9/24/2023 5:52:42 AM | [NSO Update] Luzon Grid-09/24/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13936MW, PK=8486MW, RR=340MW, NetOpMargin: AM=5109, PM=4690, EVE=3535 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CLC2 @140MW, MSLC1 @330MW, MSLC2 @315MW, MSLC3 @310MW, SCPC 3 @110MW, ILIJAN A @575MW, ILIJAN B @225MW, SUAL 2 @620MW, STA. RITA 20 @235MW, STA. RITA 30 @200MW [WEBSMS] | CLUZ
9/24/2023 5:37:53 AM | [NSO Update] Mindanao Grid-09/24/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2792MW, PK=1675MW, RR=64MW, NetOpMargin: AM=1052, PM=983, EVE=807 Highest Unit O/L: GNPK 2&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @135MW, AG5 @44MW, AG6 @164MW, AG7 @31MW, PG4 @165MW [WEBSMS] | CMIN
9/24/2023 5:35:43 AM | Luzon Grid-09/24/2023 05:35: Binga-Ambuklao 230kV Line 1 de-energized at 0534H (Planned Outage) [WEBSMS] | CLUZ
9/24/2023 5:27:47 AM | Visayas Grid-09/24/2023 05:27: Magdugo-Colon 138kV Line 2 de-energized at 0524H. (Planned outage) [WEBSMS] | CVIS
9/24/2023 5:10:29 AM | Luzon Grid-09/24/2023 05:10: BCCPP 230kV Bus 2 de-energized at 0509H (Planned Outage) [WEBSMS] | CLUZ
9/24/2023 4:26:07 AM | [NSO Update] Luzon Grid-09/24/2023 04:26: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. Trough of Low Pressure Area affecting the rest of Luzon. [WEBSMS] | CLUZ
9/24/2023 4:23:09 AM | [NSO Update] Mindanao Grid-09/24/2023 04:25: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. Trough of Low Pressure Area affecting the rest of Luzon. [WEBSMS] | CMIN
9/23/2023 8:53:56 PM | Luzon Grid-09/23/2023 20:54: Mariveles SS 500kV Bus 1 restored at 2052H (Planned Outage) [WEBSMS] | CLUZ
9/23/2023 6:52:02 PM | Mindanao Grid-09/23/2023 18:54: Agus 6 HEP Unit 1 emergency shutdown at 1849H due to governor overheating. (Unplanned Outage) [WEBSMS] | CMIN
9/23/2023 6:15:34 PM | [NSO Update] Mindanao Grid-09/23/2023 18:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2747MW, PK=2035MW, RR=58MW, NetOpMargin: EVE=654 Highest Unit O/L: GNPK 2&3 @138MW Derated Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @117MW, AG5 @38MW, AG6 @171MW, AG7 @31MW, PG4 @180MW [WEBSMS] | CMIN
9/23/2023 5:56:15 PM | [NSO Update] Luzon Grid-09/23/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13082MW, PK=9569MW, RR=318MW, NetOpMargin: EVE=3195 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CLC2 @140MW, MSLC1 @330MW, MSLC2 @315MW, MSLC3 @325MW, SCPC 3 @110MW, ILIJAN A @575MW, ILIJAN B @225MW, STA. RITA 10 @200MW, STA. RITA 20 @235MW, STA. RITA 30 @200MW [WEBSMS] | CLUZ
9/23/2023 5:52:17 PM | Visayas Grid-09/23/2023 17:52: Daanbantayan - Tabango 230 kV Line 2 energized at 1750H. (Planned Outage) [WEBSMS] | CVIS
9/23/2023 5:38:32 PM | Luzon Grid-09/23/2023 17:38: Tayabas 500kV Bus 2 restored at 1737H. (Unplanned Outage). [WEBSMS] | CLUZ
9/23/2023 4:34:58 PM | Luzon Grid-09/23/2023 16:35: Tayabas 500kV Bus 2 tripped at 1632H (Unplanned Outage). [WEBSMS] | CLUZ
9/23/2023 4:15:09 PM | Mindanao Grid-09/23/2023 16:17: Agus 5 - Aurora 138KV Line restored at 1612H. (Planned Outage) [WEBSMS] | CMIN
9/23/2023 3:40:01 PM | Luzon Grid-09/23/2023 15:40: Malaya 230kV Bus 2 restored at 1539H. (Unplanned Outage) [WEBSMS] | CLUZ
9/23/2023 3:34:46 PM | Mindanao Grid-09/23/2023 15:37: WMPC DG10 cut-out at 1514H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/23/2023 3:33:39 PM | Mindanao Grid-09/23/2023 15:36: Pulangi 4 HEP Unit 3 online at 1526H. (Unplanned Outage) [WEBSMS] | CMIN
9/23/2023 3:19:33 PM | Luzon Grid-09/23/2023 15:19: Daraga-Tiwi Plant A 230kV Line restored at 1519H. (Planned Outage) [WEBSMS] | CLUZ
9/23/2023 3:17:50 PM | Mindanao Grid-09/23/2023 15:20: Agus 6 HEP Unit 1 cut-in at 1511H. (Unplanned Outage) [WEBSMS] | CMIN
9/23/2023 2:36:33 PM | Mindanao Grid-09/23/2023 14:39: Jasaan - UPSI BESS 69KV Line restored at 1433H. (Planned Outage) [WEBSMS] | CMIN
9/23/2023 2:22:26 PM | Mindanao Grid-09/23/2023 14:25: Supreme Power Mati cut-in at 1330H. (Unplanned Outage) [WEBSMS] | CMIN
9/23/2023 2:21:30 PM | Mindanao Grid-09/23/2023 14:24: Supreme Power Mati tripped with 5.4MW at 1306H. The lowest frequency recorded is 59.43Hz (with HVDC variance RTD=-65.1/Actual=-116.9). No ALD (Unplanned Outage) [WEBSMS] | CMIN
9/23/2023 1:57:25 PM | Mindanao Grid-09/23/2023 14:00: Pulangi 4 HEP Unit 3 emergency shutdown at 1306H due to hotspot. (Unplanned Outage). Frequency dip at 59.43Hz (with HVDC variance RTD=-65.1/Actual=-116.9). [WEBSMS] | CMIN
9/23/2023 1:51:41 PM | [NSO Update] Mindanao Grid-09/23/2023 13:54: SO-initiated Market Intervention has been lifted today, 23 September 2023 at 1345H, for Visayas and Mindanao. Market will resume starting interval 1350H. [WEBSMS] | CMIN
9/23/2023 1:51:01 PM | [NSO Update] Visayas Grid-09/23/2023 13:51: SO-initiated Market Intervention has been lifted today, 23 September 2023 at 1345H, for Visayas and Mindanao. Market will resume starting interval 1350H. [WEBSMS] | CVIS
9/23/2023 1:24:55 PM | [NSO Update] Mindanao Grid-09/23/2023 13:27: SO-initiated Market Intervention is issued today, 23 September 2023, for Visayas and Mindanao starting interval 1310H due to unimplementable RTD schedule. [WEBSMS] | CMIN
9/23/2023 1:24:37 PM | [NSO Update] Visayas Grid-09/23/2023 13:24: SO-initiated Market Intervention is issued today, 23 September 2023, for Visayas and Mindanao starting interval 1310H due to unimplementable RTD schedule. [WEBSMS] | CVIS
9/23/2023 1:15:43 PM | Mindanao Grid-09/23/2023 13:18: Agus 5 - Aurora 138KV Line deenergized at 1301H. Planned outage [WEBSMS] | CMIN
9/23/2023 12:54:30 PM | [NSO Update] Mindanao Grid-09/23/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2784MW, PK=1999MW, RR=60MW, NetOpMargin: PM=725, EVE=662 Highest Unit O/L: GNPK 2&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @117MW, AG5 @38MW, AG6 @171MW, AG7 @31MW, PG4 @180MW [WEBSMS] | CMIN
9/23/2023 12:51:11 PM | [NSO Update] Luzon Grid-09/23/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13569MW, PK=10051MW, RR=428MW, NetOpMargin: PM=3090, EVE=3169 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CLC2 @140MW, MSLC1 @330MW, MSLC2 @315MW, MSLC3 @325MW, SCPC 3 @110MW, ILIJAN A @575MW, ILIJAN B @225MW, STA. RITA 10 @200MW, STA. RITA 20 @235MW, STA. RITA 30 @200MW [WEBSMS] | CLUZ
9/23/2023 11:50:41 AM | Mindanao Grid-09/23/2023 11:53: Baloi-Agus 5 138KV line restored at 1148H. (Planned Outage) [WEBSMS] | CMIN
9/23/2023 11:03:45 AM | Mindanao Grid-09/23/2023 11:06: Pulangi 4 HEP Unit 3 online at 1100H. (Unplanned Outage) [WEBSMS] | CMIN
9/23/2023 10:08:10 AM | Mindanao Grid-09/23/2023 10:10: WMPC DG10 cut-in at 0952H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/23/2023 9:38:15 AM | Visayas Grid-09/23/2023 09:38: Dumanjug SS 150 MVA 230/138 kV TR2 de-energized at 0937H. (Unplanned Outage) [WEBSMS] | CVIS
9/23/2023 9:08:24 AM | Luzon Grid-09/23/2023 09:08: Mariveles SS 500kV Bus 1 de-energized at 0908H. (Planned Outage) [WEBSMS] | CLUZ
9/23/2023 8:49:58 AM | Mindanao Grid-09/23/2023 08:52: (Correction) Pulangi 4 HEP Unit 3 emergency shutdown at 0824H due to hotspot in busbar terminal connector. (Unplanned Outage). Frequency dip at 59.71Hz (gradual unloading implemented). [WEBSMS] | CMIN
9/23/2023 8:41:45 AM | Luzon Grid-09/23/2023 08:41: Labrador SS 230kV Bus 2 de-energized at 0841H. (Planned Outage) [WEBSMS] | CLUZ
9/23/2023 8:39:58 AM | Mindanao Grid-09/23/2023 08:42: Pulangi 4 HEP Unit 3 emergency shutdown at 0824H due to problem in its newly installed PCB. (Unplanned Outage). Frequency dip at 59.71Hz (gradual unloading implemented). [WEBSMS] | CMIN
9/23/2023 8:35:12 AM | Luzon Grid-09/23/2023 08:35: Balsik-SBMA 230kV Line de-energized at 0834H. (Planned Outage) [WEBSMS] | CLUZ
9/23/2023 8:15:42 AM | Mindanao Grid-09/23/2023 08:18: Culaman - Malita BESS 69KV Line deenergized at 0802H. (Planned Outage) [WEBSMS] | CMIN
9/23/2023 8:01:52 AM | Mindanao Grid-09/23/2023 08:04: Pulangi 4 HEP Unit 3 online at 0751H. (Unplanned Outage) [WEBSMS] | CMIN
9/23/2023 7:43:42 AM | Mindanao Grid-09/23/2023 07:46: Tudaya2 cut-in at 0638H. (Unplanned Outage. Affected by load shifting activity of Toril-Digos 69 kV line). [WEBSMS] | CMIN
9/23/2023 7:42:22 AM | Mindanao Grid-09/23/2023 07:45: Tudaya2 shutdown at 0526H. (Unplanned Outage. Affected by load shifting activity of Toril-Digos 69 kV line). [WEBSMS] | CMIN
9/23/2023 6:58:27 AM | Mindanao Grid-09/23/2023 07:01: Baloi-Agus 5 138KV Line deenergized at 0626H. (Plannrd Outage) [WEBSMS] | CMIN
9/23/2023 6:36:13 AM | Luzon Grid-09/23/2023 06:36: Daraga-Tiwi Plant A 230kV Line de-energized at 0636H (Planned Outage) [WEBSMS] | CLUZ
9/23/2023 6:32:37 AM | Mindanao Grid-09/23/2023 06:35: Agus 5 Switchyard Bus 2 deenergized at 0629H. (Planned Outage) [WEBSMS] | CMIN
9/23/2023 6:31:24 AM | Mindanao Grid-09/23/2023 06:34: Baloi-Agus 5 138KV Line deenergized at 0626H. (Planned Outage) [WEBSMS] | CMIN
9/23/2023 6:23:11 AM | Visayas Grid-09/23/2023 06:23: Daanbantayan - Tabango 230 kV Line 2 de-energized at 0622H. (Planned Outage) [WEBSMS] | CVIS
9/23/2023 5:53:09 AM | [NSO Update] Luzon Grid-09/23/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13816MW, PK=10042MW, RR=410MW, NetOpMargin: AM=3363, PM=2497, EVE=2638 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: Calaca 2 @ 140MW, Masinloc 1 @ 330MW, Masinloc 2 @ 315MW, Masinloc 3 @ 325MW, SCPC 3 @ 110MW, Ilijan A @ 575MW, Ilijan B @ 225MW, Sta. Rita 10 @ 200MW, Sta. Rita 20 @ 235MW, Sta. Rita 30 @ 200MW [WEBSMS] | CLUZ
9/23/2023 5:49:43 AM | [NSO Update] Mindanao Grid-09/23/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2795MW, PK=1882MW, RR=60MW, NetOpMargin: AM=854, PM=752, EVE=684 Highest Unit O/L: GNPK 2 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @135MW, AG5 @44MW, AG6 @164MW, AG7 @38MW, PG4 @160MW [WEBSMS] | CMIN
9/23/2023 5:01:07 AM | Mindanao Grid-09/23/2023 05:03: Baloi SS 138kV Bus 2 restored at 0455H. (Planned Outage) [WEBSMS] | CMIN
9/23/2023 4:29:33 AM | [NSO Update] Mindanao Grid-09/23/2023 04:32: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 85 km Northeast of Infanta, Quezon (15.2�N,122.3�E). Meanwhile, another LPA was estimated based on all available data at 125 km West of Iba, Zambales (15.4�N,118.8�E). Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
9/23/2023 4:29:14 AM | [NSO Update] Visayas Grid-09/23/2023 04:29: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 85 km Northeast of Infanta, Quezon (15.2�N,122.3�E). Meanwhile, another LPA was estimated based on all available data at 125 km West of Iba, Zambales (15.4�N,118.8�E). Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
9/23/2023 4:29:03 AM | [NSO Update] Luzon Grid-09/23/2023 04:29: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 85 km Northeast of Infanta, Quezon (15.2�N,122.3�E). Meanwhile, another LPA was estimated based on all available data at 125 km West of Iba, Zambales (15.4�N,118.8�E). Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
9/23/2023 3:04:05 AM | Luzon Grid-09/23/2023 03:03: Duhat (Marilao) - Hermosa 230kV Line - energized at 0301H [WEBSMS] | CLUZ
9/23/2023 2:31:06 AM | Mindanao Grid-09/23/2023 02:33: Baloi 138kV Bus 2 de-energized at 0129H. (Planned Outage) [WEBSMS] | CMIN
9/23/2023 1:34:09 AM | Luzon Grid-09/23/2023 01:34: Sta Rita 30 online at 0133H (Unplanned Outage) [WEBSMS] | CLUZ
9/23/2023 12:36:46 AM | Luzon Grid-09/23/2023 00:36: Duhat(Marilao)-Hermosa 230kV Line de-energized at 0036H (Planned Outage) [WEBSMS] | CLUZ
9/23/2023 12:07:10 AM | Luzon Grid-09/23/2023 00:07: San Jose-Balsik 500kV Line and San Jose 750MVA T05 restored at 0005H (Planned Outage) [WEBSMS] | CLUZ
9/22/2023 11:15:18 PM | Luzon Grid-09/22/2023 23:15: Sta Rita 30 with 227MW load tripped at 2312H. Lowest Frequency is 59.39Hz (Unplanned Outage) [WEBSMS] | CLUZ
9/22/2023 11:11:46 PM | Luzon Grid-09/22/2023 23:11: Malaya 230kV Bus 2 de-energized at 2200H (Unplanned Outage) [WEBSMS] | CLUZ
9/22/2023 9:16:26 PM | Mindanao Grid-09/22/2023 21:19: WMPC DG10 Shutdown as RPS at 2113H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/22/2023 6:21:43 PM | Luzon Grid-09/22/2023 18:21: San Jose-Taytay 230kV Line 1 de-energized at 1821H (Planned Outage) [WEBSMS] | CLUZ
9/22/2023 6:15:50 PM | Luzon Grid-09/22/2023 18:15: Gamu-UPSI Gamu BESS 69kV Line restored at 1807H (Planned Outage) [WEBSMS] | CLUZ
9/22/2023 5:56:38 PM | [NSO Update] Luzon Grid-09/22/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12724MW, PK=10077MW, RR=408MW, NetOpMargin: EVE=2239 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: Calaca 2 @174MW, GMEC 1 @150MW, GMEC 2 @100MW, Masinloc 1 @330MW, Masinloc 2 @330MW, Masinloc 3 @280MW, SCPC 1 @104MW, SCPC 3 @110MW, Sual 2@620MW, Sta. Rita 10 @200MW, Sta. Rita 20 @235MW, Sta. Rita 30 @254MW, Ilijan A @575MW, Ilijan B @225MW [WEBSMS] | CLUZ
9/22/2023 5:50:38 PM | [NSO Update] Mindanao Grid-09/22/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2685MW, PK=2061MW, RR=60MW, NetOpMargin: EVE=564 Highest Unit O/L: GNPK 2 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @117MW, AG5 @38MW, AG6 @171MW, AG7 @30MW, PG4 @120MW [WEBSMS] | CMIN
9/22/2023 4:16:40 PM | Mindanao Grid-09/22/2023 16:19: WMPC DG7 shutdown as RPS at 1614H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/22/2023 4:14:56 PM | Visayas Grid-09/22/2023 16:14: CEDC unit# 1online at 1602H. (Unplanned Outage) [WEBSMS] | CVIS
9/22/2023 3:50:33 PM | Luzon Grid-09/22/2023 15:50: GMEC 2 online at 1548H. (Unplanned Outage) [WEBSMS] | CLUZ
9/22/2023 2:33:09 PM | Luzon Grid-09/22/2023 14:33: Malaya 230kV Bus 2 restored at 1432H. (Unplanned Outage) [WEBSMS] | CLUZ
9/22/2023 2:16:07 PM | Visayas Grid-09/22/2023 14:15: Daanbantayan-Compostela 230KV line 2 successful auto-reclosing @1402H. [WEBSMS] | CVIS
9/22/2023 1:36:57 PM | Luzon Grid-09/22/2023 13:37: Malaya 230kV Bus 2 tripped at 1334H. (Unplanned Outage) [WEBSMS] | CLUZ
9/22/2023 1:18:17 PM | Mindanao Grid-09/22/2023 13:21: Toril - Davao Coal Plant 138 kV L1 de- energized at 1304H. (Planned Outage) [WEBSMS] | CMIN
9/22/2023 1:10:12 PM | [NSO Update] Mindanao Grid-09/22/2023 13:13: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2718MW, PK=2158MW, RR=60MW, NetOpMargin: PM=501, EVE=537 Highest Unit O/L: GNPK 2&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @117MW, AG5 @38MW, AG6 @171MW, AG7 @30MW, PG4 @120MW [WEBSMS] | CMIN
9/22/2023 1:02:37 PM | [NSO Update] Luzon Grid-09/22/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13131MW, PK=11408MW, RR=396MW, NetOpMargin: PM=1327, EVE=1612 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CALACA 2 @174MW, MASINLOC 1 @330MW, MASINLOC 2 @325MW, MASINLOC 3 @300MW, SCPC 3 @110MW, ILIJAN A @575MW, ILIJAN B @225MW, SUAL 2 @620MW, STA. RITA 10 @200MW, STA. RITA 20 @235MW, STA. RITA 30 @254MW, GMEC 1 @150MW [WEBSMS] | CLUZ
9/22/2023 12:54:08 PM | Luzon Grid-09/22/2023 12:54: Dasmarinas-TMC 2 115kV Line auto-tripped/auto-reclosed at 1249H. (Unplanned Outage) [WEBSMS] | CLUZ
9/22/2023 12:37:46 PM | Mindanao Grid-09/22/2023 12:40: Toril - Davao Coal Plant 138 kV L2 energized at 1234H. (Unplanned Outage) [WEBSMS] | CMIN
9/22/2023 12:31:29 PM | Luzon Grid-09/22/2023 12:31: GMEC 2 tripped at 1229H WITH 87MW load. Lowest system frequency is 59.68Hz (Unplanned Outage) [WEBSMS] | CLUZ
9/22/2023 10:53:45 AM | Mindanao Grid-09/22/2023 10:56: WMPC DG7 Online as RPS at 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/22/2023 10:12:07 AM | Mindanao Grid-09/22/2023 10:14: AG6 U1 shutdown at 1000H. (Unplanned Outage). [WEBSMS] | CMIN
9/22/2023 9:33:59 AM | Mindanao Grid-09/22/2023 09:36: AG6 U1 cut-in at 0916H. (Unplanned Outage). [WEBSMS] | CMIN
9/22/2023 9:06:42 AM | Mindanao Grid-09/22/2023 09:09: WMPC DG10 cut-in as RPS at 0850H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/22/2023 7:10:38 AM | Luzon Grid-09/22/2023 07:10: Gamu-UPSI Gamu BESS 69kV Line de-energized at 0709H. (Planned Outage) [WEBSMS] | CLUZ
9/22/2023 6:24:01 AM | [NSO Update] Mindanao Grid-09/22/2023 06:26: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2745MW, PK=729MW, RR=20MW, NetOpMargin: AM=729, PM=533, EVE=511 Highest Unit O/L: GNPK 2&3 @138MW Derated Plant: FMP @242MW, MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @135MW, AG5 @38MW, AG6 @171MW, AG7 @30MW, PG4 @120MW [WEBSMS] | CMIN
9/22/2023 6:18:15 AM | [NSO Update] Luzon Grid-09/22/2023 06:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13861MW, PK=11439MW, RR=430MW, NetOpMargin: AM=1992, PM=1352, EVE=1700 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CALACA 2 @174MW, MASINLOC 1 @260MW, MASINLOC 2 @325MW, MASINLOC 3 @300MW, SCPC 3 @110MW, ILIJAN A @575MW, ILIJAN B @225MW, SUAL 2 @620MW, ST. RITA 10 @200MW, ST. RITA 20 @235MW, ST. RITA 30 @254MW [WEBSMS] | CLUZ
9/22/2023 6:06:13 AM | Luzon Grid-09/22/2023 06:06: San Jose SS 750MVA T05 de-energized at 0605H. (Planned Outage) [WEBSMS] | CLUZ
9/22/2023 5:59:14 AM | Luzon Grid-09/22/2023 05:59: San Jose-Balsik 500kV Line de-energized at 0558H. (Planned Outage) [WEBSMS] | CLUZ
9/22/2023 4:16:00 AM | [NSO Update] Mindanao Grid-09/22/2023 04:18: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
9/22/2023 4:15:20 AM | [NSO Update] Luzon Grid-09/22/2023 04:15: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
9/22/2023 4:14:56 AM | [NSO Update] Visayas Grid-09/22/2023 04:14: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
9/22/2023 3:43:52 AM | Mindanao Grid-09/22/2023 03:46: Baloi SS 138KV Bus 1 re-energized at 0332H. (Unplanned Outage) [WEBSMS] | CMIN
9/22/2023 3:26:29 AM | Luzon Grid-09/22/2023 03:26: SCPC 1 online at 0325H (Planned Outage) [WEBSMS] | CLUZ
9/22/2023 2:08:09 AM | Mindanao Grid-09/22/2023 02:10: Bunawan SS 50MVA Power Transformer 1 successfully re-energized at 0124H. From Planned Outage / Non-GOMP... [WEBSMS] | CMIN
9/22/2023 1:57:04 AM | Mindanao Grid-09/22/2023 01:59: Baloi SS 138KV Bus 1 on emergency shutdown at 0105H to conduct removal of line hardwares at Bay 8 connecting to 138KV Bus 1, and decommissioning of PCB 7-01CB08BLO, with ride-on hotspot correction activities. [WEBSMS] | CMIN
9/21/2023 10:52:13 PM | Mindanao Grid-09/21/2023 22:55: New Bataan (Euro) Hydro cut-in at 2242H. (Unplanned Outage) [WEBSMS] | CMIN
9/21/2023 9:17:16 PM | Mindanao Grid-09/21/2023 21:20: WMPC DG10 shutdown at 2114H - End of RPS - System Voltage Requirement [WEBSMS] | CMIN
9/21/2023 7:20:54 PM | Luzon Grid-09/21/2023 19:20: For Info: Trust Solar 19MVA Transformer energized at 1837H. For soaking. [WEBSMS] | CLUZ
9/21/2023 7:00:37 PM | Mindanao Grid-09/21/2023 19:03: New Bataan (Euro) Hydro tripped with load of 1.7MW at 1834H. (Unplanned Outage). Frequency dip: 59.92Hz. Cause: Fault at plant-owned/maintained transmission line. [WEBSMS] | CMIN
9/21/2023 5:49:13 PM | [NSO Update] Luzon Grid-09/21/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12932MW, PK=10809MW, RR=408MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CALACA 2 @150MW, MASINLOC 1 @330MW, MASINLOC 2 @280MW, MASINLOC 3 @320MW, SAN LORENZO 50 @200MW, SCPC 3 @110MW, ILIJAN A @545MW, ILIJAN B @255MW, SUAL 2 @620MW, ST. RITA 30 @254MW, ST. RITA 10 @200MW, ST. RITA 20 @235MW [WEBSMS] | CLUZ
9/21/2023 5:40:32 PM | [NSO Update] Mindanao Grid-09/21/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2647MW, PK=2112MW, RR=60MW, NetOpMargin: EVE=476 Highest Unit O/L: GNPK 2&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @107MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @120MW [WEBSMS] | CMIN
9/21/2023 4:17:25 PM | Mindanao Grid-09/21/2023 16:20: WMPC DG07 shutdown at 1613H - End of RPS System Voltage Requirement [WEBSMS] | CMIN
9/21/2023 2:41:25 PM | Luzon Grid-09/21/2023 14:41: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1440H. (Planned Outage) [WEBSMS] | CLUZ
9/21/2023 1:07:56 PM | Mindanao Grid-09/21/2023 13:10: Nabunturan - Masara 138kV L restored at 1259H. (Unplanned Outage) [WEBSMS] | CMIN
9/21/2023 1:06:57 PM | Mindanao Grid-09/21/2023 13:09: Nabunturan - Masara 138kV line tripped at 1248H. (Unplanned Outage) [WEBSMS] | CMIN
9/21/2023 12:57:31 PM | [NSO Update] Luzon Grid-09/21/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13440MW, PK=12021MW, RR=436MW, NetOpMargin: PM=983, EVE=1541 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CALACA 2 @150MW, MASINLOC 1 @330MW, MASINLOC 2 @280MW, MASINLOC 3 @300MW, SAN LORENZO 50 @200MW, SCPC 3 @110MW, ILIJAN A @545MW, ILIJAN B @255MW, SUAL 2 @620MW, ST. RITA 30 @254MW, ST. RITA 10 @200MW, ST. RITA 20 @180MW [WEBSMS] | CLUZ
9/21/2023 12:40:00 PM | [NSO Update] Mindanao Grid-09/21/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2675MW, PK=2162MW, RR=60MW, NetOpMargin: PM=453, EVE=473 Highest Unit O/L: GNPK 2&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @107MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @120MW [WEBSMS] | CMIN
9/21/2023 12:07:38 PM | Mindanao Grid-09/21/2023 12:10: Toril - Davao Coal Plant 138 kV L1 restored at 1206H. (Planned Outage) [WEBSMS] | CMIN
9/21/2023 10:51:41 AM | Mindanao Grid-09/21/2023 10:54: WMPC DG07 cut-in at 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/21/2023 10:42:04 AM | Mindanao Grid-09/21/2023 10:44: Agus 6 HEP Unit 1 cut-out at 1035H. End of RTD (Note: unit under test and commissioning). [WEBSMS] | CMIN
9/21/2023 9:34:15 AM | Mindanao Grid-09/21/2023 09:37: Toril - Davao Coal Plant 138 kV L1 de-energized at 0932H. (Planned Outage) [WEBSMS] | CMIN
9/21/2023 9:21:02 AM | Luzon Grid-09/21/2023 09:21: Sta. Rita 20 online at 0918H. (Unplanned Outage) [WEBSMS] | CLUZ
9/21/2023 9:19:51 AM | Mindanao Grid-09/21/2023 09:22: Toril - Davao Coal Plant 138 kV L2 de-energized at 0831H. (Unplanned Outage) [WEBSMS] | CMIN
9/21/2023 9:17:29 AM | Mindanao Grid-09/21/2023 09:20: Agus 6 HEP Unit 1 cut-in at 0915H. (from Unplanned Outage) [WEBSMS] | CMIN
9/21/2023 9:04:24 AM | Luzon Grid-09/21/2023 09:04: Dasmarinas-TMC II (Ternate) 115kV Linede-energized at 0903H. (Planned Outage) [WEBSMS] | CLUZ
9/21/2023 8:55:34 AM | Mindanao Grid-09/21/2023 08:58: WMPC DG10 cut-in at 0850H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/21/2023 5:55:12 AM | [NSO Update] Luzon Grid-09/21/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13423MW, PK=11546MW, RR=430MW, NetOpMargin: AM=1447, PM=684, EVE=896 Highest Unit O/L: GNPD U2 @ 668MW Derated Plant: CALACA 2 @150MW, MASINLOC 1 @290MW, MASINLOC 2 @280MW, MASINLOC 3 @310MW, SAN LORENZO 50 @200MW, SCPC 3 @110MW, ILIJAN A @545MW, ILIJAN B @255MW, SUAL 2 @620MW, ST. RITA 30 @254MW [WEBSMS] | CLUZ
9/21/2023 5:32:54 AM | [NSO Update] Mindanao Grid-09/21/2023 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2689MW, PK=2112MW, RR=60MW, NetOpMargin: AM=517, PM=481, EVE=487 Highest Unit O/L: GNPK 2 & 3 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @107MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @120MW [WEBSMS] | CMIN
9/21/2023 4:34:22 AM | Luzon Grid-09/21/2023 04:34: Dona Imelda(Araneta)-Kamuning 115kV line restored at 0433H (Planned Outage) [WEBSMS] | CLUZ
9/21/2023 4:07:32 AM | [NSO Update] Mindanao Grid-09/21/2023 04:10: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CMIN
9/21/2023 4:07:15 AM | [NSO Update] Visayas Grid-09/21/2023 04:06: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CVIS
9/21/2023 4:06:59 AM | [NSO Update] Luzon Grid-09/21/2023 04:06: Weather Advisory: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CLUZ
9/21/2023 3:32:02 AM | Mindanao Grid-09/21/2023 03:35: Euro Hydro (NBT) online at 0323H. Unplanned Outage. [WEBSMS] | CMIN
9/21/2023 1:28:50 AM | Mindanao Grid-09/21/2023 01:31: Lake Mainit HEPP (AGC) Online at 2258H. Unplanned Outage. [WEBSMS] | CMIN
9/21/2023 12:39:48 AM | Luzon Grid-09/21/2023 00:40: Dona Imelda(Araneta)-Kamuning 115kV line - de-energized at 0039H (Planned Outage) [WEBSMS] | CLUZ
9/21/2023 12:35:51 AM | Luzon Grid-09/21/2023 00:36: Sta Rita Module 20 - tripped at 0029H from 237MW load. (Unplanned Outage). The lowest system frequency was 59.363Hz. [WEBSMS] | CLUZ
9/21/2023 12:14:14 AM | Luzon Grid-09/21/2023 00:14: GNPD Unit 1 shutdown at 0012H (Planned Outage). [WEBSMS] | CLUZ
9/20/2023 10:47:36 PM | Mindanao Grid-09/20/2023 22:50: Euro Hydro (NBT) with 1.7MW gross generation tripped/Isolated due to loss of power affected by the forced outage of NORDECO 13.8kV line. Unplanned Outage. [WEBSMS] | CMIN
9/20/2023 10:42:35 PM | Mindanao Grid-09/20/2023 22:45: Lake Mainit HEPP (AGC) with 10.5MW gross generation tripped at 2232H. Indication: 86,Z Generator Master Trip Relay. Unplanned Outage. [WEBSMS] | CMIN
9/20/2023 9:54:04 PM | Mindanao Grid-09/20/2023 21:57: TM1 Unit #1 shutdown at 2147H, from MO dispatched as energy. Follow RTD. [WEBSMS] | CMIN
9/20/2023 9:16:31 PM | Mindanao Grid-09/20/2023 21:19: WMPC DG10 shutdown at 2113H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
9/20/2023 8:58:29 PM | Luzon Grid-09/20/2023 20:58: San Lorenzo Module 50 online at 2056H (Unplanned Outage) [WEBSMS] | CLUZ
9/20/2023 6:14:33 PM | Mindanao Grid-09/20/2023 18:17: NBT (Euro Hydro) online at 1725H, Unplanned Outage [WEBSMS] | CMIN
9/20/2023 5:59:30 PM | Luzon Grid-09/20/2023 17:59: Naga-Tiwi C 230kV line 2 - restored at 1758H (Planned Outage) [WEBSMS] | CLUZ
9/20/2023 5:57:51 PM | Mindanao Grid-09/20/2023 18:00: WMPC DG02 online at 1748H. MO dispatched as energy. Follow RTD. [WEBSMS] | CMIN
9/20/2023 5:54:28 PM | [NSO Update] Mindanao Grid-09/20/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2781MW, PK=2108MW, RR=60MW, NetOpMargin: EVE=613 Highest Unit O/L: GNPK 2&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @110MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @120MW [WEBSMS] | CMIN
9/20/2023 5:51:16 PM | Luzon Grid-09/20/2023 17:51: Binga PCB 8-01CB24BIZ - de-energized at 1750H (Unplanned Outage) [WEBSMS] | CLUZ
9/20/2023 5:50:53 PM | Mindanao Grid-09/20/2023 17:53: Bunawan SS 138KV Bus 1 re-energized at 1739H. From Planned Outage /Non-GOMP. [WEBSMS] | CMIN
9/20/2023 5:40:29 PM | [NSO Update] Luzon Grid-09/20/2023 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13095MW, PK=11148MW, RR=402MW, NetOpMargin: EVE=1545 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @180MW CLC2 @174MW, MSLC1 @330MW, MSLC2 @330MW, MSLC3 @280MW, SCPC 3 @110MW, ILIJAN A @545MW, ILIJAN B @255MW [WEBSMS] | CLUZ
9/20/2023 5:07:29 PM | Mindanao Grid-09/20/2023 17:10: New Bataan Hydroelectric Powerplant tripped with 1.7 MW load at 1638H due to voltage fluctuation at NORDECO feeder. (Unplanned Outage) [WEBSMS] | CMIN
9/20/2023 4:26:30 PM | Mindanao Grid-09/20/2023 16:29: WMPC DG02 shutdown at 1614H - End of RPS System Voltage Requirement [WEBSMS] | CMIN
9/20/2023 4:23:32 PM | Luzon Grid-09/20/2023 16:23: San Lorenzo 50 with 248MW load tripped at 1618H. Lowest System Frequency is 59.38Hz (Unplanned Outage) [WEBSMS] | CLUZ
9/20/2023 3:47:44 PM | Luzon Grid-09/20/2023 15:48: Lamao-SCPC 230kV Tie Line 1 restored at 1546H (Planned Outage) [WEBSMS] | CLUZ
9/20/2023 3:39:48 PM | Luzon Grid-09/20/2023 15:40: Lumban-Malaya 230kV Line 2 restored at 1538H (Planned Outage) [WEBSMS] | CLUZ
9/20/2023 3:30:36 PM | Luzon Grid-09/20/2023 15:30: Calaca-SLPGC 230kV L2 restored at 1525H (Unplanned Outage) [WEBSMS] | CLUZ
9/20/2023 2:22:05 PM | Visayas Grid-09/20/2023 14:21: Pajo 69kV Feeder restored at 1419H. (Unplanned outage) [WEBSMS] | CVIS
9/20/2023 2:12:25 PM | Visayas Grid-09/20/2023 14:12: Lanao 69 kV Feeder restored at 1409H. (Unplanned outage) [WEBSMS] | CVIS
9/20/2023 1:54:31 PM | Visayas Grid-09/20/2023 13:54: Leyte-Cebu SIPS activated @1349H. [WEBSMS] | CVIS
9/20/2023 1:28:46 PM | Mindanao Grid-09/20/2023 13:31: Bunawan SS 138kV Bus No. 1 de-energized at 1315H. (Planned Outage) [WEBSMS] | CMIN
9/20/2023 1:27:46 PM | [NSO Update] Visayas Grid-09/20/2023 13:27: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1324H with power going to Visayas. [WEBSMS] | CVIS
9/20/2023 1:26:43 PM | [NSO Update] Mindanao Grid-09/20/2023 13:29: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1324H with power going to Visayas. [WEBSMS] | CMIN
9/20/2023 1:23:58 PM | [NSO Update] Mindanao Grid-09/20/2023 13:27: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1315H from reverse power direction. [WEBSMS] | CMIN
9/20/2023 1:23:54 PM | [NSO Update] Visayas Grid-09/20/2023 13:23: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1315H from reverse power direction. [WEBSMS] | CVIS
9/20/2023 1:18:09 PM | Luzon Grid-09/20/2023 13:18: SLPGC 1 emergency shutdown at 1309H (Unplanned Outage) [WEBSMS] | CLUZ
9/20/2023 1:05:09 PM | [NSO Update] Luzon Grid-09/20/2023 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14285MW, PK=11869MW, RR=396MW, NetOpMargin: PM=2019, EVE=2209 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @174MW, MSLC1 @330MW, MSLC2 @330MW, MSLC3 @280MW, SCPC 3 @110MW, SLPGC 1 @55MW, ILIJAN A @545MW, ILIJAN B @255MW [WEBSMS] | CLUZ
9/20/2023 12:51:54 PM | [NSO Update] Mindanao Grid-09/20/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2811MW, PK=2107MW, RR=60MW, NetOpMargin: PM=645, EVE=663 Highest Unit O/L: GNPK 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @110MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @120MW [WEBSMS] | CMIN
9/20/2023 12:04:12 PM | Mindanao Grid-09/20/2023 12:07: GN Power Unit #2 online at 1156H from reserved shutdown. Follow RTD. [WEBSMS] | CMIN
9/20/2023 9:42:48 AM | [NSO Update] Mindanao Grid-09/20/2023 09:45: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0942H with power going to Mindanao. [WEBSMS] | CMIN
9/20/2023 9:42:31 AM | [NSO Update] Visayas Grid-09/20/2023 09:42: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0942H with power going to Mindanao. [WEBSMS] | CVIS
9/20/2023 9:24:40 AM | Mindanao Grid-09/20/2023 09:27: Kauswagan - GNPK 230kV L1 de-energized at 0917H. (Planned Outage) [WEBSMS] | CMIN
9/20/2023 9:22:08 AM | [NSO Update] Mindanao Grid-09/20/2023 09:25: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0921H from forward power direction. [WEBSMS] | CMIN
9/20/2023 9:21:47 AM | [NSO Update] Visayas Grid-09/20/2023 09:21: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0921H from forward power direction. [WEBSMS] | CVIS
9/20/2023 8:55:24 AM | Mindanao Grid-09/20/2023 08:58: WMPC DG10 online at 0850H as RPS-System Voltage Requirement. [WEBSMS] | CMIN
9/20/2023 7:22:43 AM | Luzon Grid-09/20/2023 07:23: Lumban-Malaya 230kV Line 2 de-energized at 0722H (Planned Outage) [WEBSMS] | CLUZ
9/20/2023 6:36:31 AM | Luzon Grid-09/20/2023 06:36: Naga-Tiwi C 230kV Line 2 de-energized at 0635H (Planned Outage) [WEBSMS] | CLUZ
9/20/2023 5:54:49 AM | [NSO Update] Mindanao Grid-09/20/2023 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2908MW, PK=2090MW, RR=60MW, NetOpMargin: AM=758, PM=621, EVE=637 Highest Unit O/L: GNPK 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @110MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @120MW [WEBSMS] | CMIN
9/20/2023 5:41:29 AM | [NSO Update] Luzon Grid-09/20/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14585MW, PK=11488MW, RR=430MW, NetOpMargin: AM=2667, PM=2334, EVE=2459 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @174MW, MSLC1 @310MW, MSLC2 @295MW, MSLC3 @325MW, SCPC 3 @110MW, SLPGC 1 @55MW, ILIJAN A @ 545MW, ILIJAN B @255MW [WEBSMS] | CLUZ
9/20/2023 4:18:34 AM | [NSO Update] Luzon Grid-09/20/2023 04:18: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CLUZ
9/20/2023 4:16:14 AM | [NSO Update] Mindanao Grid-09/20/2023 04:19: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CMIN
9/20/2023 4:13:49 AM | [NSO Update] Visayas Grid-09/20/2023 04:13: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CVIS
9/19/2023 10:47:06 PM | Luzon Grid-09/19/2023 22:47: Calaca-SLPGC 230kV L2 de-energized at 2245H (Unplanned Outage) [WEBSMS] | CLUZ
9/19/2023 9:46:08 PM | Luzon Grid-09/19/2023 21:46: Balasik-Mariveles 500kV L2 autotripped/reclosed at 2141H (Unplanned Outage) [WEBSMS] | CLUZ
9/19/2023 9:19:19 PM | Mindanao Grid-09/19/2023 21:19: WMPC DG10 shutdown at 2113H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
9/19/2023 8:55:53 PM | "Mindanao Grid-09/19/2023 20:55: TM1 Unit #1 shutdown at 2042H, from MO dispatched as energy. Follow RTD. [WEBSMS]" | CMIN
9/19/2023 8:31:44 PM | Mindanao Grid-09/19/2023 20:31: WMPC DG02 and DG07 both shutdown at 1859H from MO dispatched as energy. Follow RTD. [WEBSMS] | CMIN
9/19/2023 8:30:27 PM | "Mindanao Grid-09/19/2023 20:30: WMPC DG05 shutdown at 1854H, from MO dispatched as energy. Follow RTD. [WEBSMS]" | CMIN
9/19/2023 8:29:20 PM | "Mindanao Grid-09/19/2023 20:29: TM2 Unit #2 Shutdown at 2022H, from MO dispatched as energy. Follow RTD. [WEBSMS]" | CMIN
9/19/2023 6:18:29 PM | "Mindanao Grid-09/19/2023 18:18: WMPC DG02, DG05 and DG07 online at 1752H, 1759H and 1800H respectively. MO dispatched (Follow RTD) [WEBSMS]" | CMIN
9/19/2023 6:00:33 PM | "[NSO Update] Mindanao Grid-09/19/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2841MW, PK=2069MW, RR=60MW, NetOpMargin: EVE=712 Highest Unit O/L: GNPK 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @153MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @120MW [WEBSMS]" | CMIN
9/19/2023 5:53:19 PM | [NSO Update] Visayas Grid-09/19/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2555MW, PK=2183MW, RR=87MW, NetOpMargin: EVE=284 Highest Unit O/L: THVI 1@169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @324MW, PGPP1 @62.5MW, TPC (Carmen) @30MW, THVI 2 @130MW [WEBSMS] | CVIS
9/19/2023 5:52:22 PM | Luzon Grid-09/19/2023 17:55: Naga-Tiwi C 230kV Line 1 restored at 1754H (Planned Outage) [WEBSMS] | CLUZ
9/19/2023 5:47:37 PM | "[NSO Update] Luzon Grid-09/19/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13425MW, PK=10837MW, RR=429MW, NetOpMargin: EVE=2159 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @174MW, MSLC1 @310MW, MSLC2 @295MW, MSLC3 @325MW, SCPC 3 @110MW, SLPGC 1 @55MW, SAN LO 60 @165MW, ILIJAN A @545MW, ILIJAN B @255MW, STA.RITA 30 @80MW [WEBSMS]" | CLUZ
9/19/2023 5:06:46 PM | Mindanao Grid-09/19/2023 17:06: Bunawan - DRA 138KV L2 (new line) successfully energized at 1630H. [WEBSMS] | CMIN
9/19/2023 4:31:32 PM | Luzon Grid-09/19/2023 16:31: Sta. Rita 30 online at 1629H (Unplanned Outage) [WEBSMS] | CLUZ
9/19/2023 4:23:59 PM | Mindanao Grid-09/19/2023 16:23: WMPC DG02 shutdown at 1614H - End of RPS System Voltage Requirement [WEBSMS] | CMIN
9/19/2023 3:40:09 PM | Luzon Grid-09/19/2023 15:40: Lumban-Malaya 230kV Line 1 restored at 1537H (Planned Outage) [WEBSMS] | CLUZ
9/19/2023 2:34:56 PM | Visayas Grid-09/19/2023 14:34: CEDC U1 emergency cut-out at 1433H, possible tube leak. (Unplanned Outage) [WEBSMS] | CVIS
9/19/2023 1:50:35 PM | [NSO Update] Visayas Grid-09/19/2023 13:50: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1348H from reverse power direction. [WEBSMS] | CVIS
9/19/2023 1:50:29 PM | [NSO Update] Mindanao Grid-09/19/2023 13:53: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1348H from reverse power direction. [WEBSMS] | CMIN
9/19/2023 12:59:47 PM | [NSO Update] Luzon Grid-09/19/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13875MW, PK=11749MW, RR=452MW, NetOpMargin: PM=1675, EVE=2003 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @174MW, MSLC1 @300MW, MSLC2 @280MW, SCPC 3 @110MW, SLPGC 1 @55MW, SAN LO 60 @165MW, ILIJAN A @545MW, ILIJAN B @255MW [WEBSMS] | CLUZ
9/19/2023 12:49:51 PM | [NSO Update] Mindanao Grid-09/19/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2879MW, PK=2172MW, RR=60MW, NetOpMargin: PM=647, EVE=649 Highest Unit O/L: GNPK 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @153MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @120MW [WEBSMS] | CMIN
9/19/2023 11:11:48 AM | Mindanao Grid-09/19/2023 11:14: WMPC DG02 cut-in at 1050H. RPS - System Voltage Requirement [WEBSMS] | CMIN
9/19/2023 9:57:17 AM | [NSO Update] Mindanao Grid-09/19/2023 10:00: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0954H with power going to Mindanao. [WEBSMS] | CMIN
9/19/2023 9:57:04 AM | [NSO Update] Visayas Grid-09/19/2023 09:56: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0954H with power going to Mindanao. [WEBSMS] | CVIS
9/19/2023 9:28:35 AM | [NSO Update] Mindanao Grid-09/19/2023 09:31: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0927H from forward power direction. [WEBSMS] | CMIN
9/19/2023 9:28:28 AM | [NSO Update] Visayas Grid-09/19/2023 09:28: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0927H from forward power direction. [WEBSMS] | CVIS
9/19/2023 9:08:31 AM | Mindanao Grid-09/19/2023 09:11: Agus 4 Unit 1 cut-in at 0902H. (Unplanned Outage) [WEBSMS] | CMIN
9/19/2023 8:58:34 AM | Mindanao Grid-09/19/2023 09:01: WMPC DG10 cut-in at 0852H. RPS - System Voltage Requirement [WEBSMS] | CMIN
9/19/2023 7:10:28 AM | Luzon Grid-09/19/2023 07:10: Lumban-Malaya 230kV Line 1 de-energized at 0709H (Planned Outage) [WEBSMS] | CLUZ
9/19/2023 6:38:14 AM | Luzon Grid-09/19/2023 06:38: Naga-Tiwi C 230kV Line 1 de-energized at 0637H (Planned Outage) [WEBSMS] | CLUZ
9/19/2023 5:44:22 AM | [NSO Update] Mindanao Grid-09/19/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2948MW, PK=2073MW, RR=60MW, NetOpMargin: AM=814, PM=596, EVE=643 Highest Unit O/L: GNPK 3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @105MW, AG4 @103MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @120MW [WEBSMS] | CMIN
9/19/2023 5:42:44 AM | [NSO Update] Luzon Grid-09/19/2023 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13958MW, PK=11455MW, RR=439MW, NetOpMargin: AM=2064, PM=2096, EVE=2087 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @174MW, MSLC1 @290MW, MSLC2 @280MW, MSLC3 @300MW, SCPC 3 @110MW, SLPGC 1 @50MW, SAN LO 60 @165MW, ILIJAN A @525MW, ILIJAN B @255MW [WEBSMS] | CLUZ
9/19/2023 5:36:57 AM | Luzon Grid-09/19/2023 05:37: Batangas T05 and T04 unloop at 0532H and Sta. Rita-San Lorezo 230kV Bus 1 and 2 looped at 0535H (Unplanned Outage) [WEBSMS] | CLUZ
9/19/2023 4:54:45 AM | [NSO Update] Mindanao Grid-09/19/2023 04:57: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CMIN
9/19/2023 4:54:31 AM | [NSO Update] Visayas Grid-09/19/2023 04:54: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CVIS
9/19/2023 2:22:24 AM | Luzon Grid-09/19/2023 02:22: San Lorenzo Module 60 online at 0218H (Unplanned Outage) [WEBSMS] | CLUZ
9/19/2023 1:34:42 AM | Luzon Grid-09/19/2023 01:34: Sta. Rita 30 shutdown at 0133H (Unplanned Outage) [WEBSMS] | CLUZ
9/19/2023 12:04:28 AM | Visayas Grid-09/19/2023 00:04: Magdugo-Calongcalong 138 KV Line 2 energized at 0002H. (Planned Outage) [WEBSMS] | CVIS
9/18/2023 11:48:58 PM | Mindanao Grid-09/18/2023 23:51: SPGI (Biomass) online at 2312H. Unplanned Outage. [WEBSMS] | CMIN
9/18/2023 10:54:12 PM | Luzon Grid-09/18/2023 22:54: San Gabriel shutdown at 2254H (Unplanned Outage) [WEBSMS] | CLUZ
9/18/2023 10:15:54 PM | Mindanao Grid-09/18/2023 22:18: GN Power Unit #4 with 112.69MW gross generation tripped at 2156H, resulted to UFR/ALD activation with total load drop=42.29MW. Frequency Dip=59.109Hz. Unplanned Outage. Details to Follow. [WEBSMS] | CMIN
9/18/2023 9:29:05 PM | Mindanao Grid-09/18/2023 21:32: WMPC DG10 shutdown at 2122H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
9/18/2023 8:54:39 PM | Luzon Grid-09/18/2023 20:54: San Lorenzo 60 tripped with 123MW load at 2050H. The lowest frequency recorded is 59.621Hz. (Unplanned Outage) [WEBSMS] | CLUZ
9/18/2023 8:48:20 PM | Luzon Grid-09/18/2023 20:48: San Lorenzo 60 change over from gas to oil at 2046H (Unplanned Outage) [WEBSMS] | CLUZ
9/18/2023 8:17:18 PM | Mindanao Grid-09/18/2023 20:20: SPGI (BIOMASS) with 5.92MW gross generation tripped at 1930H. Indication: Neutral Displacement Protection Alarm. Unplanned Outage. [WEBSMS] | CMIN
9/18/2023 7:54:37 PM | Mindanao Grid-09/18/2023 19:57: TM2 Unit #2 shutdown at 1944H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
9/18/2023 6:44:29 PM | Luzon Grid-09/18/2023 18:44: SLPGC 1 online at 1839H (Unplanned Outage) [WEBSMS] | CLUZ
9/18/2023 5:59:11 PM | Mindanao Grid-09/18/2023 18:02: WMPC DG05 with 6.6MW gross generation tripped at 1746H. Indication: Turbo Charger A-Bank Turbine Side Alarm. Unplanned Outage. [WEBSMS] | CMIN
9/18/2023 5:57:53 PM | [NSO Update] Mindanao Grid-09/18/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2884MW, PK=2083MW, RR=60MW, NetOpMargin: EVE=741 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @95MW, AG4 @82MW, AG5 @34MW, AG6 @149MW, AG7 @31MW, PG4 @120MW [WEBSMS] | CMIN
9/18/2023 5:55:42 PM | Mindanao Grid-09/18/2023 17:58: TM2 Unit #2 online at 1738H. MO dispatched. Follow RTD. [WEBSMS] | CMIN
9/18/2023 5:53:11 PM | [NSO Update] Luzon Grid-09/18/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13895MW, PK=10591MW, RR=415MW, NetOpMargin: EVE=2889 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @150MW, CLC2 @174MW, MSLC1 @290MW, MSLC2 @280MW, MSLC3 @310MW, SCPC 3 @110MW [WEBSMS] | CLUZ
9/18/2023 4:25:19 PM | Mindanao Grid-09/18/2023 16:28: WMPC DG02 shutdown at 1614H - End of RPS System Voltage Requirement [WEBSMS] | CMIN
9/18/2023 2:47:42 PM | [NSO Update] Mindanao Grid-09/18/2023 14:50: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1329H with power going to Visayas [WEBSMS] | CMIN
9/18/2023 2:44:44 PM | [NSO Update] Visayas Grid-09/18/2023 14:44: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1329H with power going to Visayas. [WEBSMS] | CVIS
9/18/2023 2:12:35 PM | Mindanao Grid-09/18/2023 14:15: LAMSAN online at 1254H. (Unplanned outage). [WEBSMS] | CMIN
9/18/2023 2:11:51 PM | Mindanao Grid-09/18/2023 14:14: LAMSAN tripped with 13.5MW load at 1241H. (Unplanned outage). Frequency dipped at 59.9Hz. Affected by SKU-Simuay 69 kV feeder tripping. [WEBSMS] | CMIN
9/18/2023 1:27:27 PM | Mindanao Grid-09/18/2023 13:30: Mt. Apo 3 cut-in at 1319H. (Unplanned Outage). (Note: Indication of tripping: Turbine lockout relay 86T) [WEBSMS] | CMIN
9/18/2023 1:27:26 PM | [NSO Update] Mindanao Grid-09/18/2023 13:30: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2917MW, PK=2107MW, RR=60MW, NetOpMargin: PM=750, EVE=802 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @95MW, AG4 @82MW, AG5 @34MW, AG6 @149MW, AG7 @31MW, PG4 @120MW [WEBSMS] | CMIN
9/18/2023 1:24:44 PM | [NSO Update] Visayas Grid-09/18/2023 13:24: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1319H from reverse power direction [WEBSMS] | CVIS
9/18/2023 1:23:29 PM | [NSO Update] Mindanao Grid-09/18/2023 13:26: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1319H from reverse power direction. [WEBSMS] | CMIN
9/18/2023 1:09:56 PM | [NSO Update] Mindanao Grid-09/18/2023 13:12: SO Initiated Market Intervention has been lifted today 18 September 2023 at 1305H for Luzon, Visayas and Mindanao. Market will resume starting interval 1310H. [WEBSMS] | CMIN
9/18/2023 1:09:28 PM | [NSO Update] Visayas Grid-09/18/2023 13:09: SO Initiated Market Intervention has been lifted today 18 September 2023 at 1305H for Luzon, Visayas and Mindanao. Market will resume starting interval 1310H. [WEBSMS] | CVIS
9/18/2023 1:08:56 PM | [NSO Update] Luzon Grid-09/18/2023 13:09: SO Initiated Market Intervention has been lifted today 18 September 2023 at 1305H for Luzon, Visayas and Mindanao. Market will resume starting interval 1310H. [WEBSMS] | CLUZ
9/18/2023 1:07:12 PM | [NSO Update] Luzon Grid-09/18/2023 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14584MW, PK=11323MW, RR=452MW, NetOpMargin: PM=2809, EVE=3139 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 1 @ 220MW, Calaca 2 @ 174MW, Masinloc 1 @ 290MW, Masinloc 2 @ 280MW, Masinloc 3 @ 310MW, SCPC 3 @ 110MW, Ilijan A @ 485MW, Ilijan B @ 255MW [WEBSMS] | CLUZ
9/18/2023 12:53:34 PM | [NSO Update] Mindanao Grid-09/18/2023 12:56: SO Initiated Market Intervention is issued today 18 September 2023 for Luzon, Visayas and Mindanao starting interval 1255H due to unimplementable RTD schedule. [WEBSMS] | CMIN
9/18/2023 12:53:04 PM | [NSO Update] Visayas Grid-09/18/2023 12:52: SO Initiated Market Intervention is issued today 18 September 2023 for Luzon, Visayas and Mindanao starting interval 1255H due to unimplementable RTD schedule. [WEBSMS] | CVIS
9/18/2023 12:52:57 PM | [NSO Update] Luzon Grid-09/18/2023 12:53: SO Initiated Market Intervention is issued today 18 September 2023 for Luzon, Visayas and Mindanao starting interval 1255H due to unimplementable RTD schedule. [WEBSMS] | CLUZ
9/18/2023 11:52:25 AM | Mindanao Grid-09/18/2023 11:55: Mt. Apo 3 tripped with load of 3.2MW at 1126H. (Unplanned Outage). Frequency rise: 60.15Hz. Indication: for verification. [WEBSMS] | CMIN
9/18/2023 11:09:31 AM | Mindanao Grid-09/18/2023 11:12: WMPC DG02 cut-in at 1052H. RPS - System Voltage Requirement [WEBSMS] | CMIN
9/18/2023 10:45:23 AM | [NSO Update] Visayas Grid-09/18/2023 10:45: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1042H with power going to Mindanao. [WEBSMS] | CVIS
9/18/2023 10:44:02 AM | [NSO Update] Mindanao Grid-09/18/2023 10:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1042H with power going to Mindanao. [WEBSMS] | CMIN
9/18/2023 10:28:28 AM | [NSO Update] Visayas Grid-09/18/2023 10:28: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1026H from forward power direction. [WEBSMS] | CVIS
9/18/2023 10:28:00 AM | [NSO Update] Mindanao Grid-09/18/2023 10:30: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1026H from forward power direction. [WEBSMS] | CMIN
9/18/2023 10:22:51 AM | Visayas Grid-09/18/2023 10:22: 138KV Colon-KSPC line 2 de-energized at 1017H per request from KSPC plant. (Planned Outage). [WEBSMS] | CVIS
9/18/2023 9:46:26 AM | Mindanao Grid-09/18/2023 09:49: WMPC DG10 cut-in at 0854H. RPS - System Voltage Requirement [WEBSMS] | CMIN
9/18/2023 9:08:35 AM | Luzon Grid-09/18/2023 09:08: San Jose-Malolos 230kV line and Malolos 150MVA T01 restored at 0908H (Planned Outage) [WEBSMS] | CLUZ
9/18/2023 9:03:08 AM | Visayas Grid-09/18/2023 09:02: Mandaue SS TR1 100MVA de-energized at 0845H schedule activity. (Planned Outage.) [WEBSMS] | CVIS
9/18/2023 8:53:43 AM | Mindanao Grid-09/18/2023 08:56: STEAG Unit 2 emergency shutdown at 0835H due to tube leak. (Unplanned Outage). Frequency dip at 59.67Hz (load drop of 12MW + backfeed power of 7MW) [WEBSMS] | CMIN
9/18/2023 8:06:29 AM | Mindanao Grid-09/18/2023 08:09: Pulangi 4 HEP Unit 3 shutdown at 0802H. (PMS, Non-GOMP) [WEBSMS] | CMIN
9/18/2023 7:51:01 AM | Mindanao Grid-09/18/2023 07:53: STEAG requested for emergency shutdown of STEAG Unit 2 due to tube leak. Gradual unloading commenced at 0743H. [WEBSMS] | CMIN
9/18/2023 7:34:31 AM | Luzon Grid-09/18/2023 07:34: Quezon(Balintawak)-Dona Imelda(Araneta) 230kV Line restored at 0733H (Planned Outage) [WEBSMS] | CLUZ
9/18/2023 5:57:44 AM | [NSO Update] Luzon Grid-09/18/2023 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14795MW, PK=10643MW, RR=424MW, NetOpMargin: AM=3728, PM=2558, EVE=2964 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 230MW, Calaca 2 @ 174MW, Masinloc 1 @ 290MW, Masinloc 2 @ 280MW, Masinloc 3 @ 310MW, SCPC 3 @ 110MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
9/18/2023 5:55:07 AM | [NSO Update] Mindanao Grid-09/18/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3037MW, PK=2074MW, RR=60MW, NetOpMargin: AM=902, PM=812, EVE=793 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @95MW, AG4 @82MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @120MW [WEBSMS] | CMIN
9/18/2023 5:10:21 AM | Mindanao Grid-09/18/2023 05:13: Jasaan-Butuan 138kv Line restored at 0506H. (Planned outage) [WEBSMS] | CMIN
9/18/2023 3:57:28 AM | [NSO Update] Mindanao Grid-09/18/2023 04:00: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CMIN
9/18/2023 3:57:26 AM | [NSO Update] Visayas Grid-09/18/2023 03:57: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CVIS
9/18/2023 3:57:22 AM | [NSO Update] Luzon Grid-09/18/2023 03:57: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CLUZ
9/18/2023 2:50:24 AM | Mindanao Grid-09/18/2023 02:53: Lake Mainit HEPP (AGC) online at 0236H. Unplanned Outage. [WEBSMS] | CMIN
9/18/2023 2:33:21 AM | Luzon Grid-09/18/2023 02:33: Las Pinas (Zapote) 300MVA T03 restored at 0232H (Planned Outage) [WEBSMS] | CLUZ
9/18/2023 2:32:25 AM | Mindanao Grid-09/18/2023 02:35: Lake Mainit HEPP (AGC) with 10.5MW gross generation tripped at 0216H. Indication:50BF. Frequency Dip=59.8Hz. Unplanned Outage. [WEBSMS] | CMIN
9/17/2023 11:14:59 PM | Luzon Grid-09/17/2023 23:15: Ilijan ST2 online at 2313H (Unplanned Outage) [WEBSMS] | CLUZ
9/17/2023 10:34:19 PM | Mindanao Grid-09/17/2023 22:37: FDC Unit #3 shutdown at 2215H for scheduled PMS. (Planned Outage) [WEBSMS] | CMIN
9/17/2023 10:18:21 PM | Luzon Grid-09/17/2023 22:18: Calaca-SLPGC 230kV Line 1 restored at 2218H (Unplanned Outage) [WEBSMS] | CLUZ
9/17/2023 10:16:06 PM | Luzon Grid-09/17/2023 22:16: Las Pinas (Zapote) SS 300MVA T03 de-energized at 2215H (Planned Outage) [WEBSMS] | CLUZ
9/17/2023 9:47:33 PM | Luzon Grid-09/17/2023 21:47: Calaca-SLPGC 230kV Line 2 restored at 2146H (Unplanned Outage) [WEBSMS] | CLUZ
9/17/2023 9:46:28 PM | Mindanao Grid-09/17/2023 21:49: Butuan SS 138kV Bus 2 restored/energized 2143H. Planned outage [WEBSMS] | CMIN
9/17/2023 9:41:24 PM | Visayas Grid-09/17/2023 21:41: Naga-CD1 TR1 138 KV line energized at 2122H. (Planned Outage) [WEBSMS] | CVIS
9/17/2023 9:40:30 PM | Visayas Grid-09/17/2023 21:40: Naga-CD1 TR2 138 KV line de-energized/energized at 2116H/2138H, facilitate reclosing of CD1 TR 1. (Unplanned Outage) [WEBSMS] | CVIS
9/17/2023 9:17:44 PM | Luzon Grid-09/17/2023 21:17: Correction: Calaca-SLPGC 230kV Line 2 tripped via SLPGC side at 2055H (Unplanned Outage) [WEBSMS] | CLUZ
9/17/2023 9:15:53 PM | Luzon Grid-09/17/2023 21:16: Calaca-SLPGC 230kV Line 2 tripped via SLPGC side at 2055H (Planned Outage) [WEBSMS] | CLUZ
9/17/2023 9:10:31 PM | Luzon Grid-09/17/2023 21:10: Quezon(Balintawak)-Dona Imelda(Araneta) 230kV Line de-energized at 2105H (Planned Outage) [WEBSMS] | CLUZ
9/17/2023 9:08:38 PM | Luzon Grid-09/17/2023 21:08: Calaca-SLPGC 230kV Line 1 and SLPGC Unit 1 (86MW) tripped at 2055H. (Unplanned Outage) [WEBSMS] | CLUZ
9/17/2023 8:03:07 PM | Luzon Grid-09/17/2023 20:03: Taytay (Dolores) 300MVA T01 restored at 2003H (Planned Outage) [WEBSMS] | CLUZ
9/17/2023 7:53:53 PM | Luzon Grid-09/17/2023 19:54: Ilijan GT2-2 online at 1952H (Unplanned Outage) [WEBSMS] | CLUZ
9/17/2023 7:29:12 PM | Luzon Grid-09/17/2023 19:29: Binan-Calamba 230kV Line 2 auto-tripped/auto-reclosed at 1926H (Unplanned Outage) [WEBSMS] | CLUZ
9/17/2023 7:09:53 PM | Visayas Grid-09/17/2023 19:09: Naga-CDI TR2 138 KV Line energized at 1908H. (Unplanned Outage) [WEBSMS] | CVIS
9/17/2023 6:51:59 PM | Visayas Grid-09/17/2023 18:51: Naga-CDI TR2 tripped at 1846H, upon closing of TR1 per TPVI request. (No generation involved) [WEBSMS] | CVIS
9/17/2023 6:35:51 PM | Luzon Grid-09/17/2023 18:36: Ambuklao-Bayombong 230kV Line 1 restored at 1835H (Planned Outage) [WEBSMS] | CLUZ
9/17/2023 6:31:34 PM | Luzon Grid-09/17/2023 18:31: Dasmarinas - Las Pinas 230kV Line 1 autotripped/autoreclosed at 1826H (Unplanned Outage) [WEBSMS] | CLUZ
9/17/2023 6:06:06 PM | Mindanao Grid-09/17/2023 18:09: Butuan SS 138kV Bus 2 de-energized 1802H. Planned outage. [WEBSMS] | CMIN
9/17/2023 5:58:41 PM | [NSO Update] Luzon Grid-09/17/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13799MW, PK=9953MW, RR=314MW, NetOpMargin: EVE=3532 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 290MW, Masinloc 2 @ 280MW, Masinloc 3 @ 310MW, SCPC 3 @ 110MW, SLPGC 1 @ 80MW [WEBSMS] | CLUZ
9/17/2023 5:56:52 PM | [NSO Update] Mindanao Grid-09/17/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3188MW, PK=1886MW, RR=58MW, NetOpMargin: EVE=1244 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @95MW, AG4 @98MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @180MW [WEBSMS] | CMIN
9/17/2023 5:16:45 PM | Visayas Grid-09/17/2023 17:16: THVI U2 cut in at 1715H. [WEBSMS] | CVIS
9/17/2023 4:20:52 PM | Mindanao Grid-09/17/2023 16:23: Corrected: Agusan Lake Mainit Hydro (AGC) with 10.5MW gross generation tripped at 1213H. Indication: 50BF. Frequency dip=60.1Hz. (Unplanned Outage) [WEBSMS] | CMIN
9/17/2023 4:12:19 PM | [NSO Update] Mindanao Grid-09/17/2023 16:15: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1610H for Luzon, Visayas and Mindanao. Market will resume starting interval 1615H. [WEBSMS] | CMIN
9/17/2023 4:12:08 PM | [NSO Update] Visayas Grid-09/17/2023 16:11: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1610H for Luzon, Visayas and Mindanao. Market will resume starting interval 1615H. [WEBSMS] | CVIS
9/17/2023 4:11:54 PM | [NSO Update] Luzon Grid-09/17/2023 16:12: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1610H for Luzon, Visayas and Mindanao. Market will resume starting interval 1615H. [WEBSMS] | CLUZ
9/17/2023 3:57:57 PM | [NSO Update] Mindanao Grid-09/17/2023 16:00: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao starting interval 1600H due to unimplementable RTD schedule. [WEBSMS] | CMIN
9/17/2023 3:56:54 PM | [NSO Update] Visayas Grid-09/17/2023 15:56: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao starting interval 1600H due to unimplementable RTD schedule. [WEBSMS] | CVIS
9/17/2023 3:56:09 PM | [NSO Update] Luzon Grid-09/17/2023 15:56: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao starting interval 1600H due to unimplementable RTD schedule. [WEBSMS] | CLUZ
9/17/2023 3:28:08 PM | [NSO Update] Mindanao Grid-09/17/2023 15:31: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1525H for Luzon, Visayas and Mindanao. Market will resume starting interval 1530H. [WEBSMS] | CMIN
9/17/2023 3:27:31 PM | [NSO Update] Visayas Grid-09/17/2023 15:27: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1525H for Luzon, Visayas and Mindanao. Market will resume starting interval 1530H. [WEBSMS] | CVIS
9/17/2023 3:26:36 PM | [NSO Update] Luzon Grid-09/17/2023 15:26: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1525H for Luzon, Visayas and Mindanao. Market will resume starting interval 1530H. [WEBSMS] | CLUZ
9/17/2023 2:52:32 PM | [NSO Update] Mindanao Grid-09/17/2023 14:55: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao starting interval 1450H due to unimplementable RTD schedule. [WEBSMS] | CMIN
9/17/2023 2:52:08 PM | [NSO Update] Visayas Grid-09/17/2023 14:51: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao starting interval 1450H due to unimplementable RTD schedule. [WEBSMS] | CVIS
9/17/2023 2:50:03 PM | [NSO Update] Luzon Grid-09/17/2023 14:50: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao starting interval 1450H due to unimplementable RTD schedule. [WEBSMS] | CLUZ
9/17/2023 2:33:51 PM | [NSO Update] Mindanao Grid-09/17/2023 14:36: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1430H for Luzon, Visayas and Mindanao. Market will resume starting interval 1435H. [WEBSMS] | CMIN
9/17/2023 2:33:12 PM | [NSO Update] Visayas Grid-09/17/2023 14:32: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1430H for Luzon, Visayas and Mindanao. Market will resume starting interval 1435H. [WEBSMS] | CVIS
9/17/2023 2:32:44 PM | [NSO Update] Luzon Grid-09/17/2023 14:32: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1430H for Luzon, Visayas and Mindanao. Market will resume starting interval 1435H. [WEBSMS] | CLUZ
9/17/2023 2:25:15 PM | Mindanao Grid-09/17/2023 14:28: STEAG Unit #1 online at 1413H. (Unplanned Outage). [WEBSMS] | CMIN
9/17/2023 2:01:00 PM | [NSO Update] Luzon Grid-09/17/2023 14:01: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao starting interval 1400H due to unimplementable RTD schedule. [WEBSMS] | CLUZ
9/17/2023 2:00:40 PM | [NSO Update] Visayas Grid-09/17/2023 14:00: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao starting interval 1400H due to unimplementable RTD schedule. [WEBSMS] | CVIS
9/17/2023 2:00:30 PM | [NSO Update] Mindanao Grid-09/17/2023 14:03: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao starting interval 1400H due to unimplementable RTD schedule. [WEBSMS] | CMIN
9/17/2023 1:41:48 PM | [NSO Update] Mindanao Grid-09/17/2023 13:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3108MW, PK=1751MW, RR=60MW, NetOpMargin: PM=1297, EVE=1124 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @95MW, AG4 @98MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @160MW [WEBSMS] | CMIN
9/17/2023 1:23:15 PM | Mindanao Grid-09/17/2023 13:26: Pulangi 4 HEP Unit 2 cut-in at 1252H. (Unplanned Outage) [WEBSMS] | CMIN
9/17/2023 1:19:00 PM | [NSO Update] Luzon Grid-09/17/2023 13:19: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14365MW, PK=9472MW, RR=340MW, NetOpMargin: PM=4553, EVE=3517 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, GMEC 2 @240MW, MSLC1 @290MW, MSLC2 @250MW, MSLC3 @310MW, SCPC 3 @110MW, SLPGC 1 @80MW, ILIJAN A @ 570MW [WEBSMS] | CLUZ
9/17/2023 12:56:14 PM | [NSO Update] Mindanao Grid-09/17/2023 12:59: SO initiated Market Intervention is issued and lifted today 17 September 2023 for Luzon, Visayas and Mindanao for interval 1230H due to unimplementable RTD schedule. Market will resume at starting interval 1235H. [WEBSMS] | CMIN
9/17/2023 12:55:23 PM | [NSO Update] Visayas Grid-09/17/2023 12:55: SO initiated Market Intervention is issued and lifted today 17 September 2023 for Luzon, Visayas and Mindanao for interval 1230H due to unimplementable RTD schedule. Market will resume at starting interval 1235H. [WEBSMS] | CVIS
9/17/2023 12:52:47 PM | [NSO Update] Luzon Grid-09/17/2023 12:52: SO Initiated Market Intervention is issued today and lifted 17 September 2023 for Luzon, Visayas and Mindanao for interval 1230H due to unimplementable RTD schedule. Market will resume at starting interval 1235H. [WEBSMS] | CLUZ
9/17/2023 12:36:28 PM | Mindanao Grid-09/17/2023 12:39: Agusan Lake Mainit Hydro cut-in at 1229H. (Unplanned Outage) [WEBSMS] | CMIN
9/17/2023 12:20:39 PM | [NSO Update] Mindanao Grid-09/17/2023 12:23: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1215H for Luzon, Visayas and Mindanao. Market will resume starting interval 1220H. [WEBSMS] | CMIN
9/17/2023 12:20:23 PM | [NSO Update] Visayas Grid-09/17/2023 12:20: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1215H for Luzon, Visayas and Mindanao. Market will resume starting interval 1220H. [WEBSMS] | CVIS
9/17/2023 12:19:57 PM | [NSO Update] Luzon Grid-09/17/2023 12:20: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1215H for Luzon, Visayas and Mindanao. Market will resume starting interval 1220H. [WEBSMS] | CLUZ
9/17/2023 12:18:59 PM | [NSO Update] Mindanao Grid-09/17/2023 12:21: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao for interval 1200H due to unimplementable RTD. [WEBSMS] | CMIN
9/17/2023 12:18:19 PM | [NSO Update] Visayas Grid-09/17/2023 12:18: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao for interval 1200H due to unimplementable RTD. [WEBSMS] | CVIS
9/17/2023 12:18:00 PM | Mindanao Grid-09/17/2023 12:20: Agusan Lake Mainit Hydro tripped with 10.5MW load at 1213H. (Unplanned Outage) [WEBSMS] | CMIN
9/17/2023 12:17:53 PM | [NSO Update] Luzon Grid-09/17/2023 12:18: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao for interval 1200H due to unimplementable RTD. [WEBSMS] | CLUZ
9/17/2023 11:39:54 AM | [NSO Update] Mindanao Grid-09/17/2023 11:42: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1130H for Luzon, Visayas and Mindanao. Market will resume starting interval 1135H. [WEBSMS] | CMIN
9/17/2023 11:39:46 AM | [NSO Update] Visayas Grid-09/17/2023 11:39: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1130H for Luzon, Visayas and Mindanao. Market will resume starting interval 1135H. [WEBSMS] | CVIS
9/17/2023 11:38:49 AM | [NSO Update] Luzon Grid-09/17/2023 11:38: SO Initiated Market Intervention has been lifted today 17 September 2023 at 1130H for Luzon, Visayas and Mindanao. Market will resume starting interval 1135H. [WEBSMS] | CLUZ
9/17/2023 11:34:45 AM | Luzon Grid-09/17/2023 11:34: Taytay (Dolores) 300MVA T01 de-energized at 1132H (Planned Outage) [WEBSMS] | CLUZ
9/17/2023 11:19:47 AM | [NSO Update] Mindanao Grid-09/17/2023 11:22: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao for interval 1115H due to unimplementable RTD. [WEBSMS] | CMIN
9/17/2023 11:19:42 AM | [NSO Update] Visayas Grid-09/17/2023 11:19: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao for interval 1115H due to unimplementable RTD. [WEBSMS] | CVIS
9/17/2023 11:19:37 AM | [NSO Update] Luzon Grid-09/17/2023 11:19: SO Initiated Market Intervention is issued today 17 September 2023 for Luzon, Visayas and Mindanao for interval 1115H due to unimplementable RTD. [WEBSMS] | CLUZ
9/17/2023 11:15:36 AM | Luzon Grid-09/17/2023 11:15: Dona Imelda (Araneta)-Sta Mesa 115kV line 2 restored at 1113H (Planned Outage) [WEBSMS] | CLUZ
9/17/2023 10:09:41 AM | Mindanao Grid-09/17/2023 10:12: Pulangi 4 HEP Unit 2 emergency shutdown at 1003H to facilitate cooling water backflow operation. (Unplanned Outage) [WEBSMS] | CMIN
9/17/2023 9:17:21 AM | Mindanao Grid-09/17/2023 09:20: Talomo A (TL1) Unit 1 and Unit 2 cut-in at 0739H and 0842H, respectively. (Unplanned Outage) [WEBSMS] | CMIN
9/17/2023 9:14:17 AM | Mindanao Grid-09/17/2023 09:17: Talomo A (TL1) Unit 1 and Unit 2 cut-in at 0739H and 0842H, respectively. [WEBSMS] | CMIN
9/17/2023 9:11:36 AM | Mindanao Grid-09/17/2023 09:14: Agusan Lake Mainit Hydro cut-in at 0856H. (Unplanned Outage) [WEBSMS] | CMIN
9/17/2023 8:48:04 AM | Mindanao Grid-09/17/2023 08:51: Agusan Lake Mainit Hydro tripped with 10.6MW load at 0841H. (Unplanned Outage) [WEBSMS] | CMIN
9/17/2023 8:24:37 AM | Visayas Grid-09/17/2023 08:24: Daanbantayan SS 69KV Lanao fdr restored at 0821H, customer owned line (CEBECO 2) [WEBSMS] | CVIS
9/17/2023 8:14:00 AM | Visayas Grid-09/17/2023 08:13: Daanbantayan SS 69KV Lanao fdr tripped at 0724H, load 19.07MW, customer owned line (CEBECO 2). [WEBSMS] | CVIS
9/17/2023 6:38:14 AM | Luzon Grid-09/17/2023 06:38: Ambuklao-Bayombong 230kV Line 1 de-energized at 0636H (Planned Outage) [WEBSMS] | CLUZ
9/17/2023 6:10:37 AM | [NSO Update] Mindanao Grid-09/17/2023 06:13: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3080MW, PK=1680MW, RR=60MW, NetOpMargin: AM=1339, PM=1279, EVE=1132 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @95MW, AG4 @98MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @180MW [WEBSMS] | CMIN
9/17/2023 6:05:56 AM | Mindanao Grid-09/17/2023 06:08: Jasaan-Butuan 138kV line de-energized 0602H. Planned outage [WEBSMS] | CMIN
9/17/2023 6:05:41 AM | [NSO Update] Luzon Grid-09/17/2023 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14665MW, PK=9068MW, RR=334MW, NetOpMargin: AM=5263, PM=4476, EVE=3502 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, GMEC 2 @160MW, MSLC1 @290MW, MSLC2 @280MW, MSLC3 @310MW, SCPC 3 @110MW, SLPGC 1 @80MW [WEBSMS] | CLUZ
9/17/2023 6:00:32 AM | Luzon Grid-09/17/2023 06:00: San Jose 300MVA T01 was restored at 0558H (Planned Outage). San Jose new PCB 6-04CB04SJO was energized at the same time. [WEBSMS] | CLUZ
9/17/2023 4:38:03 AM | Luzon Grid-09/17/2023 04:38: San Jose 83MVA T01(Customer owned) restored at 0437H (Planned Outage) [WEBSMS] | CLUZ
9/17/2023 4:11:55 AM | [NSO Update] Mindanao Grid-09/17/2023 04:14: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CMIN
9/17/2023 4:11:40 AM | [NSO Update] Visayas Grid-09/17/2023 04:11: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CVIS
9/17/2023 4:11:26 AM | [NSO Update] Luzon Grid-09/17/2023 04:11: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CLUZ
9/17/2023 1:32:48 AM | Luzon Grid-09/17/2023 01:32: Malolos 150MVA T01 - de-energized at 0126H (Planned Outage) [WEBSMS] | CLUZ
9/17/2023 1:19:55 AM | Luzon Grid-09/17/2023 01:20: San Jose-Malolos 230kV line - de-energized at 0118H (Planned Outage) [WEBSMS] | CLUZ
9/17/2023 12:53:37 AM | Luzon Grid-09/17/2023 00:53: Malolos 150MVA T02 - restored at 0046H (Planned Outage) [WEBSMS] | CLUZ
9/17/2023 12:43:15 AM | Luzon Grid-09/17/2023 00:43: Dona Imelda(Araneta)-Sta Mesa 115kV line 2 - de-energized at 0041H (Planned Outage). [WEBSMS] | CLUZ
9/17/2023 12:32:49 AM | Mindanao Grid-09/17/2023 00:35: TSI Unit #1 shutdown at 0025H. Planned Outage [WEBSMS] | CMIN
9/17/2023 12:25:37 AM | Luzon Grid-09/17/2023 00:25: San Jose 83MVA T01(Customer owned) -de-energized at 0021H (Planned Outage) [WEBSMS] | CLUZ
9/17/2023 12:23:51 AM | Luzon Grid-09/17/2023 00:24: Malolos 150MVA T02 - de-energized at 0021H (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 11:37:34 PM | Visayas Grid-09/16/2023 23:37: Colon-Magdugo 138 KV Line 3 energized at 2334H. (Planned Outage) [WEBSMS] | CVIS
9/16/2023 10:46:14 PM | Luzon Grid-09/16/2023 22:46: San Jose 300MVA T01 - de-energized at 2243H (Planned Outage). [WEBSMS] | CLUZ
9/16/2023 10:14:10 PM | Visayas Grid-09/16/2023 22:13: Naga-CD1 transformer 2 138 KV Line energized at 2205H, per TPVI request. (Unplanned Outage) [WEBSMS] | CVIS
9/16/2023 9:18:16 PM | Luzon Grid-09/16/2023 21:18: Muntinlupa 300MVA T04 and Muntinlupa-Gardner 115kV line 2 were restored at 2115H (Planned Outage). [WEBSMS] | CLUZ
9/16/2023 9:15:28 PM | Visayas Grid-09/16/2023 21:15: Naga-CD1 transformer 2 Line de-energized at 2105H, CD1 personnel request due to flooded sump pit. [WEBSMS] | CVIS
9/16/2023 9:11:28 PM | Visayas Grid-09/16/2023 21:11: Colon-Dumanjug 138 KV line 2 energized at 2111H. [WEBSMS] | CVIS
9/16/2023 8:33:44 PM | Visayas Grid-09/16/2023 20:33: Naga-CD1TR1 138 KV Line tripped at 2014H. [WEBSMS] | CVIS
9/16/2023 8:18:27 PM | Visayas Grid-09/16/2023 20:18: Colon-Dumanjug 138 KV line 2 tripped at 2014H, under assessment. [WEBSMS] | CVIS
9/16/2023 8:17:46 PM | Luzon Grid-09/16/2023 20:17: Bacnotan-CIP II 69kV line - restored at 2017H (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 6:51:27 PM | Luzon Grid-09/16/2023 18:51: San Jose 115kV Bus 1 - energized at 1850H (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 6:04:32 PM | [NSO Update] Mindanao Grid-09/16/2023 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3197MW, PK=2049MW, RR=58MW, NetOpMargin: EVE=1090 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @90MW, AG4 @103MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @160MW [WEBSMS] | CMIN
9/16/2023 5:59:48 PM | Luzon Grid-09/16/2023 17:59: For info: Commissioning of Laoag - Marcos 69kV Line New Main Protection completed at 1757H. [WEBSMS] | CLUZ
9/16/2023 5:59:34 PM | [NSO Update] Luzon Grid-09/16/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13776MW, PK=10141MW, RR=314MW, NetOpMargin: EVE=3321 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @220MW, CLC2 @174MW, MSLC1 @290MW, MSLC2 @280MW, MSLC3 @310MW, SCPC 3 @110MW, SLPGC 1 @75MW, SLPGC 2 @60MW, ILIJAN A @570MW [WEBSMS] | CLUZ
9/16/2023 5:48:54 PM | Luzon Grid-09/16/2023 17:49: Laoag - Marcos 69kV line restored at 1747H. (On-going commissioning) [WEBSMS] | CLUZ
9/16/2023 5:36:29 PM | Luzon Grid-09/16/2023 17:36: Bauang-Bacnotan and Bacnotan-San Esteban 230kV Lines restored at 1734H and 1735H respectively. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 5:34:07 PM | Luzon Grid-09/16/2023 17:34: Bauang-La Trinidad 230kV line 2 looped at Bauang side at 1733H. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 5:28:45 PM | Luzon Grid-09/16/2023 17:28: Binga - La Trinidad 230kV Line 1 restored at 1728H. (Unplanned Outage) [WEBSMS] | CLUZ
9/16/2023 5:01:02 PM | Luzon Grid-09/16/2023 17:01: Hermosa-BCCPP 230kV Line 1 restored at 1659H. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 5:00:28 PM | Luzon Grid-09/16/2023 17:00: Binga - La Trinidad 230kV Line 1 tripped at 1655H. (Unplanned Outage) [WEBSMS] | CLUZ
9/16/2023 4:23:50 PM | Visayas Grid-09/16/2023 16:23: Daanlungsod-Calongcalong 138kV Line 1 energized at 1622H. (Planned Outage) [WEBSMS] | CVIS
9/16/2023 4:06:44 PM | Luzon Grid-09/16/2023 16:06: Binga-Ambuklao 230kV Line 2 restored at 1606H. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 3:17:28 PM | Visayas Grid-09/16/2023 15:17: Dumanjug 138kV Bus 1 energized at 1514H. (Planned Outage) [WEBSMS] | CVIS
9/16/2023 3:17:03 PM | Mindanao Grid-09/16/2023 15:19: WMPC DG09 shutdown at 1513H - End of RPS System Voltage Requirement [WEBSMS] | CMIN
9/16/2023 2:22:32 PM | Mindanao Grid-09/16/2023 14:25: STEAG U2 online at 1412H. (Unplanned Outage) [WEBSMS] | CMIN
9/16/2023 2:20:23 PM | Luzon Grid-09/16/2023 14:20: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1419H. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 12:42:15 PM | [NSO Update] Mindanao Grid-09/16/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3128MW, PK=1985MW, RR=60MW, NetOpMargin: PM=1083, EVE=1060 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @90MW, AG4 @103MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @148MW [WEBSMS] | CMIN
9/16/2023 12:39:46 PM | [NSO Update] Luzon Grid-09/16/2023 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14517MW, PK=10692MW, RR=306MW, NetOpMargin: PM=3518, EVE=3305 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CLC1 @220MW, CLC2 @174MW, MSLC1 @290MW, MSLC2 @280MW, MSLC3 @310MW, SCPC 3 @110MW, SLPGC 1 @75MW, SLPGC 2 @60MW, Ilijan A @570MW [WEBSMS] | CLUZ
9/16/2023 11:09:59 AM | Luzon Grid-09/16/2023 11:10: San Juan (Kalayaan)-Lumban 230kV Line 1 restored at 1109H. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 9:57:16 AM | Mindanao Grid-09/16/2023 10:00: WMPC DG09 online at 0951H - RPS System Voltage Requirement [WEBSMS] | CMIN
9/16/2023 9:44:00 AM | Visayas Grid-09/16/2023 09:43: Dumanjug 138kV Bus 1 de-energized at 0840H. (Unplanned Outage) [WEBSMS] | CVIS
9/16/2023 9:42:09 AM | Visayas Grid-09/16/2023 09:41: Daanlungsod-Calongcalong 138kV Line 1 de-energized at 0755H. (Planned Outage) [WEBSMS] | CVIS
9/16/2023 9:40:04 AM | Visayas Grid-09/16/2023 09:39: Daanlungsod 138kV Bus 1 de-energized at 0732H. (Planned Outage) [WEBSMS] | CVIS
9/16/2023 9:02:37 AM | Luzon Grid-09/16/2023 09:02: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0901H. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 8:37:30 AM | Luzon Grid-09/16/2023 08:37: Binga-Ambuklao 230kV Line 2 de-energized at 0837H. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 8:08:53 AM | Luzon Grid-09/16/2023 08:09: San Jose SS 115kV Bus 1 de-energized at 0808H. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 8:04:09 AM | Mindanao Grid-09/16/2023 08:07: Bunawan SS 50MVA Power Transformer de-energized 0801H. Planned outage [WEBSMS] | CMIN
9/16/2023 7:46:43 AM | Luzon Grid-09/16/2023 07:46: Muntinlupa(Sucat)-Gardner 115kV Tie Line 2 and Muntinlupa (Sucat) SS 300MVA T04 de-energized at 0745H and 0746H respectively. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 7:35:06 AM | Luzon Grid-09/16/2023 07:35: San Juan (Kalayaan)-Lumban 230kV Line 1 de-energized at 0735H. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 7:25:17 AM | Luzon Grid-09/16/2023 07:25: Hermosa-BCCPP 230kV Line 1 de-energized at 0725H. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 6:45:19 AM | Luzon Grid-09/16/2023 06:43: Bauang-Bacnotan and Bacnotan-San Esteban 230kV Lines de-energized at 0641H. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 6:17:31 AM | Luzon Grid-09/16/2023 06:17: Bacnotan-CIP 2 69kV Line de-energized at 0617H. (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 6:15:08 AM | Luzon Grid-09/16/2023 06:03: Las Pinas (Zapote) - CBP1A & CBP1A-Legaspi 115kV Line restored at 0543H (Planned Outage) [WEBSMS] | CLUZ
9/16/2023 6:10:55 AM | [NSO Update] Mindanao Grid-09/16/2023 06:13: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3133MW, PK=1933MW, RR=60MW, NetOpMargin: AM=1140, PM=1121, EVE=1151 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @90MW, AG4 @103MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @148MW [WEBSMS] | CMIN
9/16/2023 6:10:21 AM | [NSO Update] Visayas Grid-09/16/2023 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2358MW, PK=1890MW, RR=87MW, NetOpMargin: AM=382, PM=300, EVE=233 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 324MW, PGPP1 @ 73.5MW [WEBSMS] | CVIS
9/16/2023 6:03:32 AM | [NSO Update] Luzon Grid-09/16/2023 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14344MW, PK=10277MW, RR=300MW, NetOpMargin: AM=3767, PM=3063, EVE=2771 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC1 @220MW, CLC2 @174MW, MSLC1 @290MW, MSLC2 @270MW, MSLC3 @300MW, QPPL @185MW, SCPC 3 @110MW, SLPGC 1 @60MW, SLPGC 2 @35MW, Ilijan A @570MW [WEBSMS] | CLUZ
9/16/2023 5:26:42 AM | Visayas Grid-09/16/2023 05:26: KSPC U2 cut-out from the system at 0001H for APMS. [WEBSMS] | CVIS
9/16/2023 4:33:30 AM | Luzon Grid-09/16/2023 04:33: QPPL online at 0432H (Unplanned Outage) [WEBSMS] | CLUZ
9/16/2023 4:29:14 AM | [NSO Update] Mindanao Grid-09/16/2023 04:32: Weather Update: Southwest Monsoon affecting the western section of Southern Luzon and Visayas. [WEBSMS] | CMIN
9/16/2023 4:24:37 AM | [NSO Update] Luzon Grid-09/16/2023 04:24: Weather Update: Southwest Monsoon affecting the western section of Southern Luzon and Visayas. [WEBSMS] | CLUZ
9/16/2023 4:22:49 AM | [NSO Update] Visayas Grid-09/16/2023 04:22: Weather Update: Southwest Monsoon affecting the western section of Southern Luzon and Visayas. [WEBSMS] | CVIS
9/15/2023 11:25:26 PM | Visayas Grid-09/15/2023 23:25: Daanbantayan SS 69KV Lanao fdr tripped/energized at 2302H/2317H, load 21.9MW, customer owned line (CEBECO 2). [WEBSMS] | CVIS
9/15/2023 11:24:24 PM | Luzon Grid-09/15/2023 23:24: San Esteban-Laoag 230kV Line 2 auto-tripped and auto-reclosed both side at 2316H (Unplanned Outage) [WEBSMS] | CLUZ
9/15/2023 9:17:35 PM | Mindanao Grid-09/15/2023 21:20: GenSAn SS 138KV Bus 1 restored at 2106H. (Planned Outage) [WEBSMS] | CMIN
9/15/2023 6:12:26 PM | [NSO Update] Mindanao Grid-09/15/2023 18:15: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3120MW, PK=2071MW, RR=60MW, NetOpMargin: EVE=989 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @90MW, AG4 @103MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @160MW [WEBSMS] | CMIN
9/15/2023 6:10:16 PM | [NSO Update] Visayas Grid-09/15/2023 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2425MW, PK=2090MW, RR=86MW, NetOpMargin: EVE=249 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 324MW, PGPP1 @ 75MW [WEBSMS] | CVIS
9/15/2023 6:03:13 PM | [NSO Update] Luzon Grid-09/15/2023 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13378MW, PK=10315MW, RR=408MW, NetOpMargin: EVE=2655 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC1 @230MW, CLC2 @174MW, MSLC1 @280MW, MSLC2 @270MW, MSLC3 @280MW, SCPC 3 @110MW, SLPGC 1 @70MW, SLPGC 2 @60MW [WEBSMS] | CLUZ
9/15/2023 4:22:01 PM | Mindanao Grid-09/15/2023 16:24: Mt. Apo Unit #2 online at 1612H. Unplanned Outage [WEBSMS] | CMIN
9/15/2023 3:58:49 PM | Luzon Grid-09/15/2023 15:58: Bauang-La Trinidad 230kV line 2 -autotripped and autoreclosed at 1545H (Unplanned Outage) [WEBSMS] | CLUZ
9/15/2023 3:46:21 PM | Mindanao Grid-09/15/2023 15:48: Mt. Apo Unit #2 with 30MW gross generation tripped at 1535H, due to Cooling Basin Level Very Low. Frequency Dip=59.5133Hz. Unplanned Outage. [WEBSMS] | CMIN
9/15/2023 2:09:53 PM | Luzon Grid-09/15/2023 14:09: Tayabas-Naga 230kV line 2 - restored at 1407H (Planned Outage) [WEBSMS] | CLUZ
9/15/2023 12:53:18 PM | [NSO Update] Luzon Grid-09/15/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13805MW, PK=11260MW, RR=448MW, NetOpMargin: PM=2097, EVE=2343 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 230MW, Calaca 2 @ 174MW, GMEC 1 @ 240MW, GMEC 2 @ 240MW, Masinloc 1 @ 280MW, Masinloc 2 @ 270MW, Masinloc 3 @ 310MW, SCPC 3 @ 110MW, SLPGC 1 @ 65MW, SLPGC 2 @ 60MW [WEBSMS] | CLUZ
9/15/2023 12:52:18 PM | [NSO Update] Visayas Grid-09/15/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2506MW, PK=2178MW, RR=92MW, NetOpMargin: PM=237, EVE=252 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 20MW, Leyte A @ 318MW, PGPP1 @ 75MW [WEBSMS] | CVIS
9/15/2023 12:51:21 PM | [NSO Update] Mindanao Grid-09/15/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3179MW, PK=2077MW, RR=60MW, NetOpMargin: PM=1042, EVE=1079 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @90MW, AG4 @103MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @168MW [WEBSMS] | CMIN
9/15/2023 11:14:53 AM | Luzon Grid-09/15/2023 11:14: Balsik PCB 9-01CB08BIK - energized at 1114H. (Planned Outage) [WEBSMS] | CLUZ
9/15/2023 11:12:06 AM | Mindanao Grid-09/15/2023 11:14: Agus 4 Unit #1 with 41MW on emergency shutdown at 1100H due to Governor Hunting. Frequency Dip=59.6379Hz. Unplanned Outage. [WEBSMS] | CMIN
9/15/2023 10:24:08 AM | Luzon Grid-09/15/2023 10:24: Ilijan PCB 9-01CB04ILJ - energized at 1022H. (Unplanned Outage) [WEBSMS] | CLUZ
9/15/2023 9:34:52 AM | Mindanao Grid-09/15/2023 09:36: Gen. Santos SS 138KV Bus 1 de-energized at 0908H. (Planned Outage) [WEBSMS] | CMIN
9/15/2023 9:23:04 AM | Mindanao Grid-09/15/2023 09:25: Agus 4 Unit #1 online at 0859H from PMS (GOMP). Planned Outage. [WEBSMS] | CMIN
9/15/2023 9:19:54 AM | Mindanao Grid-09/15/2023 09:21: WMPC DG09 online at 0851H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
9/15/2023 8:38:00 AM | Mindanao Grid-09/15/2023 08:40: Matanano SS 230KV Bus 2 deenergized at 0832H. Planned Outage) [WEBSMS] | CMIN
9/15/2023 8:02:39 AM | Luzon Grid-09/15/2023 08:02: Balsik PCB 9-01CB08BIK - de-energized at 0801H. (Planned Outage) [WEBSMS] | CLUZ
9/15/2023 7:32:09 AM | Luzon Grid-09/15/2023 07:32: Ilijan PCB 9-01CB04ILJ - de-energized at 0731H (Unplanned Outage). [WEBSMS] | CLUZ
9/15/2023 6:38:53 AM | Luzon Grid-09/15/2023 06:38: Tayabas-Naga 230kV line 2 was de-energized at 0637H (Planned Outage). [WEBSMS] | CLUZ
9/15/2023 6:00:33 AM | [NSO Update] Visayas Grid-09/15/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2448MW, PK=2130MW, RR=87MW, NetOpMargin: AM=231, PM=187, EVE=235 Highest Unit O/L: THVI 1 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @324MW, PGPP1 @75MW, TPC-Carmen @20MW [WEBSMS] | CVIS
9/15/2023 5:59:57 AM | [NSO Update] Mindanao Grid-09/15/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3186MW, PK=2095MW, RR=60MW, NetOpMargin: AM=1031, PM=977, EVE=1076 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @90MW, AG4 @103MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @168MW [WEBSMS] | CMIN
9/15/2023 5:50:45 AM | [NSO Update] Luzon Grid-09/15/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14010MW, PK=10965MW, RR=438MW, NetOpMargin: AM=2607, PM=2456, EVE=2685 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @230MW, CLC2 @174MW, MSLC1 @280MW, MSLC2 @270MW, MSLC3 @320MW, SCPC 3 @110MW, SLPGC 1 @65MW, SLPGC 2 @60MW [WEBSMS] | CLUZ
9/15/2023 5:19:59 AM | [NSO Update] Mindanao Grid-09/15/2023 05:22: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 405 km North Northeast of Itbayat, Batanes (24.3 N, 122.8 E). Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
9/15/2023 5:19:39 AM | [NSO Update] Visayas Grid-09/15/2023 05:19: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 405 km North Northeast of Itbayat, Batanes (24.3 N, 122.8 E). Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
9/15/2023 5:19:25 AM | [NSO Update] Luzon Grid-09/15/2023 05:19: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 405 km North Northeast of Itbayat, Batanes (24.3 N, 122.8 E). Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
9/15/2023 4:35:38 AM | Visayas Grid-09/15/2023 04:35: CEDC U-3 cut-in to the system at 0156H initial load 8MW. [WEBSMS] | CVIS
9/15/2023 3:39:17 AM | Luzon Grid-09/15/2023 03:39: Malolos-Hermosa 230kV Line restored at 0336H (Planned Outage) [WEBSMS] | CLUZ
9/15/2023 2:17:35 AM | Luzon Grid-09/15/2023 02:17: Malolos-Hermosa 230kV Line de-energized at 0217H (Planned Outage) [WEBSMS] | CLUZ
9/14/2023 10:34:25 PM | Visayas Grid-09/14/2023 22:34: CEDC U-3 tripped at 2222H with a load of 82.61MW no customer affected, under assessment. [WEBSMS] | CVIS
9/14/2023 9:24:32 PM | Mindanao Grid-09/14/2023 21:26: WMPC DG09 shutdown at 2109H. End of RPS. System Voltage Requirement. [WEBSMS] | CMIN
9/14/2023 8:10:33 PM | Luzon Grid-09/14/2023 20:10: Laoag-Pasuquin Solar 115kV Line restored at 2009H (Planned Outage) [WEBSMS] | CLUZ
9/14/2023 7:34:34 PM | Mindanao Grid-09/14/2023 19:36: San Francisco - Bislig 138kV L restored at 1929H. (Unplanned Outage) [WEBSMS] | CMIN
9/14/2023 6:49:46 PM | Mindanao Grid-09/14/2023 18:51: San Francisco - Bislig 138kV L auto-tripped at 1835H. (Unplanned Outage) [WEBSMS] | CMIN
9/14/2023 5:54:15 PM | [NSO Update] Visayas Grid-09/14/2023 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2475MW, PK=2105MW, RR=85MW, NetOpMargin: EVE=286 Highest Unit O/L: THVI 1 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @324MW, PGPP1 @72.5MW [WEBSMS] | CVIS
9/14/2023 5:53:32 PM | [NSO Update] Mindanao Grid-09/14/2023 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3084MW, PK=2113MW, RR=60MW, NetOpMargin: EVE=910 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @90MW, AG4 @103MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @157.5MW [WEBSMS] | CMIN
9/14/2023 5:49:54 PM | [NSO Update] Luzon Grid-09/14/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13429MW, PK=10542MW, RR=421MW, NetOpMargin: EVE=2466 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @174MW, MSLC1 @280MW, MSLC2 @270MW, MSLC3 @310MW, SCPC 3 @110MW, SLPGC 1 @95MW, SLPGC 2 @60MW [WEBSMS] | CLUZ
9/14/2023 5:03:03 PM | Mindanao Grid-09/14/2023 17:05: General Santos SS 138KV Bus 2 restored at 1654H. (Unplanned Outage) [WEBSMS] | CMIN
9/14/2023 4:23:12 PM | Mindanao Grid-09/14/2023 16:25: WMPC DG01 shutdown at 1614H. End of RPS-System voltage requirement. [WEBSMS] | CMIN
9/14/2023 3:57:01 PM | Luzon Grid-09/14/2023 15:57: Tayabas-Naga 230kV Line 1 restored at 1556H (Planned Outage) [WEBSMS] | CLUZ
9/14/2023 1:59:11 PM | Mindanao Grid-09/14/2023 14:01: Lugait - Opol 138kv Line restored at 1356H. Unplanned outage. [WEBSMS] | CMIN
9/14/2023 1:38:53 PM | Mindanao Grid-09/14/2023 13:40: Lugait - Opol 138KV line tripped at 1321H. (Unplanned Outage) [WEBSMS] | CMIN
9/14/2023 12:47:14 PM | [NSO Update] Luzon Grid-09/14/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13832MW, PK=10938MW, RR=458MW, NetOpMargin: PM=2436, EVE=2509 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 170MW, Calaca 2 @ 173MW, Masinloc 1 @ 280MW, Masinloc 2 @ 270MW, Masinloc 3 @ 280MW, SCPC 3 @ 110MW, SLPGC 1 @ 95MW, SLPGC 2 @ 60MW [WEBSMS] | CLUZ
9/14/2023 12:45:17 PM | [NSO Update] Visayas Grid-09/14/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2496MW, PK=2162MW, RR=90MW, NetOpMargin: PM=244, EVE=297 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 312MW, PGPP1 @ 72.5MW [WEBSMS] | CVIS
9/14/2023 12:44:39 PM | [NSO Update] Mindanao Grid-09/14/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3126MW, PK=2124MW, RR=60MW, NetOpMargin: PM=942, EVE=982 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @90MW, AG4 @103MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @157.5MW [WEBSMS] | CMIN
9/14/2023 10:58:17 AM | Mindanao Grid-09/14/2023 11:00: WMPC DG1 Online at 1054H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/14/2023 8:55:43 AM | Mindanao Grid-09/14/2023 08:57: General Santos SS 138KV Bus 2 de-energized at 0847H. (Unplanned Outage) [WEBSMS] | CMIN
9/14/2023 8:54:22 AM | Mindanao Grid-09/14/2023 08:56: WMPC DG09 online at 0851H. For RPS. System Voltage Requirement. [WEBSMS] | CMIN
9/14/2023 8:46:13 AM | Visayas Grid-09/14/2023 08:45: Colon - Calong-calong 138 kV Line 2 de-energized at 0844H. (Planned Outage) [WEBSMS] | CVIS
9/14/2023 6:37:41 AM | Luzon Grid-09/14/2023 06:37: Tayabas-Naga 230kV Line 1 de-energized at 0637H (Planned Outage) [WEBSMS] | CLUZ
9/14/2023 6:08:13 AM | Luzon Grid-09/14/2023 06:08: Laoag-Pasuquin Solar 115kV Line (CO) de-energized at 0607H (Planned Outage) [WEBSMS] | CLUZ
9/14/2023 6:07:06 AM | [NSO Update] Mindanao Grid-09/14/2023 06:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3131MW, PK=2070MW, RR=60MW, NetOpMargin: AM=1001, PM=882, EVE=919 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @90MW, AG4 @103MW, AG5 @38MW, AG6 @149MW, AG7 @31MW, PG4 @157.5MW [WEBSMS] | CMIN
9/14/2023 6:04:57 AM | [NSO Update] Visayas Grid-09/14/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2368MW, PK=2064MW, RR=91.4MW, NetOpMargin: AM=213, PM=310, EVE=285 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 324MW [WEBSMS] | CVIS
9/14/2023 5:48:48 AM | [NSO Update] Luzon Grid-09/14/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13993MW, PK=10815MW, RR=444MW, NetOpMargin: AM=2734, PM=2433, EVE=2848 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC2 @173MW, MSLC1 @280MW, MSLC2 @270MW, MSLC3 @280MW, SCPC 3 @110MW, SLPGC 1 @90MW, SLPGC 2 @50MW [WEBSMS] | CLUZ
9/14/2023 4:32:50 AM | [NSO Update] Luzon Grid-09/14/2023 04:32: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 395 km East Northeast of Itbayat, Batanes (22.6�N, 125.1�E). Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
9/14/2023 4:32:04 AM | [NSO Update] Mindanao Grid-09/14/2023 04:34: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 395 km East Northeast of Itbayat, Batanes (22.6�N, 125.1�E). Southwest Monsoon affecting the country. [WEBSMS] | CMIN
9/14/2023 4:29:51 AM | [NSO Update] Visayas Grid-09/14/2023 04:29: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 395 km East Northeast of Itbayat, Batanes (22.6�N, 125.1�E). Southwest Monsoon affecting the country. [WEBSMS] | CVIS
9/14/2023 2:22:10 AM | Visayas Grid-09/14/2023 02:21: Isabel-IASCO 138 kV Line 1 and Isabel-Pasar Line 1 tripped at 0208H. (Unplanned outage) [WEBSMS] | CVIS
9/14/2023 12:49:05 AM | Mindanao Grid-09/14/2023 00:51: FDC Unit #2 online at 0033H, from reserved shutdown. [WEBSMS] | CMIN
9/13/2023 9:24:21 PM | Mindanao Grid-09/13/2023 21:26: WMPC DG9 Shutdown at 2110H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/13/2023 7:06:40 PM | Visayas Grid-09/13/2023 19:06: Magdugo 230/138KV 300MVA Transformer # 2 energized @1904H. ( Unplanned Outage ) [WEBSMS] | CVIS
9/13/2023 6:18:16 PM | Mindanao Grid-09/13/2023 18:20: PSF U2 Online at 1814H. Follow RTD. [WEBSMS] | CMIN
9/13/2023 5:56:37 PM | [NSO Update] Mindanao Grid-09/13/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3031MW, PK=2069MW, RR=68MW, NetOpMargin: EVE=894 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @90MW, AG4 @96MW, AG5 @34MW, AG6 @144MW, AG7 @29MW, PG4 @115MW [WEBSMS] | CMIN
9/13/2023 5:54:42 PM | [NSO Update] Visayas Grid-09/13/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2372MW, PK=1991MW, RR=86MW, NetOpMargin: EVE=295 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 324MW [WEBSMS] | CVIS
9/13/2023 5:43:07 PM | [NSO Update] Luzon Grid-09/13/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13406MW, PK=10048MW, RR=435MW, NetOpMargin: EVE=2923 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC2 @173MW, MSLC1 @280MW, MSLC2 @270MW, MSLC3 @280MW, SCPC 3 @110MW, SLPGC 1 @85MW, SLPGC 2 @80MW [WEBSMS] | CLUZ
9/13/2023 4:19:09 PM | Mindanao Grid-09/13/2023 16:21: WMPC DG01 shutdown at 1614H. From RPS. System Voltage Requirement. [WEBSMS] | CMIN
9/13/2023 3:41:26 PM | Visayas Grid-09/13/2023 15:41: Pajo 69 kV Line restored at 1537H. (Unplanned Outage) [WEBSMS] | CVIS
9/13/2023 3:35:17 PM | Mindanao Grid-09/13/2023 15:37: TMI U2 cut-out at 1523H. (Planned outage) Ancillary testing. [WEBSMS] | CMIN
9/13/2023 2:59:15 PM | Visayas Grid-09/13/2023 14:58: Magdugo 230/138KV 300MVA Transformer # 2 tripped @1444H. ( Unplanned Outage ). [WEBSMS] | CVIS
9/13/2023 2:51:28 PM | Mindanao Grid-09/13/2023 14:53: Manolo SS 138KV Bus 2 restored at 1439H. (Planned Outage) [WEBSMS] | CMIN
9/13/2023 1:38:40 PM | Visayas Grid-09/13/2023 13:38: Lapu-lapu - Pajo 69 kV Line tripped at 1335H. (Unplanned Outage) [WEBSMS] | CVIS
9/13/2023 12:48:01 PM | [NSO Update] Luzon Grid-09/13/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13790MW, PK=11201MW, RR=467MW, NetOpMargin: PM=2122, EVE=2567 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 220MW, Calaca 2 @ 140MW, GMEC 2 @ 240MW, Masinloc 1 @ 280MW, Masinloc 2 @ 270MW, Masinloc 3 @ 270MW, SCPC 3 @ 110MW, SLPGC 1 @ 75MW, SLPGC 2 @ 75MW [WEBSMS] | CLUZ
9/13/2023 12:46:20 PM | [NSO Update] Visayas Grid-09/13/2023 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2523MW, PK=2202MW, RR=91MW, NetOpMargin: PM=229, EVE=285 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 324MW [WEBSMS] | CVIS
9/13/2023 12:45:42 PM | [NSO Update] Mindanao Grid-09/13/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3075MW, PK=2122MW, RR=70MW, NetOpMargin: PM=883, EVE=908 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @90MW, AG4 @96MW, AG5 @34MW, AG6 @144MW, AG7 @29MW, PG4 @115MW [WEBSMS] | CMIN
9/13/2023 11:00:02 AM | Mindanao Grid-09/13/2023 11:02: WMPC DG01 online at 1051H. For RPS-System Voltage Requirement. [WEBSMS] | CMIN
9/13/2023 10:04:15 AM | Mindanao Grid-09/13/2023 10:06: TM1 U2 Online at 0957H. Ancillary Reserve Test. [WEBSMS] | CMIN
9/13/2023 10:02:52 AM | Mindanao Grid-09/13/2023 10:04: PG4 U3 Online at 0941H. (Unplanned Outage). [WEBSMS] | CMIN
9/13/2023 8:54:57 AM | Mindanao Grid-09/13/2023 08:56: WMPC DG09 online at 0851H. For RPS-System Voltage Requirement. [WEBSMS] | CMIN
9/13/2023 8:43:58 AM | Mindanao Grid-09/13/2023 08:45: Manolo SS 138KV Bus 2 de-energized at 0826H. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
9/13/2023 8:36:48 AM | Mindanao Grid-09/13/2023 08:38: PG4 U3 tripped with a load 40MW at 0829H. (Unplanned outage) [WEBSMS] | CMIN
9/13/2023 6:18:14 AM | Luzon Grid-09/13/2023 06:18: Dona Imelda(Araneta) 300MVA T01 restored at 0617H (Planned Outage) [WEBSMS] | CLUZ
9/13/2023 5:58:47 AM | [NSO Update] Luzon Grid-09/13/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13729MW, PK=10370MW, RR=448MW, NetOpMargin: AM=2911, PM=2765, EVE=2863 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 1 @170MW, CALACA 2 @150MW, GMEC 2 @240MW, MASINLOC 1 @280MW, MASINLOC 2 @270MW, MASINLOC 3 @260MW, SCPC 3 @110MW, SLPGC 1 @60MW, SLPGC 2 @55MW [WEBSMS] | CLUZ
9/13/2023 5:38:06 AM | [NSO Update] Mindanao Grid-09/13/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3189MW, PK=2119MW, RR=70MW, NetOpMargin: AM=1000, PM=912, EVE=884 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @90MW, AG4 @96MW, AG5 @34MW, AG6 @144MW, AG7 @29MW, PG4 @115MW [WEBSMS] | CMIN
9/13/2023 5:37:24 AM | [NSO Update] Visayas Grid-09/13/2023 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2644MW, PK=2216MW, RR=88MW, NetOpMargin: AM=340, PM=278, EVE=285 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 324MW [WEBSMS] | CVIS
9/13/2023 4:08:06 AM | [NSO Update] Mindanao Grid-09/13/2023 04:10: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 610 km East of Itbayat, Batanes (21.2�N, 127.7�E). Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
9/13/2023 4:07:45 AM | [NSO Update] Visayas Grid-09/13/2023 04:07: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 610 km East of Itbayat, Batanes (21.2�N, 127.7�E). Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
9/13/2023 4:07:18 AM | [NSO Update] Luzon Grid-09/13/2023 04:07: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 610 km East of Itbayat, Batanes (21.2�N, 127.7�E). Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
9/13/2023 12:42:12 AM | Luzon Grid-09/13/2023 00:42: Dona Imelda(Araneta) 300MVA T01 was de-energized at 0041H. (Planned Outage) [WEBSMS] | CLUZ
9/12/2023 10:46:42 PM | Visayas Grid-09/12/2023 22:46: Tabango-Kananga 230KV Line 1 and Tabango SS 230kV Bus 1 tripped at 2239H. (Unplanned Outage) [WEBSMS] | CVIS
9/12/2023 9:19:14 PM | Mindanao Grid-09/12/2023 21:21: WMPC DG9 Shutdown a2109H. End of RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/12/2023 8:25:01 PM | Mindanao Grid-09/12/2023 20:27: WMPC DG5 Shutdown at 2021H. Follow RTD. [WEBSMS] | CMIN
9/12/2023 8:18:28 PM | Mindanao Grid-09/12/2023 20:20: WMPC DG5 Online at 2003H. Follow RTD. [WEBSMS] | CMIN
9/12/2023 8:16:17 PM | Mindanao Grid-09/12/2023 20:18: MA3 Online at 2009H. (Unplanned Outage). [WEBSMS] | CMIN
9/12/2023 8:11:32 PM | [NSO Update] Mindanao Grid-09/12/2023 20:13: SO Initiated Market Intervention has been lifted today 12 September 2023 at 2005H for Luzon, Visayas and Mindanao. Market will resume starting interval 2010H. [WEBSMS] | CMIN
9/12/2023 8:11:11 PM | [NSO Update] Visayas Grid-09/12/2023 20:11: SO Initiated Market Intervention has been lifted today 12 September 2023 at 2005H for Luzon, Visayas and Mindanao. Market will resume starting interval 2010H. [WEBSMS] | CVIS
9/12/2023 8:10:51 PM | [NSO Update] Luzon Grid-09/12/2023 20:11: SO Initiated Market Intervention has been lifted today 12 September 2023 at 2005H for Luzon, Visayas and Mindanao. Market will resume starting interval 2010H. [WEBSMS] | CLUZ
9/12/2023 8:05:26 PM | [NSO Update] Mindanao Grid-09/12/2023 20:07: SO Initiated Market Intervention is issued today 12 September 2023 for Luzon, Visayas and Mindanao for interval 1935H due to unimplementable RTD. [WEBSMS] | CMIN
9/12/2023 8:05:05 PM | [NSO Update] Visayas Grid-09/12/2023 20:04: SO Initiated Market Intervention is issued today 12 September 2023 for Luzon, Visayas and Mindanao for interval 1935H due to unimplementable RTD. [WEBSMS] | CVIS
9/12/2023 8:04:43 PM | [NSO Update] Luzon Grid-09/12/2023 20:04: SO Initiated Market Intervention is issued today 12 September 2023 for Luzon, Visayas and Mindanao for interval 1935H due to unimplementable RTD. [WEBSMS] | CLUZ
9/12/2023 8:02:05 PM | [NSO Update] Luzon Grid-09/12/2023 20:02: SO initiated Market Intervention was issued for Luzon, Visayas and Mindanao grid due to unimplementable RTD. [WEBSMS] | CLUZ
9/12/2023 6:46:06 PM | Visayas Grid-09/12/2023 18:45: Magdugo substation 138 KV bus 2 energized at 1835H. (Planned Outage) [WEBSMS] | CVIS
9/12/2023 6:32:50 PM | Mindanao Grid-09/12/2023 18:35: NACSUR (NSD) cut-in to the Mindanao Grid at 1800H, as energy. MO RTD dispatched. [WEBSMS] | CMIN
9/12/2023 5:49:16 PM | [NSO Update] Luzon Grid-09/12/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13211MW, PK=10064MW, RR=425MW, NetOpMargin: EVE=2722 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: Calaca 1 @ 130MW, Calaca 2 @ 173MW, Masinloc 1 @ 280MW, Masinloc 2 @ 270MW, Masinloc 3 @ 260MW, SCPC 3 @ 110MW, SLPGC 1 @ 60MW, SLPGC 2 @ 55MW [WEBSMS] | CLUZ
9/12/2023 5:40:10 PM | [NSO Update] Mindanao Grid-09/12/2023 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2926MW, PK=2076MW, RR=66MW, NetOpMargin: EVE=784 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @96MW, AG5 @34MW, AG6 @144MW, AG7 @29MW, PG4 @85MW [WEBSMS] | CMIN
9/12/2023 5:39:44 PM | [NSO Update] Visayas Grid-09/12/2023 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2432MW, PK=2094MW, RR=80MW, NetOpMargin: EVE=259 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 315MW [WEBSMS] | CVIS
9/12/2023 5:36:46 PM | Mindanao Grid-09/12/2023 17:38: Manolo SS 138KV Bus 1 re-energized at 1556H. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
9/12/2023 4:18:05 PM | Mindanao Grid-09/12/2023 16:20: WMPC DG1 Shutdown at 1614H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/12/2023 1:57:31 PM | [NSO Update] Mindanao Grid-09/12/2023 13:59: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1356H with power going to Visayas. [WEBSMS] | CMIN
9/12/2023 1:56:50 PM | [NSO Update] Visayas Grid-09/12/2023 13:56: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1356H with power going to Visayas. [WEBSMS] | CVIS
9/12/2023 12:49:45 PM | [NSO Update] Luzon Grid-09/12/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13679MW, PK=11401MW, RR=462MW, NetOpMargin: PM=1816, EVE=2181 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 180MW, Calaca 2 @ 173MW, Masinloc 1 @ 280MW, Masinloc 2 @ 270MW, Masinloc 3 @ 250MW, SCPC 3 @ 110MW, SLPGC 1 @ 45MW, SLPGC 2 @ 45MW [WEBSMS] | CLUZ
9/12/2023 12:47:13 PM | [NSO Update] Visayas Grid-09/12/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2580MW, PK=2269MW, RR=89MW, NetOpMargin: PM=221, EVE=260 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, TGPP @ 112MW, Leyte A @ 315MW [WEBSMS] | CVIS
9/12/2023 12:46:23 PM | [NSO Update] Mindanao Grid-09/12/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2986MW, PK=2186MW, RR=66MW, NetOpMargin: PM=734, EVE=763 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @96MW, AG5 @34MW, AG6 @144MW, AG7 @29MW, PG4 @85MW [WEBSMS] | CMIN
9/12/2023 11:03:33 AM | Mindanao Grid-09/12/2023 11:05: TM1 Unit #1 online at 0956H, to facilitate the scheduled ASPA Test. Follow RTD. [WEBSMS] | CMIN
9/12/2023 10:55:42 AM | Mindanao Grid-09/12/2023 10:57: WMPC DG01 online at 1051H. Start of RPS-System Voltage Requirement. [WEBSMS] | CMIN
9/12/2023 10:31:21 AM | Mindanao Grid-09/12/2023 10:33: STEAG Unit #1 on emergency shutdown at 1019H, due to Boiler Fouling. (Unplanned Outage) [WEBSMS] | CMIN
9/12/2023 10:12:14 AM | Mindanao Grid-09/12/2023 10:14: Baloi-Tagoloan 138kV line auto-tripped at 0908H but successfully auto-reclosed. Unplanned Outage [WEBSMS] | CMIN
9/12/2023 10:06:43 AM | [NSO Update] Mindanao Grid-09/12/2023 10:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1005H from forward power direction. [WEBSMS] | CMIN
9/12/2023 10:06:25 AM | [NSO Update] Visayas Grid-09/12/2023 10:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1005H from forward power direction. [WEBSMS] | CVIS
9/12/2023 9:10:51 AM | Visayas Grid-09/12/2023 09:10: Lapulapu-Pajo 13.8 KV fdr tripped at 0852H. (Unplanned Outage) [WEBSMS] | CVIS
9/12/2023 9:09:57 AM | Mindanao Grid-09/12/2023 09:12: SPC (Mati Diesel) online at 0900H. Follow RTD. [WEBSMS] | CMIN
9/12/2023 9:09:30 AM | Visayas Grid-09/12/2023 09:09: Magdugo substation 138 KV bus 2 de-energized at 0905H. (Planned Outage) [WEBSMS] | CVIS
9/12/2023 8:59:05 AM | Mindanao Grid-09/12/2023 09:01: WMPC DG09 online at 0851H. Start of RPS-System Voltage Requirement. [WEBSMS] | CMIN
9/12/2023 8:23:07 AM | Mindanao Grid-09/12/2023 08:25: Manolo SS 138KV Bus 1 de-energized at 0812H. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
9/12/2023 5:49:50 AM | [NSO Update] Luzon Grid-09/12/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13918MW, PK=11346MW, RR=442MW, NetOpMargin: AM=2130, PM=1593, EVE=2055 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 1 @150MW, CALACA 2 @173MW, MASINLOC 1 @280MW, MASINLOC 2 @270MW, MASINLOC 3 @250MW, SCPC 3 @110MW, SLPGC 1 @90MW, SLPGC 2 @85MW [WEBSMS] | CLUZ
9/12/2023 5:42:04 AM | [NSO Update] Mindanao Grid-09/12/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2991MW, PK=2172MW, RR=66MW, NetOpMargin: AM=754, PM=691, EVE=711 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @96MW, AG5 @34MW, AG6 @144MW, AG7 @29MW, PG4 @85MW [WEBSMS] | CMIN
9/12/2023 5:41:09 AM | [NSO Update] Visayas Grid-09/12/2023 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2546MW, PK=2213MW, RR=88MW, NetOpMargin: AM=246, PM=235, EVE=271 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC-Thermal 1A @82MW, TGPP @112MW, LEYTE A @321MW, TPC-Carmen @30MW [WEBSMS] | CVIS
9/12/2023 4:05:32 AM | [NSO Update] Luzon Grid-09/12/2023 04:05: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 790 km East Northeast of Basco, Batanes (21.9�N, 129.4�E). Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
9/12/2023 4:03:28 AM | [NSO Update] Mindanao Grid-09/12/2023 04:05: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 790 km East Northeast of Basco, Batanes (21.9�N, 129.4�E). Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
9/12/2023 4:03:14 AM | [NSO Update] Visayas Grid-09/12/2023 04:03: Weather Advisory: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 790 km East Northeast of Basco, Batanes (21.9�N, 129.4�E). Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
9/12/2023 2:03:35 AM | Luzon Grid-09/12/2023 02:03: QPPL emergency shutdown at 0202H (Unplanned Outage) [WEBSMS] | CLUZ
9/11/2023 11:51:44 PM | Mindanao Grid-09/11/2023 23:53: MCC Unit 2 online at 2348H. Planned outage. Non-GOMP. [WEBSMS] | CMIN
9/11/2023 9:18:42 PM | Mindanao Grid-09/11/2023 21:20: WMPC DG09 shutdown at 2111H End of RPS-System Voltage Requirements. [WEBSMS] | CMIN
9/11/2023 6:58:27 PM | Mindanao Grid-09/11/2023 19:00: Euro Hydro (NBT) with 1MW gross generation tripped/Isolated at 1820H due to loss of power. Affected by the forced outage of NORDECO 69kV line. (Unplanned Outage) [WEBSMS] | CMIN
9/11/2023 6:49:41 PM | Mindanao Grid-09/11/2023 18:51: STEAG Unit #2 on emergency shutdown at 1845H, due to Boiler Fouling. Unplanned Outage. [WEBSMS] | CMIN
9/11/2023 5:59:17 PM | [NSO Update] Visayas Grid-09/11/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2447MW, PK=2115MW, RR=87MW, NetOpMargin: EVE=245 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC-Thermal 1A @82MW, TGPP @112MW, LEYTE A @322MW, TPC-Carmen @30MW [WEBSMS] | CVIS
9/11/2023 5:59:06 PM | [NSO Update] Mindanao Grid-09/11/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2983MW, PK=2070MW, RR=56MW, NetOpMargin: EVE=857 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @80MW, AG4 @90MW, AG5 @32MW, AG6 @144MW, AG7 @28MW, PG4 @85MW [WEBSMS] | CMIN
9/11/2023 5:36:17 PM | [NSO Update] Luzon Grid-09/11/2023 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13763MW, PK=10713MW, RR=458MW, NetOpMargin: EVE=2592 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC1 @280MW, MSLC2 @270MW, MSLC3 @230MW, SCPC 3 @110MW, SLPGC 1 @90MW, SLPGC 2 @85MW [WEBSMS] | CLUZ
9/11/2023 4:35:09 PM | Mindanao Grid-09/11/2023 16:37: Mt. Apo Unit #3 with 3.2MW gross generation, tripped at 1610H due to PH Level High High. (Unplanned Outage) [WEBSMS] | CMIN
9/11/2023 4:17:06 PM | Mindanao Grid-09/11/2023 16:19: WMPC DG01 shutdown at 1613H; RPS - System Voltage Requirement [WEBSMS] | CMIN
9/11/2023 4:08:45 PM | Luzon Grid-09/11/2023 16:08: For info: Cabanatuan PCB 8-02CB24CBN restored at 1528H (Unplanned Outage) [WEBSMS] | CLUZ
9/11/2023 2:48:24 PM | Luzon Grid-09/11/2023 14:48: Cabanatuan PCB 8-02CB24CBN tripped at 1435H (Unplanned Outage) [WEBSMS] | CLUZ
9/11/2023 2:33:31 PM | Mindanao Grid-09/11/2023 14:35: Agus 2 Unit 1 online at 1424H. (Unplanned Outage) [WEBSMS] | CMIN
9/11/2023 1:12:14 PM | [NSO Update] Luzon Grid-09/11/2023 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14354MW, PK=11406MW, RR=462MW, NetOpMargin: PM=2486, EVE=2627 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @210MW, CLC2 @173MW, MSLC1 @280MW, MSLC2 @270MW, MSLC3 @250MW, SCPC 3 @110MW, SLPGC 1 @100MW, SLPGC 2 @75MW [WEBSMS] | CLUZ
9/11/2023 1:06:08 PM | [NSO Update] Mindanao Grid-09/11/2023 13:08: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3022MW, PK=2197MW, RR=56MW, NetOpMargin: PM=769, EVE=820 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @80MW, AG4 @90MW, AG5 @32MW, AG6 @144MW, AG7 @28MW, PG4 @85MW [WEBSMS] | CMIN
9/11/2023 1:04:52 PM | [NSO Update] Visayas Grid-09/11/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2624MW, PK=2251MW, RR=94MW, NetOpMargin: PM=279, EVE=304 Highest Unit O/L: THVI 1 @169MW Derated Plant: TPC-Thermal 1A @82MW, TGPP @112MW, LEYTE A @313MW, TPC-Carmen @30MW [WEBSMS] | CVIS
9/11/2023 11:07:22 AM | Mindanao Grid-09/11/2023 11:09: WMPC DG01 online at 1051H; RPS - System Voltage Requirement [WEBSMS] | CMIN
9/11/2023 9:12:32 AM | Mindanao Grid-09/11/2023 09:14: Supreme Power Mati Online at 0852H. Follow RTD. [WEBSMS] | CMIN
9/11/2023 6:27:53 AM | Luzon Grid-09/11/2023 06:28: Taytay 300MVA T01 was restored at 0625H. (Planned Outage) [WEBSMS] | CLUZ
9/11/2023 6:03:48 AM | [NSO Update] Mindanao Grid-09/11/2023 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3052MW, PK=2003MW, RR=56MW, NetOpMargin: AM=993, PM=903, EVE=944 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @30MW, AG2 @80MW, AG4 @90MW, AG5 @32MW, AG6 @144MW, AG7 @28MW, PG4 @85MW [WEBSMS] | CMIN
9/11/2023 6:03:36 AM | [NSO Update] Visayas Grid-09/11/2023 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2382MW, PK=2096MW, RR=92MW, NetOpMargin: AM=194, PM=246, EVE=255 Highest Unit O/L: THVI 1 @169MW Derated Plant: TPC-Thermal 1A @82MW, TGPP @112MW, LEYTE A @295MW, TPC-Carmen @30MW [WEBSMS] | CVIS
9/11/2023 5:59:46 AM | [NSO Update] Luzon Grid-09/11/2023 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14233MW, PK=10691MW, RR=453MW, NetOpMargin: AM=3089, PM=2418, EVE=2771 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @160MW, CLC2 @173MW, MSLC1 @280MW, MSLC2 @270MW, MSLC3 @150MW, SCPC 3 @110MW, SLPGC 1 @90MW, SLPGC 2 @65MW, ILIJAN A @570MW [WEBSMS] | CLUZ
9/11/2023 5:15:34 AM | Mindanao Grid-09/11/2023 05:17: Maco-Nabunturan 138kV Line energized/restored at 0511H. Planned Outage (PO) [WEBSMS] | CMIN
9/11/2023 4:23:22 AM | [NSO Update] Mindanao Grid-09/11/2023 04:25: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 875 km East Northeast of Extreme Northern Luzon (23.5 N, 129.8 E). Southwest Monsoon affecting Mindanao. [WEBSMS] | CMIN
9/11/2023 4:23:06 AM | [NSO Update] Visayas Grid-09/11/2023 04:22: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 875 km East Northeast of Extreme Northern Luzon (23.5 N, 129.8 E). Southwest Monsoon affecting Mindanao. [WEBSMS] | CVIS
9/11/2023 4:22:54 AM | [NSO Update] Luzon Grid-09/11/2023 04:23: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 875 km East Northeast of Extreme Northern Luzon (23.5 N, 129.8 E). Southwest Monsoon affecting Mindanao. [WEBSMS] | CLUZ
9/11/2023 2:38:33 AM | Luzon Grid-09/11/2023 02:38: Taytay 300MVA T01 was de-energized at 0228H. (Planned Outage) [WEBSMS] | CLUZ
9/11/2023 2:01:38 AM | Luzon Grid-09/11/2023 02:01: San Jose 300MVA T02 was restored at 0159H. (Planned Outage) [WEBSMS] | CLUZ
9/10/2023 11:32:47 PM | Luzon Grid-09/10/2023 23:32: San Jose 300MVA T02 was de-energized at 2331H. (Planned Outage) [WEBSMS] | CLUZ
9/10/2023 8:49:16 PM | Luzon Grid-09/10/2023 20:49: Dasmarinas-Tayabas 500kV line was restored at 2046H (Unplanned Outage). [WEBSMS] | CLUZ
9/10/2023 8:29:50 PM | Visayas Grid-09/10/2023 20:29: Toledo 40MVA TR 2 energized at 2024H. (Unplanned Outage) [WEBSMS] | CVIS
9/10/2023 7:46:38 PM | Mindanao Grid-09/10/2023 19:48: PG4 U3 Online at 1944H. (Planned Outage). [WEBSMS] | CMIN
9/10/2023 7:08:19 PM | Mindanao Grid-09/10/2023 19:10: PG4 U1 Online at 1906H. (Planned Outage). [WEBSMS] | CMIN
9/10/2023 6:18:23 PM | [NSO Update] Mindanao Grid-09/10/2023 18:20: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2938MW, PK=1907MW, RR=56MW, NetOpMargin: EVE=975 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @80MW, AG4 @90MW, AG5 @32MW, AG6 @144MW, AG7 @28MW, PG4 @35MW [WEBSMS] | CMIN
9/10/2023 6:18:05 PM | [NSO Update] Luzon Grid-09/10/2023 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13352MW, PK=9861MW, RR=314MW, NetOpMargin: EVE=3177 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC1 @300MW, MSLC2 @200MW, MSLC3 @180MW, SLPGC 1 @90MW, SLPGC 2 @60MW [WEBSMS] | CLUZ
9/10/2023 6:11:33 PM | [NSO Update] Visayas Grid-09/10/2023 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2388MW, PK=2005MW, RR=87MW, NetOpMargin: EVE=296 Highest Unit O/L: THVI 1 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @300MW, TPC-Carmen @30MW [WEBSMS] | CVIS
9/10/2023 5:55:55 PM | Luzon Grid-09/10/2023 17:56: Balsik-Olongapo 230kV Linerestored at 1754H. (Planned Outage) [WEBSMS] | CLUZ
9/10/2023 5:23:55 PM | Visayas Grid-09/10/2023 17:23: Naga - CDPP1 138 kV line 2 energized at 1720H. (Planned Outage) [WEBSMS] | CVIS
9/10/2023 5:17:08 PM | Visayas Grid-09/10/2023 17:16: Toledo 40MVA TR 2 tripped at 1706H. (Unplanned Outage) [WEBSMS] | CVIS
9/10/2023 4:32:12 PM | Mindanao Grid-09/10/2023 16:34: Manolo Fortich-Maramag 138kV Line1 restored 1630H. Planned outage / Part of ERC approved MSUP Stage 1 Sched 4. [WEBSMS] | CMIN
9/10/2023 4:08:10 PM | Mindanao Grid-09/10/2023 16:10: PG4 U2 online at 1559H. (Planned Outage). [WEBSMS] | CMIN
9/10/2023 3:14:39 PM | Visayas Grid-09/10/2023 15:14: Naga-CDPP 138kV Line 1 restored at 1513H. (Unplanned Outage) [WEBSMS] | CVIS
9/10/2023 3:13:07 PM | Visayas Grid-09/10/2023 15:12: Naga-CDPP 138kV Line 1 tripped at 1450H. (Unplanned Outage) [WEBSMS] | CVIS
9/10/2023 2:35:59 PM | Mindanao Grid-09/10/2023 14:38: Manolo Fortich-Maramag 138kV Line1 de-energized 1425H. Planned outage / Part of ERC approved MSUP Stage 1 Sched 4. [WEBSMS] | CMIN
9/10/2023 1:43:25 PM | Mindanao Grid-09/10/2023 13:45: San Francisco - Bislig 138k Line energized at 1336H. Unplanned outage. [WEBSMS] | CMIN
9/10/2023 12:55:12 PM | [NSO Update] Mindanao Grid-09/10/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2968MW, PK=1729MW, RR=46MW, NetOpMargin: PM=1193, EVE=1058 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @80MW, AG4 @90MW, AG5 @32MW, AG6 @144MW, AG7 @28MW, PG4 @110MW [WEBSMS] | CMIN
9/10/2023 12:52:16 PM | [NSO Update] Visayas Grid-09/10/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2502MW, PK=1838MW, RR=89MW, NetOpMargin: PM=575, EVE=345 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 288MW [WEBSMS] | CVIS
9/10/2023 12:45:17 PM | [NSO Update] Luzon Grid-09/10/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14046MW, PK=9401MW, RR=346MW, NetOpMargin: PM=4299, EVE=3030 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 300MW, Masinloc 2 @ 270MW, Masinloc 3 @ 180MW, SLPGC 1 @ 75MW, SLPGC 2 @ 60MW [WEBSMS] | CLUZ
9/10/2023 11:04:40 AM | Visayas Grid-09/10/2023 11:04: Veco-Aya 138KV line energized @ 1047H, customers request. ( Planned Outage ) [WEBSMS] | CVIS
9/10/2023 10:51:29 AM | Luzon Grid-09/10/2023 10:51: New Lal-Lo 100MVA T01 commissioned at 1050H. [WEBSMS] | CLUZ
9/10/2023 10:46:34 AM | Mindanao Grid-09/10/2023 10:48: San Francisco - Bislig 138KV line auto-tripped at 0926H. Indications at San Frans SS: ABC, M1= 94KM; At Bislig SS: ABC, M1=3.531KM. Advised for line patrol. Unplanned Outage. [WEBSMS] | CMIN
9/10/2023 10:18:44 AM | Mindanao Grid-09/10/2023 10:20: Pulangi 4 Unit #2 shutdown at 1003H to facilitate water drawdown activity. Planned Outage (Non-GOMP) [WEBSMS] | CMIN
9/10/2023 9:50:22 AM | Mindanao Grid-09/10/2023 09:52: San Francisco - Bislig 138kV Line tripped at 0926H. (Unplanned Outage). [WEBSMS] | CMIN
9/10/2023 9:42:01 AM | Luzon Grid-09/10/2023 09:42: New Lal-Lo 100MVA T01 energized at 0939H. (On-going Testing and Commissioning) [WEBSMS] | CLUZ
9/10/2023 8:14:56 AM | Mindanao Grid-09/10/2023 08:17: Pulangi 4 HEPP Unit #1 and Unit #3 shutdown at 0803H and 0805H respectively to facilitate scheduled water drawdown activity. Planned Outage (Non-GOMP). [WEBSMS] | CMIN
9/10/2023 6:21:32 AM | Mindanao Grid-09/10/2023 06:23: Lake Mainit HEPP online at 0612H. (Unplanned Outage) [WEBSMS] | CMIN
9/10/2023 6:18:23 AM | Visayas Grid-09/10/2023 06:18: Veco-Aya 138KV line de-energized @ 0610H, customers request. ( Planned Outage ) [WEBSMS] | CVIS
9/10/2023 6:14:47 AM | Luzon Grid-09/10/2023 06:14: Balsik-Olongapo 230kV Line de-energized at 0613H. (Planned Outage) [WEBSMS] | CLUZ
9/10/2023 5:45:45 AM | [NSO Update] Luzon Grid-09/10/2023 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14273MW, PK=9236MW, RR=334MW, NetOpMargin: AM=4704, PM=4236, EVE=3003 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 300MW, Masinloc 2 @ 270MW, Masinloc 3 @ 180MW, SLPGC 1 @ 75MW, SLPGC 2 @ 60MW [WEBSMS] | CLUZ
9/10/2023 5:44:24 AM | [NSO Update] Visayas Grid-09/10/2023 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2526MW, PK=1749MW, RR=87MW, NetOpMargin: AM=690, PM=458, EVE=269 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 288MW [WEBSMS] | CVIS
9/10/2023 5:43:33 AM | [NSO Update] Mindanao Grid-09/10/2023 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2977MW, PK=1670MW, RR=46MW, NetOpMargin: AM=1261, PM=1098, EVE=1021 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @80MW, AG4 @90MW, AG5 @32MW, AG6 @144MW, AG7 @28MW [WEBSMS] | CMIN
9/10/2023 5:17:21 AM | Luzon Grid-09/10/2023 05:17: Dasmarinas-Tayabas 500kV Line tripped at 0508H (Unplanned Outage) [WEBSMS] | CLUZ
9/10/2023 4:23:37 AM | [NSO Update] Luzon Grid-09/10/2023 04:23: Weather Update: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 730 km East Northeast of Extreme Northern Luzon (22.6 �N, 128.6 �E). Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CLUZ
9/10/2023 4:23:25 AM | [NSO Update] Mindanao Grid-09/10/2023 04:25: Weather Update: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 730 km East Northeast of Extreme Northern Luzon (22.6 �N, 128.6 �E). Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CMIN
9/10/2023 4:23:12 AM | [NSO Update] Visayas Grid-09/10/2023 04:23: Weather Update: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 730 km East Northeast of Extreme Northern Luzon (22.6 �N, 128.6 �E). Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CVIS
9/10/2023 3:43:53 AM | Visayas Grid-09/10/2023 03:43: Compostela Medellin 69 kV line restored at 0342H. (Unplanned Outage) [WEBSMS] | CVIS
9/10/2023 3:38:25 AM | Visayas Grid-09/10/2023 03:38: Compostela Medellin 69 kV line tripped at 0318H. (Unplanned Outage) [WEBSMS] | CVIS
9/9/2023 9:08:06 PM | Mindanao Grid-09/09/2023 21:10: NSD shutdown at 2100H. Follow RTD. [WEBSMS] | CMIN
9/9/2023 7:36:49 PM | Mindanao Grid-09/09/2023 19:38: Baloi-Aurora 138kV line restored/energized 1932H. From unplanned outage [WEBSMS] | CMIN
9/9/2023 7:07:27 PM | Visayas Grid-09/09/2023 19:07: Naga - CDPP1 138 kV line energized at 1905H. (Planned Outage) [WEBSMS] | CVIS
9/9/2023 6:03:47 PM | Mindanao Grid-09/09/2023 18:05: NSD online at 1800H. Follow RTD. [WEBSMS] | CMIN
9/9/2023 5:52:36 PM | [NSO Update] Luzon Grid-09/09/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13648MW, PK=10422MW, RR=403MW, NetOpMargin: EVE=2823 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 300MW, Masinloc 2 @ 270MW, Masinloc 3 @ 140MW, SLPGC 1 @ 55MW, SLPGC 2 @ 50MW [WEBSMS] | CLUZ
9/9/2023 5:50:20 PM | [NSO Update] Mindanao Grid-09/09/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3033MW, PK=1952MW, RR=56MW, NetOpMargin: EVE=1025 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @100MW, AG5 @32MW, AG6 @144MW, AG7 @28MW, PG4 @80MW [WEBSMS] | CMIN
9/9/2023 5:49:01 PM | [NSO Update] Visayas Grid-09/09/2023 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2368MW, PK=2052MW, RR=87MW, NetOpMargin: EVE=229 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 10MW, Leyte A @ 275MW, TGPP @ 113.2MW, PGPP1 @ 110MW [WEBSMS] | CVIS
9/9/2023 5:47:36 PM | Mindanao Grid-09/09/2023 17:49: AGC online at 1744H. (Unplanned Outage). [WEBSMS] | CMIN
9/9/2023 5:39:43 PM | Luzon Grid-09/09/2023 17:39: Bayombong - Santiago 230kV Line 1 auto-tripped/auto-reclosed successfully at both sides at 1736H. (Unplanned Outage) [WEBSMS] | CLUZ
9/9/2023 5:31:52 PM | Mindanao Grid-09/09/2023 17:33: AGC tipped with 10.5MW load at 1726H. (Unplanned Outage) [WEBSMS] | CMIN
9/9/2023 4:57:36 PM | Mindanao Grid-09/09/2023 16:59: Nabunturan-Masara 138kV Line (Customers Owned & Maintained 138kVL) restored at 1651H. Planned Outage (PO) [WEBSMS] | CMIN
9/9/2023 4:38:37 PM | Mindanao Grid-09/09/2023 16:40: Mapalad-Holcim 138kV Line (7LI1IDP-PLT) restored 1631H (CO). Requested by customer, planned outage /N-GOMP. [WEBSMS] | CMIN
9/9/2023 4:38:37 PM | Visayas Grid-09/09/2023 16:38: Toledo - Calongcalong 138 kV line energized at 1636H. (Planned Outage) [WEBSMS] | CVIS
9/9/2023 3:32:46 PM | Luzon Grid-09/09/2023 15:32: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1532H. (Planned Outage) [WEBSMS] | CLUZ
9/9/2023 3:27:09 PM | Luzon Grid-09/09/2023 15:27: Daraga-Bacman 230kV Line 2 restored at 1527H. (Planned Outage) [WEBSMS] | CLUZ
9/9/2023 3:17:52 PM | Mindanao Grid-09/09/2023 15:19: WMPC DG5 shutdown at 1514H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/9/2023 1:00:34 PM | [NSO Update] Mindanao Grid-09/09/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3062MW, PK=1936MW, RR=56MW, NetOpMargin: PM=1070, EVE=1069 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @100MW, AG5 @32MW, AG6 @144MW, AG7 @28MW, PG4 @80MW [WEBSMS] | CMIN
9/9/2023 12:53:13 PM | [NSO Update] Visayas Grid-09/09/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2533MW, PK=2060MW, RR=87MW, NetOpMargin: PM=386, EVE=287 Highest Unit O/L: THVI 1 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @295MW, TPC-Carmen @30MW [WEBSMS] | CVIS
9/9/2023 12:46:38 PM | [NSO Update] Luzon Grid-09/09/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14410MW, PK=10715MW, RR=415MW, NetOpMargin: PM=3280, EVE=3125 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC1 @300MW, MSLC2 @270MW, MSLC3 @140MW, SLPGC 1 @55MW, SLPGC 2 @50MW [WEBSMS] | CLUZ
9/9/2023 10:47:07 AM | Mindanao Grid-09/09/2023 10:49: Gensan SS 138kV Bus 02 restored 1049H from emergency shutdown. [WEBSMS] | CMIN
9/9/2023 9:55:57 AM | Mindanao Grid-09/09/2023 09:58: WMPC DG05 online at 0951H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
9/9/2023 9:04:25 AM | Luzon Grid-09/09/2023 09:04: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0903H. (Planned Outage) [WEBSMS] | CLUZ
9/9/2023 8:58:51 AM | Mindanao Grid-09/09/2023 09:00: Gensan SS 138kV Bus02 on emergency shutdown 0850H to facilitate safe passage of replacement 7-02CB08GSA underloop conductor between 7BS02GSA and 7A-04DS07GSA. [WEBSMS] | CMIN
9/9/2023 8:55:58 AM | Mindanao Grid-09/09/2023 08:58: Updated: Nabunturan-Masara 138kV Line (Customers Owned & Maintained 138kVL) de-energized at 0724H. Planned Outage (PO). [WEBSMS] | CMIN
9/9/2023 8:53:22 AM | Mindanao Grid-09/09/2023 08:55: Updated: Maco-Nabunturan 138kV Line de-energized at 0615H. Planned Outage (PO). [WEBSMS] | CMIN
9/9/2023 8:39:34 AM | Visayas Grid-09/09/2023 08:39: Naga-CDPP 1 138KV line de-energized @ 0809H, customers request. ( Planned Outage ) [WEBSMS] | CVIS
9/9/2023 8:09:43 AM | Visayas Grid-09/09/2023 08:09: Toledo-CalongCalong 138KV line de-energized @ 0804H. ( Planned Outage ) [WEBSMS] | CVIS
9/9/2023 7:32:15 AM | Mindanao Grid-09/09/2023 07:34: Nabunturan-Masara 138kV Line de-energized 0724H. Planned outage [WEBSMS] | CMIN
9/9/2023 6:45:10 AM | Luzon Grid-09/09/2023 06:43: Daraga-Bacman 230kV Line 2 de-energized at 0642H. (Planned Outage) [WEBSMS] | CLUZ
9/9/2023 6:21:13 AM | Mindanao Grid-09/09/2023 06:23: Maco-Nabunturan 138kV Line 1 de-energized 0615H. Planned outage. [WEBSMS] | CMIN
9/9/2023 5:52:43 AM | [NSO Update] Visayas Grid-09/09/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2388MW, PK=1948MW, RR=87MW, NetOpMargin: AM=353, PM=247, EVE=276 Highest Unit O/L: THVI 1 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @295MW, TPC-Carmen @30MW [WEBSMS] | CVIS
9/9/2023 5:52:37 AM | [NSO Update] Mindanao Grid-09/09/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3069MW, PK=1926MW, RR=56MW, NetOpMargin: AM=1087, PM=1007, EVE=1010 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MCO @270MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @100MW, AG5 @32MW, AG6 @144MW, AG7 @28MW, PG4 @80MW [WEBSMS] | CMIN
9/9/2023 5:46:55 AM | [NSO Update] Luzon Grid-09/09/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13986MW, PK=10137MW, RR=401MW, NetOpMargin: AM=3448, PM=3131, EVE=2804 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC1 @300MW, MSLC2 @270MW, MSLC3 @140MW, SLPGC 1 @55MW, SLPGC 2 @50MW [WEBSMS] | CLUZ
9/9/2023 4:15:35 AM | [NSO Update] Mindanao Grid-09/09/2023 04:17: Weather Update: Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CMIN
9/9/2023 4:15:18 AM | [NSO Update] Luzon Grid-09/09/2023 04:15: Weather Update: Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CLUZ
9/9/2023 4:15:08 AM | [NSO Update] Visayas Grid-09/09/2023 04:14: Weather Update: Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CVIS
9/8/2023 11:56:26 PM | Mindanao Grid-09/08/2023 23:58: PG4 U1 online at 2353H. From reserve shutdown (Planned Outage). [WEBSMS] | CMIN
9/8/2023 9:22:37 PM | Mindanao Grid-09/08/2023 21:24: WMPC DG05 shutdown at 2113H. End of RPS - System Voltage Requirement [WEBSMS] | CMIN
9/8/2023 8:00:03 PM | Mindanao Grid-09/08/2023 20:02: FDC Unit #1 Online at 1948H, from Forced Outage. Unplanned Outage. [WEBSMS] | CMIN
9/8/2023 7:16:45 PM | Mindanao Grid-09/08/2023 19:18: FDC Unit #1 with 10MW Gross Generation tripped at 1855H, due to Drum Level Low Low. Frequency=60.1Hz. Unplanned Outage. [WEBSMS] | CMIN
9/8/2023 6:57:26 PM | Mindanao Grid-09/08/2023 18:59: Euro Hydro (NBT) Online at 1820H. (Unplanned Outage) [WEBSMS] | CMIN
9/8/2023 6:21:35 PM | Mindanao Grid-09/08/2023 18:23: FDC Unit #1 Online at 1810H, from PMS (GOMP). Planned Outage. [WEBSMS] | CMIN
9/8/2023 6:08:39 PM | [NSO Update] Visayas Grid-09/08/2023 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2427MW, PK=2087MW, RR=88MW, NetOpMargin: EVE=253 Highest Unit O/L: THVI 1 @169MW Derated Plant: TPC-Thermal 1A @82MW, TGPP @113.2MW, LEYTE A @290MW, TPC-Carmen @16MW [WEBSMS] | CVIS
9/8/2023 6:07:42 PM | [NSO Update] Mindanao Grid-09/08/2023 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2898MW, PK=2072MW, RR=52MW, NetOpMargin: EVE=774 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MCO @270MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @100MW, AG5 @32MW, AG6 @144MW, AG7 @28MW, PG4 @80MW [WEBSMS] | CMIN
9/8/2023 6:04:44 PM | [NSO Update] Luzon Grid-09/08/2023 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13200MW, PK=10526MW, RR=408MW, NetOpMargin: EVE=2266 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @160MW, CLC2 @173MW, MSLC1 @300MW, MSLC2 @270MW, MSLC3 @180MW, SLPGC 1 @50MW, SLPGC 2 @50MW [WEBSMS] | CLUZ
9/8/2023 5:58:58 PM | Mindanao Grid-09/08/2023 18:01: Euro Hydro (NBT) with 0.9MW generation tripped/isolated at 1654H, affected by the forced outage of NORDECO 69kV line. (Unplanned Outage) [WEBSMS] | CMIN
9/8/2023 5:11:39 PM | Luzon Grid-09/08/2023 17:11: Ilijan GT2-2 shutdown at 1710H. (Unplanned Outage) [WEBSMS] | CLUZ
9/8/2023 4:26:00 PM | Luzon Grid-09/08/2023 16:26: Ilijan GT2-2 online at 1622H. (Unplanned Outage) [WEBSMS] | CLUZ
9/8/2023 4:02:21 PM | Mindanao Grid-09/08/2023 16:04: WMPC DG07 shutdown at 1544H. RPS - System Voltage Requirement [WEBSMS] | CMIN
9/8/2023 4:00:14 PM | Mindanao Grid-09/08/2023 16:02: WMPC DG05 online at 1530H, to replace WMPC DG07. RPS - System Voltage Requirement [WEBSMS] | CMIN
9/8/2023 3:22:30 PM | Mindanao Grid-09/08/2023 15:24: TM1 Unit #1 Shutdown at 1457H, from MO dispatched. Follow RTD. [WEBSMS] | CMIN
9/8/2023 1:54:16 PM | Mindanao Grid-09/08/2023 13:56: TM1 Unit #1 Online at 1351H. MO dispatched. Follow RTD. [WEBSMS] | CMIN
9/8/2023 1:03:47 PM | [NSO Update] Mindanao Grid-09/08/2023 13:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1303H with power going to Visayas. [WEBSMS] | CMIN
9/8/2023 1:03:30 PM | [NSO Update] Visayas Grid-09/08/2023 13:03: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1303H with power going to Visayas. [WEBSMS] | CVIS
9/8/2023 12:58:04 PM | [NSO Update] Luzon Grid-09/08/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14194MW, PK=11651MW, RR=457MW, NetOpMargin: PM=2086, EVE=2420 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 160MW, Calaca 2 @ 173MW, Masinloc 1 @ 300MW, Masinloc 2 @ 270MW, Masinloc 3 @ 180MW, SLPGC 1 @ 60MW, SLPGC 2 @ 75MW [WEBSMS] | CLUZ
9/8/2023 12:51:51 PM | [NSO Update] Mindanao Grid-09/08/2023 12:53: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1250H from reverse power direction. [WEBSMS] | CMIN
9/8/2023 12:51:36 PM | [NSO Update] Visayas Grid-09/08/2023 12:51: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1250H from reverse power direction. [WEBSMS] | CVIS
9/8/2023 12:50:56 PM | [NSO Update] Mindanao Grid-09/08/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2946MW, PK=2214MW, RR=52MW, NetOpMargin: PM=680, EVE=719 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @100MW, AG5 @32MW, AG6 @144MW, AG7 @28MW, PG4 @85MW [WEBSMS] | CMIN
9/8/2023 12:49:42 PM | [NSO Update] Visayas Grid-09/08/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2655MW, PK=2310MW, RR=92MW, NetOpMargin: PM=254, EVE=255 Highest Unit O/L: THVI 1 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 16MW, Leyte A @ 290MW, PGPP1 @ 74MW [WEBSMS] | CVIS
9/8/2023 10:54:23 AM | Mindanao Grid-09/08/2023 10:56: WMPC DG07 online at 1051H, for RPS - System Voltage Requirement [WEBSMS] | CMIN
9/8/2023 10:39:31 AM | Mindanao Grid-09/08/2023 10:41: WMPC DG01 online at 1026H, as replacement of tripped WMPC DG05. RPS-System Voltage Requirement. [WEBSMS] | CMIN
9/8/2023 10:24:07 AM | Mindanao Grid-09/08/2023 10:26: WMPC DG05 run as RPS tripped at 1014H, Indication: HT Low Pressure Stop. Unplanned Outage. [WEBSMS] | CMIN
9/8/2023 9:44:08 AM | [NSO Update] Mindanao Grid-09/08/2023 09:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0941H with power going to Mindanao. [WEBSMS] | CMIN
9/8/2023 9:43:53 AM | [NSO Update] Visayas Grid-09/08/2023 09:43: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0941H with power going to Mindanao. [WEBSMS] | CVIS
9/8/2023 9:38:13 AM | [NSO Update] Mindanao Grid-09/08/2023 09:40: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0932H from forward power direction. [WEBSMS] | CMIN
9/8/2023 9:37:57 AM | [NSO Update] Visayas Grid-09/08/2023 09:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0932H from forward power direction. [WEBSMS] | CVIS
9/8/2023 9:08:40 AM | Mindanao Grid-09/08/2023 09:10: WMPC DG05 online at 0851H, for RPS - System Voltage Requirement [WEBSMS] | CMIN
9/8/2023 5:58:33 AM | [NSO Update] Mindanao Grid-09/08/2023 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2951MW, PK=2101MW, RR=52MW, NetOpMargin: AM=798, PM=681, EVE=753 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: FMP @123MW, MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @100MW, AG5 @32MW, AG6 @144MW, AG7 @28MW, PG4 @85MW [WEBSMS] | CMIN
9/8/2023 5:57:02 AM | [NSO Update] Visayas Grid-09/08/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2625MW, PK=2253MW, RR=89MW, NetOpMargin: AM=283, PM=287, EVE=254 Highest Unit O/L: THVI 1 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @290MW, PGPP1 @74MW, TPC-Carmen @30MW [WEBSMS] | CVIS
9/8/2023 5:47:46 AM | [NSO Update] Luzon Grid-09/08/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14350MW, PK=11176MW, RR=443MW, NetOpMargin: AM=2731, PM=2138, EVE=2476 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @160MW, CLC2 @173MW, MSLC1 @300MW, MSLC2 @270MW, MSLC3 @180MW, SLPGC 1 @75MW SLPGC 2 @75MW, SAN GABRIEL @409MW [WEBSMS] | CLUZ
9/8/2023 4:40:51 AM | [NSO Update] Luzon Grid-09/08/2023 04:40: Weather Update: Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CLUZ
9/8/2023 4:37:22 AM | [NSO Update] Mindanao Grid-09/08/2023 04:39: Weather Update: Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CMIN
9/8/2023 4:34:56 AM | [NSO Update] Visayas Grid-09/08/2023 04:34: Weather Update: Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CVIS
9/8/2023 1:02:32 AM | Luzon Grid-09/08/2023 01:02: Kalayaan Unit 3 online as pump at 0100H (Unplanned Outage) [WEBSMS] | CLUZ
9/8/2023 12:47:52 AM | Mindanao Grid-09/08/2023 00:49: Baloi - Aurora 138kV Line tripped at 0020H. (Unplanned Outage). [WEBSMS] | CMIN
9/8/2023 12:25:57 AM | Luzon Grid-09/08/2023 00:25: Kalayaan Unit 3 (157MW) tripped as pump at 0020H. Highest frequency 60.45Hz (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2023 11:11:27 PM | Luzon Grid-09/07/2023 23:11: Currimao - Paguludan 69kV Line (CO) restored at 2307H (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2023 10:53:04 PM | Mindanao Grid-09/07/2023 22:55: Pulangi HEP Unit 1 shutdown at 2234H. (Reserve shutdown to store water in its reservoir in preparation for drawdown activity on 10 Sep 2023). [WEBSMS] | CMIN
9/7/2023 9:21:54 PM | Mindanao Grid-09/07/2023 21:23: WMPC DG05 shutdown at 2113H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
9/7/2023 9:09:00 PM | Mindanao Grid-09/07/2023 21:11: Lake Mainit HEPP online at 2059H. (Unplanned Outage) [WEBSMS] | CMIN
9/7/2023 9:07:28 PM | Mindanao Grid-09/07/2023 21:09: Pulangi 4 Unit #1 online at 2054H from PMS (Non-GOMP). Follow RTD. (Planned Outage) [WEBSMS] | CMIN
9/7/2023 8:40:25 PM | Mindanao Grid-09/07/2023 20:42: Corrected: Butuan-Santiago 69kV Line tripped at 1931H resulted to tripping/isolation of ASIGA HEPP with 3.6MW gross generation. Frequency=60.2Hz. Unplanned Outage [WEBSMS] | CMIN
9/7/2023 8:39:18 PM | Mindanao Grid-09/07/2023 20:41: Corrected: Butuan-Santiago 69kV Line tripped at 1931H resulted to tripping/isolation of Lake Mainit HEPP with 10.5MW gross generation. Frequency=60.2Hz. Unplanned Outage [WEBSMS] | CMIN
9/7/2023 8:32:12 PM | Mindanao Grid-09/07/2023 20:34: ASIGA HEPP Online at 1953H. (Unplanned Outage) [WEBSMS] | CMIN
9/7/2023 7:53:24 PM | Luzon Grid-09/07/2023 19:53: Currimao - Paguludan 69kV Line (CO) de-energized at 1952H (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2023 7:47:50 PM | Mindanao Grid-09/07/2023 19:49: Butuan-Santiago 69kV Line tripped at 1931H resulted to tripping/isolation of ASIGA HEPP with 3.6MW gross generation. Frequency=60.2MW. Unplanned Outage [WEBSMS] | CMIN
9/7/2023 7:46:19 PM | Mindanao Grid-09/07/2023 19:48: Butuan-Santiago 69kV Line tripped at 1931H resulted to tripping/isolation of Lake Mainit HEPP with 10.5MW gross generation. Frequency=60.2MW. Unplanned Outage [WEBSMS] | CMIN
9/7/2023 7:34:36 PM | Mindanao Grid-09/07/2023 19:36: WMPC DG10 shutdown at 1922H, from MO dispatched. Follow RTD. [WEBSMS] | CMIN
9/7/2023 6:28:51 PM | Luzon Grid-09/07/2023 18:28: San Juan-Calauan 230KV line 2 restored at 1828H (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2023 6:21:49 PM | [NSO Update] Visayas Grid-09/07/2023 18:19: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2533MW, PK=2194MW, RR=88MW, NetOpMargin: EVE=251 Highest Unit O/L: THVI 1 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @285MW, PGPP1 @74MW, TPC-Carmen @30MW [WEBSMS] | CVIS
9/7/2023 6:05:05 PM | [NSO Update] Mindanao Grid-09/07/2023 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2910MW, PK=2084MW, RR=58MW, NetOpMargin: EVE=767 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: FMP @123MW, MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @90MW, AG5 @30MW, AG6 @132MW, AG7 @27MW, PG4 @150MW [WEBSMS] | CMIN
9/7/2023 6:01:45 PM | [NSO Update] Luzon Grid-09/07/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13418MW, PK=10680MW, RR=421MW, NetOpMargin: EVE=2317 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC1 @315MW, MSLC2 @300MW, MSLC3 @170MW, SLPGC 1 @50MW SLPGC 2 @75MW, ILIJAN A @570MW [WEBSMS] | CLUZ
9/7/2023 5:39:40 PM | Mindanao Grid-09/07/2023 17:41: Euro Hydro (NBT) Online at 1730H. (Unplanned Outage) [WEBSMS] | CMIN
9/7/2023 5:25:11 PM | Visayas Grid-09/07/2023 17:24: DaanBantayan Lanao 69 KV Line restored at 1723H, delayed clearance from DU. (Unplanned Outage) [WEBSMS] | CVIS
9/7/2023 5:15:40 PM | Visayas Grid-09/07/2023 17:15: Lapulapu Pajo 69 KV feeder restored at 1701H. (Unplanned Outage). [WEBSMS] | CVIS
9/7/2023 5:11:57 PM | [NSO Update] Mindanao Grid-09/07/2023 17:14: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1703H with power going to Visayas. [WEBSMS] | CMIN
9/7/2023 5:10:57 PM | [NSO Update] Visayas Grid-09/07/2023 17:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1703H with power going to Visayas. [WEBSMS] | CVIS
9/7/2023 5:10:12 PM | [NSO Update] Mindanao Grid-09/07/2023 17:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1652H from reverse power direction. [WEBSMS] | CMIN
9/7/2023 5:08:32 PM | [NSO Update] Visayas Grid-09/07/2023 17:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1652H from reverse power direction. [WEBSMS] | CVIS
9/7/2023 4:50:29 PM | Mindanao Grid-09/07/2023 16:52: WMPC DG10 shutdown at 1613H. End of RPS-System Voltage Requirement. [WEBSMS] | CMIN
9/7/2023 4:47:50 PM | Visayas Grid-09/07/2023 16:47: TVI U2 tripped at 1634H with a load 166 MW activating Leyte-Cebu SCOPS isolating Lanao and Pajo fdr with a total load of 58.31 MW. [WEBSMS] | CVIS
9/7/2023 3:41:41 PM | Mindanao Grid-09/07/2023 15:43: TM1 Unit #1 shutdown at 1441H. Follow RTD. [WEBSMS] | CMIN
9/7/2023 3:08:00 PM | Mindanao Grid-09/07/2023 15:10: Euro Hydro (NBT) with 0.9MW generation tripped/isolated at 1454H, affected by the outage of NORDECO System 69kV line. (Unplanned Outage) [WEBSMS] | CMIN
9/7/2023 2:51:21 PM | Mindanao Grid-09/07/2023 14:53: WMPC DG07 shutdown at 1444H, from MO dispatched. Follow RTD. [WEBSMS] | CMIN
9/7/2023 2:27:18 PM | Mindanao Grid-09/07/2023 14:29: WMPC DG07 online at 1409H. MO Dispatched. Follow RTD. [WEBSMS] | CMIN
9/7/2023 2:20:41 PM | Mindanao Grid-09/07/2023 14:22: TM1 Unit #1 Online at 1410H. Follow RTD. [WEBSMS] | CMIN
9/7/2023 1:42:46 PM | Luzon Grid-09/07/2023 13:42: San Juan-Calauan 230KV line 2 auto-tripped at 1336H (Unplanned Outage). [WEBSMS] | CLUZ
9/7/2023 1:21:07 PM | Luzon Grid-09/07/2023 13:21: Ambuklao-Bayombong 230kV line 1 was restored at 1319H (Unplanned Outage). [WEBSMS] | CLUZ
9/7/2023 12:56:25 PM | [NSO Update] Visayas Grid-09/07/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2681MW, PK=2329MW, RR=92MW, NetOpMargin: PM=260, EVE=265 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @285MW, PGPP1 @74MW, TPC-Carmen @30MW [WEBSMS] | CVIS
9/7/2023 12:55:43 PM | [NSO Update] Mindanao Grid-09/07/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2950MW, PK=2215MW, RR=60MW, NetOpMargin: PM=675, EVE=727 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @90MW, AG5 @30MW, AG6 @132MW, AG7 @27MW, PG4 @150MW [WEBSMS] | CMIN
9/7/2023 12:54:04 PM | Luzon Grid-09/07/2023 12:54: SLPGC Unit 1 online at 1251H (Unplanned Outage). [WEBSMS] | CLUZ
9/7/2023 12:52:39 PM | [NSO Update] Luzon Grid-09/07/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14317MW, PK=11439MW, RR=457MW, NetOpMargin: PM=2421, EVE=2781 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC1 @315MW, MSLC2 @300MW, MSLC3 @170MW, SLPGC 2 @85MW, ILIJAN A @570MW [WEBSMS] | CLUZ
9/7/2023 11:18:50 AM | [NSO Update] Mindanao Grid-09/07/2023 11:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1040H with power going to Mindanao. [WEBSMS] | CMIN
9/7/2023 11:18:37 AM | [NSO Update] Visayas Grid-09/07/2023 11:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1040H with power going to Mindanao. [WEBSMS] | CVIS
9/7/2023 10:59:57 AM | Mindanao Grid-09/07/2023 11:02: WMPC DG10 cut-in at 1057H; RPS - System Voltage Requirement [WEBSMS] | CMIN
9/7/2023 10:29:18 AM | [NSO Update] Mindanao Grid-09/07/2023 10:31: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1027H from forward power direction. [WEBSMS] | CMIN
9/7/2023 10:28:40 AM | [NSO Update] Visayas Grid-09/07/2023 10:28: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1027H from forward power direction. [WEBSMS] | CVIS
9/7/2023 9:33:21 AM | Mindanao Grid-09/07/2023 09:35: WMPC DG05 running as RPS tripped with 6.6MW load at 0903H. Synchronized back at 0917H. (Unplanned Outage) [WEBSMS] | CMIN
9/7/2023 8:43:52 AM | Luzon Grid-09/07/2023 08:43: For info: The attempt to re-energize the tripped Ambuklao-Bayombong 230kV line 1 at 0832H through Bayombong side failed with the same faulty phase, phase B. [WEBSMS] | CLUZ
9/7/2023 8:31:33 AM | Luzon Grid-09/07/2023 08:31: SLPGC Unit 1 tripped at 0825H from 77MW load. (Unplanned Outage) [WEBSMS] | CLUZ
9/7/2023 5:54:18 AM | [NSO Update] Luzon Grid-09/07/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14305MW, PK=11031MW, RR=444MW, NetOpMargin: AM=2830, PM=2585, EVE=2951 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: Calaca 1 @ 210MW, Calaca 2 @ 173MW, GNPD 1 @ 630MW, Masinloc 1 @ 300MW, Masinloc 2 @ 290MW, Masinloc 3 @ 170MW, SLPGC 1 @ 70MW, SLPGC 2 @ 80MW, Ilijan A @ 570MW [WEBSMS] | CLUZ
9/7/2023 5:53:23 AM | [NSO Update] Visayas Grid-09/07/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2733MW, PK=2308MW, RR=89MW, NetOpMargin: AM=336, PM=274, EVE=269 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 290MW, PGPP1 @ 74MW [WEBSMS] | CVIS
9/7/2023 5:52:26 AM | [NSO Update] Mindanao Grid-09/07/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3075MW, PK=2168MW, RR=60MW, NetOpMargin: AM=847, PM=698, EVE=710 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @90MW, AG5 @30MW, AG6 @132MW, AG7 @27MW, PG4 @150MW [WEBSMS] | CMIN
9/7/2023 4:13:10 AM | [NSO Update] Visayas Grid-09/07/2023 04:13: Weather Update: Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CVIS
9/7/2023 4:12:53 AM | [NSO Update] Luzon Grid-09/07/2023 04:13: Weather Update: Southwest Monsoon affecting the western sections of Northern and Central Luzon. [WEBSMS] | CLUZ
9/7/2023 2:32:01 AM | Mindanao Grid-09/07/2023 02:34: WMPC DG07 Shutdown at 1613H (09/06/2023). From RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/6/2023 9:21:50 PM | Mindanao Grid-09/06/2023 21:24: WMPC DG05 shutdown at 2113H. End of RPS. [WEBSMS] | CMIN
9/6/2023 8:53:06 PM | Luzon Grid-09/06/2023 20:53: San Jose-Angat 115kV line 4 restored at 2052H. (Unplanned Outage) [WEBSMS] | CLUZ
9/6/2023 7:42:04 PM | Luzon Grid-09/06/2023 19:42: San Jose-Angat 115kV line 4 tripped at 1939H. (Unplanned Outage) [WEBSMS] | CLUZ
9/6/2023 6:55:15 PM | [NSO Update] Mindanao Grid-09/06/2023 18:57: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1850H with power going to Visayas. [WEBSMS] | CMIN
9/6/2023 6:55:01 PM | [NSO Update] Visayas Grid-09/06/2023 18:55: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1850H with power going to Visayas. [WEBSMS] | CVIS
9/6/2023 6:40:33 PM | [NSO Update] Mindanao Grid-09/06/2023 18:42: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1840H from reverse power direction. [WEBSMS] | CMIN
9/6/2023 6:40:18 PM | [NSO Update] Visayas Grid-09/06/2023 18:40: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1840H from reverse power direction. [WEBSMS] | CVIS
9/6/2023 5:46:28 PM | [NSO Update] Luzon Grid-09/06/2023 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13546MW, PK=10385MW, RR=420MW, NetOpMargin: EVE=2741 Highest Unit O/L: GNPD 2 @ 668MW Derated Plant: Calaca 1 @ 170MW, Calaca 2 @ 173MW, GNPD 1 @ 660MW, Masinloc 1 @ 280MW, Masinloc 2 @ 280MW, Masinloc 3 @ 160MW, SLPGC 1 @ 70MW, SLPGC 2 @ 80MW, Ilijan A @ 570MW [WEBSMS] | CLUZ
9/6/2023 5:44:20 PM | [NSO Update] Mindanao Grid-09/06/2023 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2907MW, PK=2091MW, RR=53MW, NetOpMargin: EVE=763 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @90MW, AG5 @30MW, AG6 @132MW, AG7 @27MW, PG4 @105MW [WEBSMS] | CMIN
9/6/2023 5:43:57 PM | [NSO Update] Visayas Grid-09/06/2023 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2551MW, PK=2214MW, RR=86MW, NetOpMargin: EVE=251 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 284MW, PGPP1 @ 74MW, PDPP3-E @ 8MW, PDPP3-G @ 10MW, PDPP3-H @ 9MW [WEBSMS] | CVIS
9/6/2023 3:39:22 PM | Luzon Grid-09/06/2023 15:39: Naga-Labo 230kV line 1 was restored at 1538H (Planned Outage). [WEBSMS] | CLUZ
9/6/2023 1:05:32 PM | [NSO Update] Mindanao Grid-09/06/2023 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2941MW, PK=2207MW, RR=55MW, NetOpMargin: PM=679, EVE=840 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MCO @270MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @90MW, AG5 @30MW, AG6 @132MW, AG7 @27MW, PG4 @105MW [WEBSMS] | CMIN
9/6/2023 1:04:54 PM | [NSO Update] Visayas Grid-09/06/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2709MW, PK=2367MW, RR=92MW, NetOpMargin: PM=251, EVE=251 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @280MW, PGPP1 @74MW, TPC-Carmen @30MW [WEBSMS] | CVIS
9/6/2023 1:01:11 PM | [NSO Update] Luzon Grid-09/06/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14002MW, PK=10954MW, RR=431MW, NetOpMargin: PM=2616, EVE=2828 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CLC1 @170MW, CLC2 @173MW, GNPD 1 @600MW, MSLC1 @280MW, MSLC2 @280MW, MSLC3 @160MW, SCPC 3 @120MW, SLPGC 1 @60MW, SLPGC 2 @85MW, ILIJAN A @570MW [WEBSMS] | CLUZ
9/6/2023 10:52:44 AM | Mindanao Grid-09/06/2023 10:55: WMPC DG07 cut-in at 1051H; RPS - System Voltage Requirement [WEBSMS] | CMIN
9/6/2023 10:46:36 AM | Mindanao Grid-09/06/2023 10:48: New Bataan EURO Hydro cut-in at 0945H. (Unplanned Outage) [WEBSMS] | CMIN
9/6/2023 9:58:06 AM | Mindanao Grid-09/06/2023 10:00: New Bataan EURO Hydro isolated with load of 1.1MW at 0937H. (Unplanned Outage) [WEBSMS] | CMIN
9/6/2023 9:45:12 AM | [NSO Update] Mindanao Grid-09/06/2023 09:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0943H with power going to Mindanao. [WEBSMS] | CMIN
9/6/2023 9:44:47 AM | [NSO Update] Visayas Grid-09/06/2023 09:44: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0943H with power going to Mindanao. [WEBSMS] | CVIS
9/6/2023 9:31:13 AM | Mindanao Grid-09/06/2023 09:33: WMPC DG05 cut-in at 0923H; RPS - System Voltage Requirement [WEBSMS] | CMIN
9/6/2023 9:24:24 AM | Visayas Grid-09/06/2023 09:24: KSPC Unit 1 synchronized at 0922H. (Planned outage) [WEBSMS] | CVIS
9/6/2023 7:47:17 AM | [NSO Update] Visayas Grid-09/06/2023 07:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0734H from forward power direction. [WEBSMS] | CVIS
9/6/2023 7:46:56 AM | [NSO Update] Mindanao Grid-09/06/2023 07:49: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0734H from forward power direction. [WEBSMS] | CMIN
9/6/2023 6:40:07 AM | Luzon Grid-09/06/2023 06:40: Naga-Labo 230kV line 1 was de-energized at 0637H (Planned Outage). [WEBSMS] | CLUZ
9/6/2023 5:56:40 AM | [NSO Update] Luzon Grid-09/06/2023 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14186MW, PK=10426MW, RR=421MW, NetOpMargin: AM=3339, PM=2745, EVE=2683 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC1 @180MW, CLC2 @173MW, MSLC1 @280MW, MSLC2 @280MW, MSLC3 @160MW, SCPC 3 @110MW, SLPGC 1 @75MW, SLPGC 2 @50MW, ILIJAN A @570MW [WEBSMS] | CLUZ
9/6/2023 5:48:26 AM | [NSO Update] Luzon Grid-09/06/2023 05:48: at 0400H Weather Disturbance Alert Notice (WDAN) has been lifted today, September 6, 2023 at 0400H. Tropical Depression "INENG" is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Tropical Depression INENG was estimated based on all available data at 1,240 km East Northeast of Extreme Northern Luzon (25.1 �N, 133.0 �E ) (OUTSIDE PAR). [WEBSMS] | CLUZ
9/6/2023 5:46:01 AM | [NSO Update] Mindanao Grid-09/06/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3071MW, PK=2211MW, RR=55MW, NetOpMargin: AM=804, PM=765, EVE=712 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: FMP @123MW, MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @90MW, AG5 @30MW, AG6 @132MW, AG7 @27MW, PG4 @105MW [WEBSMS] | CMIN
9/6/2023 5:45:20 AM | [NSO Update] Visayas Grid-09/06/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2636MW, PK=2284MW, RR=88.8MW, NetOpMargin: AM=263, PM=271, EVE=266 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 302MW, PGPP1 @ 74MW [WEBSMS] | CVIS
9/6/2023 5:17:47 AM | [NSO Update] Mindanao Grid-09/06/2023 05:20: Weather Disturbance Alert Notice (WDAN) has been lifted today, September 6, 2023 at 0400H. Tropical Depression "INENG" is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Tropical Depression INENG was estimated based on all available data at 1,240 km East Northeast of Extreme Northern Luzon (25.1 �N, 133.0 �E ) (OUTSIDE PAR). [WEBSMS] | CMIN
9/6/2023 5:17:05 AM | [NSO Update] Visayas Grid-09/06/2023 05:17: Weather Disturbance Alert Notice (WDAN) has been lifted today, September 6, 2023 at 0400H. Tropical Depression "INENG" is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Tropical Depression INENG was estimated based on all available data at 1,240 km East Northeast of Extreme Northern Luzon (25.1 �N, 133.0 �E ) (OUTSIDE PAR). [WEBSMS] | CVIS
9/5/2023 11:06:34 PM | [NSO Update] Mindanao Grid-09/05/2023 23:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 2302H with power going to Visayas. [WEBSMS] | CMIN
9/5/2023 11:04:44 PM | [NSO Update] Visayas Grid-09/05/2023 23:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 2302H with power going to Visayas. [WEBSMS] | CVIS
9/5/2023 10:07:03 PM | Mindanao Grid-09/05/2023 22:09: EURO Hydro cut-in at 1940H. (Unplanned Outage) [WEBSMS] | CMIN
9/5/2023 10:05:55 PM | Mindanao Grid-09/05/2023 22:08: EURO Hydro isolated with load of 1.1MW at 1910H. (Unplanned Outage) [WEBSMS] | CMIN
9/5/2023 9:25:59 PM | Mindanao Grid-09/05/2023 21:28: WMPC DG05 shutdown at 2113H. End of RPS [WEBSMS] | CMIN
9/5/2023 8:49:38 PM | [NSO Update] Mindanao Grid-09/05/2023 20:51: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 2045H from forward power direction. [WEBSMS] | CMIN
9/5/2023 8:48:44 PM | [NSO Update] Visayas Grid-09/05/2023 20:48: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 2045H from forward power direction. [WEBSMS] | CVIS
9/5/2023 7:58:20 PM | Mindanao Grid-09/05/2023 20:00: ASIGA Hydro online at 1720H (Unplanned Outage) [WEBSMS] | CMIN
9/5/2023 7:10:18 PM | Mindanao Grid-09/05/2023 19:12: WMPC DG07 shutdown at 1614H. End of RPS [WEBSMS] | CMIN
9/5/2023 6:16:25 PM | [NSO Update] Mindanao Grid-09/05/2023 18:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1813H with power going to Visayas. [WEBSMS] | CMIN
9/5/2023 6:15:02 PM | [NSO Update] Visayas Grid-09/05/2023 18:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1813H with power going to Visayas. [WEBSMS] | CVIS
9/5/2023 6:09:46 PM | [NSO Update] Mindanao Grid-09/05/2023 18:12: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2889MW, PK=2132MW, RR=53MW, NetOpMargin: EVE=704 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: FMP @123MW, MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @98MW, AG5 @34MW, AG6 @141MW, AG7 @28MW, PG4 @105MW [WEBSMS] | CMIN
9/5/2023 6:07:28 PM | [NSO Update] Visayas Grid-09/05/2023 18:05: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2514MW, PK=2171MW, RR=85.2MW, NetOpMargin: EVE=257 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 295MW, PGPP1 @ 74MW [WEBSMS] | CVIS
9/5/2023 5:59:38 PM | [NSO Update] Luzon Grid-09/05/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13325MW, PK=9917MW, RR=390MW, NetOpMargin: EVE=3018 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC1 @210MW, CLC2 @173MW, MSLC1 @280MW, MSLC2 @280MW, MSLC3 @160MW, SLPGC 1 @75MW, SLPGC 2 @75MW, SCPC 3 @110MW, Ilijan A @575MW [WEBSMS] | CLUZ
9/5/2023 5:58:34 PM | Mindanao Grid-09/05/2023 18:00: ASIGA Hydro online at 1040H (Unplanned Outage) [WEBSMS] | CMIN
9/5/2023 5:57:22 PM | Mindanao Grid-09/05/2023 17:59: LAKE MAINIT Hydro online at 1716H (Unplanned Outage) [WEBSMS] | CMIN
9/5/2023 5:38:58 PM | Mindanao Grid-09/05/2023 17:41: WMPC DG09 declared available at 1730H (from unplanned outage) [WEBSMS] | CMIN
9/5/2023 5:19:08 PM | [NSO Update] Luzon Grid-09/05/2023 17:19: Weather Update: At 3:00 PM today, the center of Tropical Depression "INENG" was estimated based on all available data at 990 km East of Extreme Northern Luzon (21.9�N, 131.4�E) with maximum sustained winds of 45 km/h near the center and gustiness of up to 55 km/h. It is moving Northeastward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
9/5/2023 5:18:04 PM | [NSO Update] Mindanao Grid-09/05/2023 17:20: Weather Update: At 3:00 PM today, the center of Tropical Depression "INENG" was estimated based on all available data at 990 km East of Extreme Northern Luzon (21.9�N, 131.4�E) with maximum sustained winds of 45 km/h near the center and gustiness of up to 55 km/h. It is moving Northeastward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CMIN
9/5/2023 5:17:17 PM | [NSO Update] Visayas Grid-09/05/2023 17:17: Weather Update: At 3:00 PM today, the center of Tropical Depression "INENG" was estimated based on all available data at 990 km East of Extreme Northern Luzon (21.9�N, 131.4�E) with maximum sustained winds of 45 km/h near the center and gustiness of up to 55 km/h. It is moving Northeastward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CVIS
9/5/2023 5:04:57 PM | [NSO Update] Mindanao Grid-09/05/2023 17:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1703H from reverse power direction. [WEBSMS] | CMIN
9/5/2023 5:04:11 PM | [NSO Update] Visayas Grid-09/05/2023 17:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1703H from reverse power direction. [WEBSMS] | CVIS
9/5/2023 4:48:26 PM | Mindanao Grid-09/05/2023 16:50: WMPC DG05 cut-in at 1633H; RPS - System Voltage Requirement; As replacement for WMPC DG09 due to fuel leak at capillary tube). [WEBSMS] | CMIN
9/5/2023 4:43:02 PM | Mindanao Grid-09/05/2023 16:45: WMPC DG09 emergency shutdown at 1633H due to fuel leak at capillary tube. (Unplanned Outage) [WEBSMS] | CMIN
9/5/2023 3:43:24 PM | Mindanao Grid-09/05/2023 15:45: NagaMin 138kV Bus 1 restored at 1528H. (Planned Outage) [WEBSMS] | CMIN
9/5/2023 2:00:05 PM | Mindanao Grid-09/05/2023 14:02: NagaMin Transformer No. 2 restored at 1358H. (Unplanned Outage) [WEBSMS] | CMIN
9/5/2023 1:52:16 PM | Mindanao Grid-09/05/2023 13:54: LAKE MAINIT Hydro tripped with 10.7MW load at 1344H. (Unplanned Outage) [WEBSMS] | CMIN
9/5/2023 1:51:16 PM | Mindanao Grid-09/05/2023 13:53: ASIGA Hydro tripped with 2.8MW load at 1344H. (Unplanned Outage) [WEBSMS] | CMIN
9/5/2023 12:53:49 PM | [NSO Update] Luzon Grid-09/05/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13808MW, PK=10557MW, RR=420MW, NetOpMargin: PM=2831, EVE=3057 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 200MW, Calaca 2 @ 173MW, Masinloc 1 @ 280MW, Masinloc 2 @ 280MW, Masinloc 3 @ 160MW, SLPGC 1 @ 70MW, SLPGC 2 @ 70MW, SCPC 3 @ 110MW, Ilijan A @ 575MW [WEBSMS] | CLUZ
9/5/2023 12:51:48 PM | [NSO Update] Visayas Grid-09/05/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2635MW, PK=2291MW, RR=92MW, NetOpMargin: PM=252, EVE=251 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 295MW, PGPP1 @ 74MW [WEBSMS] | CVIS
9/5/2023 12:50:58 PM | [NSO Update] Mindanao Grid-09/05/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3004MW, PK=2292MW, RR=55MW, NetOpMargin: PM=657, EVE=640 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @98MW, AG5 @34MW, AG6 @141MW, AG7 @28MW, PG4 @105MW [WEBSMS] | CMIN
9/5/2023 11:21:11 AM | Mindanao Grid-09/05/2023 11:23: ASIGA Hydro online at 1030H (Unplanned Outage) [WEBSMS] | CMIN
9/5/2023 11:11:57 AM | Mindanao Grid-09/05/2023 11:14: LAKE MAINIT Hydro online at 1040H (Unplanned Outage) [WEBSMS] | CMIN
9/5/2023 11:09:12 AM | Mindanao Grid-09/05/2023 11:11: NagaMin 138kV Bus 1 de-energized at 1037H. (Planned Outage) [WEBSMS] | CMIN
9/5/2023 11:06:47 AM | Mindanao Grid-09/05/2023 11:09: FDC Unit 2 cut-out at 10.52H with remaining gross generation of 17.7MW. Reason: Emergency maintenance re: tube leak at boiler backpass. [WEBSMS] | CMIN
9/5/2023 11:04:57 AM | Luzon Grid-09/05/2023 11:05: Ilijan PCB 9-02CB04ILJ energized at 1103H (Customer owned - Unplanned Outage) [WEBSMS] | CLUZ
9/5/2023 10:34:45 AM | Mindanao Grid-09/05/2023 10:37: NagaMin Transformer No. 2 tripped at 1016H. (Unplanned Outage) [WEBSMS] | CMIN
9/5/2023 10:21:35 AM | Mindanao Grid-09/05/2023 10:23: NagaMin - Zamboanga 138kV L1 restored at 0958H. (Planned Outage) [WEBSMS] | CMIN
9/5/2023 10:14:56 AM | Luzon Grid-09/05/2023 10:15: Dasmarinas-Ternate 115kV line(Customer Owned) autotripped/autoreclosed at 1011H (Unplanned Outage) [WEBSMS] | CLUZ
9/5/2023 9:33:13 AM | Mindanao Grid-09/05/2023 09:35: ASIGA Hydro with gross generation of 2.83MW isolated at 0925H affected by forced outage of Butuan-Santiago 69 kV line. [WEBSMS] | CMIN
9/5/2023 9:31:56 AM | Mindanao Grid-09/05/2023 09:34: Lake Mainit Hydro with gross generation of 10.6MW isolated at 0925H affected by forced outage of Butuan-Santiago 69 kV line. [WEBSMS] | CMIN
9/5/2023 9:08:01 AM | Mindanao Grid-09/05/2023 09:10: WMPC DG07 cut-in at 09000H; RPS - System Voltage Requirement [WEBSMS] | CMIN
9/5/2023 9:07:31 AM | Mindanao Grid-09/05/2023 09:09: WMPC DG09 cut-in at 0850H; RPS - System Voltage Requirement [WEBSMS] | CMIN
9/5/2023 9:03:14 AM | [NSO Update] Visayas Grid-09/05/2023 09:03: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0902H with power going to Mindanao. [WEBSMS] | CVIS
9/5/2023 9:03:01 AM | [NSO Update] Mindanao Grid-09/05/2023 09:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0902H with power going to Mindanao. [WEBSMS] | CMIN
9/5/2023 8:51:50 AM | [NSO Update] Mindanao Grid-09/05/2023 08:54: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0851H from forward power direction. [WEBSMS] | CMIN
9/5/2023 8:51:30 AM | [NSO Update] Visayas Grid-09/05/2023 08:51: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0851H from forward power direction. [WEBSMS] | CVIS
9/5/2023 6:54:40 AM | Mindanao Grid-09/05/2023 06:56: NagaMin - Zamboanga 138kV L1de-energized at 0648H. (Planned Outage) [WEBSMS] | CMIN
9/5/2023 6:51:07 AM | [NSO Update] Mindanao Grid-09/05/2023 06:53: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0650H with power going to Visayas. [WEBSMS] | CMIN
9/5/2023 6:50:37 AM | [NSO Update] Visayas Grid-09/05/2023 06:50: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0650H with power going to Visayas. [WEBSMS] | CVIS
9/5/2023 6:40:00 AM | [NSO Update] Mindanao Grid-09/05/2023 06:42: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0639H from reverse power direction. [WEBSMS] | CMIN
9/5/2023 6:39:44 AM | [NSO Update] Visayas Grid-09/05/2023 06:39: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0639H from reverse power direction. [WEBSMS] | CVIS
9/5/2023 5:52:18 AM | [NSO Update] Luzon Grid-09/05/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14030MW, PK=10287MW, RR=417MW, NetOpMargin: AM=3326, PM=3027, EVE=3280 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @173MW, MASINLOC 1 @280MW, MASINLOC 2 @280MW, MASINLOC 3 @150MW, SLPGC 1 @70MW, SLPGC 2 @70MW, ILIJAN A @575MW [WEBSMS] | CLUZ
9/5/2023 5:41:29 AM | [NSO Update] Visayas Grid-09/05/2023 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2619MW, PK=2270MW, RR=88MW, NetOpMargin: AM=261, PM=254, EVE=256 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 300MW, PGPP1 @ 74MW [WEBSMS] | CVIS
9/5/2023 5:36:14 AM | [NSO Update] Mindanao Grid-09/05/2023 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3218MW, PK=2334MW, RR=55MW, NetOpMargin: AM=828, PM=826, EVE=811 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @98MW, AG5 @34MW, AG6 @141MW, AG7 @28MW, PG4 @105MW [WEBSMS] | CMIN
9/5/2023 5:14:55 AM | [NSO Update] Visayas Grid-09/05/2023 05:14: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0503H with power going to Mindanao. [WEBSMS] | CVIS
9/5/2023 5:14:35 AM | [NSO Update] Mindanao Grid-09/05/2023 05:16: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0503H with power going to Mindanao. [WEBSMS] | CMIN
9/5/2023 4:55:40 AM | [NSO Update] Visayas Grid-09/05/2023 04:55: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0451H from forward power direction. [WEBSMS] | CVIS
9/5/2023 4:55:34 AM | [NSO Update] Mindanao Grid-09/05/2023 04:57: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0451H from forward power direction. [WEBSMS] | CMIN
9/5/2023 4:53:47 AM | [NSO Update] Luzon Grid-09/05/2023 04:54: Weather Advisory: At 3:00AM today, the center of Tropical Depression "INENG" was estimated based on all available data at 915 km East of Extreme Northern Luzon (21.3N, 130.7E) with maximum sustained winds of 45km/h near the center and gustiness of up to 55 km/h. It is moving Northward slowly. Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
9/5/2023 4:53:23 AM | [NSO Update] Mindanao Grid-09/05/2023 04:55: Weather Advisory: At 3:00AM today, the center of Tropical Depression "INENG" was estimated based on all available data at 915 km East of Extreme Northern Luzon (21.3N, 130.7E) with maximum sustained winds of 45km/h near the center and gustiness of up to 55 km/h. It is moving Northward slowly. Southwest Monsoon affecting the country. [WEBSMS] | CMIN
9/5/2023 4:53:19 AM | [NSO Update] Visayas Grid-09/05/2023 04:53: Weather Advisory: At 3:00AM today, the center of Tropical Depression "INENG" was estimated based on all available data at 915 km East of Extreme Northern Luzon (21.3N, 130.7E) with maximum sustained winds of 45km/h near the center and gustiness of up to 55 km/h. It is moving Northward slowly. Southwest Monsoon affecting the country. [WEBSMS] | CVIS
9/5/2023 4:38:19 AM | [NSO Update] Luzon Grid-09/05/2023 04:38: Weather Disturbance Alert Notice (WDAN) is issued at 0400H. The Low-Pressure Area inside the PAR has developed into Tropical Depression "INENG". The center was estimated based on all available data at 915 km East of Extreme Northern Luzon (21.3N, 130.7E) with max. sustained winds of 45km/h near the center and gustiness of up to 55 km/h. It is moving Northward slowly. [WEBSMS] | CLUZ
9/5/2023 4:38:14 AM | [NSO Update] Visayas Grid-09/05/2023 04:38: Weather Disturbance Alert Notice (WDAN) is issued at 0400H. The Low-Pressure Area inside the PAR has developed into Tropical Depression "INENG". The center was estimated based on all available data at 915 km East of Extreme Northern Luzon (21.3N, 130.7E) with max. sustained winds of 45km/h near the center and gustiness of up to 55 km/h. It is moving Northward slowly. [WEBSMS] | CVIS
9/5/2023 4:38:12 AM | [NSO Update] Mindanao Grid-09/05/2023 04:40: Weather Disturbance Alert Notice (WDAN) is issued at 0400H. The Low-Pressure Area inside the PAR has developed into Tropical Depression "INENG". The center was estimated based on all available data at 915 km East of Extreme Northern Luzon (21.3N, 130.7E) with max. sustained winds of 45km/h near the center and gustiness of up to 55 km/h. It is moving Northward slowly. [WEBSMS] | CMIN
9/5/2023 12:04:55 AM | Mindanao Grid-09/05/2023 00:07: Pulangi IV Unit 1 cut-out at 0002H. (Planned Outage) [WEBSMS] | CMIN
9/4/2023 11:22:51 PM | Mindanao Grid-09/04/2023 23:25: FDC U2 synchronized at 2319H. (Unplanned Outage) [WEBSMS] | CMIN
9/4/2023 11:10:40 PM | Visayas Grid-09/04/2023 23:10: Cebu SS 138 kV Bus 1 energized at 2258H, activity completed. [WEBSMS] | CVIS
9/4/2023 11:04:22 PM | Mindanao Grid-09/04/2023 23:06: Matanao-Gensan 138KV L1 re-energized at 2131H & looped at Gensan SS at 2134H. Gensan SS 138KV Bus 2 re-energized at 2135H. From Unplanned Outage... [WEBSMS] | CMIN
9/4/2023 10:55:12 PM | Mindanao Grid-09/04/2023 22:57: Gensan SS 138KV Bus 2 and Matanao-Gensan 138KV L1 were both de-energized at 2126H to conduct emergency opening of 7-02DS07GSA & 7-02DS09GSA to isolate for repair the defective PCB 7-02CB08GSA, per request from Gensan SS mngmnt. Unplanned Outage... [WEBSMS] | CMIN
9/4/2023 10:12:25 PM | [NSO Update] Mindanao Grid-09/04/2023 22:14: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 2212H with power going to Visayas. [WEBSMS] | CMIN
9/4/2023 10:12:11 PM | [NSO Update] Visayas Grid-09/04/2023 22:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 2212H with power going to Visayas. [WEBSMS] | CVIS
9/4/2023 9:23:12 PM | Mindanao Grid-09/04/2023 21:25: WMPC DG09 Shutdown at 2114H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/4/2023 7:26:46 PM | Mindanao Grid-09/04/2023 19:29: TM1 Unit #1 shutdown at 1918H. Follow RTD. [WEBSMS] | CMIN
9/4/2023 6:10:33 PM | [NSO Update] Mindanao Grid-09/04/2023 18:12: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2976MW, PK=2175MW, RR=53MW, NetOpMargin: EVE=749 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @104MW, AG5 @38MW, AG6 @146MW, AG7 @30MW, PG4 @125MW [WEBSMS] | CMIN
9/4/2023 6:09:18 PM | [NSO Update] Visayas Grid-09/04/2023 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2520MW, PK=2128MW, RR=88MW, NetOpMargin: EVE=304 Highest Unit O/L: THVI 1& 2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @290MW, PGPP1 @74MW [WEBSMS] | CVIS
9/4/2023 6:03:37 PM | Mindanao Grid-09/04/2023 18:05: TM1 Unit #1 online at 1800H. Follow RTD. [WEBSMS] | CMIN
9/4/2023 6:03:10 PM | [NSO Update] Luzon Grid-09/04/2023 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13545MW, PK=9607MW, RR=384MW, NetOpMargin: EVE=3553 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: Calaca 1 @ 230MW, Calaca 2 @ 170MW, Masinloc 1 @ 280MW, Masinloc 2 @ 280MW, Masinloc 3 @ 120MW, SLPGC 1 @ 60MW, SLPGC 2 @ 75MW, Ilijan A @ 575MW [WEBSMS] | CLUZ
9/4/2023 5:19:29 PM | [NSO Update] Visayas Grid-09/04/2023 17:19: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1715H from reverse power direction. [WEBSMS] | CVIS
9/4/2023 5:19:07 PM | [NSO Update] Mindanao Grid-09/04/2023 17:21: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1715H from reverse power direction. [WEBSMS] | CMIN
9/4/2023 4:15:22 PM | Mindanao Grid-09/04/2023 16:17: WMPC DG07 Shutdown at 1614H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/4/2023 1:36:57 PM | Mindanao Grid-09/04/2023 13:39: NACSUR cut-in at 1335H as RTD. [WEBSMS] | CMIN
9/4/2023 1:28:33 PM | Mindanao Grid-09/04/2023 13:30: KEGI Tandag cut-in at 1325H as RTD. [WEBSMS] | CMIN
9/4/2023 1:23:55 PM | Mindanao Grid-09/04/2023 13:26: Peak Power SFN U2 cut-in at 1255H as RTD. [WEBSMS] | CMIN
9/4/2023 1:01:22 PM | [NSO Update] Mindanao Grid-09/04/2023 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3054MW, PK=2240MW, RR=55MW, NetOpMargin: PM=759, EVE=730 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @104MW, AG5 @38MW, AG6 @146MW, AG7 @30MW, PG4 @125MW [WEBSMS] | CMIN
9/4/2023 12:54:18 PM | [NSO Update] Luzon Grid-09/04/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13906MW, PK=9840MW, RR=427MW, NetOpMargin: PM=3639, EVE=3919 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 230MW, Calaca 2 @ 170MW, Masinloc 1 @ 280MW, Masinloc 2 @ 280MW, Masinloc 3 @ 80MW, SLPGC 1 @ 60MW, SLPGC 2 @ 75MW, Ilijan A @ 575MW [WEBSMS] | CLUZ
9/4/2023 12:54:15 PM | [NSO Update] Visayas Grid-09/04/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2649MW, PK=2306MW, RR=92MW, NetOpMargin: PM=250, EVE=250 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 290MW, PGPP1 @ 74MW [WEBSMS] | CVIS
9/4/2023 12:33:48 PM | Mindanao Grid-09/04/2023 12:36: Pulangi 4 HEP Unit 2 cut-in at 1215H. From OMCO due to low water inflow. [WEBSMS] | CMIN
9/4/2023 12:30:38 PM | Mindanao Grid-09/04/2023 12:32: Affected ALD feeders of CEPALCO, DPLC, and NGCP restored at 1211H, 1219H and 1226H, respectively. [WEBSMS] | CMIN
9/4/2023 12:17:13 PM | Mindanao Grid-09/04/2023 12:19: ALD occurred at NGCP, CEPALCO and DLPC feeders at 1202H due to tripping of FDC U2 with 103.5 MW. The lowest frequency recorded is 59.099 Hz. [WEBSMS] | CMIN
9/4/2023 11:20:24 AM | Mindanao Grid-09/04/2023 11:22: WMPC DG07 online at 1052H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/4/2023 10:59:40 AM | [NSO Update] Mindanao Grid-09/04/2023 11:01: Weather Disturbance Alert Notice (WDAN) has been lifted today, September 4, 2023 at 1100H. Typhoon "HANNA" is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon HANNA was estimated based on all available data at 360 km Northwest of Itbayat, Batanes (23.1 �N, 119.4 �E ) (OUTSIDE PAR). [WEBSMS] | CMIN
9/4/2023 10:58:49 AM | [NSO Update] Visayas Grid-09/04/2023 10:58: Weather Disturbance Alert Notice (WDAN) has been lifted today, September 4, 2023 at 1100H. Typhoon "HANNA" is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon HANNA was estimated based on all available data at 360 km Northwest of Itbayat, Batanes (23.1 �N, 119.4 �E ) (OUTSIDE PAR). [WEBSMS] | CVIS
9/4/2023 10:58:04 AM | [NSO Update] Luzon Grid-09/04/2023 10:58: Weather Disturbance Alert Notice (WDAN) has been lifted today, September 4, 2023 at 1100H. Typhoon "HANNA" is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon HANNA was estimated based on all available data at 360 km Northwest of Itbayat, Batanes (23.1 �N, 119.4 �E ) (OUTSIDE PAR). [WEBSMS] | CLUZ
9/4/2023 10:54:33 AM | Luzon Grid-09/04/2023 10:54: Subic SS 230kV Bus 1 restored at 1054H. (Planned Outage) [WEBSMS] | CLUZ
9/4/2023 9:30:34 AM | [NSO Update] Mindanao Grid-09/04/2023 09:32: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0930H with power going to Mindanao. [WEBSMS] | CMIN
9/4/2023 9:30:14 AM | [NSO Update] Visayas Grid-09/04/2023 09:30: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0930H with power going to Mindanao. [WEBSMS] | CVIS
9/4/2023 8:58:49 AM | Luzon Grid-09/04/2023 08:59: Subic SS 230kV Bus 1 de-energized at 0857H. (Planned Outage) [WEBSMS] | CLUZ
9/4/2023 8:55:09 AM | Mindanao Grid-09/04/2023 08:57: WMPC DG09 online at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/4/2023 8:31:29 AM | [NSO Update] Mindanao Grid-09/04/2023 08:33: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0831H from forward power direction. [WEBSMS] | CMIN
9/4/2023 8:31:03 AM | [NSO Update] Visayas Grid-09/04/2023 08:31: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0831H from forward power direction. [WEBSMS] | CVIS
9/4/2023 8:28:44 AM | Visayas Grid-09/04/2023 08:28: Cebu SS 138 kV Bus 1 de-energized at 0828H. (Planned Outage) [WEBSMS] | CVIS
9/4/2023 5:51:52 AM | [NSO Update] Visayas Grid-09/04/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2628MW, PK=2278MW, RR=90MW, NetOpMargin: AM=260, PM=252, EVE=253 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @290MW, PGPP1 @74MW [WEBSMS] | CVIS
9/4/2023 5:51:13 AM | [NSO Update] Mindanao Grid-09/04/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3191MW, PK=2159MW, RR=55MW, NetOpMargin: AM=977, PM=845, EVE=831 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @104MW, AG5 @38MW, AG6 @146MW, AG7 @30MW, PG4 @100MW [WEBSMS] | CMIN
9/4/2023 5:48:08 AM | [NSO Update] Luzon Grid-09/04/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14016MW, PK=10205MW, RR=419MW, NetOpMargin: AM=3392, PM=3289, EVE=3507 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @230MW, CLC2 @170MW, MSLC1 @280MW, MSLC2 @280MW, MSLC3 @80MW, SLPGC 1 @60MW, SLPGC 2 @75MW, ILIJAN A @575MW [WEBSMS] | CLUZ
9/4/2023 5:09:17 AM | Luzon Grid-09/04/2023 05:09: Muntinlupa (Sucat) - Sun Valley 115kV Line restored at 0507H (Unplanned Outage). [WEBSMS] | CLUZ
9/4/2023 4:21:18 AM | [NSO Update] Visayas Grid-09/04/2023 04:21: Weather Update: At 3:00 AM today, the center of the eye of Typhoon HANNA was estimated based on all available data at 265 km Northwest of Itbayat, Batanes (22.6 N, 120.2 E) with maximum sustained winds of 120 km/h near the center and gustiness of up to 150 km/h. It is moving South Southwestward slowly. Southwest Monsoon affecting the country. [WEBSMS] | CVIS
9/4/2023 4:20:42 AM | [NSO Update] Mindanao Grid-09/04/2023 04:22: Weather Update: At 3:00 AM today, the center of the eye of Typhoon HANNA was estimated based on all available data at 265 km Northwest of Itbayat, Batanes (22.6 N, 120.2 E) with maximum sustained winds of 120 km/h near the center and gustiness of up to 150 km/h. It is moving South Southwestward slowly. Southwest Monsoon affecting the country. [WEBSMS] | CMIN
9/4/2023 4:20:07 AM | [NSO Update] Luzon Grid-09/04/2023 04:20: Weather Update: At 3:00 AM today, the center of the eye of Typhoon HANNA was estimated based on all available data at 265 km Northwest of Itbayat, Batanes (22.6 N, 120.2 E) with maximum sustained winds of 120 km/h near the center and gustiness of up to 150 km/h. It is moving South Southwestward slowly. Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
9/4/2023 3:30:20 AM | Luzon Grid-09/04/2023 03:30: Muntinlupa (Sucat) - Sun Valley 115kV Line de-energized at 0327H (Unplanned Outage) [WEBSMS] | CLUZ
9/4/2023 12:25:09 AM | Visayas Grid-09/04/2023 00:25: CEDC Unit 2 shutdown at 0021H. (Planned Outage) [WEBSMS] | CVIS
9/3/2023 10:30:47 PM | Mindanao Grid-09/03/2023 22:33: Zamboanga-Pitogo 138KV L1 restored 2223H. P&E requested shutdown re: On-going rehab works of Zamboanga & Pitogo SS under MSRP Stage 1 Schedule 4. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
9/3/2023 6:42:48 PM | Mindanao Grid-09/03/2023 18:45: Jasaan-Nasipit 138KV L1 re-energized at 1744H and looped at Jasaan SS at 1745H. Emergency request from NTD-MSO. [WEBSMS] | CMIN
9/3/2023 5:44:33 PM | Luzon Grid-09/03/2023 17:44: San Manuel-UPSI San Manuel BESS 69kV Line restored at 1743H. (Planned Outage) [WEBSMS] | CLUZ
9/3/2023 5:40:19 PM | [NSO Update] Mindanao Grid-09/03/2023 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3040MW, PK=1978MW, RR=53MW, NetOpMargin: EVE=1009 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @75MW, AG4 @104MW, AG5 @38MW, AG6 @146MW, AG7 @30MW, PG4 @110MW [WEBSMS] | CMIN
9/3/2023 5:39:53 PM | [NSO Update] Visayas Grid-09/03/2023 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2424MW, PK=2051MW, RR=80MW, NetOpMargin: EVE=293 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @295MW, PGPP1 @74MW, TPC-THERMAL @82MW [WEBSMS] | CVIS
9/3/2023 5:37:57 PM | [NSO Update] Luzon Grid-09/03/2023 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13756MW, PK=8856MW, RR=315MW, NetOpMargin: EVE=4585 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 2 @160MW, MASINLOC 1 @280MW, MASINLOC 2 @280MW, MASINLOC 3 @150MW, ILIJAN A @575MW [WEBSMS] | CLUZ
9/3/2023 5:19:00 PM | Luzon Grid-09/03/2023 17:19: San Manuel-UPSI San Manuel BESS 69kV Line de-energized at 1717H. (Planned Outage) [WEBSMS] | CLUZ
9/3/2023 4:05:03 PM | [NSO Update] Mindanao Grid-09/03/2023 16:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1603H with power going to Visayas. [WEBSMS] | CMIN
9/3/2023 4:04:31 PM | [NSO Update] Visayas Grid-09/03/2023 16:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1603H with power going to Visayas. [WEBSMS] | CVIS
9/3/2023 4:02:22 PM | [NSO Update] Mindanao Grid-09/03/2023 16:04: Weather Advisory: At 3:00 PM today, the center of the eye of Typhoon "HANNA" {HAIKUI} was estimated based on all available data at 240 km North Northwest of Itbayat, Batanes (22.9�N, 121.3�E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving West Northwestward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CMIN
9/3/2023 4:02:20 PM | [NSO Update] Visayas Grid-09/03/2023 16:02: Weather Advisory: At 3:00 PM today, the center of the eye of Typhoon "HANNA" {HAIKUI} was estimated based on all available data at 240 km North Northwest of Itbayat, Batanes (22.9�N, 121.3�E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving West Northwestward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CVIS
9/3/2023 4:02:15 PM | [NSO Update] Luzon Grid-09/03/2023 16:02: Weather Advisory: At 3:00 PM today, the center of the eye of Typhoon "HANNA" {HAIKUI} was estimated based on all available data at 240 km North Northwest of Itbayat, Batanes (22.9�N, 121.3�E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving West Northwestward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
9/3/2023 3:49:18 PM | Mindanao Grid-09/03/2023 15:51: Lake Mainit Hydro (APC) synchronized at 1545H from FO. (Unplanned Outage) [WEBSMS] | CMIN
9/3/2023 3:39:13 PM | Luzon Grid-09/03/2023 15:39: Dona Imelda(Araneta)-Sta. Mesa 115kV Line 1 restored at 1537H. (Planned Outage) [WEBSMS] | CLUZ
9/3/2023 3:09:46 PM | Mindanao Grid-09/03/2023 15:12: LAKE Mainit Hydro (APC) tripped with 10.5MW load at 1505H. (Unplanned Outage) [WEBSMS] | CMIN
9/3/2023 3:04:22 PM | Luzon Grid-09/03/2023 15:04: Tayabas SS 600MVA T02 restored at 1504H. (Planned Outage) [WEBSMS] | CLUZ
9/3/2023 1:17:53 PM | [NSO Update] Mindanao Grid-09/03/2023 13:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1315H from forward power direction. [WEBSMS] | CMIN
9/3/2023 1:17:45 PM | [NSO Update] Visayas Grid-09/03/2023 13:17: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1315H from forward power direction. [WEBSMS] | CVIS
9/3/2023 12:45:32 PM | [NSO Update] Mindanao Grid-09/03/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3207MW, PK=1824MW, RR=55MW, NetOpMargin: PM=1328, EVE=1093 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @80MW, AG4 @104MW, AG5 @38MW, AG6 @146MW, AG7 @30MW, PG4 @110MW [WEBSMS] | CMIN
9/3/2023 12:45:00 PM | [NSO Update] Visayas Grid-09/03/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2655MW, PK=1897MW, RR=89MW, NetOpMargin: PM=669, EVE=312 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @300MW, PGPP1 @74MW, TPC-THERMAL @82MW [WEBSMS] | CVIS
9/3/2023 12:41:08 PM | [NSO Update] Luzon Grid-09/03/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14056MW, PK=8239MW, RR=335MW, NetOpMargin: PM=5482, EVE=3993 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @160MW, MASINLOC 1 @280MW, MASINLOC 2 @280MW, MASINLOC 3 @150MW, ILIJAN A @575MW [WEBSMS] | CLUZ
9/3/2023 11:41:33 AM | Visayas Grid-09/03/2023 11:41: Cebu - Compostela 138 kV Line 2 energized at 1140H. (Planned outage) [WEBSMS] | CVIS
9/3/2023 10:52:26 AM | Luzon Grid-09/03/2023 10:52: SLTEC 2 restored at 1030H. (Unplanned Outage) [WEBSMS] | CLUZ
9/3/2023 10:51:15 AM | Luzon Grid-09/03/2023 10:42: SLTEC 2 online at 1030H. (Unplanned Outage) [WEBSMS] | CLUZ
9/3/2023 10:51:15 AM | Mindanao Grid-09/03/2023 10:53: Zamboanga SS 138KV Bus 2 re-energized at 0957H. From P&E emergency shutdown request. FO / N-GOMP. [WEBSMS] | CMIN
9/3/2023 10:42:08 AM | Mindanao Grid-09/03/2023 10:44: Jasaan-Nasipit 138KV L1 de-energized at 0804H. NTD-MSO emergency request for the repair of OPGW cut strand between line span of tower 126 & 127. Non-GOMP. [WEBSMS] | CMIN
9/3/2023 10:41:00 AM | Visayas Grid-09/03/2023 10:40: Mandaue - Paknaan 69 kV Line energized at 1040H. (Planned outage) [WEBSMS] | CVIS
9/3/2023 10:39:41 AM | Visayas Grid-09/03/2023 10:39: Mandaue - NRA 69 kV Line 2 energized at 1038H. (Planned outage) [WEBSMS] | CVIS
9/3/2023 10:26:07 AM | Visayas Grid-09/03/2023 10:26: Cebu - Mandaue 138kV Line 2 energized at 1025H. (Planned outage) [WEBSMS] | CVIS
9/3/2023 9:44:45 AM | Luzon Grid-09/03/2023 09:44: Malaya SS 300MVA T01 restored at 0943H. (Planned Outage) [WEBSMS] | CLUZ
9/3/2023 8:31:49 AM | Luzon Grid-09/03/2023 08:31: Tayabas SS 600MVA T02 de-energized at 0831H. (Planned Outage) [WEBSMS] | CLUZ
9/3/2023 8:11:17 AM | Luzon Grid-09/03/2023 08:11: Dona Imelda(Araneta)-Sta. Mesa 115kV Line 1 de-energized at 0811H. (Planned Outage) [WEBSMS] | CLUZ
9/3/2023 8:08:06 AM | Mindanao Grid-09/03/2023 08:10: Zamboanga SS 138KV Bus 2 de-energized at 0724H. P&E emergency request shutdown. On-going rehab of Zamboanga SS under MSRP Stage 1 Schedule 4. FO / N-GOMP. [WEBSMS] | CMIN
9/3/2023 6:37:07 AM | Luzon Grid-09/03/2023 06:37: San Manuel-UPSI San Manuel BESS 69kV Line restored at 0636H. (Planned Outage) [WEBSMS] | CLUZ
9/3/2023 6:15:58 AM | Luzon Grid-09/03/2023 06:16: San Manuel-UPSI San Manuel BESS 69kV Line de-energized at 0613H. (Planned Outage) [WEBSMS] | CLUZ
9/3/2023 5:57:00 AM | [NSO Update] Mindanao Grid-09/03/2023 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3084MW, PK=1777MW, RR=55MW, NetOpMargin: AM=1252, PM=1190, EVE=1058 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @80MW, AG4 @104MW, AG5 @38MW, AG6 @146MW, AG7 @30MW, PG4 @100MW [WEBSMS] | CMIN
9/3/2023 5:56:23 AM | [NSO Update] Visayas Grid-09/03/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2450MW, PK=1862MW, RR=87MW, NetOpMargin: AM=501, PM=476, EVE=269 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @295MW, PGPP1 @74MW [WEBSMS] | CVIS
9/3/2023 5:52:40 AM | [NSO Update] Luzon Grid-09/03/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14379MW, PK=8498MW, RR=340MW, NetOpMargin: AM=5541, PM=5361, EVE=4108 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @150MW, MSLC1 @280MW, MSLC2 @280MW, MSLC3 @150MW, ILIJAN A @575MW [WEBSMS] | CLUZ
9/3/2023 5:18:59 AM | Visayas Grid-09/03/2023 05:18: Mandaue-Paknaan 69kV Line de-energized at 0515H. (Planned outage) [WEBSMS] | CVIS
9/3/2023 5:17:59 AM | Visayas Grid-09/03/2023 05:17: Mandaue-NRA 69kV Line 2 de-energized at 0515H. (Planned outage) [WEBSMS] | CVIS
9/3/2023 5:16:54 AM | Visayas Grid-09/03/2023 05:16: Mandaue-Guizo 69kV Line de-energized at 0514H. (Planned outage) [WEBSMS] | CVIS
9/3/2023 5:14:46 AM | Visayas Grid-09/03/2023 05:14: Cebu-Compostela 138kV Line 2 de-energized at 0512H. (Planned outage) [WEBSMS] | CVIS
9/3/2023 5:08:17 AM | Visayas Grid-09/03/2023 05:08: Mandaue-NRA 69kV Line de-energized at 0505H. (Planned outage) [WEBSMS] | CVIS
9/3/2023 4:40:31 AM | [NSO Update] Mindanao Grid-09/03/2023 04:42: Weather Update: At 3:00 AM today, the center of the eye of Typhoon HANNA was estimated based on all available data at 225 km North Northeast of Itbayat, Batanes (22.5 N, 123.0 E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving Westward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CMIN
9/3/2023 4:39:56 AM | [NSO Update] Visayas Grid-09/03/2023 04:39: Weather Update: At 3:00 AM today, the center of the eye of Typhoon HANNA was estimated based on all available data at 225 km North Northeast of Itbayat, Batanes (22.5 N, 123.0 E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving Westward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CVIS
9/3/2023 4:39:39 AM | [NSO Update] Luzon Grid-09/03/2023 04:39: Weather Update: At 3:00 AM today, the center of the eye of Typhoon HANNA was estimated based on all available data at 225 km North Northeast of Itbayat, Batanes (22.5 N, 123.0 E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving Westward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
9/3/2023 4:08:56 AM | Visayas Grid-09/03/2023 04:08: Cebu-Mandaue 138kV Line 2 de-energized at 0406H. (Planned outage) [WEBSMS] | CVIS
9/3/2023 4:03:16 AM | Luzon Grid-09/03/2023 04:03: Malolos 150MVA T01 de-energized at 0402H (Customer owned - Planned Outage) [WEBSMS] | CLUZ
9/2/2023 11:10:04 PM | Mindanao Grid-09/02/2023 23:12: MA3 online at 2306H. (Unplanned Outage). [WEBSMS] | CMIN
9/2/2023 8:46:20 PM | [NSO Update] Visayas Grid-09/02/2023 20:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 2044H with power going to Visayas. [WEBSMS] | CVIS
9/2/2023 8:46:16 PM | [NSO Update] Mindanao Grid-09/02/2023 20:48: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 2044H with power going to Visayas. [WEBSMS] | CMIN
9/2/2023 8:35:50 PM | [NSO Update] Mindanao Grid-09/02/2023 20:38: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 2033H from reverse power direction. [WEBSMS] | CMIN
9/2/2023 8:35:41 PM | [NSO Update] Visayas Grid-09/02/2023 20:35: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 2033H from reverse power direction. [WEBSMS] | CVIS
9/2/2023 6:27:01 PM | Mindanao Grid-09/02/2023 18:29: STEAG U1 cut in at 1735H. (Unplanned outage) [WEBSMS] | CMIN
9/2/2023 6:13:14 PM | [NSO Update] Luzon Grid-09/02/2023 18:13: Weather Advisory: At 3:00 PM today, the center of the eye of Typhoon "HANNA" {HAIKUI} was estimated based on all available data at 380 km East Northeast of Itbayat, Batanes (22.4�N, 125.1�E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving West Northwestward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
9/2/2023 6:13:09 PM | [NSO Update] Visayas Grid-09/02/2023 18:13: Weather Advisory: At 3:00 PM today, the center of the eye of Typhoon "HANNA" {HAIKUI} was estimated based on all available data at 380 km East Northeast of Itbayat, Batanes (22.4�N, 125.1�E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving West Northwestward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CVIS
9/2/2023 6:13:05 PM | [NSO Update] Mindanao Grid-09/02/2023 18:15: Weather Advisory: At 3:00 PM today, the center of the eye of Typhoon "HANNA" {HAIKUI} was estimated based on all available data at 380 km East Northeast of Itbayat, Batanes (22.4�N, 125.1�E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving West Northwestward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CMIN
9/2/2023 5:52:48 PM | [NSO Update] Mindanao Grid-09/02/2023 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2941MW, PK=2093MW, RR=58MW, NetOpMargin: EVE=790 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @69MW, AG4 @90MW, AG5 @38MW, AG6 @148MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
9/2/2023 5:52:27 PM | [NSO Update] Visayas Grid-09/02/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2489MW, PK=2099MW, RR=84MW, NetOpMargin: EVE=306 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @295MW, PGPP1 @74MW, TPC-THERMAL @82MW [WEBSMS] | CVIS
9/2/2023 5:48:30 PM | [NSO Update] Luzon Grid-09/02/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13443MW, PK=9101MW, RR=358MW, NetOpMargin: EVE=3984 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 1@180MW, CALACA 2 @ 150MW, MASINLOC 1 @280MW, MASINLOC 2 @280MW, MASINLOC 3 @170MW, SLTEC 1 @110MW, ILIJAN A @575MW [WEBSMS] | CLUZ
9/2/2023 5:19:00 PM | Luzon Grid-09/02/2023 17:19: Ilijan PCB 9-02CB04ILJ de-energized at 0518H. (Unplanned Outage) [WEBSMS] | CLUZ
9/2/2023 5:03:10 PM | Visayas Grid-09/02/2023 17:03: Colon SS 50 MVA TR1 energized at 1648H. [WEBSMS] | CVIS
9/2/2023 3:52:05 PM | Luzon Grid-09/02/2023 15:52: Naga-Tiwi C 230kV Line 2 restored at 1551H. (Planned Outage) [WEBSMS] | CLUZ
9/2/2023 3:47:23 PM | Luzon Grid-09/02/2023 15:47: Tiwi C SS 230kV Bus 1 restored at 1547H. (Planned Outage) [WEBSMS] | CLUZ
9/2/2023 3:12:14 PM | Mindanao Grid-09/02/2023 15:14: WMPC DG9 Shutdown at 1510H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/2/2023 2:52:22 PM | Mindanao Grid-09/02/2023 14:54: Agus 2 Unit 1 tripped with 20MW load at 1445H . (Unplanned Outage) [WEBSMS] | CMIN
9/2/2023 1:02:37 PM | [NSO Update] Visayas Grid-09/02/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2462MW, PK=2056MW, RR=89MW, NetOpMargin: PM=316, EVE=292 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @290MW, PGPP1 @74MW, TPC-THERMAL @82MW [WEBSMS] | CVIS
9/2/2023 1:02:30 PM | [NSO Update] Mindanao Grid-09/02/2023 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3163MW, PK=2098MW, RR=60MW, NetOpMargin: PM=1004, EVE=800 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @94MW, AG4 @90MW, AG5 @38MW, AG6 @148MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
9/2/2023 12:59:14 PM | [NSO Update] Luzon Grid-09/02/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13810MW, PK=9715MW, RR=373MW, NetOpMargin: PM=3722, EVE=3814 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 1@180MW, CALACA 2 @ 150MW, MSLC1 @280MW, MSLC2 @280MW, MSLC3 @150MW, SLTEC 1 @115MW, ILIJAN A @575MW [WEBSMS] | CLUZ
9/2/2023 11:19:59 AM | Luzon Grid-09/02/2023 11:20: SLTEC 2 tripped at 1117H with 115MW load. Lowest system frequency is 59.65Hz. (Unplanned Outage) [WEBSMS] | CLUZ
9/2/2023 9:54:07 AM | Mindanao Grid-09/02/2023 09:56: WMPC DG9 online at 0950H. As RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/2/2023 8:23:23 AM | Luzon Grid-09/02/2023 08:23: Malaya SS 300MVA T01 de-energized at 0823H. (Planned Outage) [WEBSMS] | CLUZ
9/2/2023 8:16:51 AM | Luzon Grid-09/02/2023 08:16: Tiwi C SS 230kV Bus 1 de-energized at 0816H. (Planned Outage) [WEBSMS] | CLUZ
9/2/2023 8:13:09 AM | Luzon Grid-09/02/2023 08:13: Naga-Tiwi C 230kV Line 2 de-energized at 0812H. (Planned Outage) [WEBSMS] | CLUZ
9/2/2023 7:49:07 AM | [NSO Update] Mindanao Grid-09/02/2023 07:51: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0744H with power going to Mindanao. [WEBSMS] | CMIN
9/2/2023 7:46:56 AM | [NSO Update] Visayas Grid-09/02/2023 07:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0744H with power going to Mindanao. [WEBSMS] | CVIS
9/2/2023 7:29:39 AM | [NSO Update] Mindanao Grid-09/02/2023 07:31: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0708H from reverse power direction. [WEBSMS] | CMIN
9/2/2023 7:29:34 AM | [NSO Update] Visayas Grid-09/02/2023 07:29: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0708H from reverse power direction. [WEBSMS] | CVIS
9/2/2023 7:25:26 AM | Mindanao Grid-09/02/2023 07:27: Zamboanga-Pitogo 138KV L1 de-energized at 0656H. P&E requested shutdown re: On-going rehab works of Zamboanga & Pitogo SS under MSRP Stage 1 Schedule 4. Planned Outage / Non-GOMP... [WEBSMS] | CMIN
9/2/2023 7:24:06 AM | Visayas Grid-09/02/2023 07:24: Colon ss 50 Mva TR1 de-energized at 0711H. (Planned Outage) [WEBSMS] | CVIS
9/2/2023 7:22:16 AM | Visayas Grid-09/02/2023 07:22: Compostela 30 Mvar reactor de-energized at 0707H. (Planned Outage) [WEBSMS] | CVIS
9/2/2023 6:15:23 AM | [NSO Update] Mindanao Grid-09/02/2023 06:17: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3212MW, PK=2006MW, RR=60MW, NetOpMargin: AM=1146, PM=1124, EVE=943 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @94MW, AG4 @90MW, AG5 @38MW, AG6 @148MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
9/2/2023 6:13:02 AM | [NSO Update] Visayas Grid-09/02/2023 06:10: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2634MW, PK=2024MW, RR=87MW, NetOpMargin: AM=523, PM=420, EVE=342 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @300MW, PGPP1 @74MW [WEBSMS] | CVIS
9/2/2023 6:09:29 AM | [NSO Update] Luzon Grid-09/02/2023 06:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14403MW, PK=9689MW, RR=374MW, NetOpMargin: AM=4340, PM=4134, EVE=4119 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @280MW, MSLC2 @280MW, MSLC3 @150MW, SLTEC 1 @115MW, ILIJAN A @575MW [WEBSMS] | CLUZ
9/2/2023 4:28:19 AM | [NSO Update] Mindanao Grid-09/02/2023 04:30: Weather Update: At 3:00 AM today, the center of the eye of Typhoon HANNA was estimated based on all available data at 530 km East Northeast of Itbayat, Batanes (21.9 N, 126.8 E) with maximum sustained winds of 120 km/h near the center and gustiness of up to 150 km/h. It is moving Westward at 10 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CMIN
9/2/2023 4:27:58 AM | [NSO Update] Visayas Grid-09/02/2023 04:27: Weather Update: At 3:00 AM today, the center of the eye of Typhoon HANNA was estimated based on all available data at 530 km East Northeast of Itbayat, Batanes (21.9 N, 126.8 E) with maximum sustained winds of 120 km/h near the center and gustiness of up to 150 km/h. It is moving Westward at 10 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CVIS
9/2/2023 4:27:48 AM | [NSO Update] Luzon Grid-09/02/2023 04:27: Weather Update: At 3:00 AM today, the center of the eye of Typhoon HANNA was estimated based on all available data at 530 km East Northeast of Itbayat, Batanes (21.9 N, 126.8 E) with maximum sustained winds of 120 km/h near the center and gustiness of up to 150 km/h. It is moving Westward at 10 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
9/2/2023 3:31:43 AM | [NSO Update] Mindanao Grid-09/02/2023 03:33: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0329H with power going to Mindanao. [WEBSMS] | CMIN
9/2/2023 3:31:21 AM | [NSO Update] Visayas Grid-09/02/2023 03:31: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0329H with power going to Mindanao. [WEBSMS] | CVIS
9/2/2023 2:27:15 AM | [NSO Update] Mindanao Grid-09/02/2023 02:29: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0206H from forward power direction. [WEBSMS] | CMIN
9/2/2023 2:26:48 AM | [NSO Update] Visayas Grid-09/02/2023 02:26: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0206H from forward power direction. [WEBSMS] | CVIS
9/2/2023 12:05:55 AM | Mindanao Grid-09/02/2023 00:08: Pulangi 4 Unit 2 emergency shutdown at 0001H due to low water inflow. [WEBSMS] | CMIN
9/1/2023 10:55:54 PM | Luzon Grid-09/01/2023 22:56: Calaca 2 online at 2248H (Unplanned Outage) [WEBSMS] | CLUZ
9/1/2023 10:01:53 PM | [NSO Update] Mindanao Grid-09/01/2023 22:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 2157H with power going to Visayas. [WEBSMS] | CMIN
9/1/2023 10:01:35 PM | [NSO Update] Visayas Grid-09/01/2023 22:01: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 2157H with power going to Visayas. [WEBSMS] | CVIS
9/1/2023 9:55:07 PM | [NSO Update] Visayas Grid-09/01/2023 21:55: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2136H from reverse power direction. [WEBSMS] | CVIS
9/1/2023 9:54:52 PM | [NSO Update] Mindanao Grid-09/01/2023 21:57: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2136H from reverse power direction. [WEBSMS] | CMIN
9/1/2023 9:14:51 PM | Mindanao Grid-09/01/2023 21:17: WMPC DG9 Shutdown at 2113H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/1/2023 8:37:28 PM | Mindanao Grid-09/01/2023 20:39: TM2 U2 shutdown at 2034H. Follow RTD. [WEBSMS] | CMIN
9/1/2023 8:31:29 PM | Mindanao Grid-09/01/2023 20:33: PG4 U3 online at 2027H. (Unplanned Outage). [WEBSMS] | CMIN
9/1/2023 6:16:52 PM | Mindanao Grid-09/01/2023 18:19: TM2 U2 online at 1809H. Follow RTD. [WEBSMS] | CMIN
9/1/2023 6:05:38 PM | [NSO Update] Visayas Grid-09/01/2023 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2463MW, PK=2128MW, RR=85MW, NetOpMargin: EVE=250 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @260MW, PGPP1 @74MW [WEBSMS] | CVIS
9/1/2023 6:05:13 PM | [NSO Update] Mindanao Grid-09/01/2023 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2961MW, PK=2140MW, RR=58MW, NetOpMargin: EVE=763 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @94MW, AG4 @90MW, AG5 @38MW, AG6 @148MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
9/1/2023 6:01:49 PM | [NSO Update] Luzon Grid-09/01/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13697MW, PK=9950MW, RR=400MW, NetOpMargin: EVE=3347 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: MSLC1 @280MW, MSLC2 @280MW, MSLC3 @165MW, ILIJAN A @575MW [WEBSMS] | CLUZ
9/1/2023 5:25:31 PM | Mindanao Grid-09/01/2023 17:27: WMPC DG7 manually cut-out as RPS at 1722H. From RPS - System Voltage Requirement (Unplanned Outage). [WEBSMS] | CMIN
9/1/2023 5:17:08 PM | Mindanao Grid-09/01/2023 17:19: WMPC DG9 cut-in at 1712H. For replacement unit to DG7. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/1/2023 4:41:00 PM | Mindanao Grid-09/01/2023 16:43: WMPC DG5 shutdown at 1637H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/1/2023 4:14:15 PM | Mindanao Grid-09/01/2023 16:16: PG4 U3 tripped with 43MW load at 1609H. (Unplanned Outage). [WEBSMS] | CMIN
9/1/2023 4:05:11 PM | Mindanao Grid-09/01/2023 16:07: MA3 online at 1546H. (Unplanned Outage) [WEBSMS] | CMIN
9/1/2023 3:40:40 PM | Visayas Grid-09/01/2023 15:40: Col-Nay 69kV Line restored at 1536H. (Unplanned outage) [WEBSMS] | CVIS
9/1/2023 3:17:40 PM | Visayas Grid-09/01/2023 15:17: Col-Nay 69kV Line tripped at 1510H. (Unplanned outage) [WEBSMS] | CVIS
9/1/2023 2:28:32 PM | Luzon Grid-09/01/2023 14:28: Naga-Tiwi Plant A 230kV Line restored at 1428H. (Planned Outage) [WEBSMS] | CLUZ
9/1/2023 1:45:30 PM | Luzon Grid-09/01/2023 13:45: Calaca 2 tripped at 1342H with 172MW. Lowest system frequency is 59.7Hz. (Unplanned Outage) [WEBSMS] | CLUZ
9/1/2023 12:42:59 PM | [NSO Update] Visayas Grid-09/01/2023 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2630MW, PK=2282MW, RR=92MW, NetOpMargin: PM=256, EVE=263 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @317MW, PGPP1 @74MW, TPC-THERMAL @82MW [WEBSMS] | CVIS
9/1/2023 12:41:07 PM | [NSO Update] Luzon Grid-09/01/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14246MW, PK=10276MW, RR=427MW, NetOpMargin: PM=3542, EVE=3704 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 280MW, Masinloc 2 @ 280MW, Masinloc 3 @ 150MW, Ilijan A @ 575MW [WEBSMS] | CLUZ
9/1/2023 12:40:43 PM | [NSO Update] Mindanao Grid-09/01/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3122MW, PK=2260MW, RR=60MW, NetOpMargin: PM=801, EVE=751 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @94MW, AG4 @90MW, AG5 @38MW, AG6 @148MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
9/1/2023 11:35:14 AM | Mindanao Grid-09/01/2023 11:37: WMPC DG9 cut-out at 1130H. (Unplanned Outage). [WEBSMS] | CMIN
9/1/2023 11:33:41 AM | Mindanao Grid-09/01/2023 11:35: WMPC DG5 Online at 1124H. as RPS, replacement unit to DG1. [WEBSMS] | CMIN
9/1/2023 11:30:00 AM | Mindanao Grid-09/01/2023 11:32: WMPC DG1 tripped with 8.5MW at 1110H. (Unplanned Outage). [WEBSMS] | CMIN
9/1/2023 11:22:57 AM | Mindanao Grid-09/01/2023 11:25: WMPC DG7 online at 1109H For replacement unit to DG9 as RPS.. [WEBSMS] | CMIN
9/1/2023 10:56:58 AM | Mindanao Grid-09/01/2023 10:59: WMPC DG1 online at 1053H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/1/2023 10:38:41 AM | Mindanao Grid-09/01/2023 10:40: MA3 tripped with 3.2MW load at 1032H. (Unplanned Outage). [WEBSMS] | CMIN
9/1/2023 10:35:45 AM | Luzon Grid-09/01/2023 10:35: Makban Plant B - C 230kV Line de-energized at 1034H. (Unplanned Outage) [WEBSMS] | CLUZ
9/1/2023 10:03:49 AM | [NSO Update] Mindanao Grid-09/01/2023 10:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0959H with power going to Mindanao. [WEBSMS] | CMIN
9/1/2023 10:03:38 AM | [NSO Update] Visayas Grid-09/01/2023 10:03: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0959H with power going to Mindanao. [WEBSMS] | CVIS
9/1/2023 8:56:36 AM | Mindanao Grid-09/01/2023 08:58: WMPC DG9 cut-in at 0854H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
9/1/2023 7:33:25 AM | [NSO Update] Mindanao Grid-09/01/2023 07:35: Correction: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0730H from reverse power direction. [WEBSMS] | CMIN
9/1/2023 7:31:53 AM | [NSO Update] Mindanao Grid-09/01/2023 07:34: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0107H from reverse power direction. [WEBSMS] | CMIN
9/1/2023 7:31:07 AM | [NSO Update] Visayas Grid-09/01/2023 07:31: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0730H from reverse power direction. [WEBSMS] | CVIS
9/1/2023 6:36:24 AM | Luzon Grid-09/01/2023 06:36: Naga-Tiwi Plant A 230kV Line de-energized at 0636H. (Planned Outage) [WEBSMS] | CLUZ
9/1/2023 6:03:14 AM | [NSO Update] Luzon Grid-09/01/2023 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14398MW, PK=10274MW, RR=417MW, NetOpMargin: AM=3707, PM=3853, EVE=4396 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 1 @ 280MW, Masinloc 2 @ 280MW, Masinloc 3 @ 150MW, Ilijan A @ 575MW [WEBSMS] | CLUZ
9/1/2023 5:56:02 AM | [NSO Update] Visayas Grid-09/01/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2670MW, PK=2281MW, RR=90MW, NetOpMargin: AM=299, PM=320, EVE=260 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 315MW, PGPP1 @ 74MW, PDPP3-C @ 8MW, PDPP3-G @ 8MW [WEBSMS] | CVIS
9/1/2023 5:55:30 AM | [NSO Update] Mindanao Grid-09/01/2023 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3141MW, PK=2204MW, RR=60MW, NetOpMargin: AM=877, PM=865, EVE=865 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @94MW, AG4 @90MW, AG5 @38MW, AG6 @148MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
9/1/2023 4:31:45 AM | Mindanao Grid-09/01/2023 04:33: STEAG U2 cut-in at 0411H. (Unplanned Outage) [WEBSMS] | CMIN
9/1/2023 4:19:06 AM | [NSO Update] Luzon Grid-09/01/2023 04:19: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm "HANNA" {HAIKUI} was estimated based on all available data at 865 km East of Extreme Northern Luzon (22.0�N, 130.1�E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving West Northwestward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
9/1/2023 4:18:53 AM | [NSO Update] Mindanao Grid-09/01/2023 04:21: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm "HANNA" {HAIKUI} was estimated based on all available data at 865 km East of Extreme Northern Luzon (22.0�N, 130.1�E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving West Northwestward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CMIN
9/1/2023 4:18:33 AM | [NSO Update] Visayas Grid-09/01/2023 04:18: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm "HANNA" {HAIKUI} was estimated based on all available data at 865 km East of Extreme Northern Luzon (22.0�N, 130.1�E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving West Northwestward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CVIS
9/1/2023 1:47:02 AM | Luzon Grid-09/01/2023 01:47: San Jose-Camarin 115kV Line restored at 0143H (Planned Outage) [WEBSMS] | CLUZ
9/1/2023 1:37:10 AM | [NSO Update] Mindanao Grid-09/01/2023 01:39: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0132H with power going to Mindanao. [WEBSMS] | CMIN
9/1/2023 1:36:53 AM | [NSO Update] Visayas Grid-09/01/2023 01:36: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0132H with power going to Mindanao. [WEBSMS] | CVIS
9/1/2023 1:35:42 AM | [NSO Update] Mindanao Grid-09/01/2023 01:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0107H from reverse power direction. [WEBSMS] | CMIN
9/1/2023 1:35:21 AM | [NSO Update] Visayas Grid-09/01/2023 01:35: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0107H from reverse power direction. [WEBSMS] | CVIS
9/1/2023 12:18:32 AM | Luzon Grid-09/01/2023 00:18: San Jose-Camarin 115kV Line de-energized at 0013H (Planned Outage) [WEBSMS] | CLUZ
8/31/2023 9:48:06 PM | Luzon Grid-08/31/2023 21:48: Tiwi C 50MVA T01 de-energized at 2012H, halt commissioning work at 2144H. [WEBSMS] | CLUZ
8/31/2023 7:35:07 PM | Mindanao Grid-08/31/2023 19:37: Mt. Apo G03 (MA3) cut-in at 1926H from FO. (Unplanned Outage) [WEBSMS] | CMIN
8/31/2023 7:18:30 PM | Luzon Grid-08/31/2023 19:18: Tiwi C 50MVA T01 energized at high side at 1913H, on commissioning. [WEBSMS] | CLUZ
8/31/2023 5:57:09 PM | [NSO Update] Luzon Grid-08/31/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13771MW, PK=9492MW, RR=398MW, NetOpMargin: EVE=3881 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 155MW, Masinloc 1 @ 280MW, Masinloc 2 @ 280MW, Masinloc 3 @ 160MW, Ilijan A @ 575MW [WEBSMS] | CLUZ
8/31/2023 5:53:32 PM | [NSO Update] Visayas Grid-08/31/2023 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2522MW, PK=2170MW, RR=87MW, NetOpMargin: EVE=264 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 300MW, PGPP1 @ 65MW, PDPP3-C @ 8MW, BDPP 1 @ 3.5MW, BDPP 3 @ 3.7MW [WEBSMS] | CVIS
8/31/2023 5:52:43 PM | [NSO Update] Mindanao Grid-08/31/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2972MW, PK=2134MW, RR=59MW, NetOpMargin: EVE=779 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @97MW, AG4 @95MW, AG5 @40MW, AG6 @148MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
8/31/2023 5:52:34 PM | Luzon Grid-08/31/2023 17:52: Laoag-Balaoi Wind Farm 115kV Line restored at 1751H (Planned Outage) [WEBSMS] | CLUZ
8/31/2023 5:47:40 PM | Luzon Grid-08/31/2023 17:47: Tiwi C 230kV Bus 1 restored at 1746H (Unplanned Outage) [WEBSMS] | CLUZ
8/31/2023 4:39:27 PM | Luzon Grid-08/31/2023 16:39: For info: Sta Rita Module 40 completed the fuel changeover from oil to nat gas at 1636H [WEBSMS] | CLUZ
8/31/2023 4:18:06 PM | [NSO Update] Mindanao Grid-08/31/2023 16:20: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm "HANNA" {HAIKUI} was estimated based on all available data at 1,045 km East of Extreme Northern Luzon (21.2�N, 132.0�E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CMIN
8/31/2023 4:17:42 PM | [NSO Update] Visayas Grid-08/31/2023 16:17: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm "HANNA" {HAIKUI} was estimated based on all available data at 1,045 km East of Extreme Northern Luzon (21.2�N, 132.0�E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CVIS
8/31/2023 4:17:42 PM | Mindanao Grid-08/31/2023 16:19: WMPC DG01 cut-out at 1613H as RPS - System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
8/31/2023 4:17:24 PM | [NSO Update] Luzon Grid-08/31/2023 16:17: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm "HANNA" {HAIKUI} was estimated based on all available data at 1,045 km East of Extreme Northern Luzon (21.2�N, 132.0�E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
8/31/2023 4:13:54 PM | Luzon Grid-08/31/2023 16:13: Lal-lo - NAREDCO 69kV Line 1 restored at 1612H (Unplanned Outage) [WEBSMS] | CLUZ
8/31/2023 1:31:40 PM | Luzon Grid-08/31/2023 13:31: Lal-lo - NAREDCO 69kV Line 1 de-energized at 1331H (Unplanned Outage) [WEBSMS] | CLUZ
8/31/2023 12:52:53 PM | [NSO Update] Mindanao Grid-08/31/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2971MW, PK=2234MW, RR=60MW, NetOpMargin: PM=678, EVE=732 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @97MW, AG4 @95MW, AG5 @40MW, AG6 @148MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
8/31/2023 12:52:45 PM | [NSO Update] Visayas Grid-08/31/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2695MW, PK=2350MW, RR=88MW, NetOpMargin: PM=257, EVE=260 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @310MW, TPC-THERMAL @82MW [WEBSMS] | CVIS
8/31/2023 12:46:45 PM | [NSO Update] Luzon Grid-08/31/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14045MW, PK=10156MW, RR=440MW, NetOpMargin: PM=3449, EVE=3670 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @155MW, MASINLOC 1 @280MW, MASINLOC 2 @280MW, MASINLOC 3 @150MW, ILIJAN A @575MW [WEBSMS] | CLUZ
8/31/2023 11:07:18 AM | Mindanao Grid-08/31/2023 11:09: WMPC DG01 cut-in at 1104H as RPS - System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
8/31/2023 11:06:09 AM | Luzon Grid-08/31/2023 11:06: Mauban PCB 8-07CB04MBA emergency shutdown at 1101H due to low SF6 (Unplanned Outage) [WEBSMS] | CLUZ
8/31/2023 9:12:56 AM | Mindanao Grid-08/31/2023 09:15: WMPC DG10 cut-in at 0909H as RPS - System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
8/31/2023 8:30:37 AM | Luzon Grid-08/31/2023 08:30: For info: Sta Rita Module 10 completed the fuel changeover from oil to nat gas at 0825H [WEBSMS] | CLUZ
8/31/2023 8:01:05 AM | [NSO Update] Mindanao Grid-08/31/2023 08:03: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0800H with power going to Mindanao. [WEBSMS] | CMIN
8/31/2023 8:01:00 AM | [NSO Update] Visayas Grid-08/31/2023 08:00: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0800H with power going to Mindanao. [WEBSMS] | CVIS
8/31/2023 7:04:02 AM | [NSO Update] Mindanao Grid-08/31/2023 07:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0637H from reverse power direction. [WEBSMS] | CMIN
8/31/2023 7:03:16 AM | [NSO Update] Visayas Grid-08/31/2023 07:03: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0637H from reverse power direction. [WEBSMS] | CVIS
8/31/2023 6:18:09 AM | [NSO Update] Mindanao Grid-08/31/2023 06:20: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2978MW, PK=2240MW, RR=60MW, NetOpMargin: AM=679, PM=619, EVE=839 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @97MW, AG4 @95MW, AG5 @40MW, AG6 @148MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
8/31/2023 6:03:38 AM | [NSO Update] Visayas Grid-08/31/2023 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2777MW, PK=2406MW, RR=91MW, NetOpMargin: AM=280, PM=259, EVE=259 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @315MW, PGPP1 @74MW [WEBSMS] | CVIS
8/31/2023 5:46:37 AM | [NSO Update] Luzon Grid-08/31/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14219MW, PK=10550MW, RR=420MW, NetOpMargin: AM=3249, PM=2869, EVE=3478 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @155MW, MSLC1 @280MW, MSLC2 @280MW, MSLC3 @145MW, STA. RITA 20 @165MW, ILIJAN A @575MW [WEBSMS] | CLUZ
8/31/2023 5:20:00 AM | [NSO Update] Visayas Grid-08/31/2023 05:19: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0516H with power going to Mindanao. [WEBSMS] | CVIS
8/31/2023 5:19:07 AM | [NSO Update] Mindanao Grid-08/31/2023 05:21: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0516H with power going to Mindanao. [WEBSMS] | CMIN
8/31/2023 4:44:16 AM | [NSO Update] Mindanao Grid-08/31/2023 04:46: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm "HANNA" {HAIKUI} was estimated based on all available data at 1,215 km East of Extreme Northern Luzon (21.1�N, 133.6�E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 115 km/h. It is moving West Northwestward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CMIN
8/31/2023 4:42:59 AM | [NSO Update] Visayas Grid-08/31/2023 04:42: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm "HANNA" {HAIKUI} was estimated based on all available data at 1,215 km East of Extreme Northern Luzon (21.1�N, 133.6�E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 115 km/h. It is moving West Northwestward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CVIS
8/31/2023 4:41:34 AM | [NSO Update] Luzon Grid-08/31/2023 04:41: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm "HANNA" {HAIKUI} was estimated based on all available data at 1,215 km East of Extreme Northern Luzon (21.1�N, 133.6�E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 115 km/h. It is moving West Northwestward at 20 km/h. Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
8/31/2023 4:24:07 AM | Luzon Grid-08/31/2023 04:24: Sta Rita 20 online at 0421H (Planned Outage) [WEBSMS] | CLUZ
8/31/2023 4:01:14 AM | Luzon Grid-08/31/2023 04:01: SLTEC Unit 1 online at 0359H (Planned Outage) [WEBSMS] | CLUZ
8/31/2023 1:52:20 AM | [NSO Update] Visayas Grid-08/31/2023 01:52: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0148H from reverse power direction. [WEBSMS] | CVIS
8/31/2023 1:51:02 AM | [NSO Update] Mindanao Grid-08/31/2023 01:53: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0148H from reverse power direction. [WEBSMS] | CMIN
8/31/2023 12:18:31 AM | [NSO Update] Luzon Grid-08/31/2023 00:18: Weather Disturbance Alert Notice (WDAN) is issued at August 30, 2023 at 2300H. The Low-Pressure Area inside the PAR has developed into Severe Tropical Storm "HANNA". The center was estimated based on all available data at 1335 km East of Extreme Northern Luzon (21.1N, 134.8E) with max sustained winds of 95kmh near the center and gustiness of up to 115 km/h. It is moving Northwestward at 15 km/h. [WEBSMS] | CLUZ
8/31/2023 12:17:54 AM | [NSO Update] Mindanao Grid-08/31/2023 00:20: Weather Disturbance Alert Notice (WDAN) is issued at August 30, 2023 at 2300H. The Low-Pressure Area inside the PAR has developed into Severe Tropical Storm "HANNA". The center was estimated based on all available data at 1335 km East of Extreme Northern Luzon (21.1N, 134.8E) with max sustained winds of 95kmh near the center and gustiness of up to 115 km/h. It is moving Northwestward at 15 km/h. [WEBSMS] | CMIN
8/31/2023 12:16:46 AM | [NSO Update] Visayas Grid-08/31/2023 00:16: Weather Disturbance Alert Notice (WDAN) is issued at August 30, 2023 at 2300H. The Low-Pressure Area inside the PAR has developed into Severe Tropical Storm "HANNA". The center was estimated based on all available data at 1335 km East of Extreme Northern Luzon (21.1N, 134.8E) with max sustained winds of 95kmh near the center and gustiness of up to 115 km/h. It is moving Northwestward at 15 km/h. [WEBSMS] | CVIS
8/30/2023 11:34:04 PM | [NSO Update] Mindanao Grid-08/30/2023 23:36: Weather Disturbance Alert Notice (WDAN) has been lifted today, August 30, 2023 at 2300H. Super Typhoon "GORING" (formerly Tropical Depression) is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Super Typhoon GORING was estimated based on all available data at 265 km West of Itbayat, Batanes (OUTSIDE PAR) (20.8 �N, 119.3 �E ) [WEBSMS] | CMIN
8/30/2023 11:33:21 PM | [NSO Update] Visayas Grid-08/30/2023 23:33: Weather Disturbance Alert Notice (WDAN) has been lifted today, August 30, 2023 at 2300H. Super Typhoon "GORING" (formerly Tropical Depression) is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Super Typhoon GORING was estimated based on all available data at 265 km West of Itbayat, Batanes (OUTSIDE PAR) (20.8 �N, 119.3 �E ) [WEBSMS] | CVIS
8/30/2023 11:32:40 PM | [NSO Update] Luzon Grid-08/30/2023 23:32: Weather Disturbance Alert Notice (WDAN) has been lifted today, August 30, 2023 at 2300H. Super Typhoon "GORING" (formerly Tropical Depression) is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Super Typhoon GORING was estimated based on all available data at 265 km West of Itbayat, Batanes (OUTSIDE PAR) (20.8 �N, 119.3 �E ) [WEBSMS] | CLUZ
8/30/2023 9:16:09 PM | Mindanao Grid-08/30/2023 21:18: WMPC DG10 cut-out at 2112H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/30/2023 8:34:02 PM | Mindanao Grid-08/30/2023 20:36: WMPC DG10 cut-in at 1935H. Resumption of RPS - System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
8/30/2023 8:33:08 PM | Mindanao Grid-08/30/2023 20:35: WMPC DG10 tripped at 1926H with 8.5 MW load due to over voltage indication. (Unplanned Outage). [WEBSMS] | CMIN
8/30/2023 6:00:37 PM | [NSO Update] Mindanao Grid-08/30/2023 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3047MW, PK=2112MW, RR=59MW, NetOpMargin: EVE=876 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @97MW, AG4 @95MW, AG5 @40MW, AG6 @148MW, AG7 @33MW, PG4 @175MW [WEBSMS] | CMIN
8/30/2023 5:58:43 PM | [NSO Update] Visayas Grid-08/30/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: CAP=2513MW, PK=2156MW, RR=87MW, NetOpMargin: EVE=269 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @315MW, PGPP1 @74MW [WEBSMS] | CVIS
8/30/2023 5:50:37 PM | [NSO Update] Luzon Grid-08/30/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13373MW, PK=9901MW, RR=398MW, NetOpMargin: EVE=3074 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC1 @280MW, MSLC2 @280MW, MSLC3 @80MW, ILIJAN A @575MW [WEBSMS] | CLUZ
8/30/2023 4:15:08 PM | Mindanao Grid-08/30/2023 16:17: WMPC DG05 cut-out at 1614H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/30/2023 3:41:32 PM | Mindanao Grid-08/30/2023 15:43: Pulangi 4 HEP U3 cut-in at 1539H. (Planned Outage) [WEBSMS] | CMIN
8/30/2023 3:31:22 PM | Luzon Grid-08/30/2023 15:31: Tiwi Plant A-Tiwi Plant C 230kV Line 2 restored at 1529H (Planned Outage) [WEBSMS] | CLUZ
8/30/2023 1:02:54 PM | [NSO Update] Visayas Grid-08/30/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2755MW, PK=2399MW, RR=93MW, NetOpMargin: PM=263, EVE=253 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @326MW, PGPP1 @74MW [WEBSMS] | CVIS
8/30/2023 1:01:56 PM | [NSO Update] Mindanao Grid-08/30/2023 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3004MW, PK=2240MW, RR=60MW, NetOpMargin: PM=704, EVE=873 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MCO @270MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @97MW, AG4 @95MW, AG5 @40MW, AG6 @148MW, AG7 @33MW, PG4 @160MW [WEBSMS] | CMIN
8/30/2023 12:59:29 PM | [NSO Update] Luzon Grid-08/30/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13708MW, PK=10545MW, RR=461MW, NetOpMargin: PM=2701, EVE=3052 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC1 @280MW, MSLC2 @280MW, MSLC3 @135MW, ILIJAN A @575MW [WEBSMS] | CLUZ
8/30/2023 11:18:30 AM | Luzon Grid-08/30/2023 11:18: Tiwi C 230kV Bus 1 de-energized at 1116H (Unplanned Outage) [WEBSMS] | CLUZ
8/30/2023 10:52:43 AM | Mindanao Grid-08/30/2023 10:54: WMPC DG05 cut-in at 1050H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/30/2023 9:16:07 AM | Mindanao Grid-08/30/2023 09:18: WMPC DG10 cut-in at 0851H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/30/2023 9:14:24 AM | [NSO Update] Mindanao Grid-08/30/2023 09:16: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0911H with power going to Mindanao. [WEBSMS] | CMIN
8/30/2023 9:13:57 AM | [NSO Update] Visayas Grid-08/30/2023 09:13: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0911H with power going to Mindanao. [WEBSMS] | CVIS
8/30/2023 9:03:21 AM | [NSO Update] Mindanao Grid-08/30/2023 09:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0859H from forward power direction. [WEBSMS] | CMIN
8/30/2023 9:02:49 AM | [NSO Update] Visayas Grid-08/30/2023 09:02: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0859H from forward power direction. [WEBSMS] | CVIS
8/30/2023 6:44:15 AM | [NSO Update] Mindanao Grid-08/30/2023 06:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0631H with power going to Visayas. [WEBSMS] | CMIN
8/30/2023 6:43:56 AM | [NSO Update] Visayas Grid-08/30/2023 06:43: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 0631H with power going to Visayas. [WEBSMS] | CVIS
8/30/2023 6:42:58 AM | [NSO Update] Mindanao Grid-08/30/2023 06:45: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0623H from reverse power direction. [WEBSMS] | CMIN
8/30/2023 6:42:32 AM | [NSO Update] Visayas Grid-08/30/2023 06:42: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0623H from reverse power direction. [WEBSMS] | CVIS
8/30/2023 6:36:09 AM | Luzon Grid-08/30/2023 06:36: Tiwi Plant A-Tiwi Plant C 230kV Line 2 de-energized at 0635H (Planned Outage) [WEBSMS] | CLUZ
8/30/2023 5:49:34 AM | [NSO Update] Luzon Grid-08/30/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13801MW, PK=11027MW, RR=422MW, NetOpMargin: AM=2352, PM=1768, EVE=2535 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 280MW, Masinloc 2 @ 280MW, Masinloc 3 @ 100MW, Pagbilao 2 @ 120MW, Ilijan A @ 575MW [WEBSMS] | CLUZ
8/30/2023 5:45:31 AM | [NSO Update] Mindanao Grid-08/30/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3183MW, PK=2138MW, RR=60MW, NetOpMargin: AM=985, PM=940, EVE=1002 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @97MW, AG4 @95MW, AG5 @40MW, AG6 @148MW, AG7 @31MW, PG4 @140MW [WEBSMS] | CMIN
8/30/2023 5:44:11 AM | [NSO Update] Visayas Grid-08/30/2023 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2540MW, PK=2272MW, RR=91MW, NetOpMargin: AM=177, PM=184, EVE=260 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 326MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/30/2023 4:21:53 AM | [NSO Update] Mindanao Grid-08/30/2023 04:24: Weather Update: At 3:00 AM today, the center of the eye of Super Typhoon "GORING" {SAOLA} was estimated based on all available data over the coastal waters of Sabtang, Batanes (19.9�N, 121.7�E) with maximum sustained winds of 195 km/h near the center and gustiness of up to 240 km/h. It is moving Northwestward at 20 km/h. Southwest Monsoon affecting Central and South Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/30/2023 4:21:38 AM | [NSO Update] Visayas Grid-08/30/2023 04:21: Weather Update: At 3:00 AM today, the center of the eye of Super Typhoon "GORING" {SAOLA} was estimated based on all available data over the coastal waters of Sabtang, Batanes (19.9�N, 121.7�E) with maximum sustained winds of 195 km/h near the center and gustiness of up to 240 km/h. It is moving Northwestward at 20 km/h. Southwest Monsoon affecting Central and South Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/30/2023 4:21:12 AM | [NSO Update] Luzon Grid-08/30/2023 04:21: Weather Update: At 3:00 AM today, the center of the eye of Super Typhoon "GORING" {SAOLA} was estimated based on all available data over the coastal waters of Sabtang, Batanes (19.9�N, 121.7�E) with maximum sustained winds of 195 km/h near the center and gustiness of up to 240 km/h. It is moving Northwestward at 20 km/h. Southwest Monsoon affecting Central and South Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/30/2023 2:23:40 AM | Luzon Grid-08/30/2023 02:24: Pagbilao 2 online at 0222H (Planned Outage) [WEBSMS] | CLUZ
8/29/2023 11:34:56 PM | Mindanao Grid-08/29/2023 23:37: SEC 1 Coal PP synchronized at 2300H. (Unplanned Outage). [WEBSMS] | CMIN
8/29/2023 5:44:59 PM | [NSO Update] Luzon Grid-08/29/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13032MW, PK=10001MW, RR=398MW, NetOpMargin: EVE=2633 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 220MW, Calaca 2 @ 173MW, Masinloc 1 @ 280MW, Masinloc 2 @ 220MW, Masinloc 3 @ 150MW, Ilijan A @ 575MW [WEBSMS] | CLUZ
8/29/2023 5:43:01 PM | [NSO Update] Visayas Grid-08/29/2023 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2496MW, PK=2063MW, RR=87MW, NetOpMargin: EVE=346 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 325MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/29/2023 5:42:45 PM | [NSO Update] Mindanao Grid-08/29/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3045MW, PK=1995MW, RR=57MW, NetOpMargin: EVE=993 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @96MW, AG5 @42MW, AG6 @146MW, AG7 @34MW, PG4 @125MW [WEBSMS] | CMIN
8/29/2023 5:30:33 PM | Mindanao Grid-08/29/2023 17:33: GENSAN-LLEDO and GENSAN- POB. TUPI 69kV STL AT 1618H with loads 35.3MW and 27.2MW respectively tripped - SIPS ACTIVATION due to the tripping of SEC 1 with 118MW load - SIPS ACTIVATION. Frequency at 60.390Hz. [WEBSMS] | CMIN
8/29/2023 5:24:11 PM | Luzon Grid-08/29/2023 17:24: Tiwi Plant A-Tiwi Plant C 230kV Line 1 restored at 1722H (Planned Outage) [WEBSMS] | CLUZ
8/29/2023 5:23:18 PM | Luzon Grid-08/29/2023 17:23: iwi Plant A-Tiwi Plant C 230kV Line 1 restored at 1722H (Planned Outage) [WEBSMS] | CLUZ
8/29/2023 5:14:49 PM | Mindanao Grid-08/29/2023 17:17: ALD occurred at GENSAN-LLEDO and GENSAN- POB. TUPI 69kV STL AT 1618H with loads 35.3MW and 27.2MW respectively due to the tripping of SEC 1 with 118MW load. Frequency at 60.390Hz. [WEBSMS] | CMIN
8/29/2023 4:43:47 PM | [NSO Update] Mindanao Grid-08/29/2023 16:46: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "GORING" {SAOLA} was estimated based on all available data at 165 km East Southeast of Calayan, Cagayan (18.9�N, 123.0�E) with maximum sustained winds of 165 km/h near the center and gustiness of up to 205 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting Central and South Luzon, Visayas, and Mindanao [WEBSMS] | CMIN
8/29/2023 4:43:34 PM | [NSO Update] Visayas Grid-08/29/2023 16:43: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "GORING" {SAOLA} was estimated based on all available data at 165 km East Southeast of Calayan, Cagayan (18.9�N, 123.0�E) with maximum sustained winds of 165 km/h near the center and gustiness of up to 205 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting Central and South Luzon, Visayas, and Mindanao [WEBSMS] | CVIS
8/29/2023 4:41:02 PM | Mindanao Grid-08/29/2023 16:43: Baloi - Agus 2 138KV line 2 energized at 1613H. (Planned Outage) [WEBSMS] | CMIN
8/29/2023 4:40:17 PM | [NSO Update] Luzon Grid-08/29/2023 16:40: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "GORING" {SAOLA} was estimated based on all available data at 165 km East Southeast of Calayan, Cagayan (18.9�N, 123.0�E) with maximum sustained winds of 165 km/h near the center and gustiness of up to 205 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting Central and South Luzon, Visayas, and Mindanao [WEBSMS] | CLUZ
8/29/2023 4:16:25 PM | Mindanao Grid-08/29/2023 16:18: WMPC DG05 cut-out at 1613H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/29/2023 3:45:10 PM | Luzon Grid-08/29/2023 15:45: Balsik-SBMA 230kV Line restored at 1544H (Planned Outage) [WEBSMS] | CLUZ
8/29/2023 1:50:13 PM | Mindanao Grid-08/29/2023 13:52: Baloi - Agus 2 138KV line 2 deenergized at 1331H. (Planned Outage) [WEBSMS] | CMIN
8/29/2023 1:23:58 PM | Mindanao Grid-08/29/2023 13:26: Baloi - Agus 2 138kV Line 1 re-energized at 1318H. (Planned Outage) [WEBSMS] | CMIN
8/29/2023 1:04:08 PM | Mindanao Grid-08/29/2023 13:06: NacSur Diesel Plant cut-in at 1300H. Follow RTD. [WEBSMS] | CMIN
8/29/2023 1:03:07 PM | Mindanao Grid-08/29/2023 13:05: WMPC DG10 cut-in at 1054H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/29/2023 1:01:27 PM | [NSO Update] Visayas Grid-08/29/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2423MW, PK=2007MW, RR=91MW, NetOpMargin: PM=324, EVE=353 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @325MW, PGPP1 @74MW [WEBSMS] | CVIS
8/29/2023 1:01:17 PM | [NSO Update] Mindanao Grid-08/29/2023 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2981MW, PK=2161MW, RR=60MW, NetOpMargin: PM=760, EVE=825 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @96MW, AG5 @42MW, AG6 @146MW, AG7 @34MW, PG4 @125MW [WEBSMS] | CMIN
8/29/2023 12:56:23 PM | [NSO Update] Luzon Grid-08/29/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13490MW, PK=10973MW, RR=462MW, NetOpMargin: PM=2055, EVE=2628 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @170MW, CLC2 @173MW, MSLC1 @280MW, MSLC2 @220MW, MSLC3 @160MW, SLPGC 1 @100MW, ILIJAN A @575MW [WEBSMS] | CLUZ
8/29/2023 10:48:37 AM | [NSO Update] Mindanao Grid-08/29/2023 10:51: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0941H with power going to Mindanao. [WEBSMS] | CMIN
8/29/2023 10:48:05 AM | [NSO Update] Visayas Grid-08/29/2023 10:48: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0941H with power going to Mindanao. [WEBSMS] | CVIS
8/29/2023 10:01:09 AM | Mindanao Grid-08/29/2023 10:03: WMPC DG05 cut-in at 0922H as replacement unit for DG10 on RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/29/2023 9:21:38 AM | Mindanao Grid-08/29/2023 09:24: WMPC DG10 tripped at 0901H with 8.5 MW load due to turbo charger A bank speed sensor trouble. (Unplanned Outage). [WEBSMS] | CMIN
8/29/2023 9:19:52 AM | Mindanao Grid-08/29/2023 09:22: WMPC DG10 cut-in at 0850H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/29/2023 8:59:57 AM | [NSO Update] Mindanao Grid-08/29/2023 09:02: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0753H from reverse power direction. [WEBSMS] | CMIN
8/29/2023 8:59:10 AM | [NSO Update] Visayas Grid-08/29/2023 08:59: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0753H from reverse power direction. [WEBSMS] | CVIS
8/29/2023 8:49:43 AM | Mindanao Grid-08/29/2023 08:52: Baloi - Agus 2 138kV Line 1 deenergized at 0831H. (Planned Outage) [WEBSMS] | CMIN
8/29/2023 7:41:38 AM | Luzon Grid-08/29/2023 07:41: Correction: Balsik-SBMA 230kV Line de-energized at 0739H (Planned Outage) [WEBSMS] | CLUZ
8/29/2023 7:40:19 AM | Luzon Grid-08/29/2023 07:40: Balsik-SBMA 230kV Line de-energized at 0729H (Planned Outage) [WEBSMS] | CLUZ
8/29/2023 6:46:48 AM | Luzon Grid-08/29/2023 06:47: Tiwi Plant A-Tiwi Plant C 230kV Line 1 de-energized at 0646H (Planned Outage) [WEBSMS] | CLUZ
8/29/2023 5:55:51 AM | [NSO Update] Mindanao Grid-08/29/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3196MW, PK=2224MW, RR=60MW, NetOpMargin: AM=912, PM=926, EVE=968 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @96MW, AG5 @42MW, AG6 @146MW, AG7 @34MW, PG4 @125MW [WEBSMS] | CMIN
8/29/2023 5:53:08 AM | [NSO Update] Visayas Grid-08/29/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2579MW, PK=2295MW, RR=90.4MW, NetOpMargin: AM=194, PM=197, EVE=277 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @74MW, TPC-THERMAL @82MW [WEBSMS] | CVIS
8/29/2023 5:47:54 AM | [NSO Update] Visayas Grid-08/29/2023 05:48: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0542H with power going to Mindanao. [WEBSMS] | CVIS
8/29/2023 5:47:08 AM | [NSO Update] Mindanao Grid-08/29/2023 05:49: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0542H with power going to Mindanao. [WEBSMS] | CMIN
8/29/2023 5:45:30 AM | [NSO Update] Luzon Grid-08/29/2023 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13586MW, PK=11024MW, RR=460MW, NetOpMargin: AM=2102, PM=1594, EVE=2027 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 1 @ 170MW, Calaca 2 @ 173MW, Masinloc 1 @ 280MW, Masinloc 2 @ 280MW, Masinloc 3 @ 220MW, Masinloc 3 @ SLPGC 1 @50MW, Ilijan A @575MW [WEBSMS] | CLUZ
8/29/2023 5:13:22 AM | [NSO Update] Mindanao Grid-08/29/2023 05:15: Weather Update: The center of the eye of Typhoon "GORING" {SAOLA} was estimated based on all available data at 220 km East of Aparri, Cagayan or 220 km East Northeast of Tuguegarao City, Cagayan (18.4�N, 123.7�E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving North Northwestward at 10 km/h. [WEBSMS] | CMIN
8/29/2023 5:11:39 AM | [NSO Update] Luzon Grid-08/29/2023 05:11: at 0300H Weather Update: The center of the eye of Typhoon "GORING" {SAOLA} was estimated based on all available data at 220 km East of Aparri, Cagayan or 220 km East Northeast of Tuguegarao City, Cagayan (18.4�N, 123.7�E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving North Northwestward at 10 km/h. [WEBSMS] | CLUZ
8/29/2023 4:41:54 AM | [NSO Update] Visayas Grid-08/29/2023 04:42: Weather Update: The center of the eye of Typhoon "GORING" {SAOLA} was estimated based on all available data at 220 km East of Aparri, Cagayan or 220 km East Northeast of Tuguegarao City, Cagayan (18.4�N, 123.7�E) with maximum sustained winds of 155 km/h near the center & gustiness of up to 190 km/h. It is moving North Northwestward at 10 km/h. [WEBSMS] | CVIS
8/29/2023 2:08:03 AM | [NSO Update] Mindanao Grid-08/29/2023 02:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0203H with power going to Visayas. [WEBSMS] | CMIN
8/29/2023 2:07:09 AM | [NSO Update] Visayas Grid-08/29/2023 02:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0203H with power going to Visayas. [WEBSMS] | CVIS
8/28/2023 8:37:22 PM | [NSO Update] Visayas Grid-08/28/2023 20:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2035H with power going to Visayas. [WEBSMS] | CVIS
8/28/2023 8:36:51 PM | [NSO Update] Mindanao Grid-08/28/2023 20:39: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2035H with power going to Visayas. [WEBSMS] | CMIN
8/28/2023 8:29:12 PM | [NSO Update] Mindanao Grid-08/28/2023 20:31: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2023H with power going to Mindanao. [WEBSMS] | CMIN
8/28/2023 8:28:14 PM | [NSO Update] Visayas Grid-08/28/2023 20:28: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2023H with power going to Mindanao. [WEBSMS] | CVIS
8/28/2023 6:06:09 PM | [NSO Update] Mindanao Grid-08/28/2023 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3069MW, PK=1915MW, RR=59MW, NetOpMargin: EVE=1096 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @95MW, AG5 @44MW, AG6 @146MW, AG7 @33MW, PG4 @125MW [WEBSMS] | CMIN
8/28/2023 5:57:06 PM | [NSO Update] Visayas Grid-08/28/2023 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2500MW, PK=1952MW, RR=83MW, NetOpMargin: EVE=465 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 325MW, PGPP1 @ 74MW [WEBSMS] | CVIS
8/28/2023 5:49:47 PM | [NSO Update] Luzon Grid-08/28/2023 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13184MW, PK=9530MW, RR=400MW, NetOpMargin: EVE=3254 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @150MW, CLC2 @173MW, MSLC1 @315MW MSLC2 @300MW, MSLC3 @145MW, SAN GABRIEL @409MW [WEBSMS] | CLUZ
8/28/2023 5:12:25 PM | Luzon Grid-08/28/2023 17:12: Laoag SS 230kV Bus 2 restored at 1712H (Planned Outage) [WEBSMS] | CLUZ
8/28/2023 4:40:42 PM | Luzon Grid-08/28/2023 16:40: Balsik-SBMA 230kV Line restored at 1639H (Planned Outage) [WEBSMS] | CLUZ
8/28/2023 12:51:25 PM | [NSO Update] Luzon Grid-08/28/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13651MW, PK=9290MW, RR=385MW, NetOpMargin: PM=3977, EVE=3540 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 1 @ 180MW, Calaca 2 @ 173MW, Masinloc 1 @ 315MW, Masinloc 2 @ 300MW, Masinloc 3 @ 250MW, Ilijan A @575MW [WEBSMS] | CLUZ
8/28/2023 12:36:57 PM | [NSO Update] Visayas Grid-08/28/2023 12:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2377MW, PK=1828MW, RR=91MW, NetOpMargin: PM=459, EVE=336 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 315MW, PGPP1 @ 74MW [WEBSMS] | CVIS
8/28/2023 12:34:53 PM | [NSO Update] Mindanao Grid-08/28/2023 12:37: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3107MW, PK=1833MW, RR=60MW, NetOpMargin: PM=1213, EVE=1201 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @95MW, AG5 @42MW, AG6 @146MW, AG7 @34MW, PG4 @125MW [WEBSMS] | CMIN
8/28/2023 8:51:47 AM | Mindanao Grid-08/28/2023 08:54: Update on Agus 4 HEP Unit no. 1 cut-out at 0805H. PMS (GOMP). (Planned Outage). ETC September 29,2023. [WEBSMS] | CMIN
8/28/2023 8:45:22 AM | Mindanao Grid-08/28/2023 08:47: Agus 4 HEP Unit no. 1 cut-in at 0805H from PMS (GOMP). [WEBSMS] | CMIN
8/28/2023 8:37:51 AM | [NSO Update] Visayas Grid-08/28/2023 08:38: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0837H with power going to Mindanao. [WEBSMS] | CVIS
8/28/2023 8:37:47 AM | [NSO Update] Mindanao Grid-08/28/2023 08:40: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0837H with power going to Mindanao. [WEBSMS] | CMIN
8/28/2023 8:26:11 AM | [NSO Update] Mindanao Grid-08/28/2023 08:28: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0825H with power going to Visayas. [WEBSMS] | CMIN
8/28/2023 8:26:06 AM | [NSO Update] Visayas Grid-08/28/2023 08:26: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0825H with power going to Visayas. [WEBSMS] | CVIS
8/28/2023 7:46:57 AM | Luzon Grid-08/28/2023 07:47: Balsik-SBMA 230kV Line de-energized at 0746H (Planned Outage) [WEBSMS] | CLUZ
8/28/2023 7:00:10 AM | [NSO Update] Mindanao Grid-08/28/2023 07:02: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0658H with power going to Visayas. [WEBSMS] | CMIN
8/28/2023 7:00:05 AM | [NSO Update] Visayas Grid-08/28/2023 07:00: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0658H with power going to Visayas. [WEBSMS] | CVIS
8/28/2023 6:07:09 AM | Luzon Grid-08/28/2023 06:07: Laoag SS 230kV Bus 2 de-energized at 0607H (Planned Outage) [WEBSMS] | CLUZ
8/28/2023 5:57:11 AM | [NSO Update] Luzon Grid-08/28/2023 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13664MW, PK=8595MW, RR=400MW, NetOpMargin: AM=4669, PM=4077, EVE=3475 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 180MW, Calaca 2 @ 173MW, Masinloc 1 @ 315MW, Masinloc 2 @ 300MW, Masinloc 3 @ 145MW [WEBSMS] | CLUZ
8/28/2023 5:49:53 AM | [NSO Update] Visayas Grid-08/28/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2595MW, PK=1968MW, RR=89MW, NetOpMargin: AM=538, PM=431, EVE=262 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 315MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/28/2023 5:49:41 AM | [NSO Update] Mindanao Grid-08/28/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3198MW, PK=1794MW, RR=60MW, NetOpMargin: AM=1344, PM=1238, EVE=1118 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @95MW, AG5 @42MW, AG6 @146MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/28/2023 4:23:35 AM | [NSO Update] Mindanao Grid-08/28/2023 04:25: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "GORING" {SAOLA} was estimated based on all available data at 210 km East of Casiguran, Aurora (16.2�N, 124.1�E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving East Southeastward at 15 km/h. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/28/2023 4:23:18 AM | [NSO Update] Visayas Grid-08/28/2023 04:23: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "GORING" {SAOLA} was estimated based on all available data at 210 km East of Casiguran, Aurora (16.2�N, 124.1�E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving East Southeastward at 15 km/h. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/28/2023 4:23:02 AM | [NSO Update] Luzon Grid-08/28/2023 04:23: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "GORING" {SAOLA} was estimated based on all available data at 210 km East of Casiguran, Aurora (16.2�N, 124.1�E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving East Southeastward at 15 km/h. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/28/2023 4:13:02 AM | [NSO Update] Mindanao Grid-08/28/2023 04:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0412H from reverse power direction. [WEBSMS] | CMIN
8/28/2023 4:12:42 AM | [NSO Update] Visayas Grid-08/28/2023 04:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0412H from reverse power direction. [WEBSMS] | CVIS
8/28/2023 1:49:10 AM | Mindanao Grid-08/28/2023 01:51: GNPK U1 shutdown at 0144H. (Planned Outage - Reserved shutdown). [WEBSMS] | CMIN
8/28/2023 12:13:23 AM | Luzon Grid-08/28/2023 00:13: For info: Commissioning and energization of Lal-lo PCB 5-05CB04LAL and 5-05CB24LAL Stub Protection was completed at 0012H. [WEBSMS] | CLUZ
8/27/2023 11:39:39 PM | Luzon Grid-08/27/2023 23:39: For info: Lal-lo - NAREDCO 69kV Line 1 looped at 2325H and declared commissioned at 2327H. [WEBSMS] | CLUZ
8/27/2023 11:18:49 PM | Mindanao Grid-08/27/2023 23:21: GNPK U3 Online at 2315H. (Planned Outage). [WEBSMS] | CMIN
8/27/2023 11:17:42 PM | Luzon Grid-08/27/2023 23:17: Lal-lo - NAREDCO 69kV Line 1 energized at Lal-lo side at 2310H (Ongoing Commissioning) [WEBSMS] | CLUZ
8/27/2023 8:38:42 PM | [NSO Update] Mindanao Grid-08/27/2023 20:41: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2037H with power going to Mindanao. [WEBSMS] | CMIN
8/27/2023 8:38:15 PM | [NSO Update] Visayas Grid-08/27/2023 20:38: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2037H with power going to Mindanao. [WEBSMS] | CVIS
8/27/2023 7:44:57 PM | Mindanao Grid-08/27/2023 19:47: Lake Mainit (AGC) HEP tripped with 10.5MW at 1913H. (Unplanned Outage) [WEBSMS] | CMIN
8/27/2023 7:44:51 PM | [NSO Update] Visayas Grid-08/27/2023 19:44: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1943H from reverse power direction. [WEBSMS] | CVIS
8/27/2023 7:44:31 PM | [NSO Update] Mindanao Grid-08/27/2023 19:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1943H from reverse power direction. [WEBSMS] | CMIN
8/27/2023 6:44:42 PM | Luzon Grid-08/27/2023 18:44: Ilijan GT1-2 online at 1843H (Unplanned Outage) [WEBSMS] | CLUZ
8/27/2023 5:47:35 PM | [NSO Update] Luzon Grid-08/27/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12593MW, PK=8716MW, RR=310MW, NetOpMargin: EVE=3567 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 180MW, Calaca 2 @ 173MW, Masinloc 1 @ 315MW, Masinloc 2 @ 300MW, Masinloc 3 @ 150MW, Ilijan A @ 150MW [WEBSMS] | CLUZ
8/27/2023 5:46:11 PM | [NSO Update] Visayas Grid-08/27/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2404MW, PK=2011MW, RR=87MW, NetOpMargin: EVE=305 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 315MW, PGPP 1 @ 36.5MW [WEBSMS] | CVIS
8/27/2023 5:45:27 PM | [NSO Update] Mindanao Grid-08/27/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3088MW, PK=1885MW, RR=59MW, NetOpMargin: EVE=1144 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @126MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
8/27/2023 5:41:56 PM | Visayas Grid-08/27/2023 17:42: Calongcalong SS 50 MVA 139/69 kV Transformer 1 energized at 1740H. (Planned Outage) [WEBSMS] | CVIS
8/27/2023 5:25:08 PM | Luzon Grid-08/27/2023 17:25: Ilijan A ST1 online at 1724H (Unplanned Outage) [WEBSMS] | CLUZ
8/27/2023 5:16:21 PM | [NSO Update] Luzon Grid-08/27/2023 17:16: Weather Update: At 3:00 PM today, the center of the eye of Super Typhoon "GORING" {SAOLA} was estimated based on all available data at 95 km East Northeast of Casiguran, Aurora (16.5�N,123.0�E) with max sustained winds of 185 km/h near the center and gustiness of up to 230 km/h. It is moving South Southeastward slowly. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/27/2023 5:16:06 PM | [NSO Update] Mindanao Grid-08/27/2023 17:18: Weather Update: At 3:00 PM today, the center of the eye of Super Typhoon "GORING" {SAOLA} was estimated based on all available data at 95 km East Northeast of Casiguran, Aurora (16.5�N,123.0�E) with max sustained winds of 185 km/h near the center and gustiness of up to 230 km/h. It is moving South Southeastward slowly. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/27/2023 5:15:53 PM | [NSO Update] Visayas Grid-08/27/2023 17:16: Weather Update: At 3:00 PM today, the center of the eye of Super Typhoon "GORING" {SAOLA} was estimated based on all available data at 95 km East Northeast of Casiguran, Aurora (16.5�N,123.0�E) with max sustained winds of 185 km/h near the center and gustiness of up to 230 km/h. It is moving South Southeastward slowly. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/27/2023 4:49:27 PM | Mindanao Grid-08/27/2023 16:51: Agus 2 U1 HEP synchronize at 1638H. (Planned Outage) [WEBSMS] | CMIN
8/27/2023 3:54:15 PM | Luzon Grid-08/27/2023 15:54: Ilijan A GT1-1 online at 1552H (Unplanned Outage) [WEBSMS] | CLUZ
8/27/2023 12:41:59 PM | [NSO Update] Luzon Grid-08/27/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12811MW, PK=8323MW, RR=333MW, NetOpMargin: PM=4155, EVE=3141 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: CALACA 1 @180MW, CALACA 2 @173MW, MASINLOC 1 @315MW, MASINLOC 2 @300MW, MSLC3 @150MW [WEBSMS] | CLUZ
8/27/2023 12:36:26 PM | [NSO Update] Visayas Grid-08/27/2023 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2543MW, PK=1961MW, RR=91MW, NetOpMargin: PM=491, EVE=246 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @315MW, PGPP1 @74MW [WEBSMS] | CVIS
8/27/2023 12:34:24 PM | [NSO Update] Mindanao Grid-08/27/2023 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3126MW, PK=1727MW, RR=60MW, NetOpMargin: PM=1338, EVE=1201 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @85MW, AG4 @126MW, AG5 @40MW, AG6 @149MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
8/27/2023 11:39:44 AM | Luzon Grid-08/27/2023 11:39: For info: Sta Rita Module 40 completed the fuel changeover from oil to nat gas at 1136H [WEBSMS] | CLUZ
8/27/2023 11:37:56 AM | Mindanao Grid-08/27/2023 11:40: Tacurong 138/69/13.8 kV T4 (100 MVA) energized 1044H. Planned Outage (PO00AB)/Non-GOMP. [WEBSMS] | CMIN
8/27/2023 11:15:55 AM | Luzon Grid-08/27/2023 11:16: Ilijan GT1-1 tripped from 14MW load at 1114H (Unplanned Outage) [WEBSMS] | CLUZ
8/27/2023 11:15:46 AM | [NSO Update] Visayas Grid-08/27/2023 11:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1111H with power going to Mindanao. [WEBSMS] | CVIS
8/27/2023 11:15:39 AM | [NSO Update] Mindanao Grid-08/27/2023 11:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1111H with power going to Mindanao. [WEBSMS] | CMIN
8/27/2023 11:12:19 AM | Luzon Grid-08/27/2023 11:12: Ilijan GT1-1 online at 1110H (Unplanned Outage). [WEBSMS] | CLUZ
8/27/2023 9:56:51 AM | [NSO Update] Visayas Grid-08/27/2023 09:56: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0955H with power going to Visayas. [WEBSMS] | CVIS
8/27/2023 9:56:46 AM | [NSO Update] Mindanao Grid-08/27/2023 09:59: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0955H with power going to Visayas. [WEBSMS] | CMIN
8/27/2023 7:53:43 AM | Visayas Grid-08/27/2023 07:53: Calongcalong Ss 50MVA Tr 1 de-energized at 0750H. (Planned Outage) [WEBSMS] | CVIS
8/27/2023 7:00:35 AM | Mindanao Grid-08/27/2023 07:02: Tacurong 138/69/13.8 kV T4 (100 MVA) deenergized 0651H. Planned Outage (PO00AB)/Non-GOMP. [WEBSMS] | CMIN
8/27/2023 6:33:00 AM | Luzon Grid-08/27/2023 06:33: Ilijan PCB 9-02CB04ILJ emergency shutdown at 0628H for rectification of hydraulic oil leak on Phase C (Unplanned Outage) [WEBSMS] | CLUZ
8/27/2023 5:55:53 AM | [NSO Update] Mindanao Grid-08/27/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2864MW, PK=1674MW, RR=60MW, NetOpMargin: AM=1131, PM=960, EVE=756 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @85MW, AG4 @126MW, AG5 @40MW, AG6 @149MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
8/27/2023 5:55:31 AM | [NSO Update] Visayas Grid-08/27/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2482MW, PK=1783MW, RR=89MW, NetOpMargin: AM=610, PM=560, EVE=266 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @335MW, PGPP1 @74MW [WEBSMS] | CVIS
8/27/2023 5:51:30 AM | [NSO Update] Luzon Grid-08/27/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13362MW, PK=8672MW, RR=332MW, NetOpMargin: AM=4358, PM=3638, EVE=2717 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @190MW, CLC2 @173MW, MSLC1 @315MW, MSLC2 @305MW, MSLC3 @270MW [WEBSMS] | CLUZ
8/27/2023 4:20:54 AM | [NSO Update] Mindanao Grid-08/27/2023 04:23: Weather Update: At 3:00 AM today, the center of the eye of Super Typhoon GORING was estimated based on all available data over the coastal waters of Palanan, Isabela (17.1N, 123.0 E) with maximum sustained winds of 185 km/h near the center and gustiness of up to 230 km/h. It is moving South Southwestward slowly. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/27/2023 4:20:35 AM | [NSO Update] Visayas Grid-08/27/2023 04:20: Weather Update: At 3:00 AM today, the center of the eye of Super Typhoon GORING was estimated based on all available data over the coastal waters of Palanan, Isabela (17.1N, 123.0 E) with maximum sustained winds of 185 km/h near the center and gustiness of up to 230 km/h. It is moving South Southwestward slowly. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/27/2023 4:20:12 AM | [NSO Update] Luzon Grid-08/27/2023 04:20: Weather Update: At 3:00 AM today, the center of the eye of Super Typhoon GORING was estimated based on all available data over the coastal waters of Palanan, Isabela (17.1N, 123.0 E) with maximum sustained winds of 185 km/h near the center and gustiness of up to 230 km/h. It is moving South Southwestward slowly. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/26/2023 9:59:15 PM | Visayas Grid-08/26/2023 21:59: Calongcalong 50 MVA TR2 energized at 2157H. (Planned Outage) [WEBSMS] | CVIS
8/26/2023 7:45:01 PM | Luzon Grid-08/26/2023 19:45: Ilijan GT1-1 (83MW) and ST1-1 (65MW) tripped at 1939H. [WEBSMS] | CLUZ
8/26/2023 7:36:52 PM | Luzon Grid-08/26/2023 19:37: Ilijan GT1-2 (116MW) tripped at 1933H. Lowest system frequency is 59.484Hz [WEBSMS] | CLUZ
8/26/2023 6:01:07 PM | [NSO Update] Mindanao Grid-08/26/2023 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2863MW, PK=2037MW, RR=20MW, NetOpMargin: EVE=806 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @85MW, AG4 @118MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @145MW [WEBSMS] | CMIN
8/26/2023 6:00:08 PM | [NSO Update] Visayas Grid-08/26/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2503MW, PK=2172MW, RR=87MW, NetOpMargin: EVE=244 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @320MW, PGPP1 @74MW [WEBSMS] | CVIS
8/26/2023 5:55:09 PM | [NSO Update] Mindanao Grid-08/26/2023 17:57: Weather Update: At 3:00 PM today, the center of the eye of Typhoon GORING was estimated based on all available data at 160 km East Southeast of Aparri, Cagayan or 145 km East Northeast of Tuguegarao City, Cagayan (18.0N, 123.1E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving Southward at 10 km/h. [WEBSMS] | CMIN
8/26/2023 5:54:48 PM | [NSO Update] Visayas Grid-08/26/2023 17:54: Weather Update: At 3:00 PM today, the center of the eye of Typhoon GORING was estimated based on all available data at 160 km East Southeast of Aparri, Cagayan or 145 km East Northeast of Tuguegarao City, Cagayan (18.0N, 123.1E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving Southward at 10 km/h. [WEBSMS] | CVIS
8/26/2023 5:54:22 PM | [NSO Update] Luzon Grid-08/26/2023 17:54: Weather Update: At 3:00 PM today, the center of the eye of Typhoon GORING was estimated based on all available data at 160 km East Southeast of Aparri, Cagayan or 145 km East Northeast of Tuguegarao City, Cagayan (18.0N, 123.1E) with maximum sustained winds of 155 km/h near the center and gustiness of up to 190 km/h. It is moving Southward at 10 km/h. [WEBSMS] | CLUZ
8/26/2023 5:52:38 PM | [NSO Update] Luzon Grid-08/26/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13494MW, PK=9067MW, RR=398MW, NetOpMargin: EVE=4029 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @200MW, CLC2 @173MW, MSLC1 @315MW, MSLC2 @300MW, MSLC3 @330MW, ILIJAN A @575MW [WEBSMS] | CLUZ
8/26/2023 4:45:43 PM | Luzon Grid-08/26/2023 16:45: Balsik-Olongapo 230kV Line restored at 1645H (Planned Outage) [WEBSMS] | CLUZ
8/26/2023 3:38:17 PM | Mindanao Grid-08/26/2023 15:40: MA3 tripped with 3.2MW load at 1528H. (Unplanned Outage). [WEBSMS] | CMIN
8/26/2023 3:22:45 PM | Luzon Grid-08/26/2023 15:22: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1519H (Planned Outage) [WEBSMS] | CLUZ
8/26/2023 3:16:50 PM | Mindanao Grid-08/26/2023 15:19: WMPC DG09 cut-out at 1514H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/26/2023 3:09:58 PM | Visayas Grid-08/26/2023 15:10: Colon-KSPC 138 KV Line 1 energized at 1509H. (Planned Outage) [WEBSMS] | CVIS
8/26/2023 1:09:22 PM | [NSO Update] Mindanao Grid-08/26/2023 13:11: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2868MW, PK=1865MW, RR=20MW, NetOpMargin: PM=983, EVE=805 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @85MW, AG4 @126MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
8/26/2023 1:06:09 PM | [NSO Update] Visayas Grid-08/26/2023 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2710MW, PK=2226MW, RR=88MW, NetOpMargin: PM=396, EVE=226 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @315MW, PGPP1 @74MW, TPC-THERMAL @82MW [WEBSMS] | CVIS
8/26/2023 1:00:50 PM | [NSO Update] Luzon Grid-08/26/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13897MW, PK=10195MW, RR=429MW, NetOpMargin: PM=3273, EVE=3123 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 1 @200MW, CALACA 2 @173MW, MASINLOC1 @315MW, MASINLOC2 @300MW, MASINLOC3 @330MW, SAN GABRIEL @409MW, Ilijan A @575MW [WEBSMS] | CLUZ
8/26/2023 12:19:16 PM | [NSO Update] Mindanao Grid-08/26/2023 12:21: Weather Update: The center of the eye of Typhoon GORING was estimated based on all available data, including those from Aparri Weather Radar, at 155 km East of Aparri, Cagayan (18.3 �N, 123.1 �E ). With Maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving South Southwestward at 10 km/h. [WEBSMS] | CMIN
8/26/2023 12:18:28 PM | [NSO Update] Visayas Grid-08/26/2023 12:18: Weather Update: The center of the eye of Typhoon GORING was estimated based on all available data, including those from Aparri Weather Radar, at 155 km East of Aparri, Cagayan (18.3 �N, 123.1 �E ). With Maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving South Southwestward at 10 km/h. [WEBSMS] | CVIS
8/26/2023 12:17:55 PM | [NSO Update] Luzon Grid-08/26/2023 12:18: at 1100H Weather Update: The center of the eye of Typhoon GORING was estimated based on all available data, including those from Aparri Weather Radar, at 155 km East of Aparri, Cagayan (18.3 �N, 123.1 �E ). With Maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving South Southwestward at 10 km/h. [WEBSMS] | CLUZ
8/26/2023 12:03:54 PM | [NSO Update] Mindanao Grid-08/26/2023 12:06: Weather Update: The center of the eye of Typhoon GORING was estimated based on all available data, including those from Aparri Weather Radar, at 155 km East of Aparri, Cagayan (18.3 �N, 123.1 �E ). [WEBSMS] | CMIN
8/26/2023 12:02:42 PM | [NSO Update] Visayas Grid-08/26/2023 12:02: Weather Update: The center of the eye of Typhoon GORING was estimated based on all available data, including those from Aparri Weather Radar, at 155 km East of Aparri, Cagayan (18.3 �N, 123.1 �E ). [WEBSMS] | CVIS
8/26/2023 12:00:34 PM | [NSO Update] Luzon Grid-08/26/2023 12:00: Weather Update: The center of the eye of Typhoon GORING was estimated based on all available data, including those from Aparri Weather Radar, at 155 km East of Aparri, Cagayan (18.3 �N, 123.1 �E ). [WEBSMS] | CLUZ
8/26/2023 9:53:29 AM | Mindanao Grid-08/26/2023 09:55: WMPC DG09 online as RPS at 0950H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/26/2023 9:04:56 AM | Luzon Grid-08/26/2023 09:05: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0903H (Planned Outage) [WEBSMS] | CLUZ
8/26/2023 8:35:27 AM | [NSO Update] Mindanao Grid-08/26/2023 08:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0831H with power going to Mindanao. [WEBSMS] | CMIN
8/26/2023 8:34:07 AM | [NSO Update] Visayas Grid-08/26/2023 08:34: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0831H with power going to Mindanao. [WEBSMS] | CVIS
8/26/2023 7:43:46 AM | Luzon Grid-08/26/2023 07:43: Balsik-Olongapo 230kV Line de-energized at 0741H (Planned Outage) [WEBSMS] | CLUZ
8/26/2023 7:08:34 AM | [NSO Update] Mindanao Grid-08/26/2023 07:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0704H with power going to Visayas. [WEBSMS] | CMIN
8/26/2023 7:07:12 AM | [NSO Update] Visayas Grid-08/26/2023 07:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0704H with power going to Visayas. [WEBSMS] | CVIS
8/26/2023 6:43:44 AM | Visayas Grid-08/26/2023 06:43: Calongcalong Ss 50MVA Tr 2 de-energized at 0635H. (Planned Outage) [WEBSMS] | CVIS
8/26/2023 5:48:44 AM | [NSO Update] Visayas Grid-08/26/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2445MW, PK=2001MW, RR=89MW, NetOpMargin: AM=355, PM=361, EVE=227 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @74MW, TPC-THERMAL @82MW [WEBSMS] | CVIS
8/26/2023 5:48:36 AM | [NSO Update] Mindanao Grid-08/26/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2869MW, PK=1924MW, RR=20MW, NetOpMargin: AM=925, PM=899, EVE=750 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @85MW, AG4 @126MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @140MW [WEBSMS] | CMIN
8/26/2023 5:44:54 AM | [NSO Update] Luzon Grid-08/26/2023 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14136MW, PK=10359MW, RR=416MW, NetOpMargin: AM=3361, PM=3023, EVE=3089 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 1 @200MW, CALACA 2 @173MW, MASINLOC1 @315MW, MASINLOC2 @300MW, MASINLOC3 @330MW, SAN GABRIEL @409MW [WEBSMS] | CLUZ
8/26/2023 4:42:30 AM | [NSO Update] Luzon Grid-08/26/2023 04:42: Weather Advisory: At 3:00 AM today, the center of Typhoon "GORING" {SAOLA} was estimated based on all available data at 195 km East of Calayan, Cagayan (19.1�N, 123.3�E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving Southwestward at 10 km/h. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/26/2023 4:42:26 AM | [NSO Update] Visayas Grid-08/26/2023 04:42: Weather Advisory: At 3:00 AM today, the center of Typhoon "GORING" {SAOLA} was estimated based on all available data at 195 km East of Calayan, Cagayan (19.1�N, 123.3�E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving Southwestward at 10 km/h. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/26/2023 4:42:22 AM | [NSO Update] Mindanao Grid-08/26/2023 04:44: Weather Advisory: At 3:00 AM today, the center of Typhoon "GORING" {SAOLA} was estimated based on all available data at 195 km East of Calayan, Cagayan (19.1�N, 123.3�E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving Southwestward at 10 km/h. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/26/2023 2:54:22 AM | Mindanao Grid-08/26/2023 02:56: GN Power (GKP) Coal Power Plant emergency shutdown at 0250H due to suspected boiler tube leak. No ETC. (Unplanned Outage). [WEBSMS] | CMIN
8/26/2023 2:04:23 AM | Luzon Grid-08/26/2023 02:04: San Jose PCB 9-06CB04SJO restored at 0204H (Unplanned Outage) [WEBSMS] | CLUZ
8/26/2023 1:07:00 AM | Luzon Grid-08/26/2023 01:07: San Jose PCB 9-06CB04SJO emergency shutdown at 0106H due to sudden decrease of SF6 gas pressure at associated DS 9A-06DS05SJO. (Unplanned Outage) [WEBSMS] | CLUZ
8/25/2023 11:46:18 PM | Luzon Grid-08/25/2023 23:46: Sta Rita Module 20 shutdown at 2342H (Planned Outage). [WEBSMS] | CLUZ
8/25/2023 10:50:30 PM | Mindanao Grid-08/25/2023 22:52: GNPK unit 1 cut-in at 2246H. [WEBSMS] | CMIN
8/25/2023 9:41:25 PM | Mindanao Grid-08/25/2023 21:43: WMPC DG09 cut-out at 2123H from RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/25/2023 7:03:19 PM | Luzon Grid-08/25/2023 19:03: QPPL online at 1851H (Unplanned Outage) [WEBSMS] | CLUZ
8/25/2023 5:39:53 PM | [NSO Update] Mindanao Grid-08/25/2023 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2955MW, PK=2115MW, RR=20MW, NetOpMargin: EVE=820 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @76MW, AG4 @118MW, AG5 @40MW, AG6 @141MW, AG7 @33MW, PG4 @145MW [WEBSMS] | CMIN
8/25/2023 5:36:31 PM | [NSO Update] Visayas Grid-08/25/2023 17:36: Weather Advisory: At 3:00 PM today, the center of Severe Tropical Storm "GORING" {SAOLA} was estimated based on all available data at 225 km East Southeast of Basco, Batanes (19.7�N, 124.0�E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving Southeastward slowly. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/25/2023 5:34:26 PM | [NSO Update] Visayas Grid-08/25/2023 17:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2516MW, PK=2182MW, RR=87MW, NetOpMargin: EVE=247 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 318MW, PGPP1 @ 74MW [WEBSMS] | CVIS
8/25/2023 5:33:54 PM | [NSO Update] Mindanao Grid-08/25/2023 17:36: Weather Advisory: At 3:00 PM today, the center of Severe Tropical Storm "GORING" {SAOLA} was estimated based on all available data at 225 km East Southeast of Basco, Batanes (19.7�N, 124.0�E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving Southeastward slowly. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/25/2023 5:33:43 PM | [NSO Update] Luzon Grid-08/25/2023 17:33: Weather Advisory: At 3:00 PM today, the center of Severe Tropical Storm "GORING" {SAOLA} was estimated based on all available data at 225 km East Southeast of Basco, Batanes (19.7�N, 124.0�E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving Southeastward slowly. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/25/2023 5:30:32 PM | [NSO Update] Luzon Grid-08/25/2023 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13192MW, PK=10258MW, RR=420MW, NetOpMargin: EVE=2514 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 325MW, Masinloc 2 @ 250MW, SLPGC 2 @ 130MW, Sta. Rita 20 @ 215MW [WEBSMS] | CLUZ
8/25/2023 4:54:38 PM | [NSO Update] Mindanao Grid-08/25/2023 16:56: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1653H with power going to Visayas. [WEBSMS] | CMIN
8/25/2023 4:54:35 PM | [NSO Update] Visayas Grid-08/25/2023 16:54: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1653H with power going to Visayas. [WEBSMS] | CVIS
8/25/2023 4:53:27 PM | [NSO Update] Mindanao Grid-08/25/2023 16:55: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1640H with power going to Mindanao. [WEBSMS] | CMIN
8/25/2023 4:53:12 PM | [NSO Update] Visayas Grid-08/25/2023 16:53: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1640H with power going to Mindanao. [WEBSMS] | CVIS
8/25/2023 4:30:17 PM | Mindanao Grid-08/25/2023 16:32: WMPC DG07 cut-out at 1613H from RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/25/2023 4:30:06 PM | Luzon Grid-08/25/2023 16:30: Balsik-Olongapo 230kV Line restored at 1629H (Unplanned Outage) [WEBSMS] | CLUZ
8/25/2023 3:49:51 PM | Visayas Grid-08/25/2023 15:49: Carcon - Sangi 34.5 kV Line 1 energized at 1546H. (Planned Outage) [WEBSMS] | CVIS
8/25/2023 2:53:38 PM | Mindanao Grid-08/25/2023 14:55: Agus 5 HEP Unit no. 2 cut-in at 14:08:41H. (Unplanned Outage) [WEBSMS] | CMIN
8/25/2023 1:28:57 PM | [NSO Update] Mindanao Grid-08/25/2023 13:31: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2989MW, PK=2040MW, RR=20MW, NetOpMargin: PM=929, EVE=910 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @76MW, AG4 @126MW, AG5 @40MW, AG6 @141MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
8/25/2023 1:16:15 PM | [NSO Update] Visayas Grid-08/25/2023 13:14: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2689MW, PK=2402MW, RR=91MW, NetOpMargin: PM=196, EVE=255 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 318MW, PGPP1 @ 74MW [WEBSMS] | CVIS
8/25/2023 1:09:43 PM | [NSO Update] Luzon Grid-08/25/2023 13:09: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13706MW, PK=11237MW, RR=458MW, NetOpMargin: PM=2011, EVE=2492 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 2 @ 250MW, Masinloc 3 @ 330MW, SLPGC 2 @ 130MW, Sta. Rita 20 @ 215MW [WEBSMS] | CLUZ
8/25/2023 1:04:11 PM | Mindanao Grid-08/25/2023 13:06: NSD cut-in at 1300H. Follow RTD. [WEBSMS] | CMIN
8/25/2023 12:05:16 PM | Mindanao Grid-08/25/2023 12:07: NSD cut-out at 1200H. Follow RTD. [WEBSMS] | CMIN
8/25/2023 11:52:57 AM | Mindanao Grid-08/25/2023 11:55: AG5 U2 Emergency shutdown at 1150H due to leakage at Turbine Fit. (Unplanned Outage). [WEBSMS] | CMIN
8/25/2023 11:31:35 AM | Mindanao Grid-08/25/2023 11:33: NSD online at 1130H. Follow RTD. [WEBSMS] | CMIN
8/25/2023 11:04:30 AM | Mindanao Grid-08/25/2023 11:06: FDC U3 online at 1100H. (Unplanned Outage). [WEBSMS] | CMIN
8/25/2023 10:55:15 AM | Mindanao Grid-08/25/2023 10:57: WMPC DG7 cut-in at 1053H. For RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/25/2023 10:45:05 AM | Mindanao Grid-08/25/2023 10:47: MA U3 cut-in at 1038H. From FO. (Unplanned Outage). [WEBSMS] | CMIN
8/25/2023 10:05:49 AM | Luzon Grid-08/25/2023 10:05: Balsik-Olongapo 230kV Line de-energized at 1005H (Unplanned Outage) [WEBSMS] | CLUZ
8/25/2023 9:44:30 AM | [NSO Update] Mindanao Grid-08/25/2023 09:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0943H with power going to Mindanao. [WEBSMS] | CMIN
8/25/2023 9:43:47 AM | [NSO Update] Visayas Grid-08/25/2023 09:43: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0943H with power going to Mindanao. [WEBSMS] | CVIS
8/25/2023 9:10:58 AM | Mindanao Grid-08/25/2023 09:13: AG2 U1cut-out at 0905H. (Planned Outage). [WEBSMS] | CMIN
8/25/2023 9:08:12 AM | [NSO Update] Mindanao Grid-08/25/2023 09:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0904H with power going to Visayas. [WEBSMS] | CMIN
8/25/2023 9:06:29 AM | [NSO Update] Visayas Grid-08/25/2023 09:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0904H with power going to Visayas. [WEBSMS] | CVIS
8/25/2023 9:03:12 AM | Mindanao Grid-08/25/2023 09:05: WMPC DG10 cut-in at 0900H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/25/2023 8:13:26 AM | Visayas Grid-08/25/2023 08:13: Carcon - Sangi 34.5 kV Line 1 de-energized at 0807H. (Planned Outage) [WEBSMS] | CVIS
8/25/2023 5:58:11 AM | [NSO Update] Luzon Grid-08/25/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13873MW, PK=10800MW, RR=439MW, NetOpMargin: AM=2634, PM=2084, EVE=2499 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 325MW, Masinloc 2 @ 250MW, Masinloc 3 @ 330MW, SLPGC 2 @ 130MW, Sta. Rita 20 @ 215MW [WEBSMS] | CLUZ
8/25/2023 5:55:05 AM | Mindanao Grid-08/25/2023 05:57: STEAG Unit 1 emergency shutdown at 0550H due to boiler fouling. (Unplanned Outage) [WEBSMS] | CMIN
8/25/2023 5:46:32 AM | [NSO Update] Visayas Grid-08/25/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2533MW, PK=2262MW, RR=89MW, NetOpMargin: AM=181, PM=182, EVE=249 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 335MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/25/2023 5:45:50 AM | [NSO Update] Mindanao Grid-08/25/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2989MW, PK=2010MW, RR=20MW, NetOpMargin: AM=960, PM=893, EVE=899 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @76MW, AG4 @126MW, AG5 @40MW, AG6 @141MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
8/25/2023 4:52:46 AM | Luzon Grid-08/25/2023 04:52: Kalayaan Units 1 (156MW) & 2 (148MW) tripped as pump at 0447H and 0446H, respectively. (Unplanned Outage) [WEBSMS] | CLUZ
8/25/2023 4:24:13 AM | [NSO Update] Luzon Grid-08/25/2023 04:24: Weather Update: At 3:00 AM today, the center of Tropical Storm "GORING" {SAOLA} was estimated based on all available data at 220 km East Southeast of Basco, Batanes (19.9�N, 124.0�E) with maximum sustained winds of 75 km/h near the center and gustiness of up to 90 km/h. It is moving Southwestward slowly. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/25/2023 4:24:00 AM | [NSO Update] Mindanao Grid-08/25/2023 04:26: Weather Update: At 3:00 AM today, the center of Tropical Storm "GORING" {SAOLA} was estimated based on all available data at 220 km East Southeast of Basco, Batanes (19.9�N, 124.0�E) with maximum sustained winds of 75 km/h near the center and gustiness of up to 90 km/h. It is moving Southwestward slowly. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/25/2023 4:23:47 AM | [NSO Update] Visayas Grid-08/25/2023 04:23: Weather Update: At 3:00 AM today, the center of Tropical Storm "GORING" {SAOLA} was estimated based on all available data at 220 km East Southeast of Basco, Batanes (19.9�N, 124.0�E) with maximum sustained winds of 75 km/h near the center and gustiness of up to 90 km/h. It is moving Southwestward slowly. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/24/2023 9:58:43 PM | Mindanao Grid-08/24/2023 22:01: Mt. Apo (MA3) Geothermal Power plant synchronized at 2149H. Unplanned Outage. [WEBSMS] | CMIN
8/24/2023 9:46:08 PM | Mindanao Grid-08/24/2023 21:48: WMPC DG10 cut-out at 2113H. RPS-System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
8/24/2023 9:07:02 PM | Luzon Grid-08/24/2023 21:07: QPPL (39MW) tripped at 2105H (Unplanned Outage) [WEBSMS] | CLUZ
8/24/2023 8:40:37 PM | Mindanao Grid-08/24/2023 20:42: Euro Hydro (NBT) HEPP synchronized at 2022H. Unplanned Outage [WEBSMS] | CMIN
8/24/2023 8:38:32 PM | Mindanao Grid-08/24/2023 20:40: NACSUR (NSD) cut-out at 2000H as energy. Dispatched by MO. Follow RTD. [WEBSMS] | CMIN
8/24/2023 8:25:08 PM | Luzon Grid-08/24/2023 20:25: QPPL online at 1957H (Unplanned Outage) [WEBSMS] | CLUZ
8/24/2023 6:41:32 PM | Mindanao Grid-08/24/2023 18:43: NACSUR (NSD) cut-in at 1802H as energy. Dispatched by MO. Follow RTD. [WEBSMS] | CMIN
8/24/2023 6:37:58 PM | Luzon Grid-08/24/2023 18:38: Concepcion-Concepcion BESS 69kV Line restored at 1835H (Planned Outage) [WEBSMS] | CLUZ
8/24/2023 6:36:28 PM | Mindanao Grid-08/24/2023 18:38: Euro Hydro (NBT) HEPP tripped with 1.5MW load at 1708H. Unplanned Outage [WEBSMS] | CMIN
8/24/2023 5:58:28 PM | [NSO Update] Luzon Grid-08/24/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13165MW, PK=10530MW, RR=398MW, NetOpMargin: EVE=2236 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 320MW, Masinloc 2 @ 250MW, SLPGC 1 @ 140MW, Ilijan A @ 550MW [WEBSMS] | CLUZ
8/24/2023 5:48:07 PM | [NSO Update] Visayas Grid-08/24/2023 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2487MW, PK=2133MW, RR=87MW, NetOpMargin: EVE=267 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 335MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/24/2023 5:47:38 PM | [NSO Update] Mindanao Grid-08/24/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3056MW, PK=2075MW, RR=20MW, NetOpMargin: EVE=961 Highest Unit O/L: GNPK 3 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @100MW, AG4 @118MW, AG5 @40MW, AG6 @126MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
8/24/2023 5:25:51 PM | [NSO Update] Mindanao Grid-08/24/2023 17:28: Weather update: At 3:00 PM today, the center of Tropical Storm "GORING" {SAOLA}was estimated based on all available data at 265 km East of Basco, Batanes (20.3�N, 124.5�E) with maximum sustained winds of 75 km/h near the center and gustiness of up to 90 km/h. It is moving Northwestward at 10 km/h. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/24/2023 5:25:08 PM | [NSO Update] Visayas Grid-08/24/2023 17:25: Weather update: At 3:00 PM today, the center of Tropical Storm "GORING" {SAOLA}was estimated based on all available data at 265 km East of Basco, Batanes (20.3�N, 124.5�E) with maximum sustained winds of 75 km/h near the center and gustiness of up to 90 km/h. It is moving Northwestward at 10 km/h. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/24/2023 5:22:09 PM | [NSO Update] Luzon Grid-08/24/2023 17:22: Weather update: At 3:00 PM today, the center of Tropical Storm "GORING" {SAOLA}was estimated based on all available data at 265 km East of Basco, Batanes (20.3�N, 124.5�E) with maximum sustained winds of 75 km/h near the center and gustiness of up to 90 km/h. It is moving Northwestward at 10 km/h. Southwest Monsoon affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/24/2023 5:18:44 PM | [NSO Update] Visayas Grid-08/24/2023 17:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1714H with power going to Visayas. [WEBSMS] | CVIS
8/24/2023 5:18:32 PM | [NSO Update] Mindanao Grid-08/24/2023 17:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1714H with power going to Visayas. [WEBSMS] | CMIN
8/24/2023 5:17:48 PM | [NSO Update] Mindanao Grid-08/24/2023 17:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1701H. [WEBSMS] | CMIN
8/24/2023 5:17:35 PM | [NSO Update] Visayas Grid-08/24/2023 17:17: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1701H. [WEBSMS] | CVIS
8/24/2023 5:12:57 PM | Mindanao Grid-08/24/2023 17:15: NACSUR (NSD) cut-out at 1700H as energy. Dispatched by MO. Follow RTD. [WEBSMS] | CMIN
8/24/2023 5:04:50 PM | Mindanao Grid-08/24/2023 17:07: WMPC DG01 cut-out at 1614H. RPS-System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
8/24/2023 4:15:17 PM | Visayas Grid-08/24/2023 16:15: Carcon - Sangi 34.5 kV Line 2 energized at 1611H activity completed. [WEBSMS] | CVIS
8/24/2023 3:55:04 PM | Mindanao Grid-08/24/2023 15:57: FDC (FMP) Unit No.3 emergency shutdown at 1526H due to boiler seal pot line-B leaking. (Unplanned Outage) [WEBSMS] | CMIN
8/24/2023 3:23:00 PM | Mindanao Grid-08/24/2023 15:25: Agus 6 HEP Unit 5 cut-in at 1503H from Planned Outage (PMS-GOMP). [WEBSMS] | CMIN
8/24/2023 3:03:01 PM | Mindanao Grid-08/24/2023 15:05: Peak Power San Francisco U2 cut-in at 1500H as energy. Follow RTD [WEBSMS] | CMIN
8/24/2023 2:20:39 PM | Mindanao Grid-08/24/2023 14:22: NACSUR (NSD) cut-in at 1400H as energy. Dispatched by MO. Follow RTD. [WEBSMS] | CMIN
8/24/2023 1:43:47 PM | [NSO Update] Visayas Grid-08/24/2023 13:43: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1342H with power going to Mindanao. [WEBSMS] | CVIS
8/24/2023 1:43:43 PM | [NSO Update] Mindanao Grid-08/24/2023 13:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1342H with power going to Mindanao. [WEBSMS] | CMIN
8/24/2023 1:42:13 PM | [NSO Update] Visayas Grid-08/24/2023 13:42: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1323H with power going to Visayas. [WEBSMS] | CVIS
8/24/2023 1:25:35 PM | [NSO Update] Mindanao Grid-08/24/2023 13:27: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1323H with power going to Visayas. [WEBSMS] | CMIN
8/24/2023 1:06:50 PM | Mindanao Grid-08/24/2023 13:09: Toril-Davao Coal Plant 138kV L2 de-energized 1302H. Planned outage [WEBSMS] | CMIN
8/24/2023 12:55:54 PM | [NSO Update] Mindanao Grid-08/24/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3190MW, PK=2181MW, RR=20MW, NetOpMargin: PM=990, EVE=994 Highest Unit O/L: GNPK 3&4 @ 138MW Derated Plant: MCC @150MW,MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @100MW, AG4 @118MW, AG5 @40MW, AG6 @106MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
8/24/2023 12:43:54 PM | [NSO Update] Visayas Grid-08/24/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2546MW, PK=2251MW, RR=92MW, NetOpMargin: PM=204, EVE=263 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @335MW, PGPP1 @74MW [WEBSMS] | CVIS
8/24/2023 12:32:44 PM | [NSO Update] Luzon Grid-08/24/2023 12:32: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13615MW, PK=11444MW, RR=462MW, NetOpMargin: PM=1708, EVE=2053 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @173MW, MASINLOC1 @320MW, MASINLOC2 @250MW, SLPGC 1 @75MW, ILIJAN A @505MW [WEBSMS] | CLUZ
8/24/2023 12:09:00 PM | Mindanao Grid-08/24/2023 12:11: WMPC DG10 online at 1159H. RPS-System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
8/24/2023 11:48:49 AM | Mindanao Grid-08/24/2023 11:51: WMPC DG10 tripped at 1131H due to Plug Connection Loop Test. (Unplanned Outage) [WEBSMS] | CMIN
8/24/2023 10:53:09 AM | Mindanao Grid-08/24/2023 10:55: WMPC DG01 online at 1050H as RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/24/2023 10:27:26 AM | Mindanao Grid-08/24/2023 10:29: WMPC DG10 online at 1021H as replacement of DG05 which tripped earlier. RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/24/2023 10:24:07 AM | Mindanao Grid-08/24/2023 10:26: WMPC DG05 tripped at 1012H, due to HT High Pressure. (Unplanned Outage) [WEBSMS] | CMIN
8/24/2023 8:54:27 AM | Mindanao Grid-08/24/2023 08:56: WMPC DG05 online at 0850H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/24/2023 8:15:39 AM | Visayas Grid-08/24/2023 08:15: Carcon - Sangi 34.5 kV Line 2 de-energized at 0810H. (Planned Outage) [WEBSMS] | CVIS
8/24/2023 7:49:03 AM | Luzon Grid-08/24/2023 07:49: QPPL tripped at 0746H (Unplanned Outage) [WEBSMS] | CLUZ
8/24/2023 7:23:26 AM | Luzon Grid-08/24/2023 07:23: QPPL online at 0721H (Unplanned Outage) [WEBSMS] | CLUZ
8/24/2023 6:24:34 AM | [NSO Update] Luzon Grid-08/24/2023 06:24: Weather Disturbance Alert Notice (WDAN) is issued at 0500H. The Low-Pressure Area inside the PAR has developed into Tropical Depression �GORING�. The center was estimated based on all available data at 400km East Northeast of Aparri, Cagayan (19.2N, 125.3E) with max sustained winds of 55kmh near the center and gustiness of up to 70 km/h. It is moving West Northwestward slowly. [WEBSMS] | CLUZ
8/24/2023 6:24:08 AM | [NSO Update] Mindanao Grid-08/24/2023 06:26: Weather Disturbance Alert Notice (WDAN) is issued at 0500H. The Low-Pressure Area inside the PAR has developed into Tropical Depression �GORING�. The center was estimated based on all available data at 400km East Northeast of Aparri, Cagayan (19.2N, 125.3E) with max sustained winds of 55kmh near the center and gustiness of up to 70 km/h. It is moving West Northwestward slowly. [WEBSMS] | CMIN
8/24/2023 6:23:53 AM | [NSO Update] Visayas Grid-08/24/2023 06:23: Weather Disturbance Alert Notice (WDAN) is issued at 0500H. The Low-Pressure Area inside the PAR has developed into Tropical Depression �GORING�. The center was estimated based on all available data at 400km East Northeast of Aparri, Cagayan (19.2N, 125.3E) with max sustained winds of 55kmh near the center and gustiness of up to 70 km/h. It is moving West Northwestward slowly. [WEBSMS] | CVIS
8/24/2023 5:47:51 AM | [NSO Update] Luzon Grid-08/24/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13782MW, PK=11289MW, RR=382MW, NetOpMargin: AM=2111, PM=1613, EVE=2192 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC1 @320MW, MSLC2 @250MW, SLPGC 1 @75MW, ILIJAN A @505MW [WEBSMS] | CLUZ
8/24/2023 5:35:55 AM | [NSO Update] Visayas Grid-08/24/2023 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2559MW, PK=2191MW, RR=89MW, NetOpMargin: AM=279, PM=238, EVE=287 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @335MW, PGPP1 @74MW [WEBSMS] | CVIS
8/24/2023 5:35:28 AM | [NSO Update] Mindanao Grid-08/24/2023 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3191MW, PK=2100MW, RR=20MW, NetOpMargin: AM=1071, PM=1057, EVE=1062 Highest Unit O/L: GNPK 3&4 @138MW Derated Plant: MCC @150MW,MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @100MW, AG4 @109MW, AG5 @40MW, AG6 @106MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
8/24/2023 5:02:59 AM | [NSO Update] Mindanao Grid-08/24/2023 05:05: Weather Update: At 3:00 AM today, the center of the Tropical Depression (outside PAR) was estimated based on all available data at 400 km East Northeast of Aparri, Cagayan (19.2 N, 125.3 E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving West Northwestward slowly. Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/24/2023 5:02:42 AM | [NSO Update] Visayas Grid-08/24/2023 05:02: Weather Update: At 3:00 AM today, the center of the Tropical Depression (outside PAR) was estimated based on all available data at 400 km East Northeast of Aparri, Cagayan (19.2 N, 125.3 E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving West Northwestward slowly. Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/24/2023 5:02:11 AM | [NSO Update] Luzon Grid-08/24/2023 05:02: Weather Update: At 3:00 AM today, the center of the Tropical Depression (outside PAR) was estimated based on all available data at 400 km East Northeast of Aparri, Cagayan (19.2 N, 125.3 E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving West Northwestward slowly. Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/24/2023 4:28:49 AM | Luzon Grid-08/24/2023 04:28: Balsik 1000MVA Transfomer Bank 1 restored at 0428H (Planned Outage) [WEBSMS] | CLUZ
8/24/2023 2:43:34 AM | Luzon Grid-08/24/2023 02:43: Sta Rita Module 20 completed the fuel changeover from gas to oil at 0239H. [WEBSMS] | CLUZ
8/24/2023 12:49:01 AM | Visayas Grid-08/24/2023 00:49: Magdugo - Calongcalong 138 kV Line 1 energized at 0046H. (Planned Outage) [WEBSMS] | CVIS
8/24/2023 12:14:32 AM | Luzon Grid-08/24/2023 00:14: Sta Rita Module 10 completed the fuel changeover form gas to oil at 0011H. [WEBSMS] | CLUZ
8/23/2023 11:37:17 PM | Mindanao Grid-08/23/2023 23:39: GNPK Unit 1 cut-out at 2329H on reserved shutdown. [WEBSMS] | CMIN
8/23/2023 11:26:16 PM | Visayas Grid-08/23/2023 23:26: Cebu SS bus 1 energized at 2323H. (Planned Outage) [WEBSMS] | CVIS
8/23/2023 11:17:04 PM | Luzon Grid-08/23/2023 23:17: Muntinlupa 115kV Bus 1 was energized at 2312H (Planned Outage). [WEBSMS] | CLUZ
8/23/2023 10:53:38 PM | Luzon Grid-08/23/2023 22:53: Muntinlupa 115kV Bus 1 and Muntinlupa 50MVAR Capacitor Bank 1 were de-energized at 2251H (Planned Outage). [WEBSMS] | CLUZ
8/23/2023 9:43:31 PM | Mindanao Grid-08/23/2023 21:45: WMPC DG01 cut-out at 2114H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/23/2023 9:38:51 PM | Luzon Grid-08/23/2023 21:38: Ilijan GT2-2 shutdown at 2137H (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2023 9:17:14 PM | Luzon Grid-08/23/2023 21:17: Ilijan ST2 shutdown at 2115H (Unplanned Outage). [WEBSMS] | CLUZ
8/23/2023 8:40:26 PM | Luzon Grid-08/23/2023 20:40: Balsik 1000MVA Transfomer Bank 1 was de-energized at 2038H (Planned Outage). [WEBSMS] | CLUZ
8/23/2023 8:26:46 PM | Luzon Grid-08/23/2023 20:26: Sta Rita Module 40 fuel changeover from gas to oil was completed at 2016H. [WEBSMS] | CLUZ
8/23/2023 8:08:29 PM | Mindanao Grid-08/23/2023 20:10: Nickle Asia Diesel Plant cut-out at 2000H from energy (RTD) dispatch. [WEBSMS] | CMIN
8/23/2023 7:13:31 PM | Mindanao Grid-08/23/2023 19:15: Mt. Apo 3 Binary Plant tripped with 3.2 MW at 1854H due to acid dosage problem. (Unplanned Outage) [WEBSMS] | CMIN
8/23/2023 6:54:07 PM | Mindanao Grid-08/23/2023 18:56: Nickle Asia Diesel Plant cut-in at 1800H as energy (RTD). [WEBSMS] | CMIN
8/23/2023 6:39:41 PM | Luzon Grid-08/23/2023 18:39: QPPL tripped at 1837H(41MW) (Unplanned Outage). [WEBSMS] | CLUZ
8/23/2023 6:21:51 PM | Mindanao Grid-08/23/2023 18:24: Butuan - San Franscisco 138kV Line tripped at 17:55:25 H and autoreclosed at 17:55:28 H. (Unplanned Outage) [WEBSMS] | CMIN
8/23/2023 6:11:29 PM | Luzon Grid-08/23/2023 18:11: SLPGC Unit 1 online at 1807H (Unplanned Outage). [WEBSMS] | CLUZ
8/23/2023 5:55:13 PM | Luzon Grid-08/23/2023 17:55: QPPL online at 1748H from an unplanned outage. [WEBSMS] | CLUZ
8/23/2023 5:54:30 PM | [NSO Update] Mindanao Grid-08/23/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3144MW, PK=2041MW, RR=20MW, NetOpMargin: EVE=1083 Highest Unit O/L: GNPK 1&3 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @100MW, AG4 @113MW, AG5 @40MW, AG6 @106MW, AG7 @34MW, PG4 @135MW [WEBSMS] | CMIN
8/23/2023 5:46:31 PM | [NSO Update] Visayas Grid-08/23/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2420MW, PK=2041MW, RR=87MW, NetOpMargin: EVE=292 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @333MW, PGPP1 @75MW, TPC-THERMAL @82MW [WEBSMS] | CVIS
8/23/2023 5:40:40 PM | [NSO Update] Luzon Grid-08/23/2023 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12784MW, PK=10624MW, RR=432MW, NetOpMargin: EVE=1728 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC1 @325MW, MSLC2 @140MW, SLPGC 2 @120MW, ILIJAN A @340MW, ILIJAN B @165MW [WEBSMS] | CLUZ
8/23/2023 5:14:18 PM | Mindanao Grid-08/23/2023 17:16: Nickle Asia Diesel Plant cut-out at 1703H from energy (RTD) dispatch. [WEBSMS] | CMIN
8/23/2023 5:12:20 PM | Mindanao Grid-08/23/2023 17:14: Kidapawan SS 50MVA Transformer No. 2 re-energized at 1703H. (Unplanned Outage) [WEBSMS] | CMIN
8/23/2023 5:12:07 PM | Mindanao Grid-08/23/2023 17:14: Mt. Apo 3 Binary Plant cut-in at 1703H. (Unplanned Outage) [WEBSMS] | CMIN
8/23/2023 4:56:00 PM | Mindanao Grid-08/23/2023 16:58: Agus 1 Unit 1 HEP cut-in at 1638H. (Planned Outage) [WEBSMS] | CMIN
8/23/2023 4:36:35 PM | Mindanao Grid-08/23/2023 16:38: GNPK Unit 4 cut-in at 1622H. (Unplanned Outage) [WEBSMS] | CMIN
8/23/2023 4:17:21 PM | Mindanao Grid-08/23/2023 16:19: WMPC DG10 cut-out at 1611H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/23/2023 3:09:25 PM | Luzon Grid-08/23/2023 15:09: Ambuklao - Bayombong 230kV Line 1 & 2 auto-tripped/auto-reclosed successfully at both sides at 1446H (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2023 2:58:06 PM | Luzon Grid-08/23/2023 14:58: Ambuklao - Bayombong 230kV Line 1 auto-tripped/auto-reclosed successfully at both sides at 1446H (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2023 2:02:55 PM | Mindanao Grid-08/23/2023 14:05: Kauswagan-GNPK 230kV L4 energized 1400H. Planned outage / Non GOMP [WEBSMS] | CMIN
8/23/2023 1:17:07 PM | Mindanao Grid-08/23/2023 13:19: Pulangi 4 Unit #2 online at 1259H. (Planned Outage) [WEBSMS] | CMIN
8/23/2023 1:08:28 PM | Mindanao Grid-08/23/2023 13:10: STEAG Unit #2 shutdown at 1300H, emergency shutdown due to fouling of boiler. follow RTD. (Unplanned Outage) [WEBSMS] | CMIN
8/23/2023 1:05:48 PM | Mindanao Grid-08/23/2023 13:08: Maramag-Pulangi 4 138kV L2 energized 1259H with newly installed 7-08CB24MRM. Planned outage / Non GOMP [WEBSMS] | CMIN
8/23/2023 12:51:42 PM | Mindanao Grid-08/23/2023 12:53: WMPC DG05 run as RPS tripped at 1059H due to B-Bank Turbine Side Shock Pulse Alarm. (Unplanned Outage) [WEBSMS] | CMIN
8/23/2023 12:51:10 PM | [NSO Update] Mindanao Grid-08/23/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3005MW, PK=2062MW, RR=20MW, NetOpMargin: PM=923, EVE=964 Highest Unit O/L: GNPK 1&3@138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG2 @100MW, AG4 @110MW, AG5 @30MW, AG6 @106MW, AG7 @32MW, PG4 @135MW [WEBSMS] | CMIN
8/23/2023 12:49:44 PM | [NSO Update] Visayas Grid-08/23/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2531MW, PK=2217MW, RR=91MW, NetOpMargin: PM=223, EVE=291 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 333MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/23/2023 12:44:57 PM | [NSO Update] Luzon Grid-08/23/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13441MW, PK=11613MW, RR=477MW, NetOpMargin: PM=1352, EVE=1836 Highest Unit O/L: GNPD 1& 2 @668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 325MW, Masinloc 2 @ 130MW, Ilijan A @ 340MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
8/23/2023 12:44:16 PM | [NSO Update] Visayas Grid-08/23/2023 12:44: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1242H with power going to Visayas [WEBSMS] | CVIS
8/23/2023 12:44:15 PM | Mindanao Grid-08/23/2023 12:46: WMPC DG01 online at 1051H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/23/2023 12:43:54 PM | [NSO Update] Mindanao Grid-08/23/2023 12:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1242H with power going to Visayas [WEBSMS] | CMIN
8/23/2023 12:08:16 PM | [NSO Update] Visayas Grid-08/23/2023 12:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1207H with power going to Visayas. [WEBSMS] | CVIS
8/23/2023 12:08:12 PM | [NSO Update] Mindanao Grid-08/23/2023 12:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1207H with power going to Visayas. [WEBSMS] | CMIN
8/23/2023 9:56:03 AM | Mindanao Grid-08/23/2023 09:58: GNPK Unit #4 shutdown at 0905H, to facilitate Installation of Outdoor GIS Refilling Station. Follow RTD. (Unplanned Outage). [WEBSMS] | CMIN
8/23/2023 9:33:23 AM | Mindanao Grid-08/23/2023 09:35: Kauswagan-GNPK 230kV L4 de-energized 0926H to facilitate installation of the U4 Outdoor GIS SF6 refilling station as requested by GNPK [WEBSMS] | CMIN
8/23/2023 9:32:26 AM | Mindanao Grid-08/23/2023 09:34: Agus 1 Unit #1 shutdown at 0909H, to facilitate cleaning of unit�s main strainer. Follow RTD. (Planned Outage) [WEBSMS] | CMIN
8/23/2023 9:28:57 AM | Luzon Grid-08/23/2023 09:29: Bolo-Sual 230kV L1 restored at 0928H (Unplanned Outage). [WEBSMS] | CLUZ
8/23/2023 9:20:45 AM | Luzon Grid-08/23/2023 09:20: Sta. Rita Module 20 online at 0919H (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2023 8:28:02 AM | Visayas Grid-08/23/2023 08:28: Cebu SS bus 1 de-energized at 0825H. (Planned Outage) [WEBSMS] | CVIS
8/23/2023 8:12:39 AM | Mindanao Grid-08/23/2023 08:14: Pulangi 4 Unit #2 shutdown at 0810H, to facilitate simulation of back up protection of NPC Pulangi IV HEP unit # 2 in preparation for the energization of newly installed 7-08CB24MRM. Follow RTD. (Planned Outage) [WEBSMS] | CMIN
8/23/2023 8:08:31 AM | Luzon Grid-08/23/2023 08:08: Concepcion-Concepcion BESS 69kV Line de-energized at 0807H (Planned Outage) [WEBSMS] | CLUZ
8/23/2023 8:03:18 AM | Visayas Grid-08/23/2023 08:03: Colon SS 138 KV bus 2 energized at 0752H. (Planned Outage) [WEBSMS] | CVIS
8/23/2023 7:51:00 AM | Luzon Grid-08/23/2023 07:51: Masinloc Unit 2 online at 0749H (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2023 6:53:28 AM | Luzon Grid-08/23/2023 06:53: Sta. Rita Module 20 (169MW) tripped at 0650H. Lowest system frequency is 59.243Hz. [WEBSMS] | CLUZ
8/23/2023 5:56:25 AM | [NSO Update] Luzon Grid-08/23/2023 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13564MW, PK=11387MW, RR=382MW, NetOpMargin: AM=1795, PM=1402, EVE=1908 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 325MW, Ilijan A @ 340MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
8/23/2023 5:53:40 AM | [NSO Update] Mindanao Grid-08/23/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3067MW, PK=2129MW, RR=20MW, NetOpMargin: AM=918, PM=920, EVE=874 Highest Unit O/L: GNPK 1, 2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @100MW, AG4 @110MW, AG5 @30MW, AG6 @106MW, AG7 @32MW, PG4 @65MW [WEBSMS] | CMIN
8/23/2023 5:53:05 AM | [NSO Update] Visayas Grid-08/23/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2588MW, PK=2095MW, RR=89MW, NetOpMargin: AM=403, PM=234, EVE=253 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 333MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/23/2023 5:49:34 AM | Luzon Grid-08/23/2023 05:49: Muntinlupa 300MVA T02 restored at 0548H (Planned Outage) [WEBSMS] | CLUZ
8/23/2023 5:29:09 AM | Luzon Grid-08/23/2023 05:29: Taytay 230kV Bus 1 restored at 0527H (Planned Outage) [WEBSMS] | CLUZ
8/23/2023 5:09:55 AM | Luzon Grid-08/23/2023 05:10: Bolo-Sual 230kV L1 de-energized at 0509H (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2023 4:50:21 AM | Visayas Grid-08/23/2023 04:50: Colon SS 138 kV Bus no. 2 de-energized at 0449H. (Planned Outage) [WEBSMS] | CVIS
8/23/2023 4:48:00 AM | Mindanao Grid-08/23/2023 04:50: GNPK Unit #3 online at 0438H, from reserve shutdown. Follow RTD. [WEBSMS] | CMIN
8/23/2023 4:38:00 AM | Visayas Grid-08/23/2023 04:38: Colon SS 100 MVA 138/69 kV Transformer no. 2 de-energized at 0433H. (Planned Outage) [WEBSMS] | CVIS
8/23/2023 4:24:33 AM | [NSO Update] Luzon Grid-08/23/2023 04:24: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 570 km East of Aparri, Cagayan (19.1�N, 127.0�E). Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/23/2023 4:24:15 AM | [NSO Update] Mindanao Grid-08/23/2023 04:26: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 570 km East of Aparri, Cagayan (19.1�N, 127.0�E). Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/23/2023 4:23:59 AM | [NSO Update] Visayas Grid-08/23/2023 04:24: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 570 km East of Aparri, Cagayan (19.1�N, 127.0�E). Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/23/2023 3:42:23 AM | Luzon Grid-08/23/2023 03:42: Sta Rita Module 30 online at 0339H (Unplanned Outage) [WEBSMS] | CLUZ
8/23/2023 2:01:12 AM | Mindanao Grid-08/23/2023 02:03: NagaMin 138kV Transformer No. 3 energized 0137H Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/23/2023 1:29:14 AM | Luzon Grid-08/23/2023 01:29: Muntinlupa 300MVA T02 de-energized at 0127H (Planned Outage) [WEBSMS] | CLUZ
8/23/2023 1:18:20 AM | Mindanao Grid-08/23/2023 01:20: NagaMin 138kV Transformer No. 3 deenergized 0019H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/22/2023 11:47:06 PM | Luzon Grid-08/22/2023 23:47: Sta. Rita Module 40 online at 2343H (Unplanned Outage). [WEBSMS] | CLUZ
8/22/2023 11:40:22 PM | Luzon Grid-08/22/2023 23:40: Masinloc U2 @88MW tripped at 2331H. Lowest system frequency is 59.68Hz (Unplanned Outage) [WEBSMS] | CLUZ
8/22/2023 10:49:46 PM | Luzon Grid-08/22/2023 22:38: Tayatay 230kV Bus 1 de-energized at 2237H (Planned Outage) [WEBSMS] | CLUZ
8/22/2023 10:48:17 PM | Luzon Grid-08/22/2023 22:48: Tayatay 230kV Bus 1 de-energized at 2237H (Planned Outage) [WEBSMS] | CLUZ
8/22/2023 10:31:02 PM | Luzon Grid-08/22/2023 22:31: Batangas transformers 4 and 5 parallel at 2156H (Unplanned Outage) [WEBSMS] | CLUZ
8/22/2023 9:48:49 PM | Luzon Grid-08/22/2023 21:48: Sta. Rita-San Lorenzo 230kV Bus A & B unloop at 2145H (Unplanned Outage) [WEBSMS] | CLUZ
8/22/2023 9:20:16 PM | Mindanao Grid-08/22/2023 21:22: WMPC DG05 cut-out at 2114H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/22/2023 9:12:21 PM | Luzon Grid-08/22/2023 21:12: QPPL tripped with 85MW load at 2109H (Unplanned Outage) [WEBSMS] | CLUZ
8/22/2023 7:58:25 PM | Visayas Grid-08/22/2023 19:58: 69kV Lapulapu-Pajo Feeder restored at 1852H. Unplanned outage [WEBSMS] | CVIS
8/22/2023 7:56:10 PM | Luzon Grid-08/22/2023 19:56: QPPL online at 1953H (Unplanned Outage) [WEBSMS] | CLUZ
8/22/2023 6:01:11 PM | [NSO Update] Luzon Grid-08/22/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11968MW, PK=10579MW, RR=318MW, NetOpMargin: EVE=1070 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 325MW, Masinloc 2 @ 150MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
8/22/2023 5:59:33 PM | [NSO Update] Mindanao Grid-08/22/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3234MW, PK=2246MW, RR=20MW, NetOpMargin: EVE=968 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @100MW, AG4 @126MW, AG5 @40MW, AG6 @106MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
8/22/2023 5:56:14 PM | [NSO Update] Visayas Grid-08/22/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2505MW, PK=2094MW, RR=87MW, NetOpMargin: EVE=324 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 330MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/22/2023 5:30:22 PM | Visayas Grid-08/22/2023 17:30: 69kV Lapulapu-Pajo Feeder tripped at 1724H. Unplanned outage [WEBSMS] | CVIS
8/22/2023 5:12:02 PM | Visayas Grid-08/22/2023 17:12: Compostela-Cebu 138kV Line 2 looped at 1655H. Unplanned outage. [WEBSMS] | CVIS
8/22/2023 4:43:34 PM | Visayas Grid-08/22/2023 16:43: Compostela-Cebu 138kV Line 2 tripped at 1634H, reclosed at Compostela side. Unplanned outage. [WEBSMS] | CVIS
8/22/2023 3:47:18 PM | Luzon Grid-08/22/2023 15:47: San Jose SS 750MVA T04 restored at 1547H (Planned Outage) [WEBSMS] | CLUZ
8/22/2023 1:30:03 PM | Mindanao Grid-08/22/2023 13:32: Agus 6 Unit 5 138kV line deenergized at 1255H. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2023 1:00:48 PM | [NSO Update] Luzon Grid-08/22/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13230MW, PK=11663MW, RR=439MW, NetOpMargin: PM=1128, EVE=1591 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC1 @325MW, MSLC2 @325MW, ILIJAN B @300MW [WEBSMS] | CLUZ
8/22/2023 12:58:26 PM | [NSO Update] Mindanao Grid-08/22/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3272MW, PK=2343MW, RR=20MW, NetOpMargin: PM=909, EVE=960 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MCO @270MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @100MW, AG4 @126MW, AG5 @40MW, AG6 @106MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
8/22/2023 12:56:26 PM | [NSO Update] Visayas Grid-08/22/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2653MW, PK=2250MW, RR=91MW, NetOpMargin: PM=311, EVE=297 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @330MW, PGPP1 @75MW, TPC-Carmen @30MW [WEBSMS] | CVIS
8/22/2023 11:59:55 AM | Mindanao Grid-08/22/2023 12:02: WMPC DG05 cut-in at 1133H. Resumption of RPS - System Voltage Requirement. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2023 11:23:52 AM | Mindanao Grid-08/22/2023 11:26: WMPC DG05 tripped at 1112 with 8.5 MW load. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2023 11:07:55 AM | Mindanao Grid-08/22/2023 11:10: WMPC DG05 cut-in at 1101H. Resumption of RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/22/2023 11:06:27 AM | Mindanao Grid-08/22/2023 11:08: WMPC DG01 cut-in at 1049H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/22/2023 10:47:33 AM | Mindanao Grid-08/22/2023 10:49: WMPC DG05 tripped at 1034H with 8.5 MW load due to shock turbo pulse alarm at turbo charger B bank. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2023 10:43:11 AM | Mindanao Grid-08/22/2023 10:45: Agus 6 30 MVA Transformer totally isolated at 0925H. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2023 9:08:56 AM | Mindanao Grid-08/22/2023 09:11: Agus 6 HEP Unit 5 cut-out at 0902H. (Planned Outage) [WEBSMS] | CMIN
8/22/2023 8:58:39 AM | Mindanao Grid-08/22/2023 09:00: WMPC DG05 cut-in at 0851H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/22/2023 8:24:26 AM | Luzon Grid-08/22/2023 08:24: San Jose SS 750MVA T04 de-energized at 0823H (Planned Outage) [WEBSMS] | CLUZ
8/22/2023 8:08:56 AM | Luzon Grid-08/22/2023 08:08: Quezon(Balintawak) 300MVA T03 restored at 0807H (Unplanned Outage) [WEBSMS] | CLUZ
8/22/2023 7:59:02 AM | Mindanao Grid-08/22/2023 08:01: Asiga (ASG) HEP tripped at 0749H with 5MW load at 0749H. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2023 7:31:29 AM | Luzon Grid-08/22/2023 07:31: Quezon(Balintawak) 300MVA T03 de-energized at 0726H (Unplanned Outage) [WEBSMS] | CLUZ
8/22/2023 7:12:48 AM | Luzon Grid-08/22/2023 07:12: San Jose-Quezon 230kV line 3 restored at 0712H (Planned Outage) [WEBSMS] | CLUZ
8/22/2023 6:20:52 AM | [NSO Update] Mindanao Grid-08/22/2023 06:23: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3276MW, PK=2124MW, RR=20MW, NetOpMargin: AM=1132, PM=973, EVE=1154 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: DCP @137.45MW, MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @100MW, AG4 @126MW, AG5 @40MW, AG6 @106MW, AG7 @34MW, PG4 @140MW [WEBSMS] | CMIN
8/22/2023 6:17:52 AM | [NSO Update] Visayas Grid-08/22/2023 06:15: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2678MW, PK=2204MW, RR=89MW, NetOpMargin: AM=385, PM=290, EVE=326 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @333MW, PGPP1 @75MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/22/2023 6:11:47 AM | [NSO Update] Luzon Grid-08/22/2023 06:11: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13320MW, PK=11255MW, RR=342MW, NetOpMargin: AM=1722, PM=877, EVE=1380 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC2 @325MW, MSLC3 @325MW, ILIJAN A @350MW, ILIJAN B @290MW [WEBSMS] | CLUZ
8/22/2023 4:59:00 AM | Visayas Grid-08/22/2023 04:59: CEDC U2 online at 0456H. (Unplanned Outage) [WEBSMS] | CVIS
8/22/2023 4:34:27 AM | [NSO Update] Mindanao Grid-08/22/2023 04:36: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/22/2023 4:33:22 AM | [NSO Update] Visayas Grid-08/22/2023 04:33: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/22/2023 4:32:35 AM | [NSO Update] Luzon Grid-08/22/2023 04:32: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/22/2023 4:19:06 AM | Luzon Grid-08/22/2023 04:19: Ilijan GT1-1 online at 0417H (Unplanned Outage) [WEBSMS] | CLUZ
8/22/2023 3:32:33 AM | Mindanao Grid-08/22/2023 03:34: Lake Mainit HEPP online at 0309H. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2023 2:44:09 AM | Mindanao Grid-08/22/2023 02:46: Lake Mainit HEPP with 10.5MW gross generation tripped at 0237H. Indication: 50BF Circuit Breaker Failure Relay Operated. (Unplanned Outage) [WEBSMS] | CMIN
8/22/2023 2:40:40 AM | Luzon Grid-08/22/2023 02:40: QPPL tripped at 0238H(63MW) (Unplanned Outage). [WEBSMS] | CLUZ
8/22/2023 1:45:39 AM | Luzon Grid-08/22/2023 01:45: QPPL online at 0144H (From an unplanned outage). [WEBSMS] | CLUZ
8/22/2023 12:27:40 AM | Mindanao Grid-08/22/2023 00:29: TSI Unit #2 shutdown at 0022H, for PMS. Follow RTD. (Planned Outage) [WEBSMS] | CMIN
8/22/2023 12:21:18 AM | Luzon Grid-08/22/2023 00:21: San Jose-Quezon 230kV line 3 was de-energized at 0020H (Planned Outage) [WEBSMS] | CLUZ
8/22/2023 12:07:16 AM | Luzon Grid-08/22/2023 00:07: Dasmarinas-Tayabas 500kV line commissioning of New Main Protection and BFR was completed at 2400H. [WEBSMS] | CLUZ
8/21/2023 11:29:45 PM | Luzon Grid-08/21/2023 23:29: Dasmarinas-Tayabas 500kV line was looped at 2327H (On-going commissioning of New Main Protection and BFR). [WEBSMS] | CLUZ
8/21/2023 11:15:04 PM | Mindanao Grid-08/21/2023 23:17: FDC Unit #1 shutdown at 2312H. Follow RTD. (Reserved Shutdown). [WEBSMS] | CMIN
8/21/2023 9:58:16 PM | Luzon Grid-08/21/2023 21:58: Limay-Batangas II (BPC) 230kV line 1 was restored at 2152H (Planned Outage) [WEBSMS] | CLUZ
8/21/2023 9:53:33 PM | Luzon Grid-08/21/2023 21:53: Limay-Batangas II (BPC) was restored at 2152H (Planned Outage). [WEBSMS] | CLUZ
8/21/2023 8:44:30 PM | [NSO Update] Visayas Grid-08/21/2023 20:44: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2037H with power going to Visayas. [WEBSMS] | CVIS
8/21/2023 8:42:11 PM | [NSO Update] Mindanao Grid-08/21/2023 20:44: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2037H with power going to Visayas. [WEBSMS] | CMIN
8/21/2023 8:39:45 PM | [NSO Update] Luzon Grid-08/21/2023 20:39: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2037H with power going to Visayas. [WEBSMS] | CLUZ
8/21/2023 6:00:38 PM | Luzon Grid-08/21/2023 18:00: San Jose 300MVA T03 loop at 1756H and San Jose San Jose T01 unlooped at 1757H (Planned Outage) [WEBSMS] | CLUZ
8/21/2023 5:59:38 PM | [NSO Update] Mindanao Grid-08/21/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: CAP=3380MW, PK=1883MW, RR=20MW, NetOpMargin: EVE=1477 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @38MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/21/2023 5:54:33 PM | [NSO Update] Visayas Grid-08/21/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2431MW, PK=2057MW, RR=87MW, NetOpMargin: EVE=286 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @335MW, PGPP1 @75MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/21/2023 5:46:42 PM | [NSO Update] Luzon Grid-08/21/2023 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12336MW, PK=9803MW, RR=320MW, NetOpMargin: EVE=2213 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @200MW, CLC2 @173MW, MSLC2 @325MW, MSLC3 @250MW, SLPGC 2 @100MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/21/2023 5:46:00 PM | Luzon Grid-08/21/2023 17:46: Hermosa-San Jose 230kV Line restored at 1743H (Planned Outage) [WEBSMS] | CLUZ
8/21/2023 4:16:58 PM | Mindanao Grid-08/21/2023 16:19: Agus 6 Unit #4 online at 1607H, from PMS. (Planned Outage) [WEBSMS] | CMIN
8/21/2023 3:54:19 PM | Luzon Grid-08/21/2023 15:54: Pagbilao EHV-Pagbilao 230kV line 1 restored at 1553H (Planned Outage) [WEBSMS] | CLUZ
8/21/2023 3:37:48 PM | Mindanao Grid-08/21/2023 15:40: FDC Unit #3 online at 1529H, from Reserved Shutdown. [WEBSMS] | CMIN
8/21/2023 1:24:55 PM | Visayas Grid-08/21/2023 13:24: Compostela - Consolacion 69 kV line de-energized/re-energized at (1158H-1253H) respectively, whole line including portion isolated. (Unplanned Outage) [WEBSMS] | CVIS
8/21/2023 1:19:24 PM | Mindanao Grid-08/21/2023 13:21: Agus 6 Unit 4 138kV tie-line restored at 1317H. (Unplanned Outage) [WEBSMS] | CMIN
8/21/2023 12:55:36 PM | [NSO Update] Visayas Grid-08/21/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2370MW, PK=1956MW, RR=91MW, NetOpMargin: PM=322, EVE=283 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @335MW, PGPP1 @75MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/21/2023 12:54:47 PM | [NSO Update] Mindanao Grid-08/21/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3415MW, PK=1829MW, RR=20MW, NetOpMargin: PM=1566, EVE=1402 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @40MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/21/2023 12:51:56 PM | [NSO Update] Luzon Grid-08/21/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12833MW, PK=9955MW, RR=405MW, NetOpMargin: PM=2473, EVE=1917 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @200MW, CLC2 @173MW, MSLC1 @200MW, MSLC2 @325MW, MSLC3 @250MW, SLPGC 2 @90MW, STA RITA 20 @200MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/21/2023 12:39:17 PM | Luzon Grid-08/21/2023 12:39: Sta. Rita 10 change over from oil to gas at 1235H (Unplanned Outage) [WEBSMS] | CLUZ
8/21/2023 12:23:11 PM | Mindanao Grid-08/21/2023 12:25: Lala - Aurora 138kV line 2 restored at 1219H. (Unplanned Outage) [WEBSMS] | CMIN
8/21/2023 11:02:20 AM | Mindanao Grid-08/21/2023 11:04: Lala - Aurora 138kV Line 2 de-energized at 1025H. (Unplanned Outage) [WEBSMS] | CMIN
8/21/2023 10:35:10 AM | Mindanao Grid-08/21/2023 10:37: Lala - Aurora 138kV line 1 restored at 1015H. (Planned Outage) [WEBSMS] | CMIN
8/21/2023 10:24:02 AM | Mindanao Grid-08/21/2023 10:26: WMPC DG08 and DG05 cut-out at 1013H and 1014H, respectively from energy (RTD) dispatch. [WEBSMS] | CMIN
8/21/2023 10:09:36 AM | Luzon Grid-08/21/2023 10:09: San Lorenzo 60 change over from oil to gas at 1005H (Unplanned Outage) [WEBSMS] | CLUZ
8/21/2023 9:45:36 AM | Mindanao Grid-08/21/2023 09:47: WMPC DG09 emergency shutdown at 0920H due to continuous surging turbo charger. (Unplanned Outage) [WEBSMS] | CMIN
8/21/2023 9:41:49 AM | Mindanao Grid-08/21/2023 09:44: WMPC DG08 and DG05 cut-in at 0923H and 0930H, respectively as energy (RTD). [WEBSMS] | CMIN
8/21/2023 9:40:58 AM | Mindanao Grid-08/21/2023 09:43: WMPC DG09 cut-in at 0909H as energy (RTD). [WEBSMS] | CMIN
8/21/2023 9:03:19 AM | Mindanao Grid-08/21/2023 09:05: Lala - Aurora 138kV Line 1 de-energized at 0811H. (Planned Outage) [WEBSMS] | CMIN
8/21/2023 9:01:33 AM | Luzon Grid-08/21/2023 09:01: San Lorenzo-Avion 230kV Line de-energized at 0900H (Planned Outage) [WEBSMS] | CLUZ
8/21/2023 7:21:41 AM | Mindanao Grid-08/21/2023 07:23: Mt. Apo 3 Binary Plant tripped with 3.2 MW at 0709H. (Unplanned Outage) [WEBSMS] | CMIN
8/21/2023 7:15:28 AM | Luzon Grid-08/21/2023 07:15: Hermosa-San Jose 230kV Line de-energized at 0711H (Planned Outage) [WEBSMS] | CLUZ
8/21/2023 7:12:09 AM | Luzon Grid-08/21/2023 07:12: San Jose 300MVA T03 loop and San Jose San Jose T01 unlooped at 0710H (Planned Outage) [WEBSMS] | CLUZ
8/21/2023 6:55:44 AM | Visayas Grid-08/21/2023 06:55: CEDC unit# 2 tripped with 58.32MW load at 0646H.(Unplanned Outage) [WEBSMS] | CVIS
8/21/2023 5:48:33 AM | [NSO Update] Luzon Grid-08/21/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13200MW, PK=9544MW, RR=396MW, NetOpMargin: AM=3260, PM=2548, EVE=1852 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 1 @200MW, CALACA 2 @173MW, MASINLOC 1 @325MW, MASINLOC 2 @325MW, MASINLOC 3 @250MW, SLPGC 2 @90MW, ST.RITA 20@200MW, SAN LORENZO 60 @200MW, ILIJAN A@250MW, ILIJAN B @250MW, [WEBSMS] | CLUZ
8/21/2023 5:46:38 AM | [NSO Update] Visayas Grid-08/21/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2485MW, PK=1891MW, RR=89MW, NetOpMargin: AM=505, PM=324, EVE=181 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-THERMAL@ 82MW, LEYTE A @335MW, PGPP1 @75MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/21/2023 5:44:42 AM | [NSO Update] Mindanao Grid-08/21/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3417MW, PK=1742MW, RR=20MW, NetOpMargin: AM=1655, PM=1492, EVE=1354 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MCO @270MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @40MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/21/2023 4:01:16 AM | [NSO Update] Mindanao Grid-08/21/2023 04:03: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/21/2023 4:01:08 AM | [NSO Update] Visayas Grid-08/21/2023 04:01: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/21/2023 4:01:05 AM | [NSO Update] Luzon Grid-08/21/2023 04:01: Weather Advisory: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/21/2023 3:30:09 AM | Visayas Grid-08/21/2023 03:30: Toledo 40MVA Transformer 2 energized at 0323H. (Planned Outage). [WEBSMS] | CVIS
8/21/2023 3:17:35 AM | Mindanao Grid-08/21/2023 03:19: Bunawan-Maco 138KV line successfully re-energized at 0234H & looped at Bunawan SS at 0236H. From Planned Outage / Non- GOMP [WEBSMS] | CMIN
8/20/2023 9:02:45 PM | Visayas Grid-08/20/2023 21:02: Colon - Magdugo 138 kV Line 2 energized at 2059H. (Planned Outage) [WEBSMS] | CVIS
8/20/2023 8:49:08 PM | Visayas Grid-08/20/2023 20:49: Compostela - Consolacion 69 kV Line re-energized at 2047H. (Unplanned Outage) [WEBSMS] | CVIS
8/20/2023 6:24:45 PM | [NSO Update] Mindanao Grid-08/20/2023 18:27: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3383MW, PK=1919MW, RR=20MW, NetOpMargin: EVE=1444 Highest Unit O/L: GNPK 1&4@138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @38MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/20/2023 6:24:06 PM | Visayas Grid-08/20/2023 18:24: Compostela - Consolacion 69 kV Line auto-tripped at 1821H. (Unplanned Outage) [WEBSMS] | CVIS
8/20/2023 6:19:17 PM | Visayas Grid-08/20/2023 18:19: Compostela - Consolacion 69 kV Line re-energized at 1818H. (Unplanned Outage) [WEBSMS] | CVIS
8/20/2023 6:14:35 PM | Visayas Grid-08/20/2023 18:14: Compostela - Consolacion 69 kV Line auto-tripped at 1759H. (Unplanned Outage) [WEBSMS] | CVIS
8/20/2023 6:11:54 PM | [NSO Update] Visayas Grid-08/20/2023 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2297MW, PK=1930MW, RR=87MW, NetOpMargin: EVE=280 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC-Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 328MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/20/2023 2:56:46 PM | Mindanao Grid-08/20/2023 14:59: Maco 138kV Bus 1 deenergized at 1411H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/20/2023 2:52:17 PM | Mindanao Grid-08/20/2023 14:54: Maco 138kV Bus 2 energized at 1300H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/20/2023 2:23:57 PM | Mindanao Grid-08/20/2023 14:26: Bunawan 138kV Bus 1 deenergized at 1343H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/20/2023 1:18:03 PM | Mindanao Grid-08/20/2023 13:20: Mt. Apo Unit #3 online at 1254H. (Unplanned outage) [WEBSMS] | CMIN
8/20/2023 1:17:52 PM | Mindanao Grid-08/20/2023 13:20: Mt. Apo Unit #3 online at 1254H. (Unplanned outage) [WEBSMS] | CMIN
8/20/2023 1:04:29 PM | [NSO Update] Luzon Grid-08/20/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13558MW, PK=9487MW, RR=299MW, NetOpMargin: PM=3772, EVE=2513 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 200MW, Calaca 2 @ 140MW, Masinloc 1 @ 325MW, Masinloc 2 @ 325MW, Masinloc 3 @ 220MW, SLPGC 2 @ 120MW, Sta. Rita 20 @ 200MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/20/2023 12:55:21 PM | [NSO Update] Luzon Grid-08/20/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13558MW, PK=9487MW, RR=299MW, NetOpMargin: PM=3772, EVE=2513 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 200MW, Calaca 2 @ 140MW, Masinloc 1 @ 325MW, Masinloc 2 @ 325MW, Masinloc 3 @ 220MW, SLPGC 2 @ 120MW, Sta. Rita 20 @ 200MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/20/2023 12:54:32 PM | [NSO Update] Mindanao Grid-08/20/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3271MW, PK=1726MW, RR=20MW, NetOpMargin: PM=1525, EVE=1291 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @40MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/20/2023 12:54:10 PM | [NSO Update] Visayas Grid-08/20/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2471MW, PK=1832MW, RR=91MW, NetOpMargin: PM=548, EVE=304 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Carmen @ 30MW, Leyte A @ 328MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/20/2023 12:53:23 PM | [NSO Update] Mindanao Grid-08/20/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3271MW, PK=1726MW, RR=20MW, NetOpMargin: PM=1525, EVE=1291 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @40MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/20/2023 12:51:36 PM | [NSO Update] Visayas Grid-08/20/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2471MW, PK=1832MW, RR=91MW, NetOpMargin: PM=548, EVE=304 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Carmen @ 30MW, Leyte A @ 328MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/20/2023 12:24:30 PM | Mindanao Grid-08/20/2023 12:24: Bunawan 138kV Bus 2 energized at 1216H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/20/2023 12:22:09 PM | Mindanao Grid-08/20/2023 12:24: Bunawan 138kV Bus 2 energized at 1216H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/20/2023 9:11:33 AM | Mindanao Grid-08/20/2023 09:13: Maco 138kV Bus 2 deenergized at 0903H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/20/2023 9:04:27 AM | Luzon Grid-08/20/2023 09:03: Calamba 230kV Bus 1 was de-energized at 0903H (Planned Outage). [WEBSMS] | CLUZ
8/20/2023 9:03:49 AM | Luzon Grid-08/20/2023 09:03: Calamba 230kV Bus 1 was de-energized at 0903H (Planned Outage). [WEBSMS] | CLUZ
8/20/2023 8:46:47 AM | Mindanao Grid-08/20/2023 08:49: Bunawan 138kV Bus 2 deenergized at 0833H. Planned Outage/Non-GOMP [WEBSMS] | CMIN
8/20/2023 8:46:06 AM | Mindanao Grid-08/20/2023 08:49: Bunawan 138kV Bus 2 deenergized at 0833H. Planned Outage/Non-GOMP [WEBSMS] | CMIN
8/20/2023 8:14:10 AM | Luzon Grid-08/20/2023 08:09: Limay-BCCPP 230kV line 2 was de-energized at 0808H (Planned Outage) [WEBSMS] | CLUZ
8/20/2023 8:09:20 AM | Luzon Grid-08/20/2023 08:09: Limay-BCCPP 230kV line 2 was de-energized at 0808H (Planned Outage) [WEBSMS] | CLUZ
8/20/2023 8:07:43 AM | Luzon Grid-08/20/2023 08:06: Limay-Batangas II (BPC) 230kV line 1 was de-energized at 0804H (Planned Outage). [WEBSMS] | CLUZ
8/20/2023 8:05:54 AM | Luzon Grid-08/20/2023 08:06: Limay-Batangas II (BPC) 230kV line 1 was de-energized at 0804H (Planned Outage). [WEBSMS] | CLUZ
8/20/2023 7:06:33 AM | Visayas Grid-08/20/2023 07:06: 138KV/34.5KV 40MVA Toledo SS Transformer #2 de-energized @0629H. ( Planned Outage ) [WEBSMS] | CVIS
8/20/2023 7:03:38 AM | Luzon Grid-08/20/2023 07:03: Avion 2 70MVA Main Unit Transformer was de-energized at 0701H (Planned Outage) [WEBSMS] | CLUZ
8/20/2023 6:54:20 AM | Luzon Grid-08/20/2023 06:53: Mexico 230kV Bus 1 was de-energized at 0653H (Planned Outage). [WEBSMS] | CLUZ
8/20/2023 6:53:40 AM | Luzon Grid-08/20/2023 06:53: Mexico 230kV Bus 1 was de-energized at 0653H (Planned Outage). [WEBSMS] | CLUZ
8/20/2023 6:25:07 AM | Luzon Grid-08/20/2023 06:06: Santiago-Gamu 230kV line was de-energized at 0605H (Planned Outage) [WEBSMS] | CLUZ
8/20/2023 6:06:34 AM | Luzon Grid-08/20/2023 06:06: Santiago-Gamu 230kV line was de-energized at 0605H (Planned Outage) [WEBSMS] | CLUZ
8/20/2023 6:04:37 AM | [NSO Update] Mindanao Grid-08/20/2023 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3271MW, PK=1571MW, RR=20MW, NetOpMargin: AM=1680, PM=1597, EVE=1370 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @40MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/20/2023 6:04:11 AM | [NSO Update] Mindanao Grid-08/20/2023 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3271MW, PK=1571MW, RR=20MW, NetOpMargin: AM=1680, PM=1597, EVE=1370 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @40MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/20/2023 5:57:50 AM | [NSO Update] Visayas Grid-08/20/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2491MW, PK=1725MW, RR=89MW, NetOpMargin: AM=678, PM=537, EVE=267 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 328MW, PGPP1 @ 75MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
8/20/2023 5:57:08 AM | [NSO Update] Visayas Grid-08/20/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2491MW, PK=1725MW, RR=89MW, NetOpMargin: AM=678, PM=537, EVE=267 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 328MW, PGPP1 @ 75MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
8/20/2023 5:54:05 AM | [NSO Update] Luzon Grid-08/20/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13714MW, PK=8875MW, RR=285MW, NetOpMargin: AM=4554, PM=4181, EVE=2965 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 190MW, Calaca 2 @ 170MW, Masinloc 2 @ 325MW, Masinloc 3 @ 220MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/20/2023 5:52:03 AM | [NSO Update] Luzon Grid-08/20/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13714MW, PK=8875MW, RR=285MW, NetOpMargin: AM=4554, PM=4181, EVE=2965 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 190MW, Calaca 2 @ 170MW, Masinloc 2 @ 325MW, Masinloc 3 @ 220MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/20/2023 5:20:44 AM | Luzon Grid-08/20/2023 05:15: San Jose SS 115kV Bus 1 de-energized at 0515H. (Planned Outage) [WEBSMS] | CLUZ
8/20/2023 5:15:26 AM | Luzon Grid-08/20/2023 05:15: San Jose SS 115kV Bus 1 de-energized at 0515H. (Planned Outage) [WEBSMS] | CLUZ
8/20/2023 4:57:22 AM | Luzon Grid-08/20/2023 04:55: BCCPP SS 230kV Bus 2 restored at 0454. (Planned Outage) [WEBSMS] | CLUZ
8/20/2023 4:55:30 AM | Luzon Grid-08/20/2023 04:55: BCCPP SS 230kV Bus 2 restored at 0454. (Planned Outage) [WEBSMS] | CLUZ
8/20/2023 4:40:23 AM | Mindanao Grid-08/20/2023 04:42: MA3 tripped with 3.2MW load at 0416H. (Unplanned Outage) [WEBSMS] | CMIN
8/20/2023 4:40:17 AM | Mindanao Grid-08/20/2023 04:42: MA3 tripped with 3.2MW load at 0416H. (Unplanned Outage) [WEBSMS] | CMIN
8/20/2023 4:21:59 AM | [NSO Update] Luzon Grid-08/20/2023 04:22: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/20/2023 4:19:03 AM | [NSO Update] Mindanao Grid-08/20/2023 04:21: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/20/2023 4:18:59 AM | [NSO Update] Mindanao Grid-08/20/2023 04:21: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/20/2023 4:11:25 AM | [NSO Update] Visayas Grid-08/20/2023 04:11: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/20/2023 4:11:09 AM | [NSO Update] Visayas Grid-08/20/2023 04:11: Weather Update: Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/20/2023 12:17:12 AM | Luzon Grid-08/20/2023 00:13: Dasmarinas-Tayabas 500kV Line de-energized at 0013H. (Planned Outage) [WEBSMS] | CLUZ
8/20/2023 12:13:38 AM | Luzon Grid-08/20/2023 00:13: Dasmarinas-Tayabas 500kV Line de-energized at 0013H. (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 9:57:09 PM | Mindanao Grid-08/19/2023 21:59: Corrected: Bunawan-Nabunturan 138KV line auto-tripped and auto-reclosed at 1932H, while Bunawan-Maco 138KV line is under Planned Outage at 0619H, resulting to the activation of Bunawan-Maco-Nabunturan SIPS, that triggered ALD of Maco SS 69KV feeders of about 57.8MW total load drop. Unplanned Outage. [WEBSMS] | CMIN
8/19/2023 9:57:07 PM | Luzon Grid-08/19/2023 21:54: Santiago - Gamu 230kV Line auto-tripped/auto-reclosed successfully at both at 2145H. (Unplanned Outage) [WEBSMS] | CLUZ
8/19/2023 9:56:45 PM | Mindanao Grid-08/19/2023 21:59: Corrected: Bunawan-Nabunturan 138KV line auto-tripped and auto-reclosed at 1932H, while Bunawan-Maco 138KV line is under Planned Outage at 0619H, resulting to the activation of Bunawan-Maco-Nabunturan SIPS, that triggered ALD of Maco SS 69KV feeders of about 57.8MW total load drop. Unplanned Outage. [WEBSMS] | CMIN
8/19/2023 9:54:52 PM | Luzon Grid-08/19/2023 21:54: Santiago - Gamu 230kV Line auto-tripped/auto-reclosed successfully at both at 2145H. (Unplanned Outage) [WEBSMS] | CLUZ
8/19/2023 9:16:37 PM | Mindanao Grid-08/19/2023 21:17: SMC Unit #1 shutdown at 2100H. Follow RTD. Emergency shutdown to facilitate replacement of DCS Analog Module Node 4 and rectification of auxiliary steam header line safety valve. (Unplanned Outage). [WEBSMS] | CMIN
8/19/2023 9:15:13 PM | Mindanao Grid-08/19/2023 21:17: SMC Unit #1 shutdown at 2100H. Follow RTD. Emergency shutdown to facilitate replacement of DCS Analog Module Node 4 and rectification of auxiliary steam header line safety valve. (Unplanned Outage). [WEBSMS] | CMIN
8/19/2023 8:55:28 PM | Mindanao Grid-08/19/2023 20:57: ALD occured at Maco SS 69KV feeders of about 57MW at 1932H due to activation of Bunawan-Maco-Nabunturan SIPS caused by auto-reclosing action of Bunawan-Nabunturan 138KV line. Unplanned Outage. [WEBSMS] | CMIN
8/19/2023 8:55:26 PM | Mindanao Grid-08/19/2023 20:57: ALD occured at Maco SS 69KV feeders of about 57MW at 1932H due to activation of Bunawan-Maco-Nabunturan SIPS caused by auto-reclosing action of Bunawan-Nabunturan 138KV line. Unplanned Outage. [WEBSMS] | CMIN
8/19/2023 7:07:06 PM | Luzon Grid-08/19/2023 19:07: BCCPP SS 230kV Bus 2 de-energized at 1906H. (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 7:06:28 PM | Luzon Grid-08/19/2023 19:07: BCCPP SS 230kV Bus 2 de-energized at 1906H. (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 6:36:27 PM | Luzon Grid-08/19/2023 18:34: Mexico-Hermosa 230kV line 1 restored at 1834H. (Planned Outage). [WEBSMS] | CLUZ
8/19/2023 6:34:43 PM | Luzon Grid-08/19/2023 18:34: Mexico-Hermosa 230kV line 1 restored at 1834H. (Planned Outage). [WEBSMS] | CLUZ
8/19/2023 6:08:08 PM | [NSO Update] Mindanao Grid-08/19/2023 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3374MW, PK=1999MW, RR=20MW, NetOpMargin: EVE=1355 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @38MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/19/2023 6:07:55 PM | [NSO Update] Mindanao Grid-08/19/2023 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3374MW, PK=1999MW, RR=20MW, NetOpMargin: EVE=1355 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @38MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/19/2023 6:03:19 PM | [NSO Update] Visayas Grid-08/19/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2360MW, PK=1979MW, RR=87MW, NetOpMargin: EVE=294 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 328MW, PGPP1 @ 75MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
8/19/2023 6:02:08 PM | [NSO Update] Visayas Grid-08/19/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2360MW, PK=1979MW, RR=87MW, NetOpMargin: EVE=294 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 328MW, PGPP1 @ 75MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
8/19/2023 5:56:25 PM | [NSO Update] Luzon Grid-08/19/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12714MW, PK=10112MW, RR=308MW, NetOpMargin: EVE=2294 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 200MW, Calaca 2 @ 170MW, Masinloc 2 @ 320MW, Masinloc 3 @ 130MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/19/2023 5:56:15 PM | [NSO Update] Luzon Grid-08/19/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12714MW, PK=10112MW, RR=308MW, NetOpMargin: EVE=2294 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 200MW, Calaca 2 @ 170MW, Masinloc 2 @ 320MW, Masinloc 3 @ 130MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/19/2023 5:33:35 PM | Luzon Grid-08/19/2023 17:33: Bauang-Balingueo 230kV line was restored at 1732H (Planned Outage). [WEBSMS] | CLUZ
8/19/2023 5:32:54 PM | Luzon Grid-08/19/2023 17:33: Bauang-Balingueo 230kV line was restored at 1732H (Planned Outage). [WEBSMS] | CLUZ
8/19/2023 5:16:10 PM | Luzon Grid-08/19/2023 17:16: Mexico-Quezon 230kV line was restored at 1713H (Unplanned Outage). [WEBSMS] | CLUZ
8/19/2023 5:15:46 PM | Visayas Grid-08/19/2023 17:15: Toledo SS 40 MVA 138/34.5 KV TR3 energized at 1714H. (Planned Outage) [WEBSMS] | CVIS
8/19/2023 5:15:45 PM | Visayas Grid-08/19/2023 17:15: Toledo SS 40 MVA 138/34.5 KV TR3 energized at 1714H. (Planned Outage) [WEBSMS] | CVIS
8/19/2023 5:09:44 PM | Luzon Grid-08/19/2023 17:08: Mexico-Quezon 230kV line auto-tripped at 1702H (Unplanned Outage). [WEBSMS] | CLUZ
8/19/2023 5:08:38 PM | Luzon Grid-08/19/2023 17:08: Mexico-Quezon 230kV line auto-tripped at 1702H (Unplanned Outage). [WEBSMS] | CLUZ
8/19/2023 4:39:32 PM | Luzon Grid-08/19/2023 16:37: Bay-Makban B 230kV line 1 was restored at 1635H (Planned Outage). [WEBSMS] | CLUZ
8/19/2023 4:37:13 PM | Luzon Grid-08/19/2023 16:37: Bay-Makban B 230kV line 1 was restored at 1635H (Planned Outage). [WEBSMS] | CLUZ
8/19/2023 3:34:32 PM | Mindanao Grid-08/19/2023 15:34: WMPC DG10 shutdown at 1512H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/19/2023 3:32:14 PM | Mindanao Grid-08/19/2023 15:34: WMPC DG10 shutdown at 1512H. RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/19/2023 1:59:45 PM | Luzon Grid-08/19/2023 13:59: Dasmarinas-TMC (Ternate) 115kV line was energized at 1358H (Planned Outage). [WEBSMS] | CLUZ
8/19/2023 1:59:10 PM | Luzon Grid-08/19/2023 13:59: Dasmarinas-TMC (Ternate) 115kV line was energized at 1358H (Planned Outage). [WEBSMS] | CLUZ
8/19/2023 12:59:25 PM | [NSO Update] Luzon Grid-08/19/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13353MW, PK=10682MW, RR=425MW, NetOpMargin: PM=2246, EVE=2101 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 200MW, Calaca 2 @ 170MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 130MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/19/2023 12:56:09 PM | [NSO Update] Luzon Grid-08/19/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13353MW, PK=10682MW, RR=425MW, NetOpMargin: PM=2246, EVE=2101 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 200MW, Calaca 2 @ 170MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 130MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/19/2023 12:54:26 PM | [NSO Update] Mindanao Grid-08/19/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3380MW, PK=1982MW, RR=20MW, NetOpMargin: PM=1377, EVE=1329 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @38MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/19/2023 12:54:16 PM | [NSO Update] Mindanao Grid-08/19/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3380MW, PK=1982MW, RR=20MW, NetOpMargin: PM=1377, EVE=1329 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @38MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/19/2023 12:54:05 PM | [NSO Update] Visayas Grid-08/19/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2356MW, PK=1982MW, RR=91MW, NetOpMargin: PM=282, EVE=296 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 328MW, PGPP1 @ 75MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
8/19/2023 12:52:27 PM | [NSO Update] Visayas Grid-08/19/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2356MW, PK=1982MW, RR=91MW, NetOpMargin: PM=282, EVE=296 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: Leyte A @ 328MW, PGPP1 @ 75MW, TPC Carmen @ 30MW [WEBSMS] | CVIS
8/19/2023 12:30:36 PM | Visayas Grid-08/19/2023 12:30: Dumanjug SS 150MVA TR 1 energized at 1226H, pre-arranged activity completed. [WEBSMS] | CVIS
8/19/2023 12:30:08 PM | Visayas Grid-08/19/2023 12:30: Dumanjug SS 150MVA TR 1 energized at 1226H, pre-arranged activity completed. [WEBSMS] | CVIS
8/19/2023 12:29:27 PM | Mindanao Grid-08/19/2023 12:31: Lamsan Online at 1227H (Unplanned Outage) [WEBSMS] | CMIN
8/19/2023 12:29:08 PM | Mindanao Grid-08/19/2023 12:31: Lamsan Online at 1227H (Unplanned Outage) [WEBSMS] | CMIN
8/19/2023 11:45:47 AM | Mindanao Grid-08/19/2023 11:47: Lamsan Tripped with 15MW at 1139H. (Unplanned Outage) [WEBSMS] | CMIN
8/19/2023 11:45:13 AM | Mindanao Grid-08/19/2023 11:47: Lamsan Tripped with 15MW at 1139H. (Unplanned Outage) [WEBSMS] | CMIN
8/19/2023 9:52:36 AM | Mindanao Grid-08/19/2023 09:54: WMPC DG10 Online at 0950H. (Planned Outage). [WEBSMS] | CMIN
8/19/2023 9:52:09 AM | Mindanao Grid-08/19/2023 09:54: WMPC DG10 Online at 0950H. (Planned Outage). [WEBSMS] | CMIN
8/19/2023 9:47:36 AM | Mindanao Grid-08/19/2023 09:46: Lamsan Online at 0927H. (Unplanned Outage). [WEBSMS] | CMIN
8/19/2023 9:44:17 AM | Mindanao Grid-08/19/2023 09:46: Lamsan Online at 0927H. (Unplanned Outage). [WEBSMS] | CMIN
8/19/2023 9:15:35 AM | Visayas Grid-08/19/2023 09:15: Dumanjug SS 150MVA TR 1 de-energized at 0908H, pre-arranged activity: ECD: 1700H. [WEBSMS] | CVIS
8/19/2023 9:15:13 AM | Visayas Grid-08/19/2023 09:15: Dumanjug SS 150MVA TR 1 de-energized at 0908H, pre-arranged activity: ECD: 1700H. [WEBSMS] | CVIS
8/19/2023 9:14:54 AM | Mindanao Grid-08/19/2023 09:17: Lamsan tripped with 15MW load at 0907H. (Unplanned Outage). [WEBSMS] | CMIN
8/19/2023 9:14:51 AM | Mindanao Grid-08/19/2023 09:17: Lamsan tripped with 15MW load at 0907H. (Unplanned Outage). [WEBSMS] | CMIN
8/19/2023 8:52:13 AM | Luzon Grid-08/19/2023 08:52: Bay-Makban B 230kV line 1 was de-energized at 0851H (Planned Outage). [WEBSMS] | CLUZ
8/19/2023 8:39:09 AM | Luzon Grid-08/19/2023 08:35: Dasmarinas-TMC(Ternate) 115kV line was de-energized at 0834H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 8:35:07 AM | Luzon Grid-08/19/2023 08:35: Dasmarinas-TMC(Ternate) 115kV line was de-energized at 0834H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 8:29:09 AM | Luzon Grid-08/19/2023 08:28: Pagbilao EHV-Pagbilao 230kV line 1 was de-energized at 0826H (Planned Outage). [WEBSMS] | CLUZ
8/19/2023 8:28:09 AM | Luzon Grid-08/19/2023 08:28: Pagbilao EHV-Pagbilao 230kV line 1 was de-energized at 0826H (Planned Outage). [WEBSMS] | CLUZ
8/19/2023 7:38:06 AM | Luzon Grid-08/19/2023 07:36: Mexico-Hermosa 230kV line 1 was de-energized at 0733H (Planned Outage). [WEBSMS] | CLUZ
8/19/2023 7:36:36 AM | Luzon Grid-08/19/2023 07:36: Mexico-Hermosa 230kV line 1 was de-energized at 0733H (Planned Outage). [WEBSMS] | CLUZ
8/19/2023 7:01:32 AM | Visayas Grid-08/19/2023 07:01: Toledo SS 40MVA TR3 de-energized at 0655H, pre-arranged maintenance activity APMS. ECD: 1800H [WEBSMS] | CVIS
8/19/2023 7:01:13 AM | Visayas Grid-08/19/2023 07:01: Toledo SS 40MVA TR3 de-energized at 0655H, pre-arranged maintenance activity APMS. ECD: 1800H [WEBSMS] | CVIS
8/19/2023 6:43:21 AM | Mindanao Grid-08/19/2023 06:45: Bunawan-Maco 138kV L1 deenergized 0619H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
8/19/2023 6:29:02 AM | Luzon Grid-08/19/2023 06:24: Balingueo-Bauang 230kV Line de-energized at 0624H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 6:24:50 AM | Luzon Grid-08/19/2023 06:24: Balingueo-Bauang 230kV Line de-energized at 0624H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 6:01:23 AM | [NSO Update] Luzon Grid-08/19/2023 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13549MW, PK=10443MW, RR=410MW, NetOpMargin: AM=2696, PM=2386, EVE=2103 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 1 @200MW, CALACA 2 @170MW, MASINLOC 1 @320MW, MASINLOC 2 @320MW, MASINLOC 3 @130MW, ILIJAN A @250MW, ILIJAN B @250MW, [WEBSMS] | CLUZ
8/19/2023 5:59:40 AM | [NSO Update] Luzon Grid-08/19/2023 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13549MW, PK=10443MW, RR=410MW, NetOpMargin: AM=2696, PM=2386, EVE=2103 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 1 @200MW, CALACA 2 @170MW, MASINLOC 1 @320MW, MASINLOC 2 @320MW, MASINLOC 3 @130MW, ILIJAN A @250MW, ILIJAN B @250MW, [WEBSMS] | CLUZ
8/19/2023 5:40:03 AM | [NSO Update] Visayas Grid-08/19/2023 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2373MW, PK=1926MW, RR=89MW, NetOpMargin: AM=358, PM=299, EVE=186 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @328MW, PGPP1 @75MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/19/2023 5:38:04 AM | [NSO Update] Mindanao Grid-08/19/2023 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3408MW, PK=1846MW, RR=20MW, NetOpMargin: AM=1541, PM=1409, EVE=1331 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @38MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/19/2023 5:37:39 AM | [NSO Update] Mindanao Grid-08/19/2023 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3408MW, PK=1846MW, RR=20MW, NetOpMargin: AM=1541, PM=1409, EVE=1331 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @38MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/19/2023 4:48:55 AM | Luzon Grid-08/19/2023 04:48: For info: Sta. Rita-San Lorenzo 230kV Bus A & B tie Breakers were closed at 0443H, looping Sta. Rita CCPP and San Lorenzo CCPP. The splitting of Batangas 300MVA T04 and T05 was completed at 0436H. Sta. Rita Modules 30 and 40 are on shutdown. [WEBSMS] | CLUZ
8/19/2023 4:48:03 AM | Luzon Grid-08/19/2023 04:48: For info: Sta. Rita-San Lorenzo 230kV Bus A & B tie Breakers were closed at 0443H, looping Sta. Rita CCPP and San Lorenzo CCPP. The splitting of Batangas 300MVA T04 and T05 was completed at 0436H. Sta. Rita Modules 30 and 40 are on shutdown. [WEBSMS] | CLUZ
8/19/2023 4:21:00 AM | [NSO Update] Visayas Grid-08/19/2023 04:19: Weather Advisory: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/19/2023 4:19:33 AM | [NSO Update] Luzon Grid-08/19/2023 04:19: Weather Advisory: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/19/2023 4:19:28 AM | [NSO Update] Visayas Grid-08/19/2023 04:19: Weather Advisory: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/19/2023 4:19:24 AM | [NSO Update] Mindanao Grid-08/19/2023 04:21: Weather Advisory: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/19/2023 4:18:55 AM | [NSO Update] Mindanao Grid-08/19/2023 04:21: Weather Advisory: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/19/2023 4:18:54 AM | [NSO Update] Luzon Grid-08/19/2023 04:19: Weather Advisory: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/19/2023 4:17:58 AM | [NSO Update] Visayas Grid-08/19/2023 04:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0412H with power going to Visayas. (Planned Outage) [WEBSMS] | CVIS
8/19/2023 4:17:54 AM | [NSO Update] Visayas Grid-08/19/2023 04:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0412H with power going to Visayas. (Planned Outage) [WEBSMS] | CVIS
8/19/2023 4:14:23 AM | [NSO Update] Mindanao Grid-08/19/2023 04:16: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0412H with power going to Visayas. (Planned Outage) [WEBSMS] | CMIN
8/19/2023 4:13:55 AM | [NSO Update] Mindanao Grid-08/19/2023 04:16: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0412H with power going to Visayas. (Planned Outage) [WEBSMS] | CMIN
8/19/2023 3:12:10 AM | Luzon Grid-08/19/2023 03:09: Las Pinas (Zapote) SS 300MVA T04 looped via low-side at 0306H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 3:09:51 AM | Luzon Grid-08/19/2023 03:09: Las Pinas (Zapote) SS 300MVA T04 looped via low-side at 0306H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 3:08:42 AM | Luzon Grid-08/19/2023 03:08: Correction: Las Pinas (Zapote) SS 300MVA T04 unlooped via low-side at 0240H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 3:07:56 AM | Luzon Grid-08/19/2023 03:08: Correction: Las Pinas (Zapote) SS 300MVA T04 unlooped via low-side at 0240H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 2:52:09 AM | Luzon Grid-08/19/2023 02:48: Las Pinas (Zapote) SS 300MVA T02 unlooped via low-side at 0240H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 2:48:40 AM | Luzon Grid-08/19/2023 02:48: Las Pinas (Zapote) SS 300MVA T02 unlooped via low-side at 0240H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 2:38:49 AM | Luzon Grid-08/19/2023 02:38: Las Pinas (Zapote) SS 300MVA T02 looped via low-side at 0236H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 2:38:38 AM | Luzon Grid-08/19/2023 02:38: Las Pinas (Zapote) SS 300MVA T02 looped via low-side at 0236H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 2:18:49 AM | Luzon Grid-08/19/2023 02:15: Correction: Las Pinas (Zapote) SS 300MVA T02 unlooped via low-side at 0211H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 2:15:09 AM | Luzon Grid-08/19/2023 02:15: Correction: Las Pinas (Zapote) SS 300MVA T02 unlooped via low-side at 0211H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 12:42:04 AM | Luzon Grid-08/19/2023 00:35: Las Pinas (Zapote) SS 300MVA T02 unlooped via low-side at 0023H (Planned Outage) [WEBSMS] | CLUZ
8/19/2023 12:35:22 AM | Luzon Grid-08/19/2023 00:35: Las Pinas (Zapote) SS 300MVA T02 unlooped via low-side at 0023H (Planned Outage) [WEBSMS] | CLUZ
8/18/2023 9:48:34 PM | Luzon Grid-08/18/2023 21:47: Correction: Sta. Rita Module 40 shutdown at 2143H (Unplanned Outage) [WEBSMS] | CLUZ
8/18/2023 9:47:13 PM | Luzon Grid-08/18/2023 21:47: Correction: Sta. Rita Module 40 shutdown at 2143H (Unplanned Outage) [WEBSMS] | CLUZ
8/18/2023 9:46:14 PM | Luzon Grid-08/18/2023 21:46: Sta. Rita Module 40 shutdown at 2043H (Unplanned Outage) [WEBSMS] | CLUZ
8/18/2023 9:35:12 PM | Mindanao Grid-08/18/2023 21:34: STEAG U1 Online at 2127H. (Unplanned Outage). [WEBSMS] | CMIN
8/18/2023 9:32:33 PM | Mindanao Grid-08/18/2023 21:34: STEAG U1 Online at 2127H. (Unplanned Outage). [WEBSMS] | CMIN
8/18/2023 9:17:11 PM | Mindanao Grid-08/18/2023 21:19: WMPC DG10 shutdown at 2114H. (Planned Outage). [WEBSMS] | CMIN
8/18/2023 8:51:49 PM | Luzon Grid-08/18/2023 20:50: Sta. Rita Module 30 shutdown at 2042H (Unplanned Outage) [WEBSMS] | CLUZ
8/18/2023 8:50:05 PM | Luzon Grid-08/18/2023 20:50: Sta. Rita Module 30 shutdown at 2042H (Unplanned Outage) [WEBSMS] | CLUZ
8/18/2023 8:23:47 PM | Luzon Grid-08/18/2023 20:22: Bacman-Palayan 230kV Line restored at 2022H (Unplanned Outage) [WEBSMS] | CLUZ
8/18/2023 8:22:47 PM | Luzon Grid-08/18/2023 20:22: Bacman-Palayan 230kV Line restored at 2022H (Unplanned Outage) [WEBSMS] | CLUZ
8/18/2023 6:11:42 PM | Luzon Grid-08/18/2023 18:06: Concepcion-San Manuel 230kV Line 1 restored at 1806H. (Planned Outage) [WEBSMS] | CLUZ
8/18/2023 6:06:12 PM | Luzon Grid-08/18/2023 18:06: Concepcion-San Manuel 230kV Line 1 restored at 1806H. (Planned Outage) [WEBSMS] | CLUZ
8/18/2023 5:53:21 PM | [NSO Update] Mindanao Grid-08/18/2023 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3231MW, PK=2244MW, RR=20MW, NetOpMargin: EVE=968 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @40MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/18/2023 5:49:34 PM | [NSO Update] Mindanao Grid-08/18/2023 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3231MW, PK=2244MW, RR=20MW, NetOpMargin: EVE=968 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @40MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/18/2023 5:46:24 PM | [NSO Update] Visayas Grid-08/18/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2466MW, PK=2117MW, RR=87MW, NetOpMargin: EVE=262 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @75MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/18/2023 5:43:42 PM | [NSO Update] Visayas Grid-08/18/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2466MW, PK=2117MW, RR=87MW, NetOpMargin: EVE=262 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @75MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/18/2023 5:43:40 PM | [NSO Update] Luzon Grid-08/18/2023 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13329MW, PK=10509MW, RR=398MW, NetOpMargin: EVE=2422 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @170MW, MASINLOC 1 @320MW, MASINLOC 2 @320MW, MASINLOC 3 @130MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/18/2023 5:41:47 PM | [NSO Update] Luzon Grid-08/18/2023 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13329MW, PK=10509MW, RR=398MW, NetOpMargin: EVE=2422 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @170MW, MASINLOC 1 @320MW, MASINLOC 2 @320MW, MASINLOC 3 @130MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/18/2023 4:16:40 PM | Mindanao Grid-08/18/2023 16:18: WMPC DG8 shutdown at 1613H. (Planned Outage). [WEBSMS] | CMIN
8/18/2023 4:16:33 PM | Mindanao Grid-08/18/2023 16:18: WMPC DG8 shutdown at 1613H. (Planned Outage). [WEBSMS] | CMIN
8/18/2023 3:48:08 PM | Luzon Grid-08/18/2023 15:47: Malaya-Ingrid 230kV line 2 restored at 1545H. (Planned Outage) [WEBSMS] | CLUZ
8/18/2023 3:47:41 PM | Luzon Grid-08/18/2023 15:47: Malaya-Ingrid 230kV line 2 restored at 1545H. (Planned Outage) [WEBSMS] | CLUZ
8/18/2023 3:43:10 PM | Mindanao Grid-08/18/2023 15:45: Agus 1-Marawe 69KV line (22.19MW) tripped by UFR/ALD due to the tripping of Steag Plant U1 (100.5MW) at 1404H, & line restored at 1433H. (Unplanned Outage) [WEBSMS] | CMIN
8/18/2023 3:42:52 PM | Mindanao Grid-08/18/2023 15:45: Agus 1-Marawe 69KV line (22.19MW) tripped by UFR/ALD due to the tripping of Steag Plant U1 (100.5MW) at 1404H, & line restored at 1433H. (Unplanned Outage) [WEBSMS] | CMIN
8/18/2023 3:38:09 PM | Mindanao Grid-08/18/2023 15:38: Nabunturan-Asuncion 69KV line (17.79MW) tripped by UFR/ALD due to tripping of Steag Plant U1 (100.5MW gross) at 1404H, restored at 1417H. (Unplanned Outage) [WEBSMS] | CMIN
8/18/2023 3:36:30 PM | Mindanao Grid-08/18/2023 15:38: Nabunturan-Asuncion 69KV line (17.79MW) tripped by UFR/ALD due to tripping of Steag Plant U1 (100.5MW gross) at 1404H, restored at 1417H. (Unplanned Outage) [WEBSMS] | CMIN
8/18/2023 2:39:44 PM | Mindanao Grid-08/18/2023 14:42: Affected ALD feeders of CEPALCO, DLPC and NGCP restored at 1411H, 1418H 1433H respectively. [WEBSMS] | CMIN
8/18/2023 2:35:06 PM | Mindanao Grid-08/18/2023 14:37: STEAG State Power Inc. (Mindanao Coal Fired PP) Unit 1 auto-tripped at 1404H with a gross generation loss of 100.50MW. The lowest frequency recorded is 59.0885Hz that led to UFR activation with a total ALD of 67.85MW. (Note: Details to follow while restoration of the affected 69kV feeders is on progress) [WEBSMS] | CMIN
8/18/2023 2:34:44 PM | Mindanao Grid-08/18/2023 14:37: STEAG State Power Inc. (Mindanao Coal Fired PP) Unit 1 auto-tripped at 1404H with a gross generation loss of 100.50MW. The lowest frequency recorded is 59.0885Hz that led to UFR activation with a total ALD of 67.85MW. (Note: Details to follow while restoration of the affected 69kV feeders is on progress) [WEBSMS] | CMIN
8/18/2023 2:31:57 PM | Mindanao Grid-08/18/2023 14:34: ALD occurred at NGCP, CEPALCO and DLPC at 1404H due to tripping of STEAG U1 at 100.5MW(Gross). Lowest Frequency was 59.0885Hz. [WEBSMS] | CMIN
8/18/2023 2:31:54 PM | Mindanao Grid-08/18/2023 14:34: ALD occurred at NGCP, CEPALCO and DLPC at 1404H due to tripping of STEAG U1 at 100.5MW(Gross). Lowest Frequency was 59.0885Hz. [WEBSMS] | CMIN
8/18/2023 2:16:25 PM | Mindanao Grid-08/18/2023 14:15: STEAG U1 tripped with 100.5MW load at 1404H. (Unplanned Outage) [WEBSMS] | CMIN
8/18/2023 2:13:13 PM | Mindanao Grid-08/18/2023 14:15: STEAG U1 tripped with 100.5MW load at 1404H. (Unplanned Outage) [WEBSMS] | CMIN
8/18/2023 1:51:19 PM | Luzon Grid-08/18/2023 13:50: Bacman-Palayan 230kV Line de-energized at 1349H. (Unplanned Outage) [WEBSMS] | CLUZ
8/18/2023 1:50:26 PM | Luzon Grid-08/18/2023 13:50: Bacman-Palayan 230kV Line de-energized at 1349H. (Unplanned Outage) [WEBSMS] | CLUZ
8/18/2023 1:02:58 PM | [NSO Update] Mindanao Grid-08/18/2023 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3365MW, PK=2304MW, RR=20MW, NetOpMargin: PM=1041, EVE=1075 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @40MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/18/2023 1:01:52 PM | [NSO Update] Mindanao Grid-08/18/2023 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3365MW, PK=2304MW, RR=20MW, NetOpMargin: PM=1041, EVE=1075 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @40MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/18/2023 12:56:04 PM | [NSO Update] Visayas Grid-08/18/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2626MW, PK=2207MW, RR=91MW, NetOpMargin: PM=329, EVE=325 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @333MW, PGPP1 @75MW, TPC-Carmen @30MW [WEBSMS] | CVIS
8/18/2023 12:53:45 PM | [NSO Update] Visayas Grid-08/18/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2626MW, PK=2207MW, RR=91MW, NetOpMargin: PM=329, EVE=325 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @333MW, PGPP1 @75MW, TPC-Carmen @30MW [WEBSMS] | CVIS
8/18/2023 12:50:08 PM | [NSO Update] Luzon Grid-08/18/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13871MW, PK=11713MW, RR=474MW, NetOpMargin: PM=1684, EVE=2062 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC2 @320MW, MSLC3 @130MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/18/2023 12:49:16 PM | [NSO Update] Luzon Grid-08/18/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13871MW, PK=11713MW, RR=474MW, NetOpMargin: PM=1684, EVE=2062 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC2 @320MW, MSLC3 @130MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/18/2023 11:40:48 AM | Mindanao Grid-08/18/2023 11:43: Aurora SS 138/69/13.8 kV 100MVA T2 re-energized at 1116H after re-tapping of its 13.8KV tertiary terminal. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
8/18/2023 10:52:50 AM | Mindanao Grid-08/18/2023 10:54: WMPC DG8 Online at 1050H. (Planned Outage). [WEBSMS] | CMIN
8/18/2023 10:52:21 AM | Mindanao Grid-08/18/2023 10:54: WMPC DG8 Online at 1050H. (Planned Outage). [WEBSMS] | CMIN
8/18/2023 9:17:43 AM | Mindanao Grid-08/18/2023 09:17: Aurora SS 138/69/13.8 kV 100MVA T2 de-energized at 0758H (without load) to conduct re-tapping of its 13.8KV tertiary terminal. Planned Outage [WEBSMS] | CMIN
8/18/2023 9:14:53 AM | Mindanao Grid-08/18/2023 09:17: Aurora SS 138/69/13.8 kV 100MVA T2 de-energized at 0758H (without load) to conduct re-tapping of its 13.8KV tertiary terminal. Planned Outage [WEBSMS] | CMIN
8/18/2023 9:07:42 AM | Mindanao Grid-08/18/2023 09:09: AG6 U4 cut-out at 0904H. PMS(GOMP). (Planned Outage). [WEBSMS] | CMIN
8/18/2023 9:06:58 AM | Mindanao Grid-08/18/2023 09:09: AG6 U4 cut-out at 0904H. PMS(GOMP). (Planned Outage). [WEBSMS] | CMIN
8/18/2023 8:53:00 AM | Mindanao Grid-08/18/2023 08:55: WMPC DG10 Online at 0851H. (Planned Outage). [WEBSMS] | CMIN
8/18/2023 8:52:42 AM | Mindanao Grid-08/18/2023 08:55: WMPC DG10 Online at 0851H. (Planned Outage). [WEBSMS] | CMIN
8/18/2023 6:48:09 AM | Luzon Grid-08/18/2023 06:48: Concepcion-San Manuel 230kV Line 1 de-energized at 0647H. (Planned Outage) [WEBSMS] | CLUZ
8/18/2023 6:47:33 AM | Luzon Grid-08/18/2023 06:48: Concepcion-San Manuel 230kV Line 1 de-energized at 0647H. (Planned Outage) [WEBSMS] | CLUZ
8/18/2023 6:04:10 AM | [NSO Update] Luzon Grid-08/18/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13973MW, PK=11197MW, RR=454MW, NetOpMargin: AM=2322, PM=1493, EVE=1950 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC1 @320MW, MSLC2 @320MW, MSLC3 @130MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/18/2023 6:02:11 AM | [NSO Update] Visayas Grid-08/18/2023 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2627MW, PK=2170MW, RR=89MW, NetOpMargin: AM=368, PM=238, EVE=307 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @333MW, PGPP1 @75MW, TPC-Carmen @30MW [WEBSMS] | CVIS
8/18/2023 6:01:31 AM | [NSO Update] Mindanao Grid-08/18/2023 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3377MW, PK=2189MW, RR=20MW, NetOpMargin: AM=1168, PM=1122, EVE=1132 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @40MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/18/2023 6:01:30 AM | [NSO Update] Mindanao Grid-08/18/2023 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3377MW, PK=2189MW, RR=20MW, NetOpMargin: AM=1168, PM=1122, EVE=1132 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @105MW, AG4 @118MW, AG5 @40MW, AG6 @116MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/18/2023 5:59:36 AM | [NSO Update] Visayas Grid-08/18/2023 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2627MW, PK=2170MW, RR=89MW, NetOpMargin: AM=368, PM=238, EVE=307 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @333MW, PGPP1 @75MW, TPC-Carmen @30MW [WEBSMS] | CVIS
8/18/2023 5:58:13 AM | [NSO Update] Luzon Grid-08/18/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13973MW, PK=11197MW, RR=454MW, NetOpMargin: AM=2322, PM=1493, EVE=1950 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC1 @320MW, MSLC2 @320MW, MSLC3 @130MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/18/2023 4:47:34 AM | [NSO Update] Mindanao Grid-08/18/2023 04:49: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/18/2023 4:47:34 AM | [NSO Update] Visayas Grid-08/18/2023 04:47: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/18/2023 4:47:28 AM | [NSO Update] Luzon Grid-08/18/2023 04:47: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/18/2023 4:47:27 AM | [NSO Update] Mindanao Grid-08/18/2023 04:49: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/18/2023 4:47:23 AM | [NSO Update] Visayas Grid-08/18/2023 04:47: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/18/2023 4:47:09 AM | [NSO Update] Luzon Grid-08/18/2023 04:47: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/18/2023 3:41:24 AM | Mindanao Grid-08/18/2023 03:42: Mt. Apo Unit #3 online at 0335H. Unplanned Outage [WEBSMS] | CMIN
8/18/2023 3:40:28 AM | Mindanao Grid-08/18/2023 03:42: Mt. Apo Unit #3 online at 0335H. Unplanned Outage [WEBSMS] | CMIN
8/18/2023 2:32:38 AM | Mindanao Grid-08/18/2023 02:34: Baloi-Aurora 138kV line restored/energized 0223H. From planned outage / N-GOMP [WEBSMS] | CMIN
8/18/2023 2:32:18 AM | Mindanao Grid-08/18/2023 02:34: Baloi-Aurora 138kV line restored/energized 0223H. From planned outage / N-GOMP [WEBSMS] | CMIN
8/18/2023 2:25:10 AM | Mindanao Grid-08/18/2023 02:27: Baloi-Aurora 138kV line restored/energized 0223. From planned outage / N-GOMP [WEBSMS] | CMIN
8/18/2023 2:24:41 AM | Mindanao Grid-08/18/2023 02:27: Baloi-Aurora 138kV line restored/energized 0223. From planned outage / N-GOMP [WEBSMS] | CMIN
8/18/2023 2:04:32 AM | Mindanao Grid-08/18/2023 02:06: Mt. Apo Unit #3 tripped at 0147H. Indication: PH Level High. Generation Loss=3.12MW. Unplanned Outage. [WEBSMS] | CMIN
8/18/2023 2:03:57 AM | Mindanao Grid-08/18/2023 02:06: Mt. Apo Unit #3 tripped at 0147H. Indication: PH Level High. Generation Loss=3.12MW. Unplanned Outage. [WEBSMS] | CMIN
8/18/2023 1:43:53 AM | Luzon Grid-08/18/2023 01:39: Hermosa-Marilao (Duhat) 230kV line - restored at 0137H (Planned Outage) [WEBSMS] | CLUZ
8/18/2023 1:39:28 AM | Luzon Grid-08/18/2023 01:39: Hermosa-Marilao (Duhat) 230kV line - restored at 0137H (Planned Outage) [WEBSMS] | CLUZ
8/18/2023 1:20:34 AM | Mindanao Grid-08/18/2023 01:19: Baloi-Aurora 138kV line de-energized 0103H. Planned outage / N-GOMP [WEBSMS] | CMIN
8/18/2023 1:17:37 AM | Mindanao Grid-08/18/2023 01:19: Baloi-Aurora 138kV line de-energized 0103H. Planned outage / N-GOMP [WEBSMS] | CMIN
8/18/2023 1:16:17 AM | Luzon Grid-08/18/2023 01:14: Mariveles-GNPD 500kV line 2 - restored at 0109H (Unplanned Outage) [WEBSMS] | CLUZ
8/18/2023 1:13:58 AM | Luzon Grid-08/18/2023 01:14: Mariveles-GNPD 500kV line 2 - restored at 0109H (Unplanned Outage) [WEBSMS] | CLUZ
8/17/2023 11:23:47 PM | Luzon Grid-08/17/2023 23:22: Hermosa-Marilao (Duhat) 230kV line - de-energized at 2318H (Planned Outage) [WEBSMS] | CLUZ
8/17/2023 11:22:03 PM | Luzon Grid-08/17/2023 23:22: Hermosa-Marilao (Duhat) 230kV line - de-energized at 2318H (Planned Outage) [WEBSMS] | CLUZ
8/17/2023 11:13:46 PM | Luzon Grid-08/17/2023 23:13: Meralco New Mauban 50MVA Transformer - de-energized at 2310H (Planned Outage) [WEBSMS] | CLUZ
8/17/2023 11:13:35 PM | Luzon Grid-08/17/2023 23:13: Meralco New Mauban 50MVA Transformer - de-energized at 2310H (Planned Outage) [WEBSMS] | CLUZ
8/17/2023 9:38:13 PM | Luzon Grid-08/17/2023 21:34: Mariveles-GNPD 500kV line 2 - de-energized at 2132H (Unplanned Outage). [WEBSMS] | CLUZ
8/17/2023 9:34:37 PM | Luzon Grid-08/17/2023 21:34: Mariveles-GNPD 500kV line 2 - de-energized at 2132H (Unplanned Outage). [WEBSMS] | CLUZ
8/17/2023 9:18:40 PM | Mindanao Grid-08/17/2023 21:18: WMPC DG09 shutdown at 2113H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/17/2023 9:16:35 PM | Mindanao Grid-08/17/2023 21:18: WMPC DG09 shutdown at 2113H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/17/2023 7:28:10 PM | Mindanao Grid-08/17/2023 19:28: Placer SS 100MVA Power Transformer # 3 energized without load at 1923H From planned outage / Non-GOMP. [WEBSMS] | CMIN
8/17/2023 7:26:38 PM | Mindanao Grid-08/17/2023 19:28: Placer SS 100MVA Power Transformer # 3 energized without load at 1923H From planned outage / Non-GOMP. [WEBSMS] | CMIN
8/17/2023 6:14:12 PM | [NSO Update] Visayas Grid-08/17/2023 18:12: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2487MW, PK=2089MW, RR=40MW, NetOpMargin: EVE=358 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @330MW, PGPP1 @75MW, TPC-Carmen @30MW [WEBSMS] | CVIS
8/17/2023 6:13:19 PM | [NSO Update] Mindanao Grid-08/17/2023 18:15: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3331MW, PK=2225MW, RR=20MW, NetOpMargin: EVE=1086 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @101MW, AG4 @116MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/17/2023 5:55:29 PM | [NSO Update] Luzon Grid-08/17/2023 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13221MW, PK=10824MW, RR=398MW, NetOpMargin: EVE=2000 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC2 @320MW, MSLC3 @130MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/17/2023 5:26:46 PM | Luzon Grid-08/17/2023 17:24: Bacman-Palayan Binary 230kV line and Palayan Binary 230kV Bus 1 were energized at 1709H. Palayan Binary 47MVA GSUT was energized at 1717H but Bacman-Palayan Binary 230kV line tripped afterwards. (On-going energization of Palayan Binary Plant 47MVA GSUT) [WEBSMS] | CLUZ
8/17/2023 5:24:47 PM | Luzon Grid-08/17/2023 17:24: Bacman-Palayan Binary 230kV line and Palayan Binary 230kV Bus 1 were energized at 1709H. Palayan Binary 47MVA GSUT was energized at 1717H but Bacman-Palayan Binary 230kV line tripped afterwards. (On-going energization of Palayan Binary Plant 47MVA GSUT) [WEBSMS] | CLUZ
8/17/2023 4:53:25 PM | Mindanao Grid-08/17/2023 16:54: Baloi-Villanueva 230kV L1 successfully restored at 1648H. From Planned Outage/GOMP. [WEBSMS] | CMIN
8/17/2023 4:53:24 PM | Mindanao Grid-08/17/2023 16:53: Baloi-Villanueva 230 kV Line 1 restored at 1648H. Planned Outage [WEBSMS] | CMIN
8/17/2023 4:51:52 PM | Mindanao Grid-08/17/2023 16:54: Baloi-Villanueva 230kV L1 successfully restored at 1648H. From Planned Outage/GOMP. [WEBSMS] | CMIN
8/17/2023 4:50:47 PM | Mindanao Grid-08/17/2023 16:53: Baloi-Villanueva 230 kV Line 1 restored at 1648H. Planned Outage [WEBSMS] | CMIN
8/17/2023 3:12:37 PM | Mindanao Grid-08/17/2023 15:14: WMPC DG07 shutdown at 1506H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/17/2023 3:12:24 PM | Mindanao Grid-08/17/2023 15:14: WMPC DG07 shutdown at 1506H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/17/2023 2:50:39 PM | Luzon Grid-08/17/2023 14:50: San Jose 750MVA T04 restored at 1448H (Planned Outage) [WEBSMS] | CLUZ
8/17/2023 1:07:54 PM | [NSO Update] Mindanao Grid-08/17/2023 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3374MW, PK=2296MW, RR=20MW, NetOpMargin: PM=1058, EVE=1141 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @101MW, AG4 @116MW, AG5 @38MW, AG6 @141MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/17/2023 1:07:31 PM | [NSO Update] Mindanao Grid-08/17/2023 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3374MW, PK=2296MW, RR=20MW, NetOpMargin: PM=1058, EVE=1141 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @101MW, AG4 @116MW, AG5 @38MW, AG6 @141MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/17/2023 1:07:30 PM | Luzon Grid-08/17/2023 12:59: SLPGC 1 tripped with 63MW load at 1248H (Unplanned Outage) [WEBSMS] | CLUZ
8/17/2023 1:00:06 PM | [NSO Update] Visayas Grid-08/17/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2650MW, PK=2184MW, RR=40MW, NetOpMargin: PM=426, EVE=405 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 315MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/17/2023 12:59:14 PM | Luzon Grid-08/17/2023 12:59: SLPGC 1 tripped with 63MW load at 1248H (Unplanned Outage) [WEBSMS] | CLUZ
8/17/2023 12:57:29 PM | [NSO Update] Visayas Grid-08/17/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2650MW, PK=2184MW, RR=40MW, NetOpMargin: PM=426, EVE=405 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 315MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/17/2023 12:54:04 PM | [NSO Update] Luzon Grid-08/17/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13595MW, PK=12007MW, RR=429MW, NetOpMargin: PM=1159, EVE=1603 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 130MW, SLPGC 1 @ 110MW, Ilijan A @ 250MW, Ilijan B @ 250MW, SAN GABRIEL @70MW, PAGBILAO3 @315MW [WEBSMS] | CLUZ
8/17/2023 12:51:26 PM | [NSO Update] Luzon Grid-08/17/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13595MW, PK=12007MW, RR=429MW, NetOpMargin: PM=1159, EVE=1603 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 130MW, SLPGC 1 @ 110MW, Ilijan A @ 250MW, Ilijan B @ 250MW, SAN GABRIEL @70MW, PAGBILAO3 @315MW [WEBSMS] | CLUZ
8/17/2023 11:17:18 AM | Luzon Grid-08/17/2023 11:11: San Gabriel de load from 408 to 264 with total of 144MW at1054H (Unplanned outage). [WEBSMS] | CLUZ
8/17/2023 11:11:26 AM | Luzon Grid-08/17/2023 11:11: San Gabriel de load from 408 to 264 with total of 144MW at1054H (Unplanned outage). [WEBSMS] | CLUZ
8/17/2023 10:53:25 AM | Mindanao Grid-08/17/2023 10:55: WMPC DG7 online at 1051H. (Planned Outage). [WEBSMS] | CMIN
8/17/2023 10:52:51 AM | Mindanao Grid-08/17/2023 10:55: WMPC DG7 online at 1051H. (Planned Outage). [WEBSMS] | CMIN
8/17/2023 10:34:28 AM | Visayas Grid-08/17/2023 10:34: Colon-Calongcalong 138kV Line 1 de-energized at 1033H. (Planned outage) [WEBSMS] | CVIS
8/17/2023 10:33:50 AM | Visayas Grid-08/17/2023 10:34: Colon-Calongcalong 138kV Line 1 de-energized at 1033H. (Planned outage) [WEBSMS] | CVIS
8/17/2023 10:03:53 AM | Luzon Grid-08/17/2023 10:02: Bacman-Palayan 230kV Line de-energized at 0958H (Unplanned Outage) [WEBSMS] | CLUZ
8/17/2023 10:02:28 AM | Luzon Grid-08/17/2023 10:02: Bacman-Palayan 230kV Line de-energized at 0958H (Unplanned Outage) [WEBSMS] | CLUZ
8/17/2023 8:53:18 AM | Mindanao Grid-08/17/2023 08:55: WMPC DG9 online at 0850H. (Planned Outage). [WEBSMS] | CMIN
8/17/2023 8:52:46 AM | Mindanao Grid-08/17/2023 08:55: WMPC DG9 online at 0850H. (Planned Outage). [WEBSMS] | CMIN
8/17/2023 8:42:10 AM | Mindanao Grid-08/17/2023 08:43: Baloi-Villanueva 230 kV Line 1 de-energized at 0809H to facilitate line maintenance activities. Planned Outage [WEBSMS] | CMIN
8/17/2023 8:41:27 AM | Mindanao Grid-08/17/2023 08:43: Baloi-Villanueva 230 kV Line 1 de-energized at 0809H to facilitate line maintenance activities. Planned Outage [WEBSMS] | CMIN
8/17/2023 5:52:03 AM | [NSO Update] Luzon Grid-08/17/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14120MW, PK=11511MW, RR=422MW, NetOpMargin: AM=2187, PM=1523, EVE=1946 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 320MW, Masinloc 2 @ 320MW, Masinloc 3 @ 130MW, SLPGC 1 @ 110MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/17/2023 5:51:20 AM | [NSO Update] Visayas Grid-08/17/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2609MW, PK=2194MW, RR=40MW, NetOpMargin: AM=375, PM=265, EVE=331 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 330MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/17/2023 5:50:18 AM | [NSO Update] Mindanao Grid-08/17/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3380MW, PK=2217MW, RR=20MW, NetOpMargin: AM=1144, PM=1122, EVE=1128 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @101MW, AG4 @116MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/17/2023 5:49:21 AM | [NSO Update] Visayas Grid-08/17/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2609MW, PK=2194MW, RR=40MW, NetOpMargin: AM=375, PM=265, EVE=331 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 330MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/17/2023 4:17:51 AM | [NSO Update] Luzon Grid-08/17/2023 04:17: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/17/2023 4:17:33 AM | [NSO Update] Luzon Grid-08/17/2023 04:17: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/17/2023 4:17:11 AM | [NSO Update] Mindanao Grid-08/17/2023 04:19: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/17/2023 4:16:54 AM | [NSO Update] Mindanao Grid-08/17/2023 04:19: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/17/2023 4:16:50 AM | [NSO Update] Visayas Grid-08/17/2023 04:16: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/17/2023 4:16:36 AM | [NSO Update] Visayas Grid-08/17/2023 04:16: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/17/2023 3:00:10 AM | Luzon Grid-08/17/2023 02:53: Kalayaan U1 pump online at 0246H (Unplanned Outage). Note: From Kalayaan Unit 4 to Unit 1. [WEBSMS] | CLUZ
8/17/2023 2:53:48 AM | Luzon Grid-08/17/2023 02:53: Kalayaan U1 pump online at 0246H (Unplanned Outage). Note: From Kalayaan Unit 4 to Unit 1. [WEBSMS] | CLUZ
8/17/2023 2:16:47 AM | Luzon Grid-08/17/2023 02:15: Kalayaan Unit 4 tripped as pump at 0211H (Unplanned Outage). The highest frequency is 60.412 Hz. [WEBSMS] | CLUZ
8/17/2023 2:15:09 AM | Luzon Grid-08/17/2023 02:15: Kalayaan Unit 4 tripped as pump at 0211H (Unplanned Outage). The highest frequency is 60.412 Hz. [WEBSMS] | CLUZ
8/16/2023 10:49:53 PM | Luzon Grid-08/16/2023 22:40: Las Pinas(Zapote) 230kV Bus 2 and Las Pinas(Zapote) 300MVA T01 were restored at 2234H and 2237H respectively. (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2023 10:49:44 PM | Luzon Grid-08/16/2023 22:40: Las Pinas(Zapote) 230kV Bus 2 and Las Pinas(Zapote) 300MVA T01 were restored at 2234H and 2237H respectively. (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2023 9:42:19 PM | Mindanao Grid-08/16/2023 21:43: WMPC DG09 cut-out at 2114H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2023 9:40:47 PM | Mindanao Grid-08/16/2023 21:43: WMPC DG09 cut-out at 2114H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2023 7:24:38 PM | Luzon Grid-08/16/2023 19:24: Las Pinas(Zapote) 230kV Bus 2 and Las Pinas(Zapote) 300MVA Transformer No. 1 - de-energized at 1921H (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2023 7:23:52 PM | Luzon Grid-08/16/2023 19:24: Las Pinas(Zapote) 230kV Bus 2 and Las Pinas(Zapote) 300MVA Transformer No. 1 - de-energized at 1921H (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2023 6:21:37 PM | Visayas Grid-08/16/2023 18:21: Magdugo SS 138kV Bus 2 energized at 1819H. (Planned outage) [WEBSMS] | CVIS
8/16/2023 6:21:19 PM | Visayas Grid-08/16/2023 18:21: Magdugo SS 138kV Bus 2 energized at 1819H. (Planned outage) [WEBSMS] | CVIS
8/16/2023 6:00:31 PM | [NSO Update] Mindanao Grid-08/16/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3295MW, PK=2195MW, RR=20MW, NetOpMargin: EVE=1080 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/16/2023 6:00:29 PM | [NSO Update] Luzon Grid-08/16/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13286MW, PK=10916MW, RR=398MW, NetOpMargin: EVE=1972 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 320MW, Masinloc 2 @ 315MW, Masinloc 3 @ 130MW, Ilijan A @ 250MW, Ilijan B @ 250MW, SLPGC 1 @ 35MW [WEBSMS] | CLUZ
8/16/2023 6:00:00 PM | [NSO Update] Luzon Grid-08/16/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13286MW, PK=10916MW, RR=398MW, NetOpMargin: EVE=1972 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 320MW, Masinloc 2 @ 315MW, Masinloc 3 @ 130MW, Ilijan A @ 250MW, Ilijan B @ 250MW, SLPGC 1 @ 35MW [WEBSMS] | CLUZ
8/16/2023 5:59:52 PM | [NSO Update] Visayas Grid-08/16/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2486MW, PK=2070MW, RR=40MW, NetOpMargin: EVE=376 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 328MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/16/2023 5:59:19 PM | [NSO Update] Visayas Grid-08/16/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2486MW, PK=2070MW, RR=40MW, NetOpMargin: EVE=376 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 328MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/16/2023 5:58:45 PM | [NSO Update] Mindanao Grid-08/16/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3295MW, PK=2195MW, RR=20MW, NetOpMargin: EVE=1080 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/16/2023 5:42:34 PM | Luzon Grid-08/16/2023 17:42: Bayombong-Matuno HEPP 69kV Line restored at 1741H. (Planned Outage) [WEBSMS] | CLUZ
8/16/2023 5:22:53 PM | Luzon Grid-08/16/2023 17:20: Bayombong-Matuno HEPP 69kV Line de-energized at 1719H. (Planned Outage) [WEBSMS] | CLUZ
8/16/2023 5:20:33 PM | Luzon Grid-08/16/2023 17:20: Bayombong-Matuno HEPP 69kV Line de-energized at 1719H. (Planned Outage) [WEBSMS] | CLUZ
8/16/2023 4:24:33 PM | Mindanao Grid-08/16/2023 16:26: WMPC DG07 cut-out at 1613H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2023 4:24:04 PM | Mindanao Grid-08/16/2023 16:26: WMPC DG07 cut-out at 1613H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2023 1:01:59 PM | [NSO Update] Mindanao Grid-08/16/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3363MW, PK=2339MW, RR=20MW, NetOpMargin: PM=1004, EVE=1078 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MCO @255MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @101MW, AG4 @116MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/16/2023 12:58:40 PM | [NSO Update] Mindanao Grid-08/16/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3363MW, PK=2339MW, RR=20MW, NetOpMargin: PM=1004, EVE=1078 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MCO @255MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @101MW, AG4 @116MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/16/2023 12:52:49 PM | [NSO Update] Visayas Grid-08/16/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2644MW, PK=2231MW, RR=40MW, NetOpMargin: PM=373, EVE=340 Highest Unit O/L: THVI 1&2@169MW Derated Plant: LEYTE A @330MW, PGPP1 @75MW, TPC-CARMEN@30MW [WEBSMS] | CVIS
8/16/2023 12:52:31 PM | [NSO Update] Visayas Grid-08/16/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2644MW, PK=2231MW, RR=40MW, NetOpMargin: PM=373, EVE=340 Highest Unit O/L: THVI 1&2@169MW Derated Plant: LEYTE A @330MW, PGPP1 @75MW, TPC-CARMEN@30MW [WEBSMS] | CVIS
8/16/2023 12:32:37 PM | [NSO Update] Luzon Grid-08/16/2023 12:32: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13990MW, PK=11947MW, RR=473MW, NetOpMargin: PM=1570, EVE=1966 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @173MW, MASINLOC 1 @320MW, MASINLOC 2 @315MW, MASINLOC 3 @130MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/16/2023 12:32:20 PM | [NSO Update] Luzon Grid-08/16/2023 12:32: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13990MW, PK=11947MW, RR=473MW, NetOpMargin: PM=1570, EVE=1966 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @173MW, MASINLOC 1 @320MW, MASINLOC 2 @315MW, MASINLOC 3 @130MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/16/2023 10:59:07 AM | Mindanao Grid-08/16/2023 10:57: WMPC DG07 cut-in at 1053H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2023 10:55:23 AM | Mindanao Grid-08/16/2023 10:57: WMPC DG07 cut-in at 1053H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2023 10:54:07 AM | Mindanao Grid-08/16/2023 10:53: WMPC DG09 update: cut-in at 0850H (not cut-out). From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2023 10:50:46 AM | Mindanao Grid-08/16/2023 10:53: WMPC DG09 update: cut-in at 0850H (not cut-out). From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2023 10:46:09 AM | Mindanao Grid-08/16/2023 10:48: Maco - TM1 138KV line 1 energized at 1028H. Planned outage/FO27AD/Non-GOMP. Testing and simulation of revised TM! monitoring logic. [WEBSMS] | CMIN
8/16/2023 10:45:46 AM | Mindanao Grid-08/16/2023 10:48: Maco - TM1 138KV line 1 energized at 1028H. Planned outage/FO27AD/Non-GOMP. Testing and simulation of revised TM! monitoring logic. [WEBSMS] | CMIN
8/16/2023 10:10:46 AM | Mindanao Grid-08/16/2023 10:09: WMPC DG010 declared available at 1000H from Forced Outage (07/31/2023 08:50:00, due to water leak). [WEBSMS] | CMIN
8/16/2023 10:06:59 AM | Mindanao Grid-08/16/2023 10:09: WMPC DG010 declared available at 1000H from Forced Outage (07/31/2023 08:50:00, due to water leak). [WEBSMS] | CMIN
8/16/2023 9:52:24 AM | Mindanao Grid-08/16/2023 09:54: WMPC DG09 cut-out at 0850H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2023 9:51:53 AM | Mindanao Grid-08/16/2023 09:54: WMPC DG09 cut-out at 0850H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/16/2023 9:40:32 AM | Visayas Grid-08/16/2023 09:40: Magdugo SS 138kV Bus 2 de-energized at 0933H. (Planned outage) [WEBSMS] | CVIS
8/16/2023 9:40:30 AM | Visayas Grid-08/16/2023 09:40: Magdugo SS 138kV Bus 2 de-energized at 0933H. (Planned outage) [WEBSMS] | CVIS
8/16/2023 9:22:11 AM | Mindanao Grid-08/16/2023 09:23: Maco - TM1 138KV line 1 deenergized at 0849H. Planned outage/FO27AD/Non-GOMP. Testing and simulation of revised TM! monitoring logic. [WEBSMS] | CMIN
8/16/2023 9:21:12 AM | Mindanao Grid-08/16/2023 09:23: Maco - TM1 138KV line 1 deenergized at 0849H. Planned outage/FO27AD/Non-GOMP. Testing and simulation of revised TM! monitoring logic. [WEBSMS] | CMIN
8/16/2023 9:09:33 AM | Luzon Grid-08/16/2023 09:09: SLPG1 online at 0903H. (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2023 9:09:01 AM | Luzon Grid-08/16/2023 09:09: SLPG1 online at 0903H. (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2023 5:58:41 AM | [NSO Update] Mindanao Grid-08/16/2023 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3397MW, PK=2198MW, RR=20MW, NetOpMargin: AM=1179, PM=1171, EVE=1192 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @101MW, AG4 @116MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/16/2023 5:57:07 AM | [NSO Update] Mindanao Grid-08/16/2023 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3397MW, PK=2198MW, RR=20MW, NetOpMargin: AM=1179, PM=1171, EVE=1192 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @101MW, AG4 @116MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @125MW [WEBSMS] | CMIN
8/16/2023 5:57:05 AM | [NSO Update] Visayas Grid-08/16/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2586MW, PK=2163MW, RR=40MW, NetOpMargin: AM=383, PM=287, EVE=345 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @330MW, PGPP1 @75MW [WEBSMS] | CVIS
8/16/2023 5:55:23 AM | [NSO Update] Luzon Grid-08/16/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14001MW, PK=11713MW, RR=422MW, NetOpMargin: AM=1866, PM=1536, EVE=1976 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC2 @315MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/16/2023 5:54:39 AM | [NSO Update] Visayas Grid-08/16/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2586MW, PK=2163MW, RR=40MW, NetOpMargin: AM=383, PM=287, EVE=345 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @330MW, PGPP1 @75MW [WEBSMS] | CVIS
8/16/2023 5:53:27 AM | [NSO Update] Luzon Grid-08/16/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14001MW, PK=11713MW, RR=422MW, NetOpMargin: AM=1866, PM=1536, EVE=1976 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC2 @315MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/16/2023 5:30:38 AM | Luzon Grid-08/16/2023 05:30: SLPGC 1 tripped with 10MW load at 0514H (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2023 4:48:54 AM | [NSO Update] Mindanao Grid-08/16/2023 04:50: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/16/2023 4:48:52 AM | [NSO Update] Luzon Grid-08/16/2023 04:47: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/16/2023 4:47:37 AM | [NSO Update] Mindanao Grid-08/16/2023 04:50: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/16/2023 4:47:20 AM | [NSO Update] Visayas Grid-08/16/2023 04:47: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/16/2023 4:47:00 AM | [NSO Update] Luzon Grid-08/16/2023 04:47: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/16/2023 4:46:59 AM | [NSO Update] Visayas Grid-08/16/2023 04:47: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/16/2023 1:38:24 AM | Luzon Grid-08/16/2023 01:36: Time Correction: SLPG1online at 0045H (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2023 1:36:32 AM | Luzon Grid-08/16/2023 01:36: Time Correction: SLPG1online at 0045H (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2023 1:12:05 AM | Luzon Grid-08/16/2023 01:10: Masinloc 3 online at 0106H (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2023 1:10:08 AM | Luzon Grid-08/16/2023 01:10: Masinloc 3 online at 0106H (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2023 12:51:41 AM | Luzon Grid-08/16/2023 00:50: SLPG1 online at 1245H (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2023 12:50:33 AM | Luzon Grid-08/16/2023 00:50: SLPG1 online at 1245H (Unplanned Outage) [WEBSMS] | CLUZ
8/16/2023 12:49:04 AM | Luzon Grid-08/16/2023 00:49: Araneta-Sta. Mesa 115kV L2 restored at 1248H (Planned Outage) [WEBSMS] | CLUZ
8/15/2023 11:14:58 PM | Luzon Grid-08/15/2023 23:13: Araneta-Sta. Mesa 115kV L2 de-energized at 2313H (Planned Outage) [WEBSMS] | CLUZ
8/15/2023 11:13:31 PM | Luzon Grid-08/15/2023 23:13: Araneta-Sta. Mesa 115kV L2 de-energized at 2313H (Planned Outage) [WEBSMS] | CLUZ
8/15/2023 10:19:09 PM | Luzon Grid-08/15/2023 22:05: Masinloc 3 tripped with 76MW load at 2149H (Unplanned Outage) [WEBSMS] | CLUZ
8/15/2023 10:05:27 PM | Luzon Grid-08/15/2023 22:05: Masinloc 3 tripped with 76MW load at 2149H (Unplanned Outage) [WEBSMS] | CLUZ
8/15/2023 6:24:48 PM | Luzon Grid-08/15/2023 18:25: Masinloc 3 online at 1817H (Unplanned Outage) [WEBSMS] | CLUZ
8/15/2023 6:01:33 PM | [NSO Update] Mindanao Grid-08/15/2023 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3373MW, PK=2273MW, RR=20MW, NetOpMargin: EVE=1080 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @101MW, AG4 @116MW, AG5 @40MW, AG6 @140MW, AG7 @32MW, PG4 @115MW [WEBSMS] | CMIN
8/15/2023 5:59:43 PM | [NSO Update] Visayas Grid-08/15/2023 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2489MW, PK=2093MW, RR=40MW, NetOpMargin: EVE=356 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @330MW, PGPP1 @75MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/15/2023 5:58:49 PM | Mindanao Grid-08/15/2023 18:01: Agus 1 Unit 1 HEP synchronized at 1729H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 5:56:04 PM | [NSO Update] Luzon Grid-08/15/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12998MW, PK=10876MW, RR=398MW, NetOpMargin: EVE=1724 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC2 @315MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/15/2023 5:48:36 PM | Mindanao Grid-08/15/2023 17:50: GNPK - KAUSWAGAN 230KV LINE 2 restored at 1738H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 5:47:44 PM | Mindanao Grid-08/15/2023 17:50: GNPK - KAUSWAGAN 230KV LINE 2 restored at 1738H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 5:37:58 PM | Mindanao Grid-08/15/2023 17:37: Mt. Apo (MA3) Geothermal Power plant synchronized at 1732H. Unplanned Outage. [WEBSMS] | CMIN
8/15/2023 5:34:42 PM | Mindanao Grid-08/15/2023 17:37: Mt. Apo (MA3) Geothermal Power plant synchronized at 1732H. Unplanned Outage. [WEBSMS] | CMIN
8/15/2023 5:31:16 PM | Mindanao Grid-08/15/2023 17:33: Mt. Apo (MA3) Geothermal Power plant synchronized at 1701H. But tripped again at 1703H. Unplanned Outage. [WEBSMS] | CMIN
8/15/2023 4:45:09 PM | Mindanao Grid-08/15/2023 16:47: Agus 1 50MVA transformer no. 1 (7XFO1MRW) Powerloss at 0906H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 4:44:35 PM | Mindanao Grid-08/15/2023 16:47: Agus 1 50MVA transformer no. 1 (7XFO1MRW) Powerloss at 0906H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 4:16:48 PM | Mindanao Grid-08/15/2023 16:17: WMPC DG09 cut-out at 1613H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/15/2023 4:15:21 PM | Mindanao Grid-08/15/2023 16:17: WMPC DG09 cut-out at 1613H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/15/2023 4:06:17 PM | Mindanao Grid-08/15/2023 16:06: Agus 2 - Agus 1 138KV Tie line restored at 1537H (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 4:06:16 PM | Mindanao Grid-08/15/2023 16:07: Agus 2 U1 HEP synchronize at 1540H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 4:06:15 PM | Mindanao Grid-08/15/2023 16:06: Agus 2 U2 HEP synchronize at 1532H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 4:04:48 PM | Mindanao Grid-08/15/2023 16:07: Agus 2 U1 HEP synchronize at 1540H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 4:04:27 PM | Mindanao Grid-08/15/2023 16:06: Agus 2 - Agus 1 138KV Tie line restored at 1537H (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 4:03:36 PM | Mindanao Grid-08/15/2023 16:06: Agus 2 U2 HEP synchronize at 1532H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 4:01:59 PM | Mindanao Grid-08/15/2023 16:04: Baloi - Agus 2 138KV line 1 restored at 1502H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 4:01:47 PM | Mindanao Grid-08/15/2023 16:04: Baloi - Agus 2 138KV line 1 restored at 1502H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 4:01:15 PM | Mindanao Grid-08/15/2023 16:03: Baloi - Agus 2 138KV line 2 restored at 1514H (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 4:00:37 PM | Mindanao Grid-08/15/2023 16:03: Baloi - Agus 2 138KV line 2 restored at 1514H (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 3:58:04 PM | Mindanao Grid-08/15/2023 16:00: Baloi - Agus 2 line 1 restored at 1502H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 3:41:25 PM | Mindanao Grid-08/15/2023 15:43: Agus 2 U3 HEP synchronize at 1517H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 3:41:13 PM | Mindanao Grid-08/15/2023 15:43: Agus 2 U3 HEP synchronize at 1517H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 3:38:40 PM | Mindanao Grid-08/15/2023 15:41: Matanao - Culaman 230kV Line 1 restored at 1518H. Unplanned outage. [WEBSMS] | CMIN
8/15/2023 3:38:27 PM | Mindanao Grid-08/15/2023 15:41: Matanao - Culaman 230kV Line 1 restored at 1518H. Unplanned outage. [WEBSMS] | CMIN
8/15/2023 3:36:49 PM | Mindanao Grid-08/15/2023 15:39: Matanao-Culaman 230kV Line 1 tripped at 1458H. Unplanned outage. [WEBSMS] | CMIN
8/15/2023 3:36:12 PM | Mindanao Grid-08/15/2023 15:39: Matanao-Culaman 230kV Line 1 tripped at 1458H. Unplanned outage. [WEBSMS] | CMIN
8/15/2023 3:31:10 PM | Luzon Grid-08/15/2023 15:29: Lumban-Gumaca 230kV Line 1 restored at 1528H. (Planned Outage) [WEBSMS] | CLUZ
8/15/2023 3:29:15 PM | Luzon Grid-08/15/2023 15:29: Lumban-Gumaca 230kV Line 1 restored at 1528H. (Planned Outage) [WEBSMS] | CLUZ
8/15/2023 2:55:03 PM | Luzon Grid-08/15/2023 14:48: Binga HEPP 230kV Overhead Line 1 restored at 1445H. (Unplanned Outage) [WEBSMS] | CLUZ
8/15/2023 2:48:34 PM | Luzon Grid-08/15/2023 14:48: Binga HEPP 230kV Overhead Line 1 restored at 1445H. (Unplanned Outage) [WEBSMS] | CLUZ
8/15/2023 12:52:42 PM | [NSO Update] Mindanao Grid-08/15/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3280MW, PK=2338MW, RR=20MW, NetOpMargin: PM=922, EVE=930 Highest Unit O/L: GNPK 1&4@ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @28MW, AG4 @116MW, AG5 @40MW, AG6 @140MW, AG7 @32MW, PG4 @115MW [WEBSMS] | CMIN
8/15/2023 12:51:02 PM | [NSO Update] Mindanao Grid-08/15/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3280MW, PK=2338MW, RR=20MW, NetOpMargin: PM=922, EVE=930 Highest Unit O/L: GNPK 1&4@ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @28MW, AG4 @116MW, AG5 @40MW, AG6 @140MW, AG7 @32MW, PG4 @115MW [WEBSMS] | CMIN
8/15/2023 12:48:08 PM | [NSO Update] Visayas Grid-08/15/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2610MW, PK=2283MW, RR=40MW, NetOpMargin: PM=288, EVE=337 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @330MW, PGPP1 @75MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/15/2023 12:43:23 PM | [NSO Update] Luzon Grid-08/15/2023 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13168MW, PK=11792MW, RR=465MW, NetOpMargin: PM=911, EVE=1629 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 1 @200MW, CALACA 2 @173MW, MASINLOC 1 @310MW, MASINLOC 2 @240MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/15/2023 12:24:21 PM | Mindanao Grid-08/15/2023 12:25: Maco - TM1 138KV Line 2 restored at 1158H. (Planned outage) [WEBSMS] | CMIN
8/15/2023 12:22:47 PM | Mindanao Grid-08/15/2023 12:25: Maco - TM1 138KV Line 2 restored at 1158H. (Planned outage) [WEBSMS] | CMIN
8/15/2023 11:42:10 AM | Luzon Grid-08/15/2023 11:42: San Gabriel online at 1139H. (Unplanned Outage) [WEBSMS] | CLUZ
8/15/2023 10:52:35 AM | Mindanao Grid-08/15/2023 10:54: WMPC DG09 cut-in at 1050H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/15/2023 10:52:05 AM | Mindanao Grid-08/15/2023 10:54: WMPC DG09 cut-in at 1050H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/15/2023 10:32:34 AM | Mindanao Grid-08/15/2023 10:34: WMPC DG05 cut-in at 0851H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/15/2023 10:32:05 AM | Mindanao Grid-08/15/2023 10:34: WMPC DG05 cut-in at 0851H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/15/2023 10:10:55 AM | [NSO Update] Visayas Grid-08/15/2023 10:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0833H with power going to Visayas. (MVIP Test) [WEBSMS] | CVIS
8/15/2023 10:09:28 AM | [NSO Update] Visayas Grid-08/15/2023 10:09: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0833H with power going to Visayas. (MVIP Test) [WEBSMS] | CVIS
8/15/2023 10:09:24 AM | [NSO Update] Mindanao Grid-08/15/2023 10:11: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0833H with power going to Visayas. (MVIP Test) [WEBSMS] | CMIN
8/15/2023 10:09:23 AM | [NSO Update] Mindanao Grid-08/15/2023 10:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0826H with power going to Mindanao (MVIP Test) [WEBSMS] | CMIN
8/15/2023 10:09:01 AM | [NSO Update] Mindanao Grid-08/15/2023 10:11: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0833H with power going to Visayas. (MVIP Test) [WEBSMS] | CMIN
8/15/2023 10:08:00 AM | [NSO Update] Visayas Grid-08/15/2023 10:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0826H with power going to Mindanao. (MVIP Test) [WEBSMS] | CVIS
8/15/2023 10:07:38 AM | [NSO Update] Mindanao Grid-08/15/2023 10:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0826H with power going to Mindanao (MVIP Test) [WEBSMS] | CMIN
8/15/2023 10:06:42 AM | Visayas Grid-08/15/2023 10:06: Magdugo SS 138 kV Bus 1 de-energized at 1006H. (Planned Outage) [WEBSMS] | CVIS
8/15/2023 10:03:35 AM | Luzon Grid-08/15/2023 10:03: Tayabas SS 600MVA T01 restored at 1003H. (Planned Outage) [WEBSMS] | CLUZ
8/15/2023 9:56:35 AM | Mindanao Grid-08/15/2023 09:57: Maco - TM1 138KV line 2 deenergized at 0927H. (Planned Outage) [WEBSMS] | CMIN
8/15/2023 9:55:28 AM | Mindanao Grid-08/15/2023 09:57: Maco - TM1 138KV line 2 deenergized at 0927H. (Planned Outage) [WEBSMS] | CMIN
8/15/2023 9:23:14 AM | Mindanao Grid-08/15/2023 09:24: Agus 1 HEP Unit 1 and Agus 2 HEP Unit 1, Unit 2, and Unit 3 was isolated with 121 MW load at 0906H. The lowest frequency is 59.195 Hz. No ALD (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 9:21:42 AM | Mindanao Grid-08/15/2023 09:24: Agus 1 HEP Unit 1 and Agus 2 HEP Unit 1, Unit 2, and Unit 3 was isolated with 121 MW load at 0906H. The lowest frequency is 59.195 Hz. No ALD (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 9:15:48 AM | Mindanao Grid-08/15/2023 09:16: Baloi - Agus 2 Line 1 & 2 tripped at 0906H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 9:14:05 AM | Mindanao Grid-08/15/2023 09:16: Baloi - Agus 2 Line 1 & 2 tripped at 0906H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 8:58:46 AM | Luzon Grid-08/15/2023 08:58: Binga HEPP 230kV Overhead Line 1 de-energized at 0857H. (Unplanned Outage) [WEBSMS] | CLUZ
8/15/2023 8:58:11 AM | Luzon Grid-08/15/2023 08:58: Binga HEPP 230kV Overhead Line 1 de-energized at 0857H. (Unplanned Outage) [WEBSMS] | CLUZ
8/15/2023 8:52:26 AM | Mindanao Grid-08/15/2023 08:52: Asiga HEP (ASG) tripped at 0657H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 8:49:54 AM | Mindanao Grid-08/15/2023 08:52: Asiga HEP (ASG) tripped at 0657H. (Unplanned Outage) [WEBSMS] | CMIN
8/15/2023 8:47:26 AM | Mindanao Grid-08/15/2023 08:48: Mt. Apo 3 Binary Plant cut-out at 0727H. (Planned Outage) [WEBSMS] | CMIN
8/15/2023 8:46:24 AM | Mindanao Grid-08/15/2023 08:48: Mt. Apo 3 Binary Plant cut-out at 0727H. (Planned Outage) [WEBSMS] | CMIN
8/15/2023 8:19:51 AM | Mindanao Grid-08/15/2023 08:21: Kidapawan SS Power Transformer No. 2 deenergized at 0811H. (Planned outage) [WEBSMS] | CMIN
8/15/2023 8:18:43 AM | Mindanao Grid-08/15/2023 08:21: Kidapawan SS Power Transformer No. 2 deenergized at 0811H. (Planned outage) [WEBSMS] | CMIN
8/15/2023 8:15:08 AM | Mindanao Grid-08/15/2023 08:17: Polanco SS 138KV Bus 1 deenergized at 0801H, (Planned outage) [WEBSMS] | CMIN
8/15/2023 8:14:51 AM | Mindanao Grid-08/15/2023 08:17: Polanco SS 138KV Bus 1 deenergized at 0801H, (Planned outage) [WEBSMS] | CMIN
8/15/2023 8:14:03 AM | Luzon Grid-08/15/2023 08:09: Tayabas SS 600MVA T01 de-energized at 0809H. (Planned Outage) [WEBSMS] | CLUZ
8/15/2023 8:09:43 AM | Luzon Grid-08/15/2023 08:09: Tayabas SS 600MVA T01 de-energized at 0809H. (Planned Outage) [WEBSMS] | CLUZ
8/15/2023 7:46:50 AM | [NSO Update] Mindanao Grid-08/15/2023 07:49: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0743H and de-blocked at 0744H with power going to Mindanao. (MVIP Test) [WEBSMS] | CMIN
8/15/2023 7:46:42 AM | [NSO Update] Visayas Grid-08/15/2023 07:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0743H and de-blocked at 0744H with power going to Mindanao. (MVIP Test) [WEBSMS] | CVIS
8/15/2023 7:46:31 AM | [NSO Update] Mindanao Grid-08/15/2023 07:49: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0743H and de-blocked at 0744H with power going to Mindanao. (MVIP Test) [WEBSMS] | CMIN
8/15/2023 7:46:07 AM | [NSO Update] Visayas Grid-08/15/2023 07:46: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 0743H and de-blocked at 0744H with power going to Mindanao. (MVIP Test) [WEBSMS] | CVIS
8/15/2023 7:11:14 AM | [NSO Update] Visayas Grid-08/15/2023 07:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked and de-blocked at 0657H with power going to Visayas. (MVIP Test) [WEBSMS] | CVIS
8/15/2023 7:10:42 AM | [NSO Update] Mindanao Grid-08/15/2023 07:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked and de-blocked at 0657H with power going to Visayas. (MVIP Test) [WEBSMS] | CMIN
8/15/2023 7:10:10 AM | [NSO Update] Mindanao Grid-08/15/2023 07:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked and de-blocked at 0657H with power going to Visayas. (MVIP Test) [WEBSMS] | CMIN
8/15/2023 7:10:03 AM | [NSO Update] Visayas Grid-08/15/2023 07:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked and de-blocked at 0657H with power going to Visayas. (MVIP Test) [WEBSMS] | CVIS
8/15/2023 7:08:39 AM | Luzon Grid-08/15/2023 07:08: Lumban-Gumaca 230kV Line 1 de-energized at 0707H. (Planned Outage) [WEBSMS] | CLUZ
8/15/2023 7:08:05 AM | Luzon Grid-08/15/2023 07:08: Lumban-Gumaca 230kV Line 1 de-energized at 0707H. (Planned Outage) [WEBSMS] | CLUZ
8/15/2023 7:07:25 AM | Luzon Grid-08/15/2023 07:07: San Gabriel tripped at 0659H with 128MW. Lowest system frequency is 59.61Hz. (Unplanned Outage) [WEBSMS] | CLUZ
8/15/2023 7:02:03 AM | Luzon Grid-08/15/2023 07:02: San Gabriel tripped at 0659H with 128MW. Lowest system frequency is 59.61Hz. (Unplanned Outage) [WEBSMS] | CLUZ
8/15/2023 6:14:43 AM | [NSO Update] Luzon Grid-08/15/2023 06:12: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13454MW, PK=11365MW, RR=422MW, NetOpMargin: AM=1667, PM=1048, EVE=1489 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @200MW, CLC2 @173MW, MSLC1 @310MW, MSLC2 @240MW, ILIJAN A @250MW, ILIJAN B @250MW, [WEBSMS] | CLUZ
8/15/2023 6:12:20 AM | [NSO Update] Luzon Grid-08/15/2023 06:12: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13454MW, PK=11365MW, RR=422MW, NetOpMargin: AM=1667, PM=1048, EVE=1489 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @200MW, CLC2 @173MW, MSLC1 @310MW, MSLC2 @240MW, ILIJAN A @250MW, ILIJAN B @250MW, [WEBSMS] | CLUZ
8/15/2023 5:47:55 AM | [NSO Update] Mindanao Grid-08/15/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3431MW, PK=2070MW, RR=20MW, NetOpMargin: AM=1341, PM=1123, EVE=1207 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @28MW, AG1 @35MW, AG2 @101MW, AG4 @116MW, AG5 @40MW, AG6 @140MW, AG7 @32MW, PG4 @115MW [WEBSMS] | CMIN
8/15/2023 5:45:34 AM | [NSO Update] Visayas Grid-08/15/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2496MW, PK=2182MW, RR=40MW, NetOpMargin: AM=274, PM=282, EVE=340 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @330MW, PGPP1 @74MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/15/2023 5:44:30 AM | [NSO Update] Visayas Grid-08/15/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2496MW, PK=2182MW, RR=40MW, NetOpMargin: AM=274, PM=282, EVE=340 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @330MW, PGPP1 @74MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/15/2023 4:27:14 AM | [NSO Update] Luzon Grid-08/15/2023 04:27: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/15/2023 4:26:51 AM | [NSO Update] Luzon Grid-08/15/2023 04:27: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/15/2023 4:19:44 AM | [NSO Update] Mindanao Grid-08/15/2023 04:21: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/15/2023 4:18:48 AM | [NSO Update] Mindanao Grid-08/15/2023 04:21: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/15/2023 4:18:04 AM | [NSO Update] Visayas Grid-08/15/2023 04:18: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/15/2023 4:07:51 AM | Luzon Grid-08/15/2023 04:08: San Gabriel online at 0405H. (Planned Outage) [WEBSMS] | CLUZ
8/15/2023 4:07:13 AM | Luzon Grid-08/15/2023 04:08: San Gabriel online at 0405H. (Planned Outage) [WEBSMS] | CLUZ
8/15/2023 3:53:50 AM | Luzon Grid-08/15/2023 03:52: For info: San Lorenzo-Sta Rita 230kV Busses were unlooped at 0344H while Batangas 300MVA T04 and T05 were paralleled at 0347H. (Preparation for the synchronization of San Gabriel) [WEBSMS] | CLUZ
8/15/2023 3:52:09 AM | Luzon Grid-08/15/2023 03:52: For info: San Lorenzo-Sta Rita 230kV Busses were unlooped at 0344H while Batangas 300MVA T04 and T05 were paralleled at 0347H. (Preparation for the synchronization of San Gabriel) [WEBSMS] | CLUZ
8/15/2023 3:31:18 AM | Luzon Grid-08/15/2023 03:30: Concepcion-Concepcion Solar 69kV line - restored at 0327H (Planned Outage) [WEBSMS] | CLUZ
8/15/2023 3:30:08 AM | Luzon Grid-08/15/2023 03:30: Concepcion-Concepcion Solar 69kV line - restored at 0327H (Planned Outage) [WEBSMS] | CLUZ
8/14/2023 9:34:45 PM | Mindanao Grid-08/14/2023 21:37: WMPC DG05 cut-out at 2113H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/14/2023 9:34:29 PM | Mindanao Grid-08/14/2023 21:37: WMPC DG05 cut-out at 2113H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/14/2023 9:31:54 PM | Mindanao Grid-08/14/2023 21:32: Mt. Apo 3 Binary Plant cut-in at 2019H. (Unplanned Outage) [WEBSMS] | CMIN
8/14/2023 9:30:21 PM | Mindanao Grid-08/14/2023 21:32: Mt. Apo 3 Binary Plant cut-in at 2019H. (Unplanned Outage) [WEBSMS] | CMIN
8/14/2023 9:11:11 PM | Luzon Grid-08/14/2023 21:06: Malaya-Ingrid 230kV line 2 - de-energized at 2105H (Planned Outage) [WEBSMS] | CLUZ
8/14/2023 9:06:20 PM | Luzon Grid-08/14/2023 21:06: Malaya-Ingrid 230kV line 2 - de-energized at 2105H (Planned Outage) [WEBSMS] | CLUZ
8/14/2023 8:17:45 PM | Luzon Grid-08/14/2023 20:14: San Manuel-San Manuel BESS 69kV line - restored at 2014H (Unplanned Outage) [WEBSMS] | CLUZ
8/14/2023 8:14:17 PM | Luzon Grid-08/14/2023 20:14: San Manuel-San Manuel BESS 69kV line - restored at 2014H (Unplanned Outage) [WEBSMS] | CLUZ
8/14/2023 7:44:24 PM | Luzon Grid-08/14/2023 19:43: Concepcion-Concepcion Solar 69kV line - de-energized at 1941H (Planned Outage) [WEBSMS] | CLUZ
8/14/2023 7:42:53 PM | Luzon Grid-08/14/2023 19:43: Concepcion-Concepcion Solar 69kV line - de-energized at 1941H (Planned Outage) [WEBSMS] | CLUZ
8/14/2023 6:46:06 PM | Mindanao Grid-08/14/2023 18:48: Mt. Apo 3 Binary Plant tripped at 1822H due to restricted earth fault indication. (Unplanned Outage) [WEBSMS] | CMIN
8/14/2023 6:14:05 PM | [NSO Update] Visayas Grid-08/14/2023 18:12: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2394MW, PK=2055MW, RR=40MW, NetOpMargin: EVE=2055 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @75MW, TPC-Carmen @30MW [WEBSMS] | CVIS
8/14/2023 6:13:49 PM | [NSO Update] Visayas Grid-08/14/2023 18:12: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2394MW, PK=2055MW, RR=40MW, NetOpMargin: EVE=2055 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @75MW, TPC-Carmen @30MW [WEBSMS] | CVIS
8/14/2023 6:05:42 PM | [NSO Update] Mindanao Grid-08/14/2023 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3312MW, PK=2103MW, RR=20MW, NetOpMargin: EVE=1189 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/14/2023 6:05:01 PM | [NSO Update] Mindanao Grid-08/14/2023 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3312MW, PK=2103MW, RR=20MW, NetOpMargin: EVE=1189 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/14/2023 6:00:00 PM | [NSO Update] Luzon Grid-08/14/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12460MW, PK=10911MW, RR=260MW, NetOpMargin: EVE=1289 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @150MW, CLC2 @150MW, MSLC1 @305MW, MSLC2 @290MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/14/2023 5:58:42 PM | [NSO Update] Luzon Grid-08/14/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12460MW, PK=10911MW, RR=260MW, NetOpMargin: EVE=1289 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @150MW, CLC2 @150MW, MSLC1 @305MW, MSLC2 @290MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/14/2023 4:36:25 PM | Mindanao Grid-08/14/2023 16:38: Polanco 138kV Bus No. 2 restored at 1631H. (Planned Outage) [WEBSMS] | CMIN
8/14/2023 4:36:01 PM | Mindanao Grid-08/14/2023 16:38: Polanco 138kV Bus No. 2 restored at 1631H. (Planned Outage) [WEBSMS] | CMIN
8/14/2023 2:32:42 PM | Luzon Grid-08/14/2023 14:32: Laoag-Balaoi Wind Farm 115kV Line restored at 1432H. (Planned Outage) [WEBSMS] | CLUZ
8/14/2023 1:11:31 PM | [NSO Update] Mindanao Grid-08/14/2023 13:13: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3354MW, PK=2247MW, RR=20MW, NetOpMargin: PM=1087, EVE=1164 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/14/2023 1:10:47 PM | [NSO Update] Mindanao Grid-08/14/2023 13:13: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3354MW, PK=2247MW, RR=20MW, NetOpMargin: PM=1087, EVE=1164 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/14/2023 12:52:54 PM | [NSO Update] Visayas Grid-08/14/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2551MW, PK=2254MW, RR=40MW, NetOpMargin: PM=258, EVE=308 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @315MW, PGPP1 @75MW, TPC-Carmen @30MW [WEBSMS] | CVIS
8/14/2023 12:52:16 PM | [NSO Update] Visayas Grid-08/14/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2551MW, PK=2254MW, RR=40MW, NetOpMargin: PM=258, EVE=308 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @315MW, PGPP1 @75MW, TPC-Carmen @30MW [WEBSMS] | CVIS
8/14/2023 12:49:10 PM | [NSO Update] Luzon Grid-08/14/2023 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12879MW, PK=11518MW, RR=220MW, NetOpMargin: PM=1141, EVE=1395 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @150MW, CLC2 @150MW, MSLC1 @280MW, MSLC2 @295MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/14/2023 11:29:41 AM | Mindanao Grid-08/14/2023 11:31: WMPC DG03 cut-in at 1103H as RPS - System Voltage Requirement. Replacement unit of DG06 which failed to start up. [WEBSMS] | CMIN
8/14/2023 11:29:32 AM | Mindanao Grid-08/14/2023 11:31: WMPC DG03 cut-in at 1103H as RPS - System Voltage Requirement. Replacement unit of DG06 which failed to start up. [WEBSMS] | CMIN
8/14/2023 10:10:48 AM | Mindanao Grid-08/14/2023 10:11: WMPC DG05 cut-in at 1006H as RPS - System Voltage Requirement. Replacement unit of DG09 on forced outage. [WEBSMS] | CMIN
8/14/2023 10:08:52 AM | Mindanao Grid-08/14/2023 10:11: WMPC DG05 cut-in at 1006H as RPS - System Voltage Requirement. Replacement unit of DG09 on forced outage. [WEBSMS] | CMIN
8/14/2023 10:05:48 AM | Mindanao Grid-08/14/2023 10:06: WMPC DG09 emergency shutdown at 0959H due to gas cutting in cylinder A8. (Unplanned Outage) [WEBSMS] | CMIN
8/14/2023 10:04:14 AM | Mindanao Grid-08/14/2023 10:06: WMPC DG09 emergency shutdown at 0959H due to gas cutting in cylinder A8. (Unplanned Outage) [WEBSMS] | CMIN
8/14/2023 9:06:12 AM | Mindanao Grid-08/14/2023 09:07: WMPC DG09 cut-in at 0902H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/14/2023 9:04:36 AM | Mindanao Grid-08/14/2023 09:07: WMPC DG09 cut-in at 0902H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/14/2023 8:34:23 AM | Luzon Grid-08/14/2023 08:34: Malolos SS 150MVA T01 de-energized at 0812H. (Customer Owned - Planned Outage) [WEBSMS] | CLUZ
8/14/2023 8:34:02 AM | Luzon Grid-08/14/2023 08:34: Malolos SS 150MVA T01 de-energized at 0812H. (Customer Owned - Planned Outage) [WEBSMS] | CLUZ
8/14/2023 8:22:52 AM | Mindanao Grid-08/14/2023 08:25: Polanco 138KV Bus 2 deenergized at 0808H. (Planned Outage) [WEBSMS] | CMIN
8/14/2023 8:22:45 AM | Mindanao Grid-08/14/2023 08:25: Polanco 138KV Bus 2 deenergized at 0808H. (Planned Outage) [WEBSMS] | CMIN
8/14/2023 8:07:36 AM | Luzon Grid-08/14/2023 08:07: Laoag-Balaoi Wind Farm 115kV Line de-energized at 0807H. (Planned Outage) [WEBSMS] | CLUZ
8/14/2023 8:00:41 AM | Luzon Grid-08/14/2023 07:57: Malolos SS 150MVA T01 de-energized at 0736H. (Customer Owned - Planned Outage) [WEBSMS] | CLUZ
8/14/2023 7:57:35 AM | Luzon Grid-08/14/2023 07:57: Malolos SS 150MVA T01 de-energized at 0736H. (Customer Owned - Planned Outage) [WEBSMS] | CLUZ
8/14/2023 7:09:44 AM | Luzon Grid-08/14/2023 07:09: San Jose - Malolos 230kV Line and Malolos 230kV Bus 1 both restored at 0708H. (Planned Outage) [WEBSMS] | CLUZ
8/14/2023 7:09:26 AM | Luzon Grid-08/14/2023 07:09: San Jose - Malolos 230kV Line and Malolos 230kV Bus 1 both restored at 0708H. (Planned Outage) [WEBSMS] | CLUZ
8/14/2023 6:00:36 AM | [NSO Update] Luzon Grid-08/14/2023 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13095MW, PK=11436MW, RR=220MW, NetOpMargin: AM=1439, PM=1036, EVE=1467 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 150MW, Calaca 2 @ 150MW, Masinloc 1 @ 315MW, Masinloc 2 @ 315MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/14/2023 5:56:45 AM | [NSO Update] Luzon Grid-08/14/2023 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13095MW, PK=11436MW, RR=220MW, NetOpMargin: AM=1439, PM=1036, EVE=1467 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 150MW, Calaca 2 @ 150MW, Masinloc 1 @ 315MW, Masinloc 2 @ 315MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/14/2023 5:52:44 AM | [NSO Update] Mindanao Grid-08/14/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3378MW, PK=2147MW, RR=20MW, NetOpMargin: AM=1211, PM=1065, EVE=1119 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/14/2023 5:52:41 AM | [NSO Update] Mindanao Grid-08/14/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3378MW, PK=2147MW, RR=20MW, NetOpMargin: AM=1211, PM=1065, EVE=1119 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/14/2023 5:52:34 AM | [NSO Update] Visayas Grid-08/14/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2575MW, PK=2206MW, RR=40MW, NetOpMargin: AM=329, PM=256, EVE=338 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 328MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/14/2023 5:50:43 AM | [NSO Update] Visayas Grid-08/14/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2575MW, PK=2206MW, RR=40MW, NetOpMargin: AM=329, PM=256, EVE=338 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 328MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/14/2023 4:57:14 AM | Luzon Grid-08/14/2023 04:57: Quezon(Balintawak)-Dona Imelda(Araneta) 230kV Line restored at 0456H (Planned Outage) [WEBSMS] | CLUZ
8/14/2023 4:57:06 AM | Luzon Grid-08/14/2023 04:57: Quezon(Balintawak)-Dona Imelda(Araneta) 230kV Line restored at 0456H (Planned Outage) [WEBSMS] | CLUZ
8/14/2023 4:36:05 AM | [NSO Update] Visayas Grid-08/14/2023 04:34: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/14/2023 4:36:03 AM | [NSO Update] Visayas Grid-08/14/2023 04:34: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/14/2023 4:35:59 AM | [NSO Update] Luzon Grid-08/14/2023 04:35: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/14/2023 4:35:19 AM | [NSO Update] Luzon Grid-08/14/2023 04:35: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
8/14/2023 4:34:58 AM | [NSO Update] Mindanao Grid-08/14/2023 04:37: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
8/14/2023 4:34:43 AM | [NSO Update] Visayas Grid-08/14/2023 04:34: Weather Update: Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
8/13/2023 9:10:56 PM | Luzon Grid-08/13/2023 21:11: Quezon(Balintawak)-Dona Imelda(Araneta) 230kV Line de-energized at 2108H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 9:10:29 PM | Luzon Grid-08/13/2023 21:11: Quezon(Balintawak)-Dona Imelda(Araneta) 230kV Line de-energized at 2108H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 7:43:36 PM | Luzon Grid-08/13/2023 19:36: Calaca-Sta. Rita 230kV Line 2 restored at 1936H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 7:36:36 PM | Luzon Grid-08/13/2023 19:36: Calaca-Sta. Rita 230kV Line 2 restored at 1936H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 7:10:22 PM | Mindanao Grid-08/13/2023 19:12: Gensan-Matanao 138KV Line 2 energized at 1900H. (Planned Outage) [WEBSMS] | CMIN
8/13/2023 7:10:17 PM | Mindanao Grid-08/13/2023 19:12: Gensan-Matanao 138KV Line 2 energized at 1900H. (Planned Outage) [WEBSMS] | CMIN
8/13/2023 7:07:44 PM | Mindanao Grid-08/13/2023 19:10: Gensan SS 100MVA Mobile Transformer 3 energized at 1859H. (Planned Outage) [WEBSMS] | CMIN
8/13/2023 7:07:10 PM | Mindanao Grid-08/13/2023 19:10: Gensan SS 100MVA Mobile Transformer 3 energized at 1859H. (Planned Outage) [WEBSMS] | CMIN
8/13/2023 6:35:42 PM | Mindanao Grid-08/13/2023 18:38: Davao - Toril 138KV Line 2 energized at 1826H. (Planned outage) [WEBSMS] | CMIN
8/13/2023 6:35:16 PM | Mindanao Grid-08/13/2023 18:38: Davao - Toril 138KV Line 2 energized at 1826H. (Planned outage) [WEBSMS] | CMIN
8/13/2023 5:53:55 PM | [NSO Update] Visayas Grid-08/13/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2355MW, PK=1942MW, RR=40MW, NetOpMargin: EVE=373 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 320MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/13/2023 5:53:53 PM | [NSO Update] Luzon Grid-08/13/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12353MW, PK=10078MW, RR=80MW, NetOpMargin: EVE=2195 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 315MW, Masinloc 2 @ 250MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/13/2023 5:51:32 PM | [NSO Update] Visayas Grid-08/13/2023 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2355MW, PK=1942MW, RR=40MW, NetOpMargin: EVE=373 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 320MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/13/2023 5:50:27 PM | [NSO Update] Mindanao Grid-08/13/2023 17:51: [Correction] GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3332MW, PK=2039MW, RR=20MW, NetOpMargin: EVE=1273 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/13/2023 5:49:26 PM | [NSO Update] Mindanao Grid-08/13/2023 17:51: [Correction] GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3332MW, PK=2039MW, RR=20MW, NetOpMargin: EVE=1273 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/13/2023 5:46:54 PM | [NSO Update] Mindanao Grid-08/13/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2355MW, PK=1942MW, RR=40MW, NetOpMargin: EVE=373 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 320MW, PGPP1 @ 75MW [WEBSMS] | CMIN
8/13/2023 5:46:38 PM | [NSO Update] Mindanao Grid-08/13/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2355MW, PK=1942MW, RR=40MW, NetOpMargin: EVE=373 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 320MW, PGPP1 @ 75MW [WEBSMS] | CMIN
8/13/2023 5:16:36 PM | Luzon Grid-08/13/2023 17:16: Calaca-Malamig(Sta. Rosa) 230kV Line restored at 1713H. (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 5:02:03 PM | Luzon Grid-08/13/2023 17:01: Pagbilao 230kV Bus 2 energized at 1700H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 5:01:06 PM | Luzon Grid-08/13/2023 17:01: Pagbilao 230kV Bus 2 energized at 1700H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 4:30:49 PM | [NSO Update] Visayas Grid-08/13/2023 16:30: Ormoc CS-Naga CS 350kV HVDC (Visayas-Luzon) de-blocked at 1618H (Planned Outage) [WEBSMS] | CVIS
8/13/2023 4:30:11 PM | [NSO Update] Visayas Grid-08/13/2023 16:30: Ormoc CS-Naga CS 350kV HVDC (Visayas-Luzon) de-blocked at 1618H (Planned Outage) [WEBSMS] | CVIS
8/13/2023 4:30:10 PM | [NSO Update] Luzon Grid-08/13/2023 16:29: Ormoc CS-Naga CS 350kV HVDC (Visayas-Luzon) de-blocked at 1618H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 4:29:45 PM | [NSO Update] Luzon Grid-08/13/2023 16:29: Ormoc CS-Naga CS 350kV HVDC (Visayas-Luzon) de-blocked at 1618H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 4:06:48 PM | Luzon Grid-08/13/2023 16:02: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1601H. (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 4:02:05 PM | Luzon Grid-08/13/2023 16:02: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1601H. (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 1:35:10 PM | Luzon Grid-08/13/2023 13:28: Sta. Rita 10 online at 1325H. (Unplanned Outage) [WEBSMS] | CLUZ
8/13/2023 1:27:55 PM | Luzon Grid-08/13/2023 13:28: Sta. Rita 10 online at 1325H. (Unplanned Outage) [WEBSMS] | CLUZ
8/13/2023 1:26:44 PM | [NSO Update] Mindanao Grid-08/13/2023 13:28: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3374MW, PK=1855MW, RR=20MW, NetOpMargin: PM=1499, EVE=1235 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/13/2023 1:26:17 PM | [NSO Update] Mindanao Grid-08/13/2023 13:28: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3374MW, PK=1855MW, RR=20MW, NetOpMargin: PM=1499, EVE=1235 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/13/2023 1:03:22 PM | [NSO Update] Luzon Grid-08/13/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12844MW, PK=9568MW, RR=80MW, NetOpMargin: PM=3196, EVE=2105 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC2 @250MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/13/2023 1:02:55 PM | [NSO Update] Visayas Grid-08/13/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2521MW, PK=1848MW, RR=40MW, NetOpMargin: PM=632, EVE=327 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @75MW [WEBSMS] | CVIS
8/13/2023 1:01:12 PM | [NSO Update] Visayas Grid-08/13/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2521MW, PK=1848MW, RR=40MW, NetOpMargin: PM=632, EVE=327 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @325MW, PGPP1 @75MW [WEBSMS] | CVIS
8/13/2023 12:58:19 PM | [NSO Update] Luzon Grid-08/13/2023 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12844MW, PK=9568MW, RR=80MW, NetOpMargin: PM=3196, EVE=2105 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC2 @250MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/13/2023 10:36:42 AM | Mindanao Grid-08/13/2023 10:36: Kidapawan SS Power Transformer 1 restored at 1031H. (Forced Outage) [WEBSMS] | CMIN
8/13/2023 10:34:35 AM | Mindanao Grid-08/13/2023 10:36: Kidapawan SS Power Transformer 1 restored at 1031H. (Forced Outage) [WEBSMS] | CMIN
8/13/2023 9:46:34 AM | Luzon Grid-08/13/2023 09:43: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0943H. (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 9:43:38 AM | Luzon Grid-08/13/2023 09:43: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0943H. (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 8:55:41 AM | Luzon Grid-08/13/2023 08:55: Dasmarinas 600MVA T04 restored at 0855H. (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 8:54:57 AM | Luzon Grid-08/13/2023 08:55: Dasmarinas 600MVA T04 restored at 0855H. (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 8:53:13 AM | Luzon Grid-08/13/2023 08:52: Dasmarinas 500kV Bus 1 restored at 0852H. (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 8:52:11 AM | Luzon Grid-08/13/2023 08:52: Dasmarinas 500kV Bus 1 restored at 0852H. (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 8:11:43 AM | [NSO Update] Luzon Grid-08/13/2023 08:11: Ormoc CS-Naga CS 350kV HVDC (Visayas-Luzon) blocked at 0807H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 8:11:34 AM | [NSO Update] Luzon Grid-08/13/2023 08:11: Ormoc CS-Naga CS 350kV HVDC (Visayas-Luzon) blocked at 0807H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 8:10:22 AM | [NSO Update] Visayas Grid-08/13/2023 08:10: Ormoc CS-Naga CS 350kV HVDC (Visayas-Luzon) blocked at 0807H (Planned Outage) [WEBSMS] | CVIS
8/13/2023 8:09:38 AM | [NSO Update] Visayas Grid-08/13/2023 08:10: Ormoc CS-Naga CS 350kV HVDC (Visayas-Luzon) blocked at 0807H (Planned Outage) [WEBSMS] | CVIS
8/13/2023 7:21:32 AM | Mindanao Grid-08/13/2023 07:23: Davao - Toril 138KV Line 2 deenergized at 0702H. (Planned outage) [WEBSMS] | CMIN
8/13/2023 7:21:10 AM | Mindanao Grid-08/13/2023 07:23: Davao - Toril 138KV Line 2 deenergized at 0702H. (Planned outage) [WEBSMS] | CMIN
8/13/2023 6:56:45 AM | Mindanao Grid-08/13/2023 06:59: Gensan SS 100MVA Mobile Transformer 3 deenergized at 0648H. (Planned Outage) [WEBSMS] | CMIN
8/13/2023 6:56:30 AM | Mindanao Grid-08/13/2023 06:59: Gensan SS 100MVA Mobile Transformer 3 deenergized at 0648H. (Planned Outage) [WEBSMS] | CMIN
8/13/2023 6:54:49 AM | Mindanao Grid-08/13/2023 06:56: Gensan-Matanao 138KV Line 2 deenergized at 0646H. (Planned Outage) [WEBSMS] | CMIN
8/13/2023 6:54:09 AM | Mindanao Grid-08/13/2023 06:56: Gensan-Matanao 138KV Line 2 deenergized at 0646H. (Planned Outage) [WEBSMS] | CMIN
8/13/2023 6:42:52 AM | Visayas Grid-08/13/2023 06:41: Magdugo-DaanLungsod 138 KV Line energized at 0638H. Planned outage [WEBSMS] | CVIS
8/13/2023 6:41:41 AM | Visayas Grid-08/13/2023 06:41: Magdugo-DaanLungsod 138 KV Line energized at 0638H. Planned outage [WEBSMS] | CVIS
8/13/2023 6:13:07 AM | Luzon Grid-08/13/2023 06:12: Calaca-Malamig(Sta. Rosa) 230kV Line de-energized at 0612H. (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 6:12:52 AM | Luzon Grid-08/13/2023 06:12: Calaca-Malamig(Sta. Rosa) 230kV Line de-energized at 0612H. (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 5:44:48 AM | [NSO Update] Mindanao Grid-08/13/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3385MW, PK=1582MW, RR=20MW, NetOpMargin: AM=1784, PM=1487, EVE=1185 Highest Unit O/L: GNPK 1&4@ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/13/2023 5:43:54 AM | [NSO Update] Mindanao Grid-08/13/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3385MW, PK=1582MW, RR=20MW, NetOpMargin: AM=1784, PM=1487, EVE=1185 Highest Unit O/L: GNPK 1&4@ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @104MW, AG4 @120MW, AG5 @40MW, AG6 @141MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/13/2023 5:41:39 AM | [NSO Update] Luzon Grid-08/13/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12830MW, PK=9323MW, RR=80MW, NetOpMargin: AM=3427, PM=2905, EVE=2259 Highest Unit O/L: GNPD 1 & 2@668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 315MW, Masinloc 2 @ 110MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/13/2023 5:41:24 AM | [NSO Update] Luzon Grid-08/13/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12830MW, PK=9323MW, RR=80MW, NetOpMargin: AM=3427, PM=2905, EVE=2259 Highest Unit O/L: GNPD 1 & 2@668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 315MW, Masinloc 2 @ 110MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/13/2023 5:40:12 AM | [NSO Update] Visayas Grid-08/13/2023 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2463MW, PK=1776MW, RR=40MW, NetOpMargin: AM=646, PM=620, EVE=317 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Carmen @ 30MW, Leyte A @ 320MW, PGPP1 @ 74MW [WEBSMS] | CVIS
8/13/2023 5:38:51 AM | [NSO Update] Visayas Grid-08/13/2023 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2463MW, PK=1776MW, RR=40MW, NetOpMargin: AM=646, PM=620, EVE=317 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Carmen @ 30MW, Leyte A @ 320MW, PGPP1 @ 74MW [WEBSMS] | CVIS
8/13/2023 5:06:44 AM | Luzon Grid-08/13/2023 05:06: Dasmarinas 500kV Bus 1 de-energized at 0506H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 5:06:25 AM | Luzon Grid-08/13/2023 05:06: Dasmarinas 500kV Bus 1 de-energized at 0506H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 5:06:24 AM | Luzon Grid-08/13/2023 05:03: Dasmarinas 600MVA T04 de-energized at 0503H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 5:03:36 AM | Luzon Grid-08/13/2023 05:03: Dasmarinas 600MVA T04 de-energized at 0503H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 4:56:26 AM | Mindanao Grid-08/13/2023 04:58: Placer SS 100MVA Power Transformer # 3 de-energized at 0431H to conduct replacement of OLTC tank transformer oil. Planned Outage [WEBSMS] | CMIN
8/13/2023 4:56:19 AM | Mindanao Grid-08/13/2023 04:58: Placer SS 100MVA Power Transformer # 3 de-energized at 0431H to conduct replacement of OLTC tank transformer oil. Planned Outage [WEBSMS] | CMIN
8/13/2023 4:23:45 AM | Visayas Grid-08/13/2023 04:22: Calong-calong ? Daanlungsod 138 kV Line 2 energized at 0421H. (Planned Outage) [WEBSMS] | CVIS
8/13/2023 4:22:19 AM | Visayas Grid-08/13/2023 04:22: Calong-calong � Daanlungsod 138 kV Line 2 energized at 0421H. (Planned Outage) [WEBSMS] | CVIS
8/13/2023 4:11:20 AM | [NSO Update] Mindanao Grid-08/13/2023 04:11: Weather Update: Southwest Monsoon affecting the country. [WEBSMS] | CMIN
8/13/2023 4:11:18 AM | [NSO Update] Luzon Grid-08/13/2023 04:08: Weather Update: Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
8/13/2023 4:09:11 AM | [NSO Update] Mindanao Grid-08/13/2023 04:11: Weather Update: Southwest Monsoon affecting the country. [WEBSMS] | CMIN
8/13/2023 4:09:06 AM | [NSO Update] Visayas Grid-08/13/2023 04:08: Weather Update: Southwest Monsoon affecting the country. [WEBSMS] | CVIS
8/13/2023 4:08:45 AM | [NSO Update] Visayas Grid-08/13/2023 04:08: Weather Update: Southwest Monsoon affecting the country. [WEBSMS] | CVIS
8/13/2023 4:08:21 AM | [NSO Update] Luzon Grid-08/13/2023 04:08: Weather Update: Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
8/13/2023 2:26:20 AM | Luzon Grid-08/13/2023 02:26: Malolos 230kV Bus 1 de-energized at 0211H (Planned Outage, Customer owned) [WEBSMS] | CLUZ
8/13/2023 2:22:58 AM | Luzon Grid-08/13/2023 02:16: San Jose - Malolos 230kV Line de-energized at 0213H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 2:16:28 AM | Luzon Grid-08/13/2023 02:16: San Jose - Malolos 230kV Line de-energized at 0213H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 2:12:58 AM | Luzon Grid-08/13/2023 02:12: Malolos 150MVA T02 de-energized at 0210H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 2:12:39 AM | Luzon Grid-08/13/2023 02:12: Malolos 150MVA T02 de-energized at 0210H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 2:01:42 AM | Luzon Grid-08/13/2023 02:01: Malolos 150MVA T01 energized at 0158H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 1:17:48 AM | Luzon Grid-08/13/2023 01:15: Malolos 150MVA T01 de-energized at 0112H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 1:15:18 AM | Luzon Grid-08/13/2023 01:15: Malolos 150MVA T01 de-energized at 0112H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 1:12:59 AM | Luzon Grid-08/13/2023 01:13: Malolos 150MVA T05 energized at 0105H (Planned Outage) [WEBSMS] | CLUZ
8/13/2023 12:35:06 AM | Luzon Grid-08/13/2023 00:35: Ilijan B ST2 online at 0034H (Unplanned Outage) [WEBSMS] | CLUZ
8/13/2023 12:34:25 AM | Luzon Grid-08/13/2023 00:35: Ilijan B ST2 online at 0034H (Unplanned Outage) [WEBSMS] | CLUZ
8/13/2023 12:00:29 AM | Visayas Grid-08/12/2023 23:59: Calong-calong ? Daanlungsod 138 kV Line 2 de-energized at 2358H. (Planned Outage) [WEBSMS] | CVIS
8/12/2023 11:59:02 PM | Visayas Grid-08/12/2023 23:59: Calong-calong � Daanlungsod 138 kV Line 2 de-energized at 2358H. (Planned Outage) [WEBSMS] | CVIS
8/12/2023 11:31:05 PM | Luzon Grid-08/12/2023 23:30: Ilijan B GT2-2 online at 2329H (Unplanned Outage) [WEBSMS] | CLUZ
8/12/2023 11:30:28 PM | Luzon Grid-08/12/2023 23:30: Ilijan B GT2-2 online at 2329H (Unplanned Outage) [WEBSMS] | CLUZ
8/12/2023 11:29:32 PM | Luzon Grid-08/12/2023 23:22: Malolos 150MVA T05 de-energized at 2320H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 11:22:48 PM | Luzon Grid-08/12/2023 23:22: Malolos 150MVA T05 de-energized at 2320H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 8:25:36 PM | Luzon Grid-08/12/2023 20:24: Ilijan B GT2-2 (50MW) tripped at 2021H (Unplanned Outage) [WEBSMS] | CLUZ
8/12/2023 8:24:03 PM | Luzon Grid-08/12/2023 20:24: Ilijan B GT2-2 (50MW) tripped at 2021H (Unplanned Outage) [WEBSMS] | CLUZ
8/12/2023 8:18:32 PM | Luzon Grid-08/12/2023 20:18: Ilijan B ST2 (87MW) tripped at 2008H. Ilijan B total generation loss was 156MW (from 251MW to 95MW). Lowest Frequency is 59.37Hz (Unplanned Outage) [WEBSMS] | CLUZ
8/12/2023 7:14:52 PM | Visayas Grid-08/12/2023 19:14: DaanBantayan-Tabango 230 KV line 1 energized at 1911H. (Planned Outage) [WEBSMS] | CVIS
8/12/2023 7:13:58 PM | Visayas Grid-08/12/2023 19:14: DaanBantayan-Tabango 230 KV line 1 energized at 1911H. (Planned Outage) [WEBSMS] | CVIS
8/12/2023 7:01:11 PM | Luzon Grid-08/12/2023 19:01: Hermosa-Calaguiman 69kV Line restored at 1857H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 7:00:46 PM | Luzon Grid-08/12/2023 19:01: Hermosa-Calaguiman 69kV Line restored at 1857H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 5:54:03 PM | [NSO Update] Mindanao Grid-08/12/2023 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3325MW, PK=1981MW, RR=20MW, NetOpMargin: EVE=1324 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @50MW, AG1 @35MW, AG2 @103MW, AG4 @120MW, AG5 @40MW, AG6 @139MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/12/2023 5:53:36 PM | [NSO Update] Mindanao Grid-08/12/2023 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3325MW, PK=1981MW, RR=20MW, NetOpMargin: EVE=1324 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @50MW, AG1 @35MW, AG2 @103MW, AG4 @120MW, AG5 @40MW, AG6 @139MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/12/2023 5:52:22 PM | Luzon Grid-08/12/2023 17:52: Quezon(Balintawak)-Marilao(Duhat) 230kV Line restored at 1751H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 5:52:11 PM | Luzon Grid-08/12/2023 17:52: Quezon(Balintawak)-Marilao(Duhat) 230kV Line restored at 1751H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 5:48:31 PM | [NSO Update] Visayas Grid-08/12/2023 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2399MW, PK=2014MW, RR=40MW, NetOpMargin: EVE=345 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC Carmen @ 30MW, TGPP @ 104MW, Leyte A @ 330MW, PGPP1 @ 74MW [WEBSMS] | CVIS
8/12/2023 5:48:08 PM | [NSO Update] Visayas Grid-08/12/2023 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2399MW, PK=2014MW, RR=40MW, NetOpMargin: EVE=345 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC Carmen @ 30MW, TGPP @ 104MW, Leyte A @ 330MW, PGPP1 @ 74MW [WEBSMS] | CVIS
8/12/2023 5:42:10 PM | [NSO Update] Luzon Grid-08/12/2023 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12040MW, PK=10287MW, RR=40MW, NetOpMargin: EVE=1713 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 315MW, Masinloc 2 @ 105MW, SLPGC 2 @ 60MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/12/2023 5:38:55 PM | [NSO Update] Luzon Grid-08/12/2023 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12040MW, PK=10287MW, RR=40MW, NetOpMargin: EVE=1713 Highest Unit O/L: GNPD 1&2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 315MW, Masinloc 2 @ 105MW, SLPGC 2 @ 60MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/12/2023 4:27:25 PM | Visayas Grid-08/12/2023 16:26: Compostela-Medellin 69 KV line energized at 1622H. Planned outage [WEBSMS] | CVIS
8/12/2023 4:25:58 PM | Visayas Grid-08/12/2023 16:26: Compostela-Medellin 69 KV line energized at 1622H. Planned outage [WEBSMS] | CVIS
8/12/2023 3:37:09 PM | Mindanao Grid-08/12/2023 15:39: WMPC DG05 cut-out at 1533H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/12/2023 3:37:08 PM | Mindanao Grid-08/12/2023 15:37: Aurora-Nagamin 138kV Line 1 energized at 1458H. (Planned Outage/Non-GOMP). [WEBSMS] | CMIN
8/12/2023 3:36:43 PM | Mindanao Grid-08/12/2023 15:39: WMPC DG05 cut-out at 1533H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/12/2023 3:34:50 PM | Mindanao Grid-08/12/2023 15:37: Aurora-Nagamin 138kV Line 1 energized at 1458H. (Planned Outage/Non-GOMP). [WEBSMS] | CMIN
8/12/2023 3:32:07 PM | Mindanao Grid-08/12/2023 15:33: Aurora-Polanco 138kV Line 1 energized at 1436H. (Planned Outage/GOMP). [WEBSMS] | CMIN
8/12/2023 3:31:16 PM | Mindanao Grid-08/12/2023 15:33: Aurora-Polanco 138kV Line 1 energized at 1436H. (Planned Outage/GOMP). [WEBSMS] | CMIN
8/12/2023 3:04:24 PM | Visayas Grid-08/12/2023 15:04: Compostela-Medellin 69 KV line de-energized at 1503H. Planned outage [WEBSMS] | CVIS
8/12/2023 3:03:42 PM | Visayas Grid-08/12/2023 15:04: Compostela-Medellin 69 KV line de-energized at 1503H. Planned outage [WEBSMS] | CVIS
8/12/2023 2:38:44 PM | Luzon Grid-08/12/2023 14:37: Santiago-Magat HEPP 230kV Line 2 restored at 1436H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 2:37:10 PM | Luzon Grid-08/12/2023 14:37: Santiago-Magat HEPP 230kV Line 2 restored at 1436H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 1:43:49 PM | Mindanao Grid-08/12/2023 13:44: Aurora-Nagamin 138kV Line 1 de-energized at 1332H. (Planned Outage). [WEBSMS] | CMIN
8/12/2023 1:42:00 PM | Mindanao Grid-08/12/2023 13:44: Aurora-Nagamin 138kV Line 1 de-energized at 1332H. (Planned Outage). [WEBSMS] | CMIN
8/12/2023 1:00:29 PM | [NSO Update] Luzon Grid-08/12/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12825MW, PK=10426MW, RR=170MW, NetOpMargin: PM=2229, EVE=1657 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 315MW, Masinloc 2 @ 105MW, SLPGC 2 @ 110MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/12/2023 12:53:22 PM | [NSO Update] Luzon Grid-08/12/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12825MW, PK=10426MW, RR=170MW, NetOpMargin: PM=2229, EVE=1657 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 315MW, Masinloc 2 @ 105MW, SLPGC 2 @ 110MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/12/2023 12:52:08 PM | [NSO Update] Visayas Grid-08/12/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2529MW, PK=2047MW, RR=40MW, NetOpMargin: PM=443, EVE=222 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, TGPP @ 104MW, Leyte A @ 335MW, PGPP1 @ 74MW, PDPP3-H @ 8MW [WEBSMS] | CVIS
8/12/2023 12:51:14 PM | [NSO Update] Mindanao Grid-08/12/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3366MW, PK=2038MW, RR=20MW, NetOpMargin: PM=1308, EVE=1175 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @50MW, AG1 @35MW, AG2 @103MW, AG4 @120MW, AG5 @40MW, AG6 @139MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/12/2023 12:50:31 PM | [NSO Update] Mindanao Grid-08/12/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3366MW, PK=2038MW, RR=20MW, NetOpMargin: PM=1308, EVE=1175 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @50MW, AG1 @35MW, AG2 @103MW, AG4 @120MW, AG5 @40MW, AG6 @139MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/12/2023 12:50:20 PM | [NSO Update] Visayas Grid-08/12/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2529MW, PK=2047MW, RR=40MW, NetOpMargin: PM=443, EVE=222 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, TGPP @ 104MW, Leyte A @ 335MW, PGPP1 @ 74MW, PDPP3-H @ 8MW [WEBSMS] | CVIS
8/12/2023 11:30:05 AM | Mindanao Grid-08/12/2023 11:32: Aurora 138/69/13.8 kV T2 100MVA) energized at 1120H. (Planned Outage/Non-GOMP). [WEBSMS] | CMIN
8/12/2023 11:29:50 AM | Mindanao Grid-08/12/2023 11:32: Aurora 138/69/13.8 kV T2 100MVA) energized at 1120H. (Planned Outage/Non-GOMP). [WEBSMS] | CMIN
8/12/2023 10:20:17 AM | Luzon Grid-08/12/2023 10:13: Nagsaag SS 230kV Bus 2 restored at 1013H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 10:13:44 AM | Luzon Grid-08/12/2023 10:13: Nagsaag SS 230kV Bus 2 restored at 1013H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 10:03:06 AM | Mindanao Grid-08/12/2023 10:05: WMPC DG05 cut-in at 0949H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/12/2023 10:02:52 AM | Mindanao Grid-08/12/2023 10:05: WMPC DG05 cut-in at 0949H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/12/2023 8:51:24 AM | Mindanao Grid-08/12/2023 08:51: Aurora 138/69/13.8 kV T2(100MVA) de-energized at 0819H. (Planned Outage/Non-GOMP). [WEBSMS] | CMIN
8/12/2023 8:49:28 AM | Mindanao Grid-08/12/2023 08:51: Aurora 138/69/13.8 kV T2(100MVA) de-energized at 0819H. (Planned Outage/Non-GOMP). [WEBSMS] | CMIN
8/12/2023 8:28:06 AM | Visayas Grid-08/12/2023 08:28: Sangi-Pinamungajan 34.5 KV line tripped at 0802H. Erroneous data. [WEBSMS] | CVIS
8/12/2023 8:28:01 AM | Luzon Grid-08/12/2023 08:23: Nagsaag SS 230kV Bus 2 de-energized at 0822H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 8:23:25 AM | Luzon Grid-08/12/2023 08:23: Nagsaag SS 230kV Bus 2 de-energized at 0822H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 8:18:01 AM | Luzon Grid-08/12/2023 08:12: Pagbilao SS 230kV Bus 2 de-energized at 0811H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 8:12:09 AM | Visayas Grid-08/12/2023 08:10: Compostela-Medellin 69 KV line energized at 0810H. (Planned outage) [WEBSMS] | CVIS
8/12/2023 8:12:07 AM | Luzon Grid-08/12/2023 08:12: Pagbilao SS 230kV Bus 2 de-energized at 0811H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 8:10:12 AM | Visayas Grid-08/12/2023 08:10: Compostela-Medellin 69 KV line energized at 0810H. (Planned outage) [WEBSMS] | CVIS
8/12/2023 8:09:07 AM | Visayas Grid-08/12/2023 08:07: Sangi-Pinamungajan 34.5 KV line tripped at 0802H L= 3.2 MW. [WEBSMS] | CVIS
8/12/2023 8:07:01 AM | Visayas Grid-08/12/2023 08:07: Sangi-Pinamungajan 34.5 KV line tripped at 0802H L= 3.2 MW. [WEBSMS] | CVIS
8/12/2023 7:44:35 AM | Luzon Grid-08/12/2023 07:41: Santiago-Magat HEPP 230kV Line 2 de-energized at 0740H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 7:41:12 AM | Luzon Grid-08/12/2023 07:41: Santiago-Magat HEPP 230kV Line 2 de-energized at 0740H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 7:21:47 AM | Mindanao Grid-08/12/2023 07:22: Davao-Toril 138kV Line 1 de-energized at 0706H. (Planned Outage). [WEBSMS] | CMIN
8/12/2023 7:20:33 AM | Mindanao Grid-08/12/2023 07:22: Davao-Toril 138kV Line 1 de-energized at 0706H. (Planned Outage). [WEBSMS] | CMIN
8/12/2023 6:51:15 AM | Luzon Grid-08/12/2023 06:49: Quezon(Balintawak)-Marilao(Duhat) 230kV Line de-energized at 0648H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 6:49:28 AM | Luzon Grid-08/12/2023 06:49: Quezon(Balintawak)-Marilao(Duhat) 230kV Line de-energized at 0648H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 6:43:53 AM | Luzon Grid-08/12/2023 06:43: Duhat 300MVA T01 & 230kV Bus 1 restored at 0637H and 0640H, respectively (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 6:43:25 AM | Luzon Grid-08/12/2023 06:43: Duhat 300MVA T01 & 230kV Bus 1 restored at 0637H and 0640H, respectively (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 6:38:27 AM | Mindanao Grid-08/12/2023 06:39: Aurora-Polanco 138kV Line 1 de-energized at 0615H. (Planned Outage). [WEBSMS] | CMIN
8/12/2023 6:37:32 AM | Mindanao Grid-08/12/2023 06:39: Aurora-Polanco 138kV Line 1 de-energized at 0615H. (Planned Outage). [WEBSMS] | CMIN
8/12/2023 6:30:28 AM | Visayas Grid-08/12/2023 06:30: DaanBantayan-Tabango 230 KV line 1 de-energized at 0628H. (PLanned Outage) [WEBSMS] | CVIS
8/12/2023 6:30:17 AM | Visayas Grid-08/12/2023 06:30: DaanBantayan-Tabango 230 KV line 1 de-energized at 0628H. (PLanned Outage) [WEBSMS] | CVIS
8/12/2023 6:18:28 AM | Luzon Grid-08/12/2023 06:14: Hermosa-Calaguiman 69kV Line de-energized at 0610H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 6:14:19 AM | Luzon Grid-08/12/2023 06:14: Hermosa-Calaguiman 69kV Line de-energized at 0610H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 6:11:12 AM | Visayas Grid-08/12/2023 06:11: Compostela-Medellin 69 KV line de-energized at 0608H. (Planned outage) [WEBSMS] | CVIS
8/12/2023 6:11:08 AM | Visayas Grid-08/12/2023 06:11: Compostela-Medellin 69 KV line de-energized at 0608H. (Planned outage) [WEBSMS] | CVIS
8/12/2023 5:46:40 AM | [NSO Update] Luzon Grid-08/12/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12981MW, PK=10626MW, RR=260MW, NetOpMargin: AM=2095, PM=1988, EVE=1529 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC2 @173MW, MSLC2 @105MW, SLPGC 2 @130MW, ILIJAN A @ 250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/12/2023 5:44:10 AM | [NSO Update] Luzon Grid-08/12/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12981MW, PK=10626MW, RR=260MW, NetOpMargin: AM=2095, PM=1988, EVE=1529 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC2 @173MW, MSLC2 @105MW, SLPGC 2 @130MW, ILIJAN A @ 250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/12/2023 5:34:29 AM | [NSO Update] Mindanao Grid-08/12/2023 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3387MW, PK=2081MW, RR=20MW, NetOpMargin: AM=1286, PM=1159, EVE=1067 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @50MW, AG1 @35MW, AG2 @103MW, AG4 @120MW, AG5 @40MW, AG6 @139MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/12/2023 5:33:55 AM | [NSO Update] Mindanao Grid-08/12/2023 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3387MW, PK=2081MW, RR=20MW, NetOpMargin: AM=1286, PM=1159, EVE=1067 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @50MW, AG1 @35MW, AG2 @103MW, AG4 @120MW, AG5 @40MW, AG6 @139MW, AG7 @32MW, PG4 @105MW [WEBSMS] | CMIN
8/12/2023 5:32:29 AM | [NSO Update] Visayas Grid-08/12/2023 05:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2584MW, PK=2020MW, RR=40MW, NetOpMargin: AM=523, PM=435, EVE=223 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @342MW, PGPP1 @74MW, TGPP @103MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/12/2023 5:30:35 AM | [NSO Update] Visayas Grid-08/12/2023 05:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2584MW, PK=2020MW, RR=40MW, NetOpMargin: AM=523, PM=435, EVE=223 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @342MW, PGPP1 @74MW, TGPP @103MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/12/2023 5:24:27 AM | Luzon Grid-08/12/2023 05:20: MPGC 1 online at 0518H (Commissioning Test) [WEBSMS] | CLUZ
8/12/2023 5:20:05 AM | Luzon Grid-08/12/2023 05:20: MPGC 1 online at 0518H (Commissioning Test) [WEBSMS] | CLUZ
8/12/2023 5:14:27 AM | Luzon Grid-08/12/2023 05:11: Calaca-Sta. Rita 230kV Line 2 de-energized at 0511H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 5:11:49 AM | Luzon Grid-08/12/2023 05:11: Calaca-Sta. Rita 230kV Line 2 de-energized at 0511H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 4:11:40 AM | [NSO Update] Mindanao Grid-08/12/2023 04:14: Weather Update: Southwest Monsoon affecting the country. [WEBSMS] | CMIN
8/12/2023 4:11:06 AM | [NSO Update] Mindanao Grid-08/12/2023 04:14: Weather Update: Southwest Monsoon affecting the country. [WEBSMS] | CMIN
8/12/2023 4:10:30 AM | [NSO Update] Luzon Grid-08/12/2023 04:10: Weather Update: Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
8/12/2023 4:09:55 AM | [NSO Update] Luzon Grid-08/12/2023 04:10: Weather Update: Southwest Monsoon affecting the country. [WEBSMS] | CLUZ
8/12/2023 4:09:55 AM | [NSO Update] Visayas Grid-08/12/2023 04:09: Weather Update: Southwest Monsoon affecting the country. [WEBSMS] | CVIS
8/12/2023 4:09:39 AM | [NSO Update] Visayas Grid-08/12/2023 04:09: Weather Update: Southwest Monsoon affecting the country. [WEBSMS] | CVIS
8/12/2023 4:07:48 AM | Mindanao Grid-08/12/2023 04:08: Baloi SS 138kV Busbar # 2 restored at 0332H. (From Unplanned Outage) [WEBSMS] | CMIN
8/12/2023 4:05:51 AM | Mindanao Grid-08/12/2023 04:08: Baloi SS 138kV Busbar # 2 restored at 0332H. (From Unplanned Outage) [WEBSMS] | CMIN
8/12/2023 3:57:57 AM | Mindanao Grid-08/12/2023 04:00: Baloi SS 138kV Busbar # 2 on emergency shutdown at 0104H due to repair/replacement of damaged phase B male finger contact of DS # 7-06DS07BLO. Unplanned Outage... [WEBSMS] | CMIN
8/12/2023 3:57:48 AM | Mindanao Grid-08/12/2023 04:00: Baloi SS 138kV Busbar # 2 on emergency shutdown at 0104H due to repair/replacement of damaged phase B male finger contact of DS # 7-06DS07BLO. Unplanned Outage... [WEBSMS] | CMIN
8/12/2023 3:42:48 AM | Visayas Grid-08/12/2023 03:42: Calong-calong ? Daanlungsod 138 kV Line 1 energized at 0341H. (Planned Outage) [WEBSMS] | CVIS
8/12/2023 3:42:00 AM | Visayas Grid-08/12/2023 03:42: Calong-calong � Daanlungsod 138 kV Line 1 energized at 0341H. (Planned Outage) [WEBSMS] | CVIS
8/12/2023 1:57:40 AM | Luzon Grid-08/12/2023 01:51: Duhat 300MVA T01 & 230kV Bus 1 de-energized at 0135H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 1:51:00 AM | Luzon Grid-08/12/2023 01:51: Duhat 300MVA T01 & 230kV Bus 1 de-energized at 0135H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 1:47:39 AM | Luzon Grid-08/12/2023 01:47: Lamao-SCPC 230kV Tie Line 1 de-energized at 0147H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 1:47:30 AM | Luzon Grid-08/12/2023 01:47: Lamao-SCPC 230kV Tie Line 1 de-energized at 0147H (Planned Outage) [WEBSMS] | CLUZ
8/12/2023 1:37:39 AM | Luzon Grid-08/12/2023 01:36: For Info: Commissioning of Bantay 50MVA Transformer No 1 New Main Protection completed at 0135H. [WEBSMS] | CLUZ
8/12/2023 1:36:24 AM | Luzon Grid-08/12/2023 01:36: For Info: Commissioning of Bantay 50MVA Transformer No 1 New Main Protection completed at 0135H. [WEBSMS] | CLUZ
8/12/2023 12:54:18 AM | Luzon Grid-08/12/2023 00:53: For info: Batangas 300MVA T04 and T05 on split configuration at 0048H. San Lorenzo-Sta Rita 230kV Bus 1 and 2 tie breakers were closed at 0052H looping Sta Rita and San Lorenzo. [WEBSMS] | CLUZ
8/12/2023 12:53:13 AM | Luzon Grid-08/12/2023 00:53: For info: Batangas 300MVA T04 and T05 on split configuration at 0048H. San Lorenzo-Sta Rita 230kV Bus 1 and 2 tie breakers were closed at 0052H looping Sta Rita and San Lorenzo. [WEBSMS] | CLUZ
8/12/2023 12:18:37 AM | Visayas Grid-08/12/2023 00:18: Calong-calong � Daanlungsod 138 kV Line 1 de-energized at 0017H. (Planned Outage) [WEBSMS] | CVIS
8/12/2023 12:18:06 AM | Visayas Grid-08/12/2023 00:18: Calong-calong ? Daanlungsod 138 kV Line 1 de-energized at 0017H. (Planned Outage) [WEBSMS] | CVIS
8/11/2023 11:39:58 PM | Luzon Grid-08/11/2023 23:40: San Gabriel shutdown at 2337H (Planned Outage) [WEBSMS] | CLUZ
8/11/2023 11:39:40 PM | Luzon Grid-08/11/2023 23:40: San Gabriel shutdown at 2337H (Planned Outage) [WEBSMS] | CLUZ
8/11/2023 9:45:19 PM | Mindanao Grid-08/11/2023 21:47: WMPC DG05 cut-out at 2114H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/11/2023 9:44:34 PM | Mindanao Grid-08/11/2023 21:47: WMPC DG05 cut-out at 2114H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/11/2023 6:19:03 PM | [NSO Update] Mindanao Grid-08/11/2023 18:19: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3311MW, PK=2195MW, RR=20MW, NetOpMargin: EVE=1096 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @124MW, AG5 @40MW, AG6 @139MW, AG7 @33MW, PG4 @105MW [WEBSMS] | CMIN
8/11/2023 6:17:01 PM | [NSO Update] Mindanao Grid-08/11/2023 18:19: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3311MW, PK=2195MW, RR=20MW, NetOpMargin: EVE=1096 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @124MW, AG5 @40MW, AG6 @139MW, AG7 @33MW, PG4 @105MW [WEBSMS] | CMIN
8/11/2023 6:08:22 PM | [NSO Update] Visayas Grid-08/11/2023 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2488MW, PK=2143MW, RR=40MW, NetOpMargin: EVE=305 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @342MW, PGPP1 @74MW, TGPP @103MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/11/2023 6:05:49 PM | [NSO Update] Visayas Grid-08/11/2023 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2488MW, PK=2143MW, RR=40MW, NetOpMargin: EVE=305 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: LEYTE A @342MW, PGPP1 @74MW, TGPP @103MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/11/2023 5:50:40 PM | [NSO Update] Luzon Grid-08/11/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12207MW, PK=10804MW, RR=260MW, NetOpMargin: EVE=1143 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC2 @173MW, MSLC1 @300MW, MSLC2 @105MW, SCPC 2 @65MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/11/2023 5:49:10 PM | [NSO Update] Luzon Grid-08/11/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12207MW, PK=10804MW, RR=260MW, NetOpMargin: EVE=1143 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC2 @173MW, MSLC1 @300MW, MSLC2 @105MW, SCPC 2 @65MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/11/2023 5:41:45 PM | Mindanao Grid-08/11/2023 17:44: WMPC DG05 cut-in at 1646H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/11/2023 4:49:18 PM | Mindanao Grid-08/11/2023 16:51: WMPC DG09 tripped with 8.5MW load at 0926H. From RPS. Unplanned Outage. [WEBSMS] | CMIN
8/11/2023 4:49:07 PM | Mindanao Grid-08/11/2023 16:51: WMPC DG09 tripped with 8.5MW load at 0926H. From RPS. Unplanned Outage. [WEBSMS] | CMIN
8/11/2023 4:19:30 PM | Mindanao Grid-08/11/2023 16:21: WMPC DG01 cut-out at 1614H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/11/2023 4:18:58 PM | Mindanao Grid-08/11/2023 16:21: WMPC DG01 cut-out at 1614H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/11/2023 2:25:48 PM | Luzon Grid-08/11/2023 14:25: Time correction: SCPC 2 online at 1350H (Unplanned Outage) [WEBSMS] | CLUZ
8/11/2023 2:25:39 PM | Luzon Grid-08/11/2023 14:25: Time correction: SCPC 2 online at 1350H (Unplanned Outage) [WEBSMS] | CLUZ
8/11/2023 1:55:47 PM | Luzon Grid-08/11/2023 13:55: SCPC 2 online at 0150H (Unplanned Outage) [WEBSMS] | CLUZ
8/11/2023 1:55:14 PM | Luzon Grid-08/11/2023 13:55: SCPC 2 online at 0150H (Unplanned Outage) [WEBSMS] | CLUZ
8/11/2023 1:40:30 PM | Luzon Grid-08/11/2023 13:34: Masinloc 2 online at 1332H (Unplanned Outage) [WEBSMS] | CLUZ
8/11/2023 1:34:54 PM | Luzon Grid-08/11/2023 13:34: Masinloc 2 online at 1332H (Unplanned Outage) [WEBSMS] | CLUZ
8/11/2023 1:12:52 PM | Mindanao Grid-08/11/2023 13:15: NSD Online at 1310H. Follow RTD(Planned Outage). [WEBSMS] | CMIN
8/11/2023 1:12:26 PM | Mindanao Grid-08/11/2023 13:15: NSD Online at 1310H. Follow RTD(Planned Outage). [WEBSMS] | CMIN
8/11/2023 12:47:32 PM | [NSO Update] Luzon Grid-08/11/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12995MW, PK=11803MW, RR=260MW, NetOpMargin: PM=932, EVE=1063 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 300MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/11/2023 12:47:22 PM | Mindanao Grid-08/11/2023 12:49: Kauswagan-GNPK 230kV Line 2 deenergized at 1202H. Emergency shutdown requested by GNPK. [WEBSMS] | CMIN
8/11/2023 12:47:10 PM | Mindanao Grid-08/11/2023 12:49: Kauswagan-GNPK 230kV Line 2 deenergized at 1202H. Emergency shutdown requested by GNPK. [WEBSMS] | CMIN
8/11/2023 12:47:08 PM | [NSO Update] Luzon Grid-08/11/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12995MW, PK=11803MW, RR=260MW, NetOpMargin: PM=932, EVE=1063 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 173MW, Masinloc 1 @ 300MW, Ilijan A @ 250MW, Ilijan B @ 250MW [WEBSMS] | CLUZ
8/11/2023 12:44:50 PM | [NSO Update] Visayas Grid-08/11/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2647MW, PK=2326MW, RR=40MW, NetOpMargin: PM=282, EVE=314 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 103MW, Leyte A @ 342MW, PGPP1 @ 74MW [WEBSMS] | CVIS
8/11/2023 12:44:43 PM | [NSO Update] Mindanao Grid-08/11/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3350MW, PK=2333MW, RR=20MW, NetOpMargin: PM=997, EVE=1094 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @124MW, AG5 @40MW, AG6 @139MW, AG7 @33MW, PG4 @105MW [WEBSMS] | CMIN
8/11/2023 12:44:08 PM | [NSO Update] Visayas Grid-08/11/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2647MW, PK=2326MW, RR=40MW, NetOpMargin: PM=282, EVE=314 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 103MW, Leyte A @ 342MW, PGPP1 @ 74MW [WEBSMS] | CVIS
8/11/2023 12:44:05 PM | [NSO Update] Mindanao Grid-08/11/2023 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3350MW, PK=2333MW, RR=20MW, NetOpMargin: PM=997, EVE=1094 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @124MW, AG5 @40MW, AG6 @139MW, AG7 @33MW, PG4 @105MW [WEBSMS] | CMIN
8/11/2023 12:37:08 PM | Luzon Grid-08/11/2023 12:30: Sta Rita 30 change over from oil to gas at 1228H. [WEBSMS] | CLUZ
8/11/2023 12:30:49 PM | Luzon Grid-08/11/2023 12:30: Sta Rita 30 change over from oil to gas at 1228H. [WEBSMS] | CLUZ
8/11/2023 11:30:26 AM | Luzon Grid-08/11/2023 11:25: Masinloc 2 tripped with 72.78MW load at 1121H. The lowest frequency recorded is 59.68hz. (Unplanned Outage) [WEBSMS] | CLUZ
8/11/2023 11:25:48 AM | Luzon Grid-08/11/2023 11:25: Masinloc 2 tripped with 72.78MW load at 1121H. The lowest frequency recorded is 59.68hz. (Unplanned Outage) [WEBSMS] | CLUZ
8/11/2023 10:58:57 AM | Luzon Grid-08/11/2023 10:58: Masinloc 2 online at 1056H (Unplanned Outage) [WEBSMS] | CLUZ
8/11/2023 10:58:08 AM | Luzon Grid-08/11/2023 10:58: Masinloc 2 online at 1056H (Unplanned Outage) [WEBSMS] | CLUZ
8/11/2023 10:53:59 AM | Mindanao Grid-08/11/2023 10:56: WMPC DG1 online at 1050H. (Planned Outage). [WEBSMS] | CMIN
8/11/2023 10:53:55 AM | Mindanao Grid-08/11/2023 10:56: WMPC DG1 online at 1050H. (Planned Outage). [WEBSMS] | CMIN
8/11/2023 10:31:01 AM | Visayas Grid-08/11/2023 10:30: VSO power supply source from VECO in @1029H. [WEBSMS] | CVIS
8/11/2023 10:30:21 AM | Visayas Grid-08/11/2023 10:30: VSO power supply source from VECO in @1029H. [WEBSMS] | CVIS
8/11/2023 10:19:01 AM | Luzon Grid-08/11/2023 10:19: Olongapo=SBMA 69kV Line restored and M2 protection commissioned at 1012H (Planned Outage) [WEBSMS] | CLUZ
8/11/2023 10:18:56 AM | Luzon Grid-08/11/2023 10:19: Olongapo=SBMA 69kV Line restored and M2 protection commissioned at 1012H (Planned Outage) [WEBSMS] | CLUZ
8/11/2023 9:35:34 AM | Visayas Grid-08/11/2023 09:35: VSO power supply source from VECO out @0930H, affected by customer emergency Hot Spot correction for 2 hours. [WEBSMS] | CVIS
8/11/2023 9:35:30 AM | Visayas Grid-08/11/2023 09:35: VSO power supply source from VECO out @0930H, affected by customer emergency Hot Spot correction for 2 hours. [WEBSMS] | CVIS
8/11/2023 8:57:12 AM | Mindanao Grid-08/11/2023 08:59: WMPC DG9 online at 0853H. (Planned Outage). [WEBSMS] | CMIN
8/11/2023 8:56:54 AM | Mindanao Grid-08/11/2023 08:59: WMPC DG9 online at 0853H. (Planned Outage). [WEBSMS] | CMIN
8/11/2023 8:05:29 AM | Luzon Grid-08/11/2023 07:59: Masinloc 2 tripped with 124MW load at 0752H. The lowest frequency recorded is 59.293hz. (Unplanned Outage) [WEBSMS] | CLUZ
8/11/2023 5:58:42 AM | [NSO Update] Mindanao Grid-08/11/2023 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3365MW, PK=2246MW, RR=20MW, NetOpMargin: AM=1099, PM=946, EVE=1002 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @124MW, AG5 @40MW, AG6 @139MW, AG7 @33MW, PG4 @105MW [WEBSMS] | CMIN
8/11/2023 5:55:21 AM | [NSO Update] Luzon Grid-08/11/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12805MW, PK=11789MW, RR=260MW, NetOpMargin: AM=756, PM=997, EVE=1412 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @173MW, MSLC1 @300MW, MSLC2 @150MW, ILIJAN A @250MW, ILIJAN B @250MW [WEBSMS] | CLUZ
8/11/2023 5:53:00 AM | [NSO Update] Visayas Grid-08/11/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2600MW, PK=2312MW, RR=40MW, NetOpMargin: AM=248, PM=209, EVE=178 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @103MW, LEYTE A @342MW, PGPP1 @74MW [WEBSMS] | CVIS
8/11/2023 5:33:25 AM | Luzon Grid-08/11/2023 05:33: San Lorenzo 60 online at 0531H. (Unplanned Outage) [WEBSMS] | CLUZ
8/11/2023 4:35:05 AM | [NSO Update] Mindanao Grid-08/11/2023 04:35: Weather Update: At 3:00 AM, the Low Pressure Area (LPA) was estimated based on all available data at 310 km East of Borongan City, Eastern Samar (11.5N, 128.3E). Southwest Monsoon affecting the country. [WEBSMS] | CMIN
8/11/2023 4:16:44 AM | Luzon Grid-08/11/2023 04:10: Taytay (Dolores) SS 300MVA T05 restored at 0409H (Planned Outage) [WEBSMS] | CLUZ
8/11/2023 4:06:43 AM | Luzon Grid-08/11/2023 04:05: Taytay (Dolores) SS 230kV Bus 2 restored at 0404H (Planned Outage) [WEBSMS] | CLUZ
8/11/2023 3:46:43 AM | Luzon Grid-08/11/2023 03:47: San Lorenzo 60 tripped at 0339H at 156MW (Unplanned Outage) lowest frequency - 59.374 Hz. [WEBSMS] | CLUZ
8/11/2023 3:13:22 AM | Luzon Grid-08/11/2023 03:09: Concepcion-Concepcion 1 Solar PP 69kV Line restored at 0308H (Planned Outage) [WEBSMS] | CLUZ
8/11/2023 12:39:58 AM | Luzon Grid-08/11/2023 00:34: San Lorenzo 60 online at 0030H (Unplanned Outage) [WEBSMS] | CLUZ
8/10/2023 11:36:36 PM | Luzon Grid-08/10/2023 23:32: Taytay (Dolores) SS 230kV Bus 2 de-energized at 2331H. (Planned Outage) [WEBSMS] | CLUZ
8/10/2023 10:58:26 PM | Mindanao Grid-08/10/2023 22:58: Correction on WMPC DG01 cut-out as RPS at 1614H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/10/2023 10:38:16 PM | Mindanao Grid-08/10/2023 22:41: WMPC DG09 cut-out as RPS at 2113H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/10/2023 9:28:18 PM | Luzon Grid-08/10/2023 21:28: San Lorenzo 60 tripped at 2122H (Unplanned Outage). [WEBSMS] | CLUZ
8/10/2023 7:28:13 PM | Luzon Grid-08/10/2023 19:29: Concepcion-Concepcion 1 Solar PP 69kV Line de-energized at 1928H. (Planned Outage) [WEBSMS] | CLUZ
8/10/2023 6:04:49 PM | [NSO Update] Mindanao Grid-08/10/2023 18:05: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3299MW, PK=2236MW, RR=20MW, NetOpMargin: EVE=1043 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @120MW, AG5 @40MW, AG6 @139MW, AG7 @27MW, PG4 @105MW [WEBSMS] | CMIN
8/10/2023 6:02:34 PM | [NSO Update] Visayas Grid-08/10/2023 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2520MW, PK=2160MW, RR=40MW, NetOpMargin: EVE=320 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TGPP @104MW, LEYTE A @350MW, PGPP1 @107MW [WEBSMS] | CVIS
8/10/2023 5:59:49 PM | Mindanao Grid-08/10/2023 18:01: Bunawan-Toril 230KV L1 re-energized at 1729H and looped at Toril SS at 1730H. From Planned Outage / Non-GOMP. [WEBSMS] | CMIN
8/10/2023 5:59:48 PM | [NSO Update] Luzon Grid-08/10/2023 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12048MW, PK=10951MW, RR=260MW, NetOpMargin: EVE=838 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @160MW, MSLC1 @285MW, MSLC2 @285MW, SLPGC 2 @60MW, ILIJAN A @223MW, ILIJAN B @218MW [WEBSMS] | CLUZ
8/10/2023 5:26:28 PM | Mindanao Grid-08/10/2023 17:28: Tudaya 2 HEP Unit No. 2 cut-in at 1715H as energy. Follow RTD. [WEBSMS] | CMIN
8/10/2023 4:54:45 PM | Luzon Grid-08/10/2023 16:50: San Lorenzo Module 60 online at 1647H (Unplanned Outage) [WEBSMS] | CLUZ
8/10/2023 3:39:45 PM | Luzon Grid-08/10/2023 15:35: Naga-Labo 230kV Line 2 restored at 1533H (Planned Outage) [WEBSMS] | CLUZ
8/10/2023 3:31:48 PM | Visayas Grid-08/10/2023 15:32: 2nd Lift - Sangi 34.5 kV Line energized at 1530H. (Planned Outage) [WEBSMS] | CVIS
8/10/2023 3:28:03 PM | Mindanao Grid-08/10/2023 15:30: Mt. Apo Unit 3 cut-in at 1513H as energy. Dispatched by MO. Follow RTD. [WEBSMS] | CMIN
8/10/2023 3:28:01 PM | Luzon Grid-08/10/2023 15:26: Ilijan A GT1-1 tripped at 1520H. (Unplanned Outage) [WEBSMS] | CLUZ
8/10/2023 3:23:03 PM | Mindanao Grid-08/10/2023 15:23: Updated: NACSUR (NSD) cut-in at 1305H as energy. Dispatched by MO & Follow RTD. [WEBSMS] | CMIN
8/10/2023 2:56:24 PM | Mindanao Grid-08/10/2023 14:56: KEGI Tandag cut in at 1406H. Follow RTD. [WEBSMS] | CMIN
8/10/2023 2:56:22 PM | Luzon Grid-08/10/2023 14:50: San Lorenzo Module 60 tripped at 1445H. (Unplanned outage) [WEBSMS] | CLUZ
8/10/2023 2:36:24 PM | Mindanao Grid-08/10/2023 14:38: KEGI Tandag cut in. Follow RTD. [WEBSMS] | CMIN
8/10/2023 1:29:40 PM | Luzon Grid-08/10/2023 13:28: For info: Commissioning and Energization of Balingueo New 100MVA Transformer 2 completed at 1326H. [WEBSMS] | CLUZ
8/10/2023 1:14:41 PM | [NSO Update] Mindanao Grid-08/10/2023 13:17: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3366MW, PK=2291MW, RR=20MW, NetOpMargin: PM=1055, EVE=1198 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @120MW, AG5 @40MW, AG6 @139MW, AG7 @42MW, PG4 @105MW [WEBSMS] | CMIN
8/10/2023 1:11:04 PM | [NSO Update] Visayas Grid-08/10/2023 13:11: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2658MW, PK=2348MW, RR=40MW, NetOpMargin: PM=270, EVE=325 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @350MW, TPC-CARMEN @30MW [WEBSMS] | CVIS
8/10/2023 1:06:21 PM | Mindanao Grid-08/10/2023 13:09: NSD online at 1305H. Follow RTD (Planned Outage). [WEBSMS] | CMIN
8/10/2023 12:56:19 PM | [NSO Update] Luzon Grid-08/10/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12981MW, PK=11946MW, RR=260MW, NetOpMargin: PM=776, EVE=1240 Highest Unit O/L: GNPD 1& 2@668MW Derated Plant: CLC2 @170MW, MSLC1 @285MW, MSLC2 @285MW, ILIJAN A @390MW @165, ILIJAN B @165MW, SAN SAN LO 60 @80MW [WEBSMS] | CLUZ
8/10/2023 12:22:58 PM | Luzon Grid-08/10/2023 12:19: For info: Sta Rita Module 20 completed the fuel changeover from oil to nat gas at 1200H [WEBSMS] | CLUZ
8/10/2023 11:11:12 AM | Luzon Grid-08/10/2023 11:11: For info: Sta Rita Module 20 completed the fuel changeover from nat gas to oil at 1043H [WEBSMS] | CLUZ
8/10/2023 10:51:18 AM | Mindanao Grid-08/10/2023 10:51: Bunawan-Toril 230KV L1 de-energized at 0910H. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
8/10/2023 8:52:45 AM | Mindanao Grid-08/10/2023 08:55: WMPC DG9 cut-in at 0850H. Planned Outage. [WEBSMS] | CMIN
8/10/2023 8:46:12 AM | Luzon Grid-08/10/2023 08:43: For info: Sta Rita Module 30 completed the fuel changeover from nat gas to oil at 0840H [WEBSMS] | CLUZ
8/10/2023 8:31:13 AM | Mindanao Grid-08/10/2023 08:32: Kidapawan SS 50MVA Power Transformer # 1 de-energized at 0728H. Planned Outage / Non-GOMP... [WEBSMS] | CMIN
8/10/2023 5:42:47 AM | [NSO Update] Luzon Grid-08/10/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13472MW, PK=11692MW, RR=260MW, NetOpMargin: AM=1519, PM=1067, EVE=1640 Highest Unit O/L: GNPD 1& 2@668MW Derated Plant: CALACA 2 @170MW, MASINLOC 1 @285MW, MASINLOC 2 @285MW, ILIJAN A @340MW ILIJAN B @165MW [WEBSMS] | CLUZ
8/10/2023 5:32:49 AM | [NSO Update] Mindanao Grid-08/10/2023 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3377MW, PK=2265MW, RR=20MW, NetOpMargin: AM=1092, PM=1037, EVE=1097 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @120MW, AG5 @40MW, AG6 @139MW, AG7 @42MW, PG4 @105MW [WEBSMS] | CMIN
8/10/2023 3:22:43 AM | Luzon Grid-08/10/2023 03:22: Concepcion-Concepcion Solar 69kV Line restored at 0322H (Planned Outage) [WEBSMS] | CLUZ
8/9/2023 7:35:50 PM | Luzon Grid-08/09/2023 19:36: Concepcion-Concepcion Solar 69kV Line de-energized at 1933H (Planned Outage) [WEBSMS] | CLUZ
8/9/2023 5:59:08 PM | [NSO Update] Luzon Grid-08/09/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12722MW, PK=10979MW, RR=260MW, NetOpMargin: EVE=1483 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @170MW, MASINLOC 1 @285MW, MASINLOC 2 @285MW, ILIJAN A @340MW, ILIJAN B @165MW [WEBSMS] | CLUZ
8/9/2023 5:42:10 PM | [NSO Update] Visayas Grid-08/09/2023 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2588MW, PK=2213MW, RR=40MW, NetOpMargin: EVE=335 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TGPP @100MW, LEYTE A @350MW, PGPP1 @75MW [WEBSMS] | CVIS
8/9/2023 5:39:09 PM | [NSO Update] Mindanao Grid-08/09/2023 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3315MW, PK=2275MW, RR=20MW, NetOpMargin: EVE=1019 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @134MW, AG5 @44MW, AG6 @141MW, AG7 @35MW, PG4 @105MW [WEBSMS] | CMIN
8/9/2023 5:17:09 PM | Luzon Grid-08/09/2023 17:16: Dasmarinas PCB 9-03CB24DAS restored at 1715H (Unplanned Outage) [WEBSMS] | CLUZ
8/9/2023 4:32:26 PM | Luzon Grid-08/09/2023 16:30: SCPC 2 emergency shutdown at 1626H due to oil leak at PT on the high side transformer breaker (Unplanned Outage) [WEBSMS] | CLUZ
8/9/2023 4:22:28 PM | Mindanao Grid-08/09/2023 16:23: WMPC DG7 cut-out as RPS at 1614H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/9/2023 3:59:17 PM | Visayas Grid-08/09/2023 15:59: Carcon - Sangi 34.5 kV Line 3 energized at 1558H. (Planned Outage) [WEBSMS] | CVIS
8/9/2023 3:40:25 PM | Luzon Grid-08/09/2023 15:40: Hermosa-Duhat 230kV Line restored at 1539H (Unplanned Outage) [WEBSMS] | CLUZ
8/9/2023 1:05:43 PM | [NSO Update] Mindanao Grid-08/09/2023 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3363MW, PK=2445MW, RR=20MW, NetOpMargin: PM=898, EVE=1024 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: DCP @262.45MW, MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @134MW, AG5 @44MW, AG6 @141MW, AG7 @35MW, PG4 @105MW [WEBSMS] | CMIN
8/9/2023 1:02:03 PM | [NSO Update] Visayas Grid-08/09/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2641MW, PK=2376MW, RR=40MW, NetOpMargin: PM=225, EVE=214 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, TGPP @100MW, LEYTE A @350MW, PGPP1 @75MW [WEBSMS] | CVIS
8/9/2023 12:56:58 PM | [NSO Update] Luzon Grid-08/09/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13718MW, PK=11812MW, RR=260MW, NetOpMargin: PM=1646, EVE=2048 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC1 @285MW, MSLC2 @285MW, ILIJAN A @340MW ILIJAN B @165MW, SCPC3 @60MW [WEBSMS] | CLUZ
8/9/2023 10:55:40 AM | Mindanao Grid-08/09/2023 10:55: WMPC DG7 online at 1051H. Unplanned Outage. [WEBSMS] | CMIN
8/9/2023 10:02:17 AM | Luzon Grid-08/09/2023 10:02: San Manuel-San Manuel BESS 69kV Line de-energized at 1002H (Unplanned Outage) [WEBSMS] | CLUZ
8/9/2023 9:50:09 AM | Luzon Grid-08/09/2023 09:44: SCPC 3 online at 0943H (Unplanned Outage) [WEBSMS] | CLUZ
8/9/2023 9:06:49 AM | Luzon Grid-08/09/2023 09:01: Hermosa-Duhat 230kV Line tripped again at 0859H (Unplanned Outage) [WEBSMS] | CLUZ
8/9/2023 8:58:55 AM | Mindanao Grid-08/09/2023 09:01: WMPC DG9 cut-in as RPS at 0855H. (Planned Outage) [WEBSMS] | CMIN
8/9/2023 8:56:49 AM | Luzon Grid-08/09/2023 08:57: Hermosa-Duhat 230kV Line restored at 0856H (Unplanned Outage) [WEBSMS] | CLUZ
8/9/2023 8:46:48 AM | Luzon Grid-08/09/2023 08:47: Hermosa-Duhat 230kV Line tripped at 0843H (Unplanned Outage) [WEBSMS] | CLUZ
8/9/2023 5:42:12 AM | [NSO Update] Mindanao Grid-08/09/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3381MW, PK=2441MW, RR=20MW, NetOpMargin: AM=920, PM=892, EVE=971 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MCO @270MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @134MW, AG5 @44MW, AG6 @141MW, AG7 @35MW, PG4 @105MW [WEBSMS] | CMIN
8/9/2023 5:40:15 AM | [NSO Update] Visayas Grid-08/09/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2518MW, PK=2129MW, RR=40MW, NetOpMargin: AM=349, PM=361, EVE=340 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, TGPP @100MW, LEYTE A @350MW, PGPP1 @75MW [WEBSMS] | CVIS
8/9/2023 4:46:36 AM | [NSO Update] Luzon Grid-08/09/2023 04:41: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CLUZ
8/9/2023 4:41:51 AM | [NSO Update] Visayas Grid-08/09/2023 04:42: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CVIS
8/9/2023 4:41:37 AM | [NSO Update] Mindanao Grid-08/09/2023 04:44: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CMIN
8/9/2023 12:53:45 AM | Mindanao Grid-08/09/2023 00:54: Nagamin SVC restored at 0043H. (Unplanned Outage) [WEBSMS] | CMIN
8/9/2023 12:48:43 AM | Luzon Grid-08/09/2023 00:40: Balingueno 100MVA T02 energized at high side at 0037H (Planned Outage) [WEBSMS] | CLUZ
8/8/2023 11:22:03 PM | Mindanao Grid-08/08/2023 23:22: Nagamin SVC tripped at 2216H. (Unplanned Outage) [WEBSMS] | CMIN
8/8/2023 10:52:01 PM | Mindanao Grid-08/08/2023 22:53: Asiga (ASG) HEP cut-in at 2246H. (Unplanned Outage) [WEBSMS] | CMIN
8/8/2023 10:38:43 PM | Mindanao Grid-08/08/2023 22:41: Lake Mainit (AGC) HEP cut-in at 2232H. (Unplanned Outage) [WEBSMS] | CMIN
8/8/2023 10:38:42 PM | Mindanao Grid-08/08/2023 22:40: Asiga (ASG) HEP with 3.57 MW tripped at 2216H. (Unplanned Outage) [WEBSMS] | CMIN
8/8/2023 10:28:41 PM | Mindanao Grid-08/08/2023 22:28: Lake Mainit HEP (AGC) with 10.5 MW tripped at 2216H. (Unplanned Outage) [WEBSMS] | CMIN
8/8/2023 7:45:17 PM | Mindanao Grid-08/08/2023 19:44: Kidapawan SS Power Transformer 2 restored 1938H. (planned outage) [WEBSMS] | CMIN
8/8/2023 6:14:35 PM | Mindanao Grid-08/08/2023 18:16: TM2 Unit #1 & Unit #2 both shutdown at 1624H. Follow RTD. [WEBSMS] | CMIN
8/8/2023 6:11:37 PM | [NSO Update] Visayas Grid-08/08/2023 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2360MW, PK=2037MW, RR=40MW, NetOpMargin: EVE=283 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, TGPP @80.3MW, LEYTE A @350MW, PGPP1 @75MW [WEBSMS] | CVIS
8/8/2023 6:08:35 PM | Mindanao Grid-08/08/2023 18:09: TM1 Unit #2 shutdown at 1638H. Follow RTD. [WEBSMS] | CMIN
8/8/2023 5:58:35 PM | [NSO Update] Mindanao Grid-08/08/2023 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3349MW, PK=2364MW, RR=20MW, NetOpMargin: EVE=965 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @136MW, AG5 @44MW, AG6 @141MW, AG7 @38MW, PG4 @105MW [WEBSMS] | CMIN
8/8/2023 5:56:12 PM | [NSO Update] Luzon Grid-08/08/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12359MW, PK=10938MW, RR=260MW, NetOpMargin: EVE=1161 Highest Unit O/L: GNPD 2 @668MW Derated Plant: CLC1 @210MW, CLC2 @170MW, GNPD 1 @400MW, MSLC1 @285MW, MSLC2 @285MW, ILIJAN A @340MW, ILIJAN B @165MW [WEBSMS] | CLUZ
8/8/2023 4:32:50 PM | Mindanao Grid-08/08/2023 16:35: TM2 U1 & U2 shutdown at 1624H. Follow RTD. [WEBSMS] | CMIN
8/8/2023 4:21:52 PM | Mindanao Grid-08/08/2023 16:24: WMPC DG07 shutdown at 1613H. RPS System Voltage Requirement. [WEBSMS] | CMIN
8/8/2023 2:51:51 PM | Mindanao Grid-08/08/2023 14:53: TM1 Unit #2 online at 1448H. Follow RTD. [WEBSMS] | CMIN
8/8/2023 2:51:48 PM | Luzon Grid-08/08/2023 14:49: GNPD 1 de-load from 616MW to 550MW and then from 557MW to 377MW at 1433H due to mill trouble. Lowest Frequency is 59.225Hz [WEBSMS] | CLUZ
8/8/2023 2:50:41 PM | Mindanao Grid-08/08/2023 14:53: TM1 Unit #2 online at 1448H. Follow RTD. [WEBSMS] | CMIN
8/8/2023 2:49:22 PM | Luzon Grid-08/08/2023 14:49: GNPD 1 de-load from 616MW to 550MW and then from 557MW to 377MW at 1433H due to mill trouble. Lowest Frequency is 59.225Hz [WEBSMS] | CLUZ
8/8/2023 2:41:50 PM | Mindanao Grid-08/08/2023 14:42: WMPC DG05 online at 1423H as energy. Follow RTD. [WEBSMS] | CMIN
8/8/2023 2:39:33 PM | Mindanao Grid-08/08/2023 14:42: WMPC DG05 online at 1423H as energy. Follow RTD. [WEBSMS] | CMIN
8/8/2023 2:09:59 PM | Luzon Grid-08/08/2023 14:10: Bayombong 230kV Bus 1 restored at 1405H (Planned Outage) [WEBSMS] | CLUZ
8/8/2023 2:09:45 PM | Mindanao Grid-08/08/2023 14:12: Lake Mainit HEP online at 1255H. Follow RTD. Unplanned outage. [WEBSMS] | CMIN
8/8/2023 2:09:28 PM | Mindanao Grid-08/08/2023 14:12: Lake Mainit HEP online at 1255H. Follow RTD. Unplanned outage. [WEBSMS] | CMIN
8/8/2023 2:09:27 PM | Luzon Grid-08/08/2023 14:10: Bayombong 230kV Bus 1 restored at 1405H (Planned Outage) [WEBSMS] | CLUZ
8/8/2023 2:08:29 PM | Mindanao Grid-08/08/2023 14:10: ASIGA HEP online at 1242H. Follow RTD. Unplanned outage. [WEBSMS] | CMIN
8/8/2023 2:07:45 PM | Mindanao Grid-08/08/2023 14:10: ASIGA HEP online at 1242H. Follow RTD. Unplanned outage. [WEBSMS] | CMIN
8/8/2023 1:54:28 PM | Mindanao Grid-08/08/2023 13:56: STEAG Unit 2 online at 1349H, from PMS(GOMP). Planned outage. [WEBSMS] | CMIN
8/8/2023 1:54:23 PM | Mindanao Grid-08/08/2023 13:56: STEAG Unit 2 online at 1349H, from PMS(GOMP). Planned outage. [WEBSMS] | CMIN
8/8/2023 1:05:09 PM | Mindanao Grid-08/08/2023 13:07: TM2 Unit 1 online at 1251H. Follow RTD. [WEBSMS] | CMIN
8/8/2023 1:05:08 PM | Mindanao Grid-08/08/2023 13:04: TM2 Unit 2 online at 1244H. Follow RTD. [WEBSMS] | CMIN
8/8/2023 1:04:47 PM | Mindanao Grid-08/08/2023 13:07: TM2 Unit 1 online at 1251H. Follow RTD. [WEBSMS] | CMIN
8/8/2023 1:02:14 PM | Mindanao Grid-08/08/2023 13:04: TM2 Unit 2 online at 1244H. Follow RTD. [WEBSMS] | CMIN
8/8/2023 12:46:50 PM | [NSO Update] Visayas Grid-08/08/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2723MW, PK=2400MW, RR=40MW, NetOpMargin: PM=283, EVE=329 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 80MW, Leyte A @ 357MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/8/2023 12:45:06 PM | [NSO Update] Visayas Grid-08/08/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2723MW, PK=2400MW, RR=40MW, NetOpMargin: PM=283, EVE=329 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 80MW, Leyte A @ 357MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/8/2023 12:42:11 PM | [NSO Update] Mindanao Grid-08/08/2023 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3302MW, PK=2377MW, RR=20MW, NetOpMargin: PM=905, EVE=955 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @136MW, AG5 @44MW, AG6 @141MW, AG7 @38MW, PG4 @105MW [WEBSMS] | CMIN
8/8/2023 12:41:54 PM | [NSO Update] Mindanao Grid-08/08/2023 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3302MW, PK=2377MW, RR=20MW, NetOpMargin: PM=905, EVE=955 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @136MW, AG5 @44MW, AG6 @141MW, AG7 @38MW, PG4 @105MW [WEBSMS] | CMIN
8/8/2023 12:41:52 PM | [NSO Update] Luzon Grid-08/08/2023 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13576MW, PK=11554MW, RR=260MW, NetOpMargin: PM=1762, EVE=2132 Highest Unit O/L: GNPD 1&2@ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 1 @ 285MW, Masinloc 2 @ 285MW, Ilijan A @ 340MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
8/8/2023 12:36:06 PM | [NSO Update] Luzon Grid-08/08/2023 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13576MW, PK=11554MW, RR=260MW, NetOpMargin: PM=1762, EVE=2132 Highest Unit O/L: GNPD 1&2@ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 1 @ 285MW, Masinloc 2 @ 285MW, Ilijan A @ 340MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
8/8/2023 11:28:23 AM | Mindanao Grid-08/08/2023 11:30: Butuan-Santiago 69kV Line tripped at 1113H resulted to isolation of ASIGA HEP with total gross generation loss of 3.7MW. Unplanned outage. [WEBSMS] | CMIN
8/8/2023 11:28:11 AM | Mindanao Grid-08/08/2023 11:30: Butuan-Santiago 69kV Line tripped at 1113H resulted to isolation of ASIGA HEP with total gross generation loss of 3.7MW. Unplanned outage. [WEBSMS] | CMIN
8/8/2023 11:25:57 AM | Mindanao Grid-08/08/2023 11:28: Butuan-Santiago 69kV Line tripped at 1113H resulted to isolation/tripping of Lake Mainit(APC) HEP with total gross generation 10.5MW. Unplanned outage. [WEBSMS] | CMIN
8/8/2023 11:25:56 AM | Mindanao Grid-08/08/2023 11:28: Butuan-Santiago 69kV Line tripped at 1113H resulted to isolation/tripping of Lake Mainit(APC) HEP with total gross generation 10.5MW. Unplanned outage. [WEBSMS] | CMIN
8/8/2023 11:11:36 AM | Mindanao Grid-08/08/2023 11:14: WMPC DG07 online at 1056H. RPS System Voltage Requirement. [WEBSMS] | CMIN
8/8/2023 11:10:56 AM | Mindanao Grid-08/08/2023 11:14: WMPC DG07 online at 1056H. RPS System Voltage Requirement. [WEBSMS] | CMIN
8/8/2023 10:32:38 AM | Mindanao Grid-08/08/2023 10:35: WMPC DG09 online at 0900H. RPS System Voltage Requirement. [WEBSMS] | CMIN
8/8/2023 10:32:33 AM | Mindanao Grid-08/08/2023 10:35: WMPC DG09 online at 0900H. RPS System Voltage Requirement. [WEBSMS] | CMIN
8/8/2023 9:23:17 AM | [NSO Update] Mindanao Grid-08/08/2023 09:22: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0919H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
8/8/2023 9:20:30 AM | [NSO Update] Mindanao Grid-08/08/2023 09:22: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0919H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
8/8/2023 9:20:23 AM | [NSO Update] Visayas Grid-08/08/2023 09:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0919H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
8/8/2023 9:20:20 AM | [NSO Update] Visayas Grid-08/08/2023 09:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0919H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
8/8/2023 8:21:31 AM | Luzon Grid-08/08/2023 08:16: San Jose 750MVA TO4 de-energized at 0729H (Planned Outage) [WEBSMS] | CLUZ
8/8/2023 8:16:43 AM | Luzon Grid-08/08/2023 08:16: San Jose 750MVA TO4 de-energized at 0729H (Planned Outage) [WEBSMS] | CLUZ
8/8/2023 8:06:33 AM | [NSO Update] Mindanao Grid-08/08/2023 08:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0753H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
8/8/2023 8:04:32 AM | [NSO Update] Visayas Grid-08/08/2023 08:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0753H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
8/8/2023 8:04:21 AM | [NSO Update] Mindanao Grid-08/08/2023 08:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0753H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
8/8/2023 8:04:00 AM | [NSO Update] Visayas Grid-08/08/2023 08:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0753H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
8/8/2023 6:11:28 AM | Luzon Grid-08/08/2023 06:11: Bayombong 230kV Bus 1 de-energized at 0604H (Planned Outage) [WEBSMS] | CLUZ
8/8/2023 6:10:53 AM | Luzon Grid-08/08/2023 06:11: Bayombong 230kV Bus 1 de-energized at 0604H (Planned Outage) [WEBSMS] | CLUZ
8/8/2023 5:51:28 AM | [NSO Update] Luzon Grid-08/08/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13600MW, PK=11014MW, RR=260MW, NetOpMargin: AM=2326, PM=2008, EVE=2192 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 1 @ 300MW, Masinloc 2 @ 300MW, Ilijan A @ 340MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
8/8/2023 5:49:43 AM | [NSO Update] Luzon Grid-08/08/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13600MW, PK=11014MW, RR=260MW, NetOpMargin: AM=2326, PM=2008, EVE=2192 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 1 @ 300MW, Masinloc 2 @ 300MW, Ilijan A @ 340MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
8/8/2023 5:48:47 AM | [NSO Update] Visayas Grid-08/08/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2601MW, PK=2280MW, RR=40MW, NetOpMargin: AM=281, PM=269, EVE=342 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 80MW, Leyte A @ 350MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/8/2023 5:47:53 AM | [NSO Update] Mindanao Grid-08/08/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3305MW, PK=2355MW, RR=20MW, NetOpMargin: AM=930, PM=895, EVE=978 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @136MW, AG5 @44MW, AG6 @141MW, AG7 @38MW, PG4 @105MW [WEBSMS] | CMIN
8/8/2023 5:47:23 AM | [NSO Update] Mindanao Grid-08/08/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3305MW, PK=2355MW, RR=20MW, NetOpMargin: AM=930, PM=895, EVE=978 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @136MW, AG5 @44MW, AG6 @141MW, AG7 @38MW, PG4 @105MW [WEBSMS] | CMIN
8/8/2023 5:46:32 AM | [NSO Update] Visayas Grid-08/08/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2601MW, PK=2280MW, RR=40MW, NetOpMargin: AM=281, PM=269, EVE=342 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 80MW, Leyte A @ 350MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/8/2023 4:12:17 AM | [NSO Update] Luzon Grid-08/08/2023 04:09: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CLUZ
8/8/2023 4:09:47 AM | [NSO Update] Mindanao Grid-08/08/2023 04:11: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CMIN
8/8/2023 4:09:05 AM | [NSO Update] Luzon Grid-08/08/2023 04:09: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CLUZ
8/8/2023 4:08:50 AM | [NSO Update] Mindanao Grid-08/08/2023 04:11: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CMIN
8/8/2023 4:08:37 AM | [NSO Update] Visayas Grid-08/08/2023 04:08: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CVIS
8/8/2023 4:08:26 AM | [NSO Update] Visayas Grid-08/08/2023 04:08: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CVIS
8/8/2023 3:41:27 AM | Mindanao Grid-08/08/2023 03:42: Agus 6 HEP U4 cut-in at 0337H. (Unplanned Outage). [WEBSMS] | CMIN
8/8/2023 3:39:54 AM | Mindanao Grid-08/08/2023 03:42: Agus 6 HEP U4 cut-in at 0337H. (Unplanned Outage). [WEBSMS] | CMIN
8/8/2023 1:57:31 AM | Mindanao Grid-08/08/2023 01:59: Agus 6 HEP U4 tripped with 25 MW at 0141H. (Unplanned Outage). [WEBSMS] | CMIN
8/8/2023 1:57:15 AM | Mindanao Grid-08/08/2023 01:59: Agus 6 HEP U4 tripped with 25 MW at 0141H. (Unplanned Outage). [WEBSMS] | CMIN
8/8/2023 12:04:42 AM | Mindanao Grid-08/08/2023 00:06: Pulangi 4 HEP U3 cut-out at 0002H. (Planned Outage) [WEBSMS] | CMIN
8/8/2023 12:04:12 AM | Mindanao Grid-08/08/2023 00:06: Pulangi 4 HEP U3 cut-out at 0002H. (Planned Outage) [WEBSMS] | CMIN
8/7/2023 9:21:37 PM | Mindanao Grid-08/07/2023 21:24: WMPC DG09 cut-out at 2114H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/7/2023 9:21:19 PM | Mindanao Grid-08/07/2023 21:24: WMPC DG09 cut-out at 2114H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/7/2023 8:37:58 PM | Mindanao Grid-08/07/2023 20:38: Therma Marine 2 U2 cut-out at 2023H from energy (RTD) dispatch. [WEBSMS] | CMIN
8/7/2023 8:36:27 PM | Mindanao Grid-08/07/2023 20:38: Therma Marine 2 U2 cut-out at 2023H from energy (RTD) dispatch. [WEBSMS] | CMIN
8/7/2023 8:10:24 PM | Mindanao Grid-08/07/2023 20:11: WMPC DG07 cut-out at 2006H from energy (RTD) dispatch. [WEBSMS] | CMIN
8/7/2023 8:09:31 PM | Mindanao Grid-08/07/2023 20:11: WMPC DG07 cut-out at 2006H from energy (RTD) dispatch. [WEBSMS] | CMIN
8/7/2023 8:04:37 PM | Mindanao Grid-08/07/2023 20:06: Therma Marine 2 Unit 2 cut-in at 1958H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 8:03:39 PM | Mindanao Grid-08/07/2023 20:06: Therma Marine 2 Unit 2 cut-in at 1958H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 7:50:04 PM | Mindanao Grid-08/07/2023 19:52: WMPC DG07 cut-in at 1943H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 7:49:37 PM | Mindanao Grid-08/07/2023 19:52: WMPC DG07 cut-in at 1943H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 7:24:37 PM | Mindanao Grid-08/07/2023 19:25: Therma Marine 2 Unit 2 cut-out at 1917H from energy (RTD) dispatch. [WEBSMS] | CMIN
8/7/2023 7:23:29 PM | Mindanao Grid-08/07/2023 19:25: Therma Marine 2 Unit 2 cut-out at 1917H from energy (RTD) dispatch. [WEBSMS] | CMIN
8/7/2023 6:55:41 PM | Mindanao Grid-08/07/2023 18:58: WMPC DG05 and DG07 cut-out at 1834H and 1853H, respectively from energy (RTD) dispatch. [WEBSMS] | CMIN
8/7/2023 6:28:54 PM | Mindanao Grid-08/07/2023 18:31: WMPC DG05 and DG07 cut-in at 1810H and 1813H, respectively. Follow RTD. [WEBSMS] | CMIN
8/7/2023 6:28:39 PM | Mindanao Grid-08/07/2023 18:31: WMPC DG05 and DG07 cut-in at 1810H and 1813H, respectively. Follow RTD. [WEBSMS] | CMIN
8/7/2023 6:25:19 PM | Mindanao Grid-08/07/2023 18:27: Therma Marine 2 Unit 2 cut-in at 1819H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 5:54:47 PM | [NSO Update] Mindanao Grid-08/07/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3232MW, PK=2363MW, RR=20MW, NetOpMargin: EVE=849 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/7/2023 5:54:39 PM | [NSO Update] Luzon Grid-08/07/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12907MW, PK=10512MW, RR=260MW, NetOpMargin: EVE=2135 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 1 @ 300MW, Masinloc 2 @ 300MW, Ilijan A @ 340MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
8/7/2023 5:54:18 PM | [NSO Update] Luzon Grid-08/07/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12907MW, PK=10512MW, RR=260MW, NetOpMargin: EVE=2135 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 1 @ 300MW, Masinloc 2 @ 300MW, Ilijan A @ 340MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
8/7/2023 5:53:32 PM | [NSO Update] Visayas Grid-08/07/2023 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2387MW, PK=2014MW, RR=40MW, NetOpMargin: EVE=333 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 80MW, Leyte A @ 342MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/7/2023 5:52:30 PM | [NSO Update] Mindanao Grid-08/07/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3232MW, PK=2363MW, RR=20MW, NetOpMargin: EVE=849 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/7/2023 5:52:24 PM | [NSO Update] Visayas Grid-08/07/2023 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2387MW, PK=2014MW, RR=40MW, NetOpMargin: EVE=333 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 80MW, Leyte A @ 342MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/7/2023 5:39:40 PM | Mindanao Grid-08/07/2023 17:42: Therma Marine 2 U1 and U2 cut-out at 1644H and 1655H respectively from energy (RTD) dispatch. [WEBSMS] | CMIN
8/7/2023 5:39:38 PM | Mindanao Grid-08/07/2023 17:42: Therma Marine 2 U1 and U2 cut-out at 1644H and 1655H respectively from energy (RTD) dispatch. [WEBSMS] | CMIN
8/7/2023 4:23:31 PM | Mindanao Grid-08/07/2023 16:25: WMPC DG07 cut-out at 1614H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/7/2023 4:22:52 PM | Mindanao Grid-08/07/2023 16:25: WMPC DG07 cut-out at 1614H as RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/7/2023 4:02:00 PM | Visayas Grid-08/07/2023 16:02: TPC1A on line at 1550H. (Unplanned outage) [WEBSMS] | CVIS
8/7/2023 4:01:37 PM | Visayas Grid-08/07/2023 16:02: TPC1A on line at 1550H. (Unplanned outage) [WEBSMS] | CVIS
8/7/2023 3:11:51 PM | Luzon Grid-08/07/2023 15:11: Ilijan GT1-1 online at 1500H (Unplanned Outage) [WEBSMS] | CLUZ
8/7/2023 3:11:48 PM | Luzon Grid-08/07/2023 15:11: Ilijan GT1-1 online at 1500H (Unplanned Outage) [WEBSMS] | CLUZ
8/7/2023 3:01:16 PM | Mindanao Grid-08/07/2023 15:03: Therma Marine 1 U2 cut-out at 1448H from energy (RTD) dispatch. [WEBSMS] | CMIN
8/7/2023 3:01:12 PM | Mindanao Grid-08/07/2023 15:03: Therma Marine 1 U2 cut-out at 1448H from energy (RTD) dispatch. [WEBSMS] | CMIN
8/7/2023 2:28:30 PM | Luzon Grid-08/07/2023 14:27: San Jose SS 750MVA T03 restored at 1427H (Planned Outage) [WEBSMS] | CLUZ
8/7/2023 2:27:40 PM | Luzon Grid-08/07/2023 14:27: San Jose SS 750MVA T03 restored at 1427H (Planned Outage) [WEBSMS] | CLUZ
8/7/2023 2:02:49 PM | Mindanao Grid-08/07/2023 14:03: WMPC DG05 shutdown at 1356H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 2:00:58 PM | Mindanao Grid-08/07/2023 14:03: WMPC DG05 shutdown at 1356H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 1:42:30 PM | Mindanao Grid-08/07/2023 13:44: TM1 U2 Online at 1338H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 1:34:26 PM | Mindanao Grid-08/07/2023 13:36: TM2 U1 Online at 1314H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 1:34:25 PM | Mindanao Grid-08/07/2023 13:34: TM2 U2 Online at 1259H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 1:34:03 PM | Mindanao Grid-08/07/2023 13:36: TM2 U1 Online at 1314H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 1:32:19 PM | Mindanao Grid-08/07/2023 13:34: TM2 U2 Online at 1259H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 1:19:25 PM | Mindanao Grid-08/07/2023 13:20: WMPC DG05 Online at 1313H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 1:17:54 PM | Mindanao Grid-08/07/2023 13:20: WMPC DG05 Online at 1313H. Follow RTD. [WEBSMS] | CMIN
8/7/2023 12:59:24 PM | [NSO Update] Mindanao Grid-08/07/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3290MW, PK=2471MW, RR=20MW, NetOpMargin: PM=799, EVE=1087 Highest Unit O/L: GNPK 1&4@138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/7/2023 12:57:51 PM | [NSO Update] Mindanao Grid-08/07/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3290MW, PK=2471MW, RR=20MW, NetOpMargin: PM=799, EVE=1087 Highest Unit O/L: GNPK 1&4@138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/7/2023 12:55:57 PM | [NSO Update] Visayas Grid-08/07/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2629MW, PK=2333MW, RR=40MW, NetOpMargin: PM=255, EVE=383 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @342MW, PGPP1 @75MW, TGPP @80.3MW [WEBSMS] | CVIS
8/7/2023 12:54:26 PM | [NSO Update] Visayas Grid-08/07/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2629MW, PK=2333MW, RR=40MW, NetOpMargin: PM=255, EVE=383 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: LEYTE A @342MW, PGPP1 @75MW, TGPP @80.3MW [WEBSMS] | CVIS
8/7/2023 12:54:23 PM | [NSO Update] Luzon Grid-08/07/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13614MW, PK=11182MW, RR=260MW, NetOpMargin: PM=2172, EVE=2178 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 1 @230MW, CALACA 2 @170MW, MASINLOC 1 @ 300MW, MASINLOC 2 @300MW, ILIJAN A @250MW, ILIJAN B @290MW [WEBSMS] | CLUZ
8/7/2023 12:53:30 PM | [NSO Update] Luzon Grid-08/07/2023 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13614MW, PK=11182MW, RR=260MW, NetOpMargin: PM=2172, EVE=2178 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 1 @230MW, CALACA 2 @170MW, MASINLOC 1 @ 300MW, MASINLOC 2 @300MW, ILIJAN A @250MW, ILIJAN B @290MW [WEBSMS] | CLUZ
8/7/2023 9:14:21 AM | [NSO Update] Mindanao Grid-08/07/2023 09:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0910H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
8/7/2023 9:12:35 AM | [NSO Update] Mindanao Grid-08/07/2023 09:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0910H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
8/7/2023 9:12:07 AM | [NSO Update] Visayas Grid-08/07/2023 09:11: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0910H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
8/7/2023 9:11:34 AM | [NSO Update] Visayas Grid-08/07/2023 09:11: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0910H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
8/7/2023 8:59:21 AM | [NSO Update] Mindanao Grid-08/07/2023 08:58: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0852H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
8/7/2023 8:55:47 AM | [NSO Update] Mindanao Grid-08/07/2023 08:58: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0852H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
8/7/2023 8:55:39 AM | [NSO Update] Visayas Grid-08/07/2023 08:55: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0852H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
8/7/2023 8:55:27 AM | [NSO Update] Visayas Grid-08/07/2023 08:55: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 0852H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
8/7/2023 8:54:20 AM | Mindanao Grid-08/07/2023 08:53: Baloi - Aurora 138kv line restored 0848H. (Unplanned outage) [WEBSMS] | CMIN
8/7/2023 8:51:07 AM | Mindanao Grid-08/07/2023 08:53: Baloi - Aurora 138kv line restored 0848H. (Unplanned outage) [WEBSMS] | CMIN
8/7/2023 8:49:20 AM | Mindanao Grid-08/07/2023 08:48: Baloi - Aurora 138kv line auto tripped 0838H. (Unplanned outage) [WEBSMS] | CMIN
8/7/2023 8:45:43 AM | Mindanao Grid-08/07/2023 08:48: Baloi - Aurora 138kv line auto tripped 0838H. (Unplanned outage) [WEBSMS] | CMIN
8/7/2023 8:27:12 AM | Visayas Grid-08/07/2023 08:26: TPC1A tripped with 67MW load at 0819H. (Unplanned outage) [WEBSMS] | CVIS
8/7/2023 8:26:42 AM | Visayas Grid-08/07/2023 08:26: TPC1A tripped with 67MW load at 0819H. (Unplanned outage) [WEBSMS] | CVIS
8/7/2023 6:20:54 AM | [NSO Update] Luzon Grid-08/07/2023 06:14: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13727MW, PK=11366MW, RR=260MW, NetOpMargin: AM=2101, PM=1899, EVE=2236 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @220MW, CLC2 @170MW, MSLC2 @310MW, ILIJAN A @300MW, ILIJAN B @300MW [WEBSMS] | CLUZ
8/7/2023 6:13:52 AM | [NSO Update] Luzon Grid-08/07/2023 06:14: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13727MW, PK=11366MW, RR=260MW, NetOpMargin: AM=2101, PM=1899, EVE=2236 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @220MW, CLC2 @170MW, MSLC2 @310MW, ILIJAN A @300MW, ILIJAN B @300MW [WEBSMS] | CLUZ
8/7/2023 6:11:51 AM | Mindanao Grid-08/07/2023 06:14: Kidapawan SS Power Transformer 2 de-energized 0602H. (Planned outage) [WEBSMS] | CMIN
8/7/2023 6:11:30 AM | Mindanao Grid-08/07/2023 06:14: Kidapawan SS Power Transformer 2 de-energized 0602H. (Planned outage) [WEBSMS] | CMIN
8/7/2023 6:00:55 AM | [NSO Update] Mindanao Grid-08/07/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3301MW, PK=2221MW, RR=20MW, NetOpMargin: AM=1060, PM=987, EVE=1093 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/7/2023 6:00:54 AM | Luzon Grid-08/07/2023 05:59: Ilijan ST1 online at 0541H (Unplanned Outage) [WEBSMS] | CLUZ
8/7/2023 5:59:35 AM | [NSO Update] Mindanao Grid-08/07/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3301MW, PK=2221MW, RR=20MW, NetOpMargin: AM=1060, PM=987, EVE=1093 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/7/2023 5:59:32 AM | Luzon Grid-08/07/2023 05:59: Ilijan ST1 online at 0541H (Unplanned Outage) [WEBSMS] | CLUZ
8/7/2023 5:54:07 AM | [NSO Update] Visayas Grid-08/07/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2611MW, PK=2314MW, RR=40MW, NetOpMargin: AM=258, PM=220, EVE=283 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @350MW, TPC-Carmen @40MW, TGPP @80.3MW [WEBSMS] | CVIS
8/7/2023 5:51:30 AM | [NSO Update] Visayas Grid-08/07/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2611MW, PK=2314MW, RR=40MW, NetOpMargin: AM=258, PM=220, EVE=283 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: LEYTE A @350MW, TPC-Carmen @40MW, TGPP @80.3MW [WEBSMS] | CVIS
8/7/2023 5:07:33 AM | Luzon Grid-08/07/2023 05:06: Quezon-Dona Imelda 230kV line restored at 0506H (Planned Outage) [WEBSMS] | CLUZ
8/7/2023 5:06:22 AM | Luzon Grid-08/07/2023 05:06: Quezon-Dona Imelda 230kV line restored at 0506H (Planned Outage) [WEBSMS] | CLUZ
8/7/2023 4:44:11 AM | Luzon Grid-08/07/2023 04:42: Muntinlupa (Sucat) - Sun Valley 115kV restored at 0440H (Planned Outage) [WEBSMS] | CLUZ
8/7/2023 4:42:03 AM | Luzon Grid-08/07/2023 04:42: Muntinlupa (Sucat) - Sun Valley 115kV restored at 0440H (Planned Outage) [WEBSMS] | CLUZ
8/7/2023 4:14:19 AM | [NSO Update] Visayas Grid-08/07/2023 04:14: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CVIS
8/7/2023 4:14:13 AM | [NSO Update] Mindanao Grid-08/07/2023 04:16: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CMIN
8/7/2023 4:14:12 AM | [NSO Update] Visayas Grid-08/07/2023 04:14: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CVIS
8/7/2023 4:14:10 AM | [NSO Update] Luzon Grid-08/07/2023 04:12: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CLUZ
8/7/2023 4:13:47 AM | [NSO Update] Mindanao Grid-08/07/2023 04:16: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CMIN
8/7/2023 4:12:51 AM | [NSO Update] Luzon Grid-08/07/2023 04:12: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CLUZ
8/7/2023 3:50:50 AM | Luzon Grid-08/07/2023 03:47: Ilijan GT1-2 online at 0343H. (Unplanned Outage) [WEBSMS] | CLUZ
8/7/2023 3:47:34 AM | Luzon Grid-08/07/2023 03:47: Ilijan GT1-2 online at 0343H. (Unplanned Outage) [WEBSMS] | CLUZ
8/7/2023 3:22:30 AM | Mindanao Grid-08/07/2023 03:21: Mt. Apo Unit #3 cut-in at 0315H. (Unplanned Outage) [WEBSMS] | CMIN
8/7/2023 3:19:32 AM | Mindanao Grid-08/07/2023 03:21: Mt. Apo Unit #3 cut-in at 0315H. (Unplanned Outage) [WEBSMS] | CMIN
8/7/2023 2:44:11 AM | Mindanao Grid-08/07/2023 02:46: Mt. Apo Unit #3 tripped at 0157H, due to Restricted Earth Fault. Generation Loss=3.2MW. (Unplanned Outage) [WEBSMS] | CMIN
8/7/2023 2:44:10 AM | Mindanao Grid-08/07/2023 02:46: Mt. Apo Unit #3 tripped at 0157H, due to Restricted Earth Fault. Generation Loss=3.2MW. (Unplanned Outage) [WEBSMS] | CMIN
8/7/2023 2:11:20 AM | Luzon Grid-08/07/2023 02:08: Muntinlupa (Sucat) - Sun Valley 115kV de-energized at 0202H (Planned Outage) [WEBSMS] | CLUZ
8/7/2023 2:08:37 AM | Luzon Grid-08/07/2023 02:08: Muntinlupa (Sucat) - Sun Valley 115kV de-energized at 0202H (Planned Outage) [WEBSMS] | CLUZ
8/7/2023 12:57:49 AM | Luzon Grid-08/07/2023 00:57: Ilijan ST2 online at 0056H (Unplanned Outage) [WEBSMS] | CLUZ
8/6/2023 11:30:44 PM | Luzon Grid-08/06/2023 23:27: Ilijan GT2-2 online at 2324H (Unplanned Outage). [WEBSMS] | CLUZ
8/6/2023 11:26:59 PM | Luzon Grid-08/06/2023 23:27: Ilijan GT2-2 online at 2324H (Unplanned Outage). [WEBSMS] | CLUZ
8/6/2023 11:25:46 PM | Luzon Grid-08/06/2023 23:25: Commissioning and energization of New Main Protection for Nagsaag-San Jose 500kV line 2 was completed at 2321H. [WEBSMS] | CLUZ
8/6/2023 11:17:55 PM | Luzon Grid-08/06/2023 23:12: Nagsaag-San Jose 500kV line 2 restored at 2307H (Planned Outage-On-going commissioning and energization of New Main Protection) [WEBSMS] | CLUZ
8/6/2023 11:12:22 PM | Luzon Grid-08/06/2023 23:12: Nagsaag-San Jose 500kV line 2 restored at 2307H (Planned Outage-On-going commissioning and energization of New Main Protection) [WEBSMS] | CLUZ
8/6/2023 9:20:41 PM | Luzon Grid-08/06/2023 21:18: Quezon-Dona Imelda 230kV line - de-energized at 2117H (Planned Outage). [WEBSMS] | CLUZ
8/6/2023 9:18:25 PM | Luzon Grid-08/06/2023 21:18: Quezon-Dona Imelda 230kV line - de-energized at 2117H (Planned Outage). [WEBSMS] | CLUZ
8/6/2023 6:32:49 PM | Luzon Grid-08/06/2023 18:32: Mexico PCB 8-03CB04MEX energized at 1832H (Unplanned Outage) [WEBSMS] | CLUZ
8/6/2023 6:14:25 PM | Mindanao Grid-08/06/2023 18:16: Butuan - San Francisco 138KV line restored at 1757H. (Planned outage) [WEBSMS] | CMIN
8/6/2023 6:14:06 PM | Mindanao Grid-08/06/2023 18:16: Butuan - San Francisco 138KV line restored at 1757H. (Planned outage) [WEBSMS] | CMIN
8/6/2023 5:54:19 PM | [NSO Update] Mindanao Grid-08/06/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3276MW, PK=2080MW, RR=20MW, NetOpMargin: EVE=1177 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @48MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @75MW [WEBSMS] | CMIN
8/6/2023 5:54:18 PM | Luzon Grid-08/06/2023 17:54: San Manuel-San Manuel BESS 69kV line restored at 1753H (Planned Outage). [WEBSMS] | CLUZ
8/6/2023 5:53:58 PM | [NSO Update] Mindanao Grid-08/06/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3276MW, PK=2080MW, RR=20MW, NetOpMargin: EVE=1177 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @48MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @75MW [WEBSMS] | CMIN
8/6/2023 5:53:57 PM | Luzon Grid-08/06/2023 17:54: San Manuel-San Manuel BESS 69kV line restored at 1753H (Planned Outage). [WEBSMS] | CLUZ
8/6/2023 5:53:52 PM | Luzon Grid-08/06/2023 17:48: Binan-Calaca 230kV line restored at 1747H (Planned Outage). [WEBSMS] | CLUZ
8/6/2023 5:51:06 PM | [NSO Update] Visayas Grid-08/06/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2351MW, PK=1984MW, RR=40MW, NetOpMargin: EVE=327 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @350MW, TPC-Carmen @30MW, TGPP @80.3MW [WEBSMS] | CVIS
8/6/2023 5:48:57 PM | [NSO Update] Visayas Grid-08/06/2023 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2351MW, PK=1984MW, RR=40MW, NetOpMargin: EVE=327 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @350MW, TPC-Carmen @30MW, TGPP @80.3MW [WEBSMS] | CVIS
8/6/2023 5:48:49 PM | Luzon Grid-08/06/2023 17:48: Binan-Calaca 230kV line restored at 1747H (Planned Outage). [WEBSMS] | CLUZ
8/6/2023 5:47:42 PM | Luzon Grid-08/06/2023 17:47: Sta Rita Module 30 online at 1745H (Planned Outage) [WEBSMS] | CLUZ
8/6/2023 5:44:03 PM | [NSO Update] Luzon Grid-08/06/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12356MW, PK=9494MW, RR=80MW, NetOpMargin: EVE=2782 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC2 @310MW [WEBSMS] | CLUZ
8/6/2023 5:43:52 PM | [NSO Update] Luzon Grid-08/06/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12356MW, PK=9494MW, RR=80MW, NetOpMargin: EVE=2782 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC2 @310MW [WEBSMS] | CLUZ
8/6/2023 5:30:39 PM | Mindanao Grid-08/06/2023 17:33: Agus 2 HEP U3 cut-in at 1624H. (Unplanned Outage) [WEBSMS] | CMIN
8/6/2023 5:20:33 PM | Mindanao Grid-08/06/2023 17:22: Kibawe -Tacurong 138kV Line restored at 1713H. (Planned Outage) [WEBSMS] | CMIN
8/6/2023 5:20:24 PM | Mindanao Grid-08/06/2023 17:22: Kibawe -Tacurong 138kV Line restored at 1713H. (Planned Outage) [WEBSMS] | CMIN
8/6/2023 4:27:09 PM | Luzon Grid-08/06/2023 16:25: Mexico PCB 8-03CB04MEX de-energized at 1622H due to low SF6 gas pressure alarm (Unplanned Outage). [WEBSMS] | CLUZ
8/6/2023 4:24:52 PM | Luzon Grid-08/06/2023 16:25: Mexico PCB 8-03CB04MEX de-energized at 1622H due to low SF6 gas pressure alarm (Unplanned Outage). [WEBSMS] | CLUZ
8/6/2023 4:17:10 PM | Mindanao Grid-08/06/2023 16:19: Agus 2 HEP Unit 3 138kV Tie-Line restored at 1608H. (Unplanned Outage) [WEBSMS] | CMIN
8/6/2023 4:17:09 PM | Mindanao Grid-08/06/2023 16:19: Agus 2 HEP Unit 3 138kV Tie-Line restored at 1608H. (Unplanned Outage) [WEBSMS] | CMIN
8/6/2023 1:05:36 PM | [NSO Update] Mindanao Grid-08/06/2023 13:08: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3317MW, PK=1895MW, RR=20MW, NetOpMargin: PM=1401, EVE=1271 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48MW, MA2 @30MW, AG1 @35MW, AG2 @85MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @75MW [WEBSMS] | CMIN
8/6/2023 1:05:22 PM | [NSO Update] Mindanao Grid-08/06/2023 13:08: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3317MW, PK=1895MW, RR=20MW, NetOpMargin: PM=1401, EVE=1271 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @48MW, MA2 @30MW, AG1 @35MW, AG2 @85MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @75MW [WEBSMS] | CMIN
8/6/2023 1:04:55 PM | [NSO Update] Visayas Grid-08/06/2023 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2496MW, PK=1848MW, RR=40MW, NetOpMargin: PM=608, EVE=338 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, TGPP @80.3MW, LEYTE A @342MW [WEBSMS] | CVIS
8/6/2023 1:03:50 PM | [NSO Update] Luzon Grid-08/06/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12774MW, PK=8981MW, RR=80MW, NetOpMargin: PM=3713, EVE=2609 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, GMEC 2 @150MW, MSLC2 @310MW [WEBSMS] | CLUZ
8/6/2023 1:02:41 PM | [NSO Update] Visayas Grid-08/06/2023 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2496MW, PK=1848MW, RR=40MW, NetOpMargin: PM=608, EVE=338 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, TGPP @80.3MW, LEYTE A @342MW [WEBSMS] | CVIS
8/6/2023 1:01:24 PM | [NSO Update] Luzon Grid-08/06/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12774MW, PK=8981MW, RR=80MW, NetOpMargin: PM=3713, EVE=2609 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, GMEC 2 @150MW, MSLC2 @310MW [WEBSMS] | CLUZ
8/6/2023 10:54:01 AM | Luzon Grid-08/06/2023 10:54: Bantay 115kV Bus 2 energized at 1053H (Planned Outage) [WEBSMS] | CLUZ
8/6/2023 10:53:47 AM | Luzon Grid-08/06/2023 10:54: Bantay 115kV Bus 2 energized at 1053H (Planned Outage) [WEBSMS] | CLUZ
8/6/2023 10:50:16 AM | Luzon Grid-08/06/2023 10:43: Las Pinas (Zapote) 300MVA T02 energized at 1041H (Planned Outage) [WEBSMS] | CLUZ
8/6/2023 10:47:15 AM | Mindanao Grid-08/06/2023 10:48: San Francisco 138kV Bus 1 restored at 1045H. (Planned Outage) [WEBSMS] | CMIN
8/6/2023 10:46:58 AM | Mindanao Grid-08/06/2023 10:48: San Francisco 138kV Bus 1 restored at 1045H. (Planned Outage) [WEBSMS] | CMIN
8/6/2023 10:43:44 AM | Luzon Grid-08/06/2023 10:43: Las Pinas (Zapote) 300MVA T02 energized at 1041H (Planned Outage) [WEBSMS] | CLUZ
8/6/2023 8:19:35 AM | Mindanao Grid-08/06/2023 08:17: Kibawe - Tacurong 138kV Line 1 de-energized at 0706H. (Planned Outage) [WEBSMS] | CMIN
8/6/2023 8:16:02 AM | Mindanao Grid-08/06/2023 08:17: Kibawe - Tacurong 138kV Line 1 de-energized at 0706H. (Planned Outage) [WEBSMS] | CMIN
8/6/2023 7:03:12 AM | Luzon Grid-08/06/2023 07:01: Bantay 115kV Bus 2 de-energized at 0700H (Planned Outage) [WEBSMS] | CLUZ
8/6/2023 7:01:51 AM | Luzon Grid-08/06/2023 07:01: Bantay 115kV Bus 2 de-energized at 0700H (Planned Outage) [WEBSMS] | CLUZ
8/6/2023 6:53:12 AM | Luzon Grid-08/06/2023 06:39: Las Pinas (Zapote) 300MVA T02 de-energized at 0635H (Planned Outage). [WEBSMS] | CLUZ
8/6/2023 6:48:52 AM | Luzon Grid-08/06/2023 06:39: Las Pinas (Zapote) 300MVA T02 de-energized at 0635H (Planned Outage). [WEBSMS] | CLUZ
8/6/2023 6:48:13 AM | Mindanao Grid-08/06/2023 06:47: San Francisco 138kV Bus 1 de-energized at 0611H. (Planned Outage) [WEBSMS] | CMIN
8/6/2023 6:45:43 AM | Mindanao Grid-08/06/2023 06:47: San Francisco 138kV Bus 1 de-energized at 0611H. (Planned Outage) [WEBSMS] | CMIN
8/6/2023 6:43:30 AM | Mindanao Grid-08/06/2023 06:44: Butuan - San Francisco 138kV Line de-energized at 0606H. (Planned Outage) [WEBSMS] | CMIN
8/6/2023 6:43:13 AM | Mindanao Grid-08/06/2023 06:44: Butuan - San Francisco 138kV Line de-energized at 0606H. (Planned Outage) [WEBSMS] | CMIN
8/6/2023 6:43:11 AM | Luzon Grid-08/06/2023 06:43: Las Pinas (Zapote) 300MVA T02 de-energized at 0635H (Planned Outage). [WEBSMS] | CLUZ
8/6/2023 6:19:31 AM | Luzon Grid-08/06/2023 06:14: Calaca-Binan 230kV line de-energized at 0611H (Planned Outage). [WEBSMS] | CLUZ
8/6/2023 6:14:25 AM | Luzon Grid-08/06/2023 06:14: Calaca-Binan 230kV line de-energized at 0611H (Planned Outage). [WEBSMS] | CLUZ
8/6/2023 5:56:46 AM | [NSO Update] Luzon Grid-08/06/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13017MW, PK=8964MW, RR=80MW, NetOpMargin: AM=3973, PM=3758, EVE=2692 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, GMEC 2 @ 150MW, Masinloc 2 @ 310MW [WEBSMS] | CLUZ
8/6/2023 5:51:40 AM | [NSO Update] Luzon Grid-08/06/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13017MW, PK=8964MW, RR=80MW, NetOpMargin: AM=3973, PM=3758, EVE=2692 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, GMEC 2 @ 150MW, Masinloc 2 @ 310MW [WEBSMS] | CLUZ
8/6/2023 5:50:46 AM | [NSO Update] Visayas Grid-08/06/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2497MW, PK=1832MW, RR=40MW, NetOpMargin: AM=624, PM=647, EVE=330 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 80MW, Leyte A @ 350MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/6/2023 5:50:16 AM | [NSO Update] Mindanao Grid-08/06/2023 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3295MW, PK=1887MW, RR=20MW, NetOpMargin: AM=1388, PM=1350, EVE=1203 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @105MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @55MW [WEBSMS] | CMIN
8/6/2023 5:48:19 AM | [NSO Update] Visayas Grid-08/06/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2497MW, PK=1832MW, RR=40MW, NetOpMargin: AM=624, PM=647, EVE=330 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 80MW, Leyte A @ 350MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/6/2023 5:36:10 AM | Luzon Grid-08/06/2023 05:31: Sta. Rita Module 30 shutdown at 0531H (Planned Outage) [WEBSMS] | CLUZ
8/6/2023 5:31:50 AM | Luzon Grid-08/06/2023 05:31: Sta. Rita Module 30 shutdown at 0531H (Planned Outage) [WEBSMS] | CLUZ
8/6/2023 5:13:27 AM | [NSO Update] Mindanao Grid-08/06/2023 05:14: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CMIN
8/6/2023 5:13:25 AM | [NSO Update] Luzon Grid-08/06/2023 05:12: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CLUZ
8/6/2023 5:13:10 AM | [NSO Update] Visayas Grid-08/06/2023 05:13: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CVIS
8/6/2023 5:12:53 AM | [NSO Update] Luzon Grid-08/06/2023 05:12: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CLUZ
8/6/2023 5:12:33 AM | [NSO Update] Visayas Grid-08/06/2023 05:13: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CVIS
8/6/2023 5:10:01 AM | Luzon Grid-08/06/2023 05:10: San Manuel-San Manuel BESS 69kV Line de-energized at 0508H (Planned Outage) [WEBSMS] | CLUZ
8/6/2023 12:27:45 AM | Mindanao Grid-08/06/2023 00:28: MCC Unit #2 (Balingasag) on reserved shutdown at 0002H. (Unplanned Outage) [WEBSMS] | CMIN
8/6/2023 12:27:23 AM | Mindanao Grid-08/06/2023 00:28: MCC Unit #2 (Balingasag) on reserved shutdown at 0002H. (Unplanned Outage) [WEBSMS] | CMIN
8/5/2023 6:18:57 PM | Visayas Grid-08/05/2023 18:17: Colon-Calong-calong 138kV Line2 energized at 1816H (Planned Outage) [WEBSMS] | CVIS
8/5/2023 6:16:56 PM | Visayas Grid-08/05/2023 18:17: Colon-Calong-calong 138kV Line2 energized at 1816H (Planned Outage) [WEBSMS] | CVIS
8/5/2023 5:52:34 PM | [NSO Update] Luzon Grid-08/05/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12587MW, PK=9844MW, RR=170MW, NetOpMargin: EVE=2573 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 2 @ 310MW, Pagbilao 1 @ 300MW [WEBSMS] | CLUZ
8/5/2023 5:47:52 PM | [NSO Update] Luzon Grid-08/05/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12587MW, PK=9844MW, RR=170MW, NetOpMargin: EVE=2573 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 2 @ 310MW, Pagbilao 1 @ 300MW [WEBSMS] | CLUZ
8/5/2023 5:47:35 PM | [NSO Update] Mindanao Grid-08/05/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3283MW, PK=2121MW, RR=20MW, NetOpMargin: EVE=1142 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/5/2023 5:46:51 PM | [NSO Update] Visayas Grid-08/05/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2451MW, PK=2128MW, RR=40MW, NetOpMargin: EVE=283 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 350MW, TGPP @ 80MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/5/2023 5:46:24 PM | [NSO Update] Mindanao Grid-08/05/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3283MW, PK=2121MW, RR=20MW, NetOpMargin: EVE=1142 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/5/2023 5:44:38 PM | [NSO Update] Visayas Grid-08/05/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2451MW, PK=2128MW, RR=40MW, NetOpMargin: EVE=283 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 350MW, TGPP @ 80MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/5/2023 5:14:20 PM | Mindanao Grid-08/05/2023 17:14: Pulangi 4 Unit #2 online at 1659H, Follow RTD. (Planned Outage). [WEBSMS] | CMIN
8/5/2023 5:13:26 PM | Mindanao Grid-08/05/2023 17:14: Pulangi 4 Unit #2 online at 1659H, Follow RTD. (Planned Outage). [WEBSMS] | CMIN
8/5/2023 4:35:53 PM | Luzon Grid-08/05/2023 16:35: San Esteban SS 100MVA T02 and San Esteban - Bantay 115kV Line energized at 1632H and 1633H respectively. (Planned Outage) [WEBSMS] | CLUZ
8/5/2023 4:35:15 PM | Luzon Grid-08/05/2023 16:35: San Esteban SS 100MVA T02 and San Esteban - Bantay 115kV Line energized at 1632H and 1633H respectively. (Planned Outage) [WEBSMS] | CLUZ
8/5/2023 4:32:59 PM | Visayas Grid-08/05/2023 16:32: Toledo SS 30 MVA 138/34.5 KV TR1 energized at 1628H. (Planned Outage) [WEBSMS] | CVIS
8/5/2023 4:32:09 PM | Visayas Grid-08/05/2023 16:32: Toledo SS 30 MVA 138/34.5 KV TR1 energized at 1628H. (Planned Outage) [WEBSMS] | CVIS
8/5/2023 3:18:57 PM | Visayas Grid-08/05/2023 15:19: Colon-Calong-calong 138kV Line2 de-energized at 1514H (Planned Outage) [WEBSMS] | CVIS
8/5/2023 3:18:47 PM | Visayas Grid-08/05/2023 15:19: Colon-Calong-calong 138kV Line2 de-energized at 1514H (Planned Outage) [WEBSMS] | CVIS
8/5/2023 2:54:39 PM | Visayas Grid-08/05/2023 14:54: Colon-Calong-calong 138kV Line 1 energized at 1443H (Planned Outage) [WEBSMS] | CVIS
8/5/2023 2:54:05 PM | Visayas Grid-08/05/2023 14:54: Colon-Calong-calong 138kV Line 1 energized at 1443H (Planned Outage) [WEBSMS] | CVIS
8/5/2023 1:58:59 PM | Mindanao Grid-08/05/2023 14:00: Minergy Coal Power Plant (MCC-Balingasag) Unit 1 cut-in at 1142H back to the Mindanao Grid from Unplanned Outage. Follow aggregated RTD. [WEBSMS] | CMIN
8/5/2023 12:50:46 PM | [NSO Update] Mindanao Grid-08/05/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3276MW, PK=2030MW, RR=20MW, NetOpMargin: PM=1226, EVE=1203 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/5/2023 12:50:18 PM | [NSO Update] Visayas Grid-08/05/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2590MW, PK=2046MW, RR=40MW, NetOpMargin: PM=503, EVE=318 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, TGPP @80.3MW, LEYTE A @350MW [WEBSMS] | CVIS
8/5/2023 12:49:09 PM | [NSO Update] Luzon Grid-08/05/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13116MW, PK=10122MW, RR=260MW, NetOpMargin: PM=2735, EVE=2710 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC2 @310MW, PBL1 @300MW [WEBSMS] | CLUZ
8/5/2023 12:48:32 PM | [NSO Update] Visayas Grid-08/05/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2590MW, PK=2046MW, RR=40MW, NetOpMargin: PM=503, EVE=318 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, TGPP @80.3MW, LEYTE A @350MW [WEBSMS] | CVIS
8/5/2023 12:46:36 PM | [NSO Update] Luzon Grid-08/05/2023 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13116MW, PK=10122MW, RR=260MW, NetOpMargin: PM=2735, EVE=2710 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC2 @310MW, PBL1 @300MW [WEBSMS] | CLUZ
8/5/2023 11:04:57 AM | Mindanao Grid-08/05/2023 11:06: Minergy Coal (MCC) Unit no. 1 tripped with 5.12 MW at 1039H. (Unplanned Outage) [WEBSMS] | CMIN
8/5/2023 11:04:26 AM | Mindanao Grid-08/05/2023 11:06: Minergy Coal (MCC) Unit no. 1 tripped with 5.12 MW at 1039H. (Unplanned Outage) [WEBSMS] | CMIN
8/5/2023 11:02:27 AM | Mindanao Grid-08/05/2023 11:03: Minergy Coal (MCC) Unit 1 synchronize at 1020H. Follow aggregated RTD. [WEBSMS] | CMIN
8/5/2023 11:01:42 AM | Mindanao Grid-08/05/2023 11:03: Minergy Coal (MCC) Unit 1 synchronize at 1020H. Follow aggregated RTD. [WEBSMS] | CMIN
8/5/2023 10:49:25 AM | Mindanao Grid-08/05/2023 10:50: WMPC DG09 cut-in at 0955H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/5/2023 10:49:17 AM | Mindanao Grid-08/05/2023 10:50: WMPC DG09 cut-in at 0955H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/5/2023 9:55:44 AM | Luzon Grid-08/05/2023 09:47: Gumaca - Lumban 230kV L2 auto-tripped/auto-reclosed successfully at both at 0941H. (Unplanned Outage) [WEBSMS] | CLUZ
8/5/2023 9:46:58 AM | Luzon Grid-08/05/2023 09:47: Gumaca - Lumban 230kV L2 auto-tripped/auto-reclosed successfully at both at 0941H. (Unplanned Outage) [WEBSMS] | CLUZ
8/5/2023 7:45:42 AM | Luzon Grid-08/05/2023 07:40: Las Pinas (Zapote) SS 300MVA T03 de-energized at 0738H. (Planned Outage) [WEBSMS] | CLUZ
8/5/2023 7:45:41 AM | Luzon Grid-08/05/2023 07:40: San Juan(Kalayaan)-Calauan 230kV Line 2 New Main Protection commissioned at 0737H. (End of Commissioning). [WEBSMS] | CLUZ
8/5/2023 7:40:53 AM | Luzon Grid-08/05/2023 07:40: Las Pinas (Zapote) SS 300MVA T03 de-energized at 0738H. (Planned Outage) [WEBSMS] | CLUZ
8/5/2023 7:40:02 AM | Luzon Grid-08/05/2023 07:40: San Juan(Kalayaan)-Calauan 230kV Line 2 New Main Protection commissioned at 0737H. (End of Commissioning). [WEBSMS] | CLUZ
8/5/2023 7:32:38 AM | Luzon Grid-08/05/2023 07:31: Correction: Calauan SS 230kV Bus 1 and San Juan(Kalayaan)-Calauan 230kV Line 2 restored at 0717H and 0727H respectively. (On-going commissioning) [WEBSMS] | CLUZ
8/5/2023 7:30:56 AM | Luzon Grid-08/05/2023 07:31: Correction: Calauan SS 230kV Bus 1 and San Juan(Kalayaan)-Calauan 230kV Line 2 restored at 0717H and 0727H respectively. (On-going commissioning) [WEBSMS] | CLUZ
8/5/2023 7:29:45 AM | Luzon Grid-08/05/2023 07:29: Calauan SS 230kV Bus 1 and San Juan(Kalayaan)-Calauan 230kV Line 2 restored at 0721H and 0727H respectively. (On-going commissioning) [WEBSMS] | CLUZ
8/5/2023 7:25:41 AM | Luzon Grid-08/05/2023 07:25: Limay Unit 5 Main Transformer de-energized at 0724H. (Planned Outage) [WEBSMS] | CLUZ
8/5/2023 7:25:39 AM | Luzon Grid-08/05/2023 07:25: Limay Unit 5 Main Transformer de-energized at 0724H. (Planned Outage) [WEBSMS] | CLUZ
8/5/2023 7:22:21 AM | Luzon Grid-08/05/2023 07:13: Nagsaag-San Jose 500kV Line 2 de-energized at 0713H. (Planned Outage) [WEBSMS] | CLUZ
8/5/2023 7:13:44 AM | Luzon Grid-08/05/2023 07:13: Nagsaag-San Jose 500kV Line 2 de-energized at 0713H. (Planned Outage) [WEBSMS] | CLUZ
8/5/2023 6:26:56 AM | Visayas Grid-08/05/2023 06:27: Toledo SS 30 MVA 138/34.5 KV TR1 de-energized at 0625H. (Planned Outage) [WEBSMS] | CVIS
8/5/2023 6:26:15 AM | Visayas Grid-08/05/2023 06:27: Toledo SS 30 MVA 138/34.5 KV TR1 de-energized at 0625H. (Planned Outage) [WEBSMS] | CVIS
8/5/2023 6:14:01 AM | [NSO Update] Mindanao Grid-08/05/2023 06:13: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3343MW, PK=1932MW, RR=20MW, NetOpMargin: AM=1391, PM=1273, EVE=1187 Highest Unit O/L: GNPK 1&4 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/5/2023 6:12:06 AM | [NSO Update] Mindanao Grid-08/05/2023 06:13: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3343MW, PK=1932MW, RR=20MW, NetOpMargin: AM=1391, PM=1273, EVE=1187 Highest Unit O/L: GNPK 1&4 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/5/2023 6:10:47 AM | [NSO Update] Visayas Grid-08/05/2023 06:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2455MW, PK=1967MW, RR=40MW, NetOpMargin: AM=448, PM=309, EVE=292 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @350MW, TPC-Carmen @30MW, TGPP @80.3MW [WEBSMS] | CVIS
8/5/2023 6:09:00 AM | Luzon Grid-08/05/2023 06:08: San Esteban SS 100MVA T02 de-energized at 0607H. (Planned Outage) [WEBSMS] | CLUZ
8/5/2023 6:08:59 AM | [NSO Update] Luzon Grid-08/05/2023 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12827MW, PK=9886MW, RR=260MW, NetOpMargin: AM=2680, PM=2378, EVE=2403 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC2 @130MW, GMEC 1 @150MW, MSLC2 @200MW, PBL1 @300MW, SCPC 4 @100MW, [WEBSMS] | CLUZ
8/5/2023 6:08:31 AM | Luzon Grid-08/05/2023 06:08: San Esteban SS 100MVA T02 de-energized at 0607H. (Planned Outage) [WEBSMS] | CLUZ
8/5/2023 6:08:10 AM | [NSO Update] Visayas Grid-08/05/2023 06:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2455MW, PK=1967MW, RR=40MW, NetOpMargin: AM=448, PM=309, EVE=292 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @350MW, TPC-Carmen @30MW, TGPP @80.3MW [WEBSMS] | CVIS
8/5/2023 6:05:15 AM | Luzon Grid-08/05/2023 06:05: San Esteban - Bantay 115kV Line de-energized at 0604H (Planned Outage) [WEBSMS] | CLUZ
8/5/2023 6:04:45 AM | [NSO Update] Luzon Grid-08/05/2023 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12827MW, PK=9886MW, RR=260MW, NetOpMargin: AM=2680, PM=2378, EVE=2403 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC2 @130MW, GMEC 1 @150MW, MSLC2 @200MW, PBL1 @300MW, SCPC 4 @100MW, [WEBSMS] | CLUZ
8/5/2023 5:24:12 AM | Visayas Grid-08/05/2023 05:23: Colon-Calong-calong 138kV Line 1 de-energized at 0519H (Planned Outage) [WEBSMS] | CVIS
8/5/2023 5:23:22 AM | Visayas Grid-08/05/2023 05:23: Colon-Calong-calong 138kV Line 1 de-energized at 0519H (Planned Outage) [WEBSMS] | CVIS
8/5/2023 4:18:40 AM | [NSO Update] Luzon Grid-08/05/2023 04:12: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CLUZ
8/5/2023 4:12:38 AM | [NSO Update] Luzon Grid-08/05/2023 04:12: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CLUZ
8/5/2023 4:09:24 AM | [NSO Update] Mindanao Grid-08/05/2023 04:10: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CMIN
8/5/2023 4:08:41 AM | [NSO Update] Mindanao Grid-08/05/2023 04:10: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CMIN
8/5/2023 4:07:02 AM | [NSO Update] Visayas Grid-08/05/2023 04:06: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CVIS
8/5/2023 4:06:43 AM | [NSO Update] Visayas Grid-08/05/2023 04:06: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CVIS
8/5/2023 1:01:52 AM | Luzon Grid-08/05/2023 00:57: Pagbilao Unit 2 shutdown at 0056H (Planned Outage) [WEBSMS] | CLUZ
8/5/2023 12:57:19 AM | Luzon Grid-08/05/2023 00:57: Pagbilao Unit 2 shutdown at 0056H (Planned Outage) [WEBSMS] | CLUZ
8/4/2023 11:38:43 PM | Luzon Grid-08/04/2023 23:38: San Juan(Kalayaan)-Calauan 230kV Line 2 and Calauan SS 230kV Bus 1 de-energized at 2337H (Planned Outage) [WEBSMS] | CLUZ
8/4/2023 11:38:30 PM | Luzon Grid-08/04/2023 23:38: San Juan(Kalayaan)-Calauan 230kV Line 2 and Calauan SS 230kV Bus 1 de-energized at 2337H (Planned Outage) [WEBSMS] | CLUZ
8/4/2023 10:26:48 PM | Mindanao Grid-08/04/2023 22:24: PG4 U1 online at 2204H. Unplanned outage. [WEBSMS] | CMIN
8/4/2023 10:23:01 PM | Mindanao Grid-08/04/2023 22:24: PG4 U1 online at 2204H. Unplanned outage. [WEBSMS] | CMIN
8/4/2023 9:04:35 PM | [NSO Update] Mindanao Grid-08/04/2023 21:02: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2059H with power going to Visayas (MVIP Test) [WEBSMS] | CMIN
8/4/2023 9:01:23 PM | [NSO Update] Mindanao Grid-08/04/2023 21:02: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2059H with power going to Visayas (MVIP Test) [WEBSMS] | CMIN
8/4/2023 8:59:58 PM | [NSO Update] Visayas Grid-08/04/2023 21:00: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 2059H with power going to Visayas (MVIP Test) [WEBSMS] | CVIS
8/4/2023 8:56:09 PM | Mindanao Grid-08/04/2023 20:57: Pulangi Unit #1 online at 2052H. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 8:55:28 PM | Mindanao Grid-08/04/2023 20:57: Pulangi Unit #1 online at 2052H. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 8:16:59 PM | Mindanao Grid-08/04/2023 20:18: Pulangi Unit #1 on emergency shutdown at 2004H. Generation Loss=20MW. (Unplanned outage) [WEBSMS] | CMIN
8/4/2023 8:16:14 PM | Mindanao Grid-08/04/2023 20:18: Pulangi Unit #1 on emergency shutdown at 2004H. Generation Loss=20MW. (Unplanned outage) [WEBSMS] | CMIN
8/4/2023 7:57:52 PM | Luzon Grid-08/04/2023 19:57: Bay PCB 8-01CB24BYZ restored at 1957H (Unplanned Outage) [WEBSMS] | CLUZ
8/4/2023 7:57:36 PM | Luzon Grid-08/04/2023 19:57: Bay PCB 8-01CB24BYZ restored at 1957H (Unplanned Outage) [WEBSMS] | CLUZ
8/4/2023 7:08:45 PM | Mindanao Grid-08/04/2023 19:08: Pulangi Unit #3 online at 1855H. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 7:06:41 PM | Mindanao Grid-08/04/2023 19:08: Pulangi Unit #3 online at 1855H. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 6:55:28 PM | [NSO Update] Mindanao Grid-08/04/2023 18:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3231MW, PK=2322MW, RR=20MW, NetOpMargin: EVE=888 Highest Unit O/L: GNPK 1&4 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 85MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @50MW [WEBSMS] | CMIN
8/4/2023 6:50:36 PM | [NSO Update] Visayas Grid-08/04/2023 18:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2486MW, PK=2240MW, RR=40MW, NetOpMargin: EVE=206 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 80.3MW, Leyte A @ 348MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/4/2023 6:49:31 PM | [NSO Update] Visayas Grid-08/04/2023 18:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2486MW, PK=2240MW, RR=40MW, NetOpMargin: EVE=206 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 80.3MW, Leyte A @ 348MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/4/2023 6:45:07 PM | Mindanao Grid-08/04/2023 18:46: TM2 Unit #2 shutdown at 1732H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 6:44:36 PM | Luzon Grid-08/04/2023 18:44: Bay PCB 8-01CB24BYZ de-energized at 1842H (Unplanned Outage) [WEBSMS] | CLUZ
8/4/2023 6:44:32 PM | Mindanao Grid-08/04/2023 18:46: TM2 Unit #2 shutdown at 1732H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 6:44:31 PM | Luzon Grid-08/04/2023 18:44: Bay PCB 8-01CB24BYZ de-energized at 1842H (Unplanned Outage) [WEBSMS] | CLUZ
8/4/2023 6:43:06 PM | [NSO Update] Luzon Grid-08/04/2023 18:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12967MW, PK=10083MW, RR=170MW, NetOpMargin: EVE=10083 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC1 @220MW, CLC2 @150MW, MSLC2 @200MW [WEBSMS] | CLUZ
8/4/2023 6:41:12 PM | Mindanao Grid-08/04/2023 18:42: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) with Power Reference=175MW auto-blocked at 1728H with power going to Visayas (Forward Power Direction/MVIP Test). Unplanned Outage. [WEBSMS] | CMIN
8/4/2023 6:40:26 PM | Mindanao Grid-08/04/2023 18:42: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) with Power Reference=175MW auto-blocked at 1728H with power going to Visayas (Forward Power Direction/MVIP Test). Unplanned Outage. [WEBSMS] | CMIN
8/4/2023 6:31:20 PM | Mindanao Grid-08/04/2023 18:32: Pulangi Unit #1 online at 1803H. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 6:31:12 PM | Mindanao Grid-08/04/2023 18:32: Pulangi Unit #1 online at 1803H. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 6:30:25 PM | Mindanao Grid-08/04/2023 18:30: Pulangi Unit #1 Tripped at 1741H. Generation Loss=22MW. Indication: Over Frequency. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 6:28:42 PM | Mindanao Grid-08/04/2023 18:30: Pulangi Unit #1 Tripped at 1741H. Generation Loss=22MW. Indication: Over Frequency. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 6:26:16 PM | Mindanao Grid-08/04/2023 18:27: Pulangi Unit #3 Tripped at 1730H. Generation Loss=25MW. Indication: Over Frequency. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 6:26:11 PM | Mindanao Grid-08/04/2023 18:27: Pulangi Unit #3 Tripped at 1730H. Generation Loss=25MW. Indication: Over Frequency. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 5:37:52 PM | [NSO Update] Visayas Grid-08/04/2023 17:36: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) auto-blocked at 1728H with power going to Visayas (MVIP Test) [WEBSMS] | CVIS
8/4/2023 5:37:49 PM | [NSO Update] Mindanao Grid-08/04/2023 17:38: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) auto-blocked at 1728H with power going to Visayas (MVIP Test) [WEBSMS] | CMIN
8/4/2023 5:36:48 PM | [NSO Update] Mindanao Grid-08/04/2023 17:38: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) auto-blocked at 1728H with power going to Visayas (MVIP Test) [WEBSMS] | CMIN
8/4/2023 5:36:03 PM | [NSO Update] Visayas Grid-08/04/2023 17:36: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) auto-blocked at 1728H with power going to Visayas (MVIP Test) [WEBSMS] | CVIS
8/4/2023 5:12:49 PM | Mindanao Grid-08/04/2023 17:13: TM1 Unit #2 shutdown at 1706H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 5:12:48 PM | Mindanao Grid-08/04/2023 17:11: TM2 Unit #1 shutdown at 1700H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 5:11:44 PM | Mindanao Grid-08/04/2023 17:13: TM1 Unit #2 shutdown at 1706H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 5:10:24 PM | Mindanao Grid-08/04/2023 17:11: TM2 Unit #1 shutdown at 1700H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 4:54:29 PM | [NSO Update] Mindanao Grid-08/04/2023 16:52: MO Initiated Market Intervention has been lifted today 04 August 2023 at 1645H for Luzon and Visayas and Mindanao. Market will resume starting interval 1650H. [WEBSMS] | CMIN
8/4/2023 4:54:27 PM | [NSO Update] Luzon Grid-08/04/2023 16:49: MO Initiated Market Intervention has been lifted today 04 August 2023 at 1645H for Luzon and Visayas and Mindanao. Market will resume starting interval 1650H. [WEBSMS] | CLUZ
8/4/2023 4:51:23 PM | [NSO Update] Mindanao Grid-08/04/2023 16:52: MO Initiated Market Intervention has been lifted today 04 August 2023 at 1645H for Luzon and Visayas and Mindanao. Market will resume starting interval 1650H. [WEBSMS] | CMIN
8/4/2023 4:50:41 PM | [NSO Update] Visayas Grid-08/04/2023 16:50: MO Initiated Market Intervention has been lifted today 04 August 2023 at 1645H for Luzon and Visayas and Mindanao. Market will resume starting interval 1650H. [WEBSMS] | CVIS
8/4/2023 4:49:14 PM | [NSO Update] Luzon Grid-08/04/2023 16:49: MO Initiated Market Intervention has been lifted today 04 August 2023 at 1645H for Luzon and Visayas and Mindanao. Market will resume starting interval 1650H. [WEBSMS] | CLUZ
8/4/2023 4:15:22 PM | [NSO Update] Mindanao Grid-08/04/2023 16:15: MO Initiated Market Intervention is issued today 04 August 2023 for Luzon, Visayas and Mindanao starting interval 1605H due to Publication error. [WEBSMS] | CMIN
8/4/2023 4:15:21 PM | [NSO Update] Luzon Grid-08/04/2023 16:12: MO Initiated Market Intervention is issued today 04 August 2023 for Luzon, Visayas and Mindanao starting interval 1605H due to Publication error. [WEBSMS] | CLUZ
8/4/2023 4:14:34 PM | [NSO Update] Mindanao Grid-08/04/2023 16:15: MO Initiated Market Intervention is issued today 04 August 2023 for Luzon, Visayas and Mindanao starting interval 1605H due to Publication error. [WEBSMS] | CMIN
8/4/2023 4:14:14 PM | [NSO Update] Visayas Grid-08/04/2023 16:14: MO Initiated Market Intervention is issued today 04 August 2023 for Luzon, Visayas and Mindanao starting interval 1605H due to Publication error. [WEBSMS] | CVIS
8/4/2023 4:14:12 PM | [NSO Update] Visayas Grid-08/04/2023 16:14: MO Initiated Market Intervention is issued today 04 August 2023 for Luzon, Visayas and Mindanao starting interval 1605H due to Publication error. [WEBSMS] | CVIS
8/4/2023 4:13:58 PM | [NSO Update] Visayas Grid-08/04/2023 16:14: MO Initiated Market Intervention is issued today 04 August 2023 for Luzon, Visayas and Mindanao starting interval 1605H due to Publication error. [WEBSMS] | CVIS
8/4/2023 4:12:51 PM | [NSO Update] Luzon Grid-08/04/2023 16:12: MO Initiated Market Intervention is issued today 04 August 2023 for Luzon, Visayas and Mindanao starting interval 1605H due to Publication error. [WEBSMS] | CLUZ
8/4/2023 3:55:32 PM | Mindanao Grid-08/04/2023 15:56: WMPC DG05 Shutdown at 1538H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 3:32:01 PM | Mindanao Grid-08/04/2023 15:32: TM2 Unit #1 online at 1511H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 3:31:28 PM | Mindanao Grid-08/04/2023 15:32: TM2 Unit #1 online at 1511H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 1:56:01 PM | Mindanao Grid-08/04/2023 13:57: WMPC DG05 Online at 1353H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 1:55:47 PM | Mindanao Grid-08/04/2023 13:57: WMPC DG05 Online at 1353H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 1:52:36 PM | Mindanao Grid-08/04/2023 13:53: TM1 Unit #2 online at 1345H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 12:57:37 PM | [NSO Update] Luzon Grid-08/04/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13499MW, PK=10475MW, RR=260MW, NetOpMargin: PM=2764, EVE=2909 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 220MW, Calaca 2 @ 150MW, Masinloc 1 @ 325MW, Masinloc 2 @ 200MW [WEBSMS] | CLUZ
8/4/2023 12:55:06 PM | [NSO Update] Luzon Grid-08/04/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13499MW, PK=10475MW, RR=260MW, NetOpMargin: PM=2764, EVE=2909 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 220MW, Calaca 2 @ 150MW, Masinloc 1 @ 325MW, Masinloc 2 @ 200MW [WEBSMS] | CLUZ
8/4/2023 12:54:14 PM | [NSO Update] Visayas Grid-08/04/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2501MW, PK=2263MW, RR=40MW, NetOpMargin: PM=197, EVE=176 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 80.3MW, Leyte A @ 342MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/4/2023 12:53:43 PM | [NSO Update] Visayas Grid-08/04/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2501MW, PK=2263MW, RR=40MW, NetOpMargin: PM=197, EVE=176 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 80.3MW, Leyte A @ 342MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/4/2023 12:53:41 PM | [NSO Update] Visayas Grid-08/04/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2501MW, PK=2263MW, RR=40MW, NetOpMargin: PM=197, EVE=176 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TGPP @ 80.3MW, Leyte A @ 342MW, PGPP1 @ 75MW [WEBSMS] | CVIS
8/4/2023 12:53:39 PM | [NSO Update] Mindanao Grid-08/04/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3321MW, PK=2241MW, RR=20MW, NetOpMargin: PM=1060, EVE=1123 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @85MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/4/2023 12:53:30 PM | [NSO Update] Mindanao Grid-08/04/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3321MW, PK=2241MW, RR=20MW, NetOpMargin: PM=1060, EVE=1123 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @85MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/4/2023 11:37:15 AM | Mindanao Grid-08/04/2023 11:38: TM2 Unit #2 Online at 1125H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 11:36:58 AM | Mindanao Grid-08/04/2023 11:38: TM2 Unit #2 Online at 1125H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 10:57:35 AM | Mindanao Grid-08/04/2023 10:57: TM1 Unit1 Online at 1037H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 10:56:14 AM | Mindanao Grid-08/04/2023 10:57: TM1 Unit1 Online at 1037H. Follow RTD. [WEBSMS] | CMIN
8/4/2023 10:18:23 AM | Visayas Grid-08/04/2023 10:18: Colon - KSPC 138 kV Line 1 de-energized at 1016H. (Planned Outage) [WEBSMS] | CVIS
8/4/2023 10:18:21 AM | Visayas Grid-08/04/2023 10:18: Colon - KSPC 138 kV Line 1 de-energized at 1016H. (Planned Outage) [WEBSMS] | CVIS
8/4/2023 10:18:00 AM | Visayas Grid-08/04/2023 10:18: Colon - KSPC 138 kV Line 1 de-energized at 1016H. (Planned Outage) [WEBSMS] | CVIS
8/4/2023 10:05:00 AM | Mindanao Grid-08/04/2023 10:06: Nagamin SS Transformer No.2 energized/restored at 0932H. Unplanned Outage. [WEBSMS] | CMIN
8/4/2023 9:20:50 AM | Mindanao Grid-08/04/2023 09:19: Nagamin-Zamboanga 138kV L1 energized/restored at 0854H. Unplanned Outage. [WEBSMS] | CMIN
8/4/2023 9:17:53 AM | Mindanao Grid-08/04/2023 09:19: Nagamin-Zamboanga 138kV L1 energized/restored at 0854H. Unplanned Outage. [WEBSMS] | CMIN
8/4/2023 9:15:51 AM | Mindanao Grid-08/04/2023 09:16: Nagamin-Zamboanga 138kV L1 tripped again at 0831H. Simultaneously with Nagamin SS Transformer No.2 Unplanned Outage. [WEBSMS] | CMIN
8/4/2023 9:15:50 AM | Mindanao Grid-08/04/2023 09:14: Nagamin-Zamboanga 138kV L1 tripped at 0829H but autoreclosed. Unplanned Outage. [WEBSMS] | CMIN
8/4/2023 9:15:07 AM | Mindanao Grid-08/04/2023 09:16: Nagamin-Zamboanga 138kV L1 tripped again at 0831H. Simultaneously with Nagamin SS Transformer No.2 Unplanned Outage. [WEBSMS] | CMIN
8/4/2023 9:13:01 AM | Mindanao Grid-08/04/2023 09:14: Nagamin-Zamboanga 138kV L1 tripped at 0829H but autoreclosed. Unplanned Outage. [WEBSMS] | CMIN
8/4/2023 8:27:49 AM | Mindanao Grid-08/04/2023 08:29: Agus 2 Unit #3 on emergency shutdown at 0807H. due to Flush Over of Main Disconnection Switch. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 8:27:29 AM | Mindanao Grid-08/04/2023 08:29: Agus 2 Unit #3 on emergency shutdown at 0807H. due to Flush Over of Main Disconnection Switch. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 5:54:02 AM | [NSO Update] Luzon Grid-08/04/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13550MW, PK=10356MW, RR=260MW, NetOpMargin: AM=2934, PM=2955, EVE=3215 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 1 @220MW, CALACA 2 @150MW, MASINLOC 1 @ 325MW, MASINLOC 2 @200MW [WEBSMS] | CLUZ
8/4/2023 5:42:22 AM | [NSO Update] Visayas Grid-08/04/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2713MW, PK=2285MW, RR=40MW, NetOpMargin: AM=388, PM=379, EVE=284 Highest Unit O/L: THVI 1& 2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @342MW, TPC-Carmen @30MW, TGPP @80.3MW [WEBSMS] | CVIS
8/4/2023 5:40:05 AM | [NSO Update] Visayas Grid-08/04/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2713MW, PK=2285MW, RR=40MW, NetOpMargin: AM=388, PM=379, EVE=284 Highest Unit O/L: THVI 1& 2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @342MW, TPC-Carmen @30MW, TGPP @80.3MW [WEBSMS] | CVIS
8/4/2023 5:34:03 AM | [NSO Update] Mindanao Grid-08/04/2023 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3354MW, PK=2167MW, RR=20MW, NetOpMargin: AM=1167, PM=1101, EVE=1143 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/4/2023 5:33:23 AM | [NSO Update] Mindanao Grid-08/04/2023 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3354MW, PK=2167MW, RR=20MW, NetOpMargin: AM=1167, PM=1101, EVE=1143 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @110MW, AG4 @136MW, AG5 @44MW, AG6 @149MW, AG7 @38MW, PG4 @80MW [WEBSMS] | CMIN
8/4/2023 5:17:26 AM | Mindanao Grid-08/04/2023 05:18: (Correction): FDC U1 online at 0506H. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 5:16:47 AM | Mindanao Grid-08/04/2023 05:18: (Correction): FDC U1 online at 0506H. (Unplanned Outage) [WEBSMS] | CMIN
8/4/2023 5:12:03 AM | Mindanao Grid-08/04/2023 05:13: FDC U1 online at 0405H. (Unplanned Outage). [WEBSMS] | CMIN
8/4/2023 5:11:47 AM | Mindanao Grid-08/04/2023 05:13: FDC U1 online at 0405H. (Unplanned Outage). [WEBSMS] | CMIN
8/4/2023 5:00:40 AM | Luzon Grid-08/04/2023 05:00: SCPC U3 shutdown at 0458H (Unplanned Outage) [WEBSMS] | CLUZ
8/4/2023 5:00:00 AM | Luzon Grid-08/04/2023 05:00: SCPC U3 shutdown at 0458H (Unplanned Outage) [WEBSMS] | CLUZ
8/4/2023 4:10:21 AM | [NSO Update] Visayas Grid-08/04/2023 04:08: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CVIS
8/4/2023 4:08:55 AM | [NSO Update] Mindanao Grid-08/04/2023 04:10: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CMIN
8/4/2023 4:08:33 AM | [NSO Update] Visayas Grid-08/04/2023 04:08: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CVIS
8/4/2023 4:08:26 AM | [NSO Update] Mindanao Grid-08/04/2023 04:10: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CMIN
8/4/2023 4:08:07 AM | [NSO Update] Luzon Grid-08/04/2023 04:08: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CLUZ
8/4/2023 4:07:18 AM | [NSO Update] Luzon Grid-08/04/2023 04:08: Weather Update: Southwest Monsoon affecting Luzon. [WEBSMS] | CLUZ
8/4/2023 3:01:00 AM | Mindanao Grid-08/04/2023 03:02: Affected ALD feeders of CEPALCO, DLPC and NGCP restored at 0240H, 0256H and 0257H respectively [WEBSMS] | CMIN
8/4/2023 3:00:37 AM | Mindanao Grid-08/04/2023 03:02: Affected ALD feeders of CEPALCO, DLPC and NGCP restored at 0240H, 0256H and 0257H respectively [WEBSMS] | CMIN
8/4/2023 2:55:36 AM | Mindanao Grid-08/04/2023 02:55: ALD occurred at NGCP, DLPC and CEPALCO feeders at 0234H due to tripping of FDC U1 at 66.5MW. Lowest frequency is 59.11Hz. [WEBSMS] | CMIN
8/4/2023 2:54:19 AM | Mindanao Grid-08/04/2023 02:55: ALD occurred at NGCP, DLPC and CEPALCO feeders at 0234H due to tripping of FDC U1 at 66.5MW. Lowest frequency is 59.11Hz. [WEBSMS] | CMIN
8/4/2023 12:50:31 AM | Luzon Grid-08/04/2023 00:50: NGCP and Meralco ALD-affected feeders were restored at 0040H and 0042H respectively. [WEBSMS] | CLUZ
8/4/2023 12:49:59 AM | Luzon Grid-08/04/2023 00:50: NGCP and Meralco ALD-affected feeders were restored at 0040H and 0042H respectively. [WEBSMS] | CLUZ
8/4/2023 12:42:58 AM | Luzon Grid-08/04/2023 00:42: ALD occurred at NGCP and Meralco feeders at 0032H due to the tripping of Ilijan A(340MW) and Ilijan B(165MW). The lowest system frequency is 58.999Hz. [WEBSMS] | CLUZ
8/3/2023 11:13:50 PM | Mindanao Grid-08/03/2023 23:13: GNPK U4 online at 2305H. (Unplanned outage). [WEBSMS] | CMIN
8/3/2023 11:11:42 PM | Mindanao Grid-08/03/2023 23:13: GNPK U4 online at 2305H. (Unplanned outage). [WEBSMS] | CMIN
8/3/2023 10:07:37 PM | Mindanao Grid-08/03/2023 22:06: Emergency shutdown of GNPK Unit #4 at 2156H to facilitate Resetting of Closed Main Stop Valve . (Unplanned Outage). [WEBSMS] | CMIN
8/3/2023 10:04:56 PM | Mindanao Grid-08/03/2023 22:06: Emergency shutdown of GNPK Unit #4 at 2156H to facilitate Resetting of Closed Main Stop Valve . (Unplanned Outage). [WEBSMS] | CMIN
8/3/2023 5:51:02 PM | Mindanao Grid-08/03/2023 17:50: Mt. Apo Unit #3 cut-in at 1535H. Unplanned Outage [WEBSMS] | CMIN
8/3/2023 5:49:22 PM | Mindanao Grid-08/03/2023 17:50: Mt. Apo Unit #3 cut-in at 1535H. Unplanned Outage [WEBSMS] | CMIN
8/3/2023 5:46:59 PM | [NSO Update] Mindanao Grid-08/03/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3215MW, PK=2181MW, RR=20MW, NetOpMargin: EVE=1014 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @115MW, AG4 @140MW, AG5 @47MW, AG6 @149MW, AG7 @39MW, PG4 @80MW [WEBSMS] | CMIN
8/3/2023 5:46:58 PM | [NSO Update] Luzon Grid-08/03/2023 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14108MW, PK=9629MW, RR=170MW, NetOpMargin: EVE=4309 Highest Unit O/L: GNPD 1 & 2 @668MW Derated Plant: Calaca 2 @ 150MW, Masinloc 2 @ 200MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
8/3/2023 5:46:33 PM | [NSO Update] Mindanao Grid-08/03/2023 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3215MW, PK=2181MW, RR=20MW, NetOpMargin: EVE=1014 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @115MW, AG4 @140MW, AG5 @47MW, AG6 @149MW, AG7 @39MW, PG4 @80MW [WEBSMS] | CMIN
8/3/2023 5:44:49 PM | [NSO Update] Visayas Grid-08/03/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2501MW, PK=2147MW, RR=40MW, NetOpMargin: EVE=314 Highest Unit O/L: THVI 1& 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 320MW, PDPP3-G @ 10MW, PDPP3-H @ 8MW [WEBSMS] | CVIS
8/3/2023 5:43:51 PM | [NSO Update] Visayas Grid-08/03/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2501MW, PK=2147MW, RR=40MW, NetOpMargin: EVE=314 Highest Unit O/L: THVI 1& 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 320MW, PDPP3-G @ 10MW, PDPP3-H @ 8MW [WEBSMS] | CVIS
8/3/2023 5:40:16 PM | [NSO Update] Luzon Grid-08/03/2023 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=14108MW, PK=9629MW, RR=170MW, NetOpMargin: EVE=4309 Highest Unit O/L: GNPD 1 & 2 @668MW Derated Plant: Calaca 2 @ 150MW, Masinloc 2 @ 200MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
8/3/2023 5:28:46 PM | [NSO Update] Visayas Grid-08/03/2023 17:27: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1723H with power going to Visayas. [WEBSMS] | CVIS
8/3/2023 5:27:48 PM | [NSO Update] Mindanao Grid-08/03/2023 17:29: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1723H with power going to Visayas. [WEBSMS] | CMIN
8/3/2023 5:27:32 PM | [NSO Update] Visayas Grid-08/03/2023 17:27: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1723H with power going to Visayas. [WEBSMS] | CVIS
8/3/2023 5:26:59 PM | [NSO Update] Mindanao Grid-08/03/2023 17:29: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1723H with power going to Visayas. [WEBSMS] | CMIN
8/3/2023 4:10:29 PM | Mindanao Grid-08/03/2023 16:11: TM2 Unit #2 cut-out at 1508H. Follow RTD. [WEBSMS] | CMIN
8/3/2023 4:10:16 PM | Mindanao Grid-08/03/2023 16:11: TM2 Unit #2 cut-out at 1508H. Follow RTD. [WEBSMS] | CMIN
8/3/2023 3:40:09 PM | [NSO Update] Visayas Grid-08/03/2023 15:40: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1539H with power going to Visayas (MVIP Test) [WEBSMS] | CVIS
8/3/2023 3:39:57 PM | [NSO Update] Visayas Grid-08/03/2023 15:40: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1539H with power going to Visayas (MVIP Test) [WEBSMS] | CVIS
8/3/2023 3:39:49 PM | [NSO Update] Mindanao Grid-08/03/2023 15:41: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1539H with power going to Visayas (MVIP Test) [WEBSMS] | CMIN
8/3/2023 2:49:50 PM | Mindanao Grid-08/03/2023 14:51: TM1 Unit #1 cut-out at 1439H. Follow RTD. [WEBSMS] | CMIN
8/3/2023 2:49:19 PM | Mindanao Grid-08/03/2023 14:51: TM1 Unit #1 cut-out at 1439H. Follow RTD. [WEBSMS] | CMIN
8/3/2023 2:24:18 PM | Mindanao Grid-08/03/2023 14:25: TM2 Unit #2 cut-in at 1334H. Follow RTD. [WEBSMS] | CMIN
8/3/2023 2:23:33 PM | Mindanao Grid-08/03/2023 14:25: TM2 Unit #2 cut-in at 1334H. Follow RTD. [WEBSMS] | CMIN
8/3/2023 2:00:03 PM | Mindanao Grid-08/03/2023 14:01: Tagoloan-STEAG 138kV line 2 energized at 1332H. OO07AD / Non-GOMP. [WEBSMS] | CMIN
8/3/2023 1:50:11 PM | Luzon Grid-08/03/2023 13:44: Laoag 115kV Bus A restored at 1344H (Planned Outage) [WEBSMS] | CLUZ
8/3/2023 1:44:55 PM | Luzon Grid-08/03/2023 13:44: Laoag 115kV Bus A restored at 1344H (Planned Outage) [WEBSMS] | CLUZ
8/3/2023 1:21:50 PM | Mindanao Grid-08/03/2023 13:23: TM1 U1 online at 1253H. (Unplanned Outage) [WEBSMS] | CMIN
8/3/2023 1:21:47 PM | Mindanao Grid-08/03/2023 13:23: TM1 U1 online at 1253H. (Unplanned Outage) [WEBSMS] | CMIN
8/3/2023 12:56:45 PM | [NSO Update] Luzon Grid-08/03/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14378MW, PK=10177MW, RR=260MW, NetOpMargin: PM=3941, EVE=4043 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 1 @ 200MW, Calaca 2 @ 130MW, Masinloc 2 @ 200MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
8/3/2023 12:55:53 PM | [NSO Update] Visayas Grid-08/03/2023 12:54: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2830MW, PK=2316MW, RR=40MW, NetOpMargin: PM=474, EVE=317 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, Leyte A @ 310MW, PDPP3-G @ 10MW, PDPP3-H @ 8MW [WEBSMS] | CVIS
8/3/2023 12:55:23 PM | [NSO Update] Mindanao Grid-08/03/2023 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3303MW, PK=2403MW, RR=20MW, NetOpMargin: PM=880, EVE=1048 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @115MW, AG4 @140MW, AG5 @49MW, AG6 @149MW, AG7 @39MW, PG4 @80MW [WEBSMS] | CMIN
8/3/2023 11:01:46 AM | Mindanao Grid-08/03/2023 11:01: WMPC DG1 online 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/3/2023 10:59:47 AM | Mindanao Grid-08/03/2023 11:01: WMPC DG1 online 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/3/2023 10:37:33 AM | [NSO Update] Mindanao Grid-08/03/2023 10:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1034H with power going to Visayas (MVIP Test) [WEBSMS] | CMIN
8/3/2023 10:36:24 AM | [NSO Update] Visayas Grid-08/03/2023 10:35: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1034H with power going to Visayas (MVIP Test) [WEBSMS] | CVIS
8/3/2023 10:36:01 AM | [NSO Update] Mindanao Grid-08/03/2023 10:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1034H with power going to Visayas (MVIP Test) [WEBSMS] | CMIN
8/3/2023 10:35:43 AM | [NSO Update] Visayas Grid-08/03/2023 10:35: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1034H with power going to Visayas (MVIP Test) [WEBSMS] | CVIS
8/3/2023 9:20:02 AM | Mindanao Grid-08/03/2023 09:20: MA3 trip at 0914H. Gen. Loss of 3.2MW. [WEBSMS] | CMIN
8/3/2023 9:18:43 AM | Mindanao Grid-08/03/2023 09:20: MA3 trip at 0914H. Gen. Loss of 3.2MW. [WEBSMS] | CMIN
8/3/2023 9:15:51 AM | Mindanao Grid-08/03/2023 09:16: PG4 U2 cut-out at 0912H. For reserve shutdown due to Low Water Level. [WEBSMS] | CMIN
8/3/2023 9:15:32 AM | Mindanao Grid-08/03/2023 09:16: PG4 U2 cut-out at 0912H. For reserve shutdown due to Low Water Level. [WEBSMS] | CMIN
8/3/2023 9:10:49 AM | Luzon Grid-08/03/2023 09:10: Bay(Makban) PCB 8-02CB24BYZ de-energized at 0908H (Unplanned Outage) [WEBSMS] | CLUZ
8/3/2023 9:10:34 AM | Luzon Grid-08/03/2023 09:10: Bay(Makban) PCB 8-02CB24BYZ de-energized at 0908H (Unplanned Outage) [WEBSMS] | CLUZ
8/3/2023 8:56:40 AM | Mindanao Grid-08/03/2023 08:55: WMPC DG9 cut-in as RPS at 0850H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/3/2023 8:53:47 AM | Mindanao Grid-08/03/2023 08:55: WMPC DG9 cut-in as RPS at 0850H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/3/2023 6:13:15 AM | Luzon Grid-08/03/2023 06:07: Laoag 115kV Bus A de-energized at 0606H (Planned Outage) [WEBSMS] | CLUZ
8/3/2023 6:07:36 AM | Luzon Grid-08/03/2023 06:07: Laoag 115kV Bus A de-energized at 0606H (Planned Outage) [WEBSMS] | CLUZ
8/3/2023 5:48:15 AM | [NSO Update] Mindanao Grid-08/03/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3316MW, PK=2188MW, RR=20MW, NetOpMargin: AM=1108, PM=970, EVE=1093 Highest Unit O/L: GNPK 1&4 Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @115MW, AG4 @140MW, AG5 @49MW, AG6 @149MW, AG7 @39MW, PG4 @80MW [WEBSMS] | CMIN
8/3/2023 5:45:29 AM | [NSO Update] Visayas Grid-08/03/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2755MW, PK=2267MW, RR=40MW, NetOpMargin: AM=448, PM=331, EVE=227 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @320MW [WEBSMS] | CVIS
8/3/2023 5:45:25 AM | [NSO Update] Mindanao Grid-08/03/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3316MW, PK=2188MW, RR=20MW, NetOpMargin: AM=1108, PM=970, EVE=1093 Highest Unit O/L: GNPK 1&4 Derated Plant: MCC @100MW, MPC @40MW, MA1 @47.5MW, MA2 @30MW, AG1 @35MW, AG2 @115MW, AG4 @140MW, AG5 @49MW, AG6 @149MW, AG7 @39MW, PG4 @80MW [WEBSMS] | CMIN
8/3/2023 5:43:14 AM | [NSO Update] Luzon Grid-08/03/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14157MW, PK=9918MW, RR=260MW, NetOpMargin: AM=3979, PM=3720, EVE=3750 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @150MW, MSLC2 @200MW, ILIJAN B @160MW [WEBSMS] | CLUZ
8/3/2023 5:43:07 AM | [NSO Update] Visayas Grid-08/03/2023 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2755MW, PK=2267MW, RR=40MW, NetOpMargin: AM=448, PM=331, EVE=227 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @320MW [WEBSMS] | CVIS
8/3/2023 5:40:48 AM | [NSO Update] Luzon Grid-08/03/2023 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14157MW, PK=9918MW, RR=260MW, NetOpMargin: AM=3979, PM=3720, EVE=3750 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @150MW, MSLC2 @200MW, ILIJAN B @160MW [WEBSMS] | CLUZ
8/3/2023 5:20:51 AM | [NSO Update] Visayas Grid-08/03/2023 05:20: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
8/3/2023 5:20:32 AM | [NSO Update] Luzon Grid-08/03/2023 05:20: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
8/3/2023 5:20:10 AM | [NSO Update] Mindanao Grid-08/03/2023 05:21: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
8/3/2023 5:19:56 AM | [NSO Update] Visayas Grid-08/03/2023 05:20: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
8/3/2023 5:19:54 AM | [NSO Update] Luzon Grid-08/03/2023 05:20: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
8/3/2023 5:19:54 AM | [NSO Update] Mindanao Grid-08/03/2023 05:21: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
8/2/2023 9:23:03 PM | Mindanao Grid-08/02/2023 21:22: WMPC DG9 cut-out as RPS at 2113H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/2/2023 9:21:00 PM | Mindanao Grid-08/02/2023 21:22: WMPC DG9 cut-out as RPS at 2113H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/2/2023 7:25:21 PM | Luzon Grid-08/02/2023 19:25: San Lorenzo Module 60 online at 1920H. (Unplanned Outage) [WEBSMS] | CLUZ
8/2/2023 7:13:01 PM | [NSO Update] Mindanao Grid-08/02/2023 19:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1908H from forward power direction (MVIP Test). [WEBSMS] | CMIN
8/2/2023 7:10:57 PM | [NSO Update] Visayas Grid-08/02/2023 19:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1908H from forward power direction (MVIP Test). [WEBSMS] | CVIS
8/2/2023 7:10:49 PM | [NSO Update] Mindanao Grid-08/02/2023 19:12: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1908H from forward power direction (MVIP Test). [WEBSMS] | CMIN
8/2/2023 7:10:23 PM | [NSO Update] Visayas Grid-08/02/2023 19:10: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1908H from forward power direction (MVIP Test). [WEBSMS] | CVIS
8/2/2023 6:01:15 PM | [NSO Update] Visayas Grid-08/02/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2508MW, PK=2170MW, RR=40MW, NetOpMargin: EVE=298 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @320MW, TPC-Carmen @30MW [WEBSMS] | CVIS
8/2/2023 6:00:39 PM | [NSO Update] Mindanao Grid-08/02/2023 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3261MW, PK=2211MW, RR=20MW, NetOpMargin: EVE=1030 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @115MW, AG4 @140MW, AG5 @49MW, AG6 @149MW, AG7 @38MW, PG4 @90MW [WEBSMS] | CMIN
8/2/2023 6:00:30 PM | [NSO Update] Mindanao Grid-08/02/2023 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3261MW, PK=2211MW, RR=20MW, NetOpMargin: EVE=1030 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @115MW, AG4 @140MW, AG5 @49MW, AG6 @149MW, AG7 @38MW, PG4 @90MW [WEBSMS] | CMIN
8/2/2023 5:59:20 PM | [NSO Update] Visayas Grid-08/02/2023 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2508MW, PK=2170MW, RR=40MW, NetOpMargin: EVE=298 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @320MW, TPC-Carmen @30MW [WEBSMS] | CVIS
8/2/2023 5:56:38 PM | [NSO Update] Luzon Grid-08/02/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13587MW, PK=9415MW, RR=170MW, NetOpMargin: EVE=4002 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @200MW, CLC2 @150MW, MSLC2 @150MW, ILIJAN B @300MW [WEBSMS] | CLUZ
8/2/2023 5:53:04 PM | [NSO Update] Luzon Grid-08/02/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13587MW, PK=9415MW, RR=170MW, NetOpMargin: EVE=4002 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC1 @200MW, CLC2 @150MW, MSLC2 @150MW, ILIJAN B @300MW [WEBSMS] | CLUZ
8/2/2023 5:17:09 PM | Mindanao Grid-08/02/2023 17:16: WMPC DG1 cut-out as RPS at 1713H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/2/2023 5:15:19 PM | Mindanao Grid-08/02/2023 17:16: WMPC DG1 cut-out as RPS at 1713H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/2/2023 3:36:13 PM | Luzon Grid-08/02/2023 15:30: Naga-Tayabas 230kV Line 2 restored at 1530H (Planned Outage) [WEBSMS] | CLUZ
8/2/2023 3:30:34 PM | Luzon Grid-08/02/2023 15:30: Naga-Tayabas 230kV Line 2 restored at 1530H (Planned Outage) [WEBSMS] | CLUZ
8/2/2023 1:03:37 PM | [NSO Update] Mindanao Grid-08/02/2023 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3322MW, PK=2340MW, RR=20MW, NetOpMargin: PM=962, EVE=1049 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @115MW, AG4 @140MW, AG5 @49MW, AG6 @149MW, AG7 @38MW, PG4 @90MW [WEBSMS] | CMIN
8/2/2023 12:58:48 PM | [NSO Update] Visayas Grid-08/02/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2763MW, PK=2317MW, RR=40MW, NetOpMargin: PM=406, EVE=279 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @315MW [WEBSMS] | CVIS
8/2/2023 12:57:02 PM | [NSO Update] Visayas Grid-08/02/2023 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2763MW, PK=2317MW, RR=40MW, NetOpMargin: PM=406, EVE=279 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @315MW [WEBSMS] | CVIS
8/2/2023 12:52:49 PM | [NSO Update] Luzon Grid-08/02/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14071MW, PK=9973MW, RR=260MW, NetOpMargin: PM=3837, EVE=4027 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @150MW, MSLC2 @150MW, ILIJAN B @300MW [WEBSMS] | CLUZ
8/2/2023 12:52:41 PM | [NSO Update] Luzon Grid-08/02/2023 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14071MW, PK=9973MW, RR=260MW, NetOpMargin: PM=3837, EVE=4027 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @150MW, MSLC2 @150MW, ILIJAN B @300MW [WEBSMS] | CLUZ
8/2/2023 11:30:23 AM | [NSO Update] Mindanao Grid-08/02/2023 11:31: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1124H with power going to Visayas(MVIP Test). [WEBSMS] | CMIN
8/2/2023 11:26:18 AM | [NSO Update] Visayas Grid-08/02/2023 11:25: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1124H with power going to Visayas(MVIP Test). [WEBSMS] | CVIS
8/2/2023 11:26:16 AM | [NSO Update] Visayas Grid-08/02/2023 11:25: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1124H with power going to Visayas(MVIP Test). [WEBSMS] | CVIS
8/2/2023 11:25:32 AM | [NSO Update] Visayas Grid-08/02/2023 11:25: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1124H with power going to Visayas(MVIP Test). [WEBSMS] | CVIS
8/2/2023 10:51:54 AM | Mindanao Grid-08/02/2023 10:53: WMPC DG1 cut-in as RPS at 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/2/2023 10:03:37 AM | Mindanao Grid-08/02/2023 10:04: NSD online at 1000H Follow RTD. [WEBSMS] | CMIN
8/2/2023 10:02:49 AM | Mindanao Grid-08/02/2023 10:04: NSD online at 1000H Follow RTD. [WEBSMS] | CMIN
8/2/2023 9:39:22 AM | Luzon Grid-08/02/2023 09:38: San Lorenzo Module 60 (161MW) tripped at 0933H. Lowest system frequency is 59.473Hz. [WEBSMS] | CLUZ
8/2/2023 9:37:55 AM | Luzon Grid-08/02/2023 09:38: San Lorenzo Module 60 (161MW) tripped at 0933H. Lowest system frequency is 59.473Hz. [WEBSMS] | CLUZ
8/2/2023 8:52:11 AM | Mindanao Grid-08/02/2023 08:53: WMPC DG9 cut-in as RPS at 0850H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/2/2023 7:29:17 AM | Luzon Grid-08/02/2023 07:21: Tayabas - Naga 230kV L2 de-energized at 0719H (Planned Outage) [WEBSMS] | CLUZ
8/2/2023 7:20:56 AM | Luzon Grid-08/02/2023 07:21: Tayabas - Naga 230kV L2 de-energized at 0719H (Planned Outage) [WEBSMS] | CLUZ
8/2/2023 6:02:35 AM | [NSO Update] Luzon Grid-08/02/2023 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14464MW, PK=10038MW, RR=260MW, NetOpMargin: AM=4165, PM=4114, EVE=4237 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @170MW, MASINLOC 2 @150MW, ILIJAN B @300MW [WEBSMS] | CLUZ
8/2/2023 5:56:02 AM | [NSO Update] Luzon Grid-08/02/2023 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14464MW, PK=10038MW, RR=260MW, NetOpMargin: AM=4165, PM=4114, EVE=4237 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @170MW, MASINLOC 2 @150MW, ILIJAN B @300MW [WEBSMS] | CLUZ
8/2/2023 5:37:46 AM | [NSO Update] Visayas Grid-08/02/2023 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2717MW, PK=2203MW, RR=40MW, NetOpMargin: AM=474, PM=363, EVE=394 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @340MW [WEBSMS] | CVIS
8/2/2023 5:36:15 AM | [NSO Update] Visayas Grid-08/02/2023 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2717MW, PK=2203MW, RR=40MW, NetOpMargin: AM=474, PM=363, EVE=394 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @340MW [WEBSMS] | CVIS
8/2/2023 5:34:15 AM | [NSO Update] Mindanao Grid-08/02/2023 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3332MW, PK=2157MW, RR=20MW, NetOpMargin: AM=1156, PM=1031, EVE=1082 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @115MW, AG4 @140MW, AG5 @49MW, AG6 @149MW, AG7 @38MW, PG4 @90MW [WEBSMS] | CMIN
8/2/2023 5:33:47 AM | [NSO Update] Mindanao Grid-08/02/2023 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3332MW, PK=2157MW, RR=20MW, NetOpMargin: AM=1156, PM=1031, EVE=1082 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @100MW, MPC @40MW, WMP @80MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @115MW, AG4 @140MW, AG5 @49MW, AG6 @149MW, AG7 @38MW, PG4 @90MW [WEBSMS] | CMIN
8/2/2023 4:30:54 AM | Mindanao Grid-08/02/2023 04:32: Jasaan-Butuan 138kv line restored 0427H. Unplanned outage [WEBSMS] | CMIN
8/2/2023 4:30:28 AM | Mindanao Grid-08/02/2023 04:32: Jasaan-Butuan 138kv line restored 0427H. Unplanned outage [WEBSMS] | CMIN
8/2/2023 4:16:45 AM | [NSO Update] Mindanao Grid-08/02/2023 04:16: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
8/2/2023 4:15:33 AM | [NSO Update] Visayas Grid-08/02/2023 04:14: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
8/2/2023 4:14:32 AM | [NSO Update] Mindanao Grid-08/02/2023 04:16: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
8/2/2023 4:14:09 AM | [NSO Update] Visayas Grid-08/02/2023 04:14: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
8/2/2023 4:13:47 AM | [NSO Update] Luzon Grid-08/02/2023 04:14: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
8/2/2023 4:13:23 AM | [NSO Update] Luzon Grid-08/02/2023 04:14: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
8/2/2023 12:59:07 AM | Luzon Grid-08/02/2023 00:52: Bolo-Masinloc 230kV line 2 was restored at 0050H. (Unplanned Outage) [WEBSMS] | CLUZ
8/2/2023 12:52:19 AM | Luzon Grid-08/02/2023 00:52: Bolo-Masinloc 230kV line 2 was restored at 0050H. (Unplanned Outage) [WEBSMS] | CLUZ
8/2/2023 12:04:34 AM | Visayas Grid-08/02/2023 00:04: KSPC U1 shutdown at 0001H (Planned outage) [WEBSMS] | CVIS
8/2/2023 12:04:26 AM | Visayas Grid-08/02/2023 00:04: KSPC U1 shutdown at 0001H (Planned outage) [WEBSMS] | CVIS
8/1/2023 11:22:41 PM | Luzon Grid-08/01/2023 23:22: Bolo-Masinloc 230kV line 2 auto-tripped at 2317H, auto-reclosed successfully at Bolo side. (Unplanned Outage) [WEBSMS] | CLUZ
8/1/2023 11:22:25 PM | Luzon Grid-08/01/2023 23:22: Bolo-Masinloc 230kV line 2 auto-tripped at 2317H, auto-reclosed successfully at Bolo side. (Unplanned Outage) [WEBSMS] | CLUZ
8/1/2023 11:09:05 PM | Mindanao Grid-08/01/2023 23:08: Mt. Apo Unit #3 Cut-in at 2300H, from Forced Outage. Follow RTD. [WEBSMS] | CMIN
8/1/2023 11:07:07 PM | Mindanao Grid-08/01/2023 23:08: Mt. Apo Unit #3 Cut-in at 2300H, from Forced Outage. Follow RTD. [WEBSMS] | CMIN
8/1/2023 10:54:05 PM | Mindanao Grid-08/01/2023 22:52: Mt. Apo Unit #3 tripped at 2215H. Indication: Caustic Soda Tank Level Very Low. LD=3MW. Forced Outage. [WEBSMS] | CMIN
8/1/2023 10:51:06 PM | Mindanao Grid-08/01/2023 22:52: Mt. Apo Unit #3 tripped at 2215H. Indication: Caustic Soda Tank Level Very Low. LD=3MW. Forced Outage. [WEBSMS] | CMIN
8/1/2023 9:17:22 PM | Mindanao Grid-08/01/2023 21:16: WMPC DG9 cut-out as RPS at 2113H. From RPS -System Voltage Requirement. [WEBSMS] | CMIN
8/1/2023 9:15:04 PM | Mindanao Grid-08/01/2023 21:16: WMPC DG9 cut-out as RPS at 2113H. From RPS -System Voltage Requirement. [WEBSMS] | CMIN
8/1/2023 9:08:57 PM | Mindanao Grid-08/01/2023 21:10: MA3 cut-in at 2106H. From FO. [WEBSMS] | CMIN
8/1/2023 8:35:55 PM | Luzon Grid-08/01/2023 20:36: Kalayaan Unit 4 online at 2021H (Unplanned Outage) [WEBSMS] | CLUZ
8/1/2023 8:15:39 PM | Luzon Grid-08/01/2023 20:11: Kalayaan Unit 4 tripped at 2003H while conducting Grid Compliance Test (Unplanned Outage). [WEBSMS] | CLUZ
8/1/2023 8:11:39 PM | Luzon Grid-08/01/2023 20:11: Kalayaan Unit 4 tripped at 2003H while conducting Grid Compliance Test (Unplanned Outage). [WEBSMS] | CLUZ
8/1/2023 6:54:04 PM | Mindanao Grid-08/01/2023 18:55: WMPC DG5 cut-out as RPS at 1849H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/1/2023 6:54:03 PM | Mindanao Grid-08/01/2023 18:55: WMPC DG5 cut-out as RPS at 1849H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/1/2023 6:28:59 PM | Mindanao Grid-08/01/2023 18:28: Jasaan-Butuan 138kv line auto tripped 1816H. Unplanned outage [WEBSMS] | CMIN
8/1/2023 6:26:47 PM | Mindanao Grid-08/01/2023 18:28: Jasaan-Butuan 138kv line auto tripped 1816H. Unplanned outage [WEBSMS] | CMIN
8/1/2023 6:23:58 PM | Mindanao Grid-08/01/2023 18:22: AGC trip at 1816H. Gen. Loss of 11MW. Ind.: U3 50BF CB Failure Relay Trip. [WEBSMS] | CMIN
8/1/2023 6:20:40 PM | Mindanao Grid-08/01/2023 18:22: AGC trip at 1816H. Gen. Loss of 11MW. Ind.: U3 50BF CB Failure Relay Trip. [WEBSMS] | CMIN
8/1/2023 6:05:39 PM | [NSO Update] Mindanao Grid-08/01/2023 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3321MW, PK=2135MW, RR=20MW, NetOpMargin: EVE=1166 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @115MW, AG4 @146MW, AG5 @48MW, AG6 @149MW, AG7 @40MW, PG4 @90MW [WEBSMS] | CMIN
8/1/2023 6:05:25 PM | [NSO Update] Mindanao Grid-08/01/2023 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3321MW, PK=2135MW, RR=20MW, NetOpMargin: EVE=1166 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @115MW, AG4 @146MW, AG5 @48MW, AG6 @149MW, AG7 @40MW, PG4 @90MW [WEBSMS] | CMIN
8/1/2023 5:45:53 PM | [NSO Update] Visayas Grid-08/01/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2599MW, PK=2188MW, RR=40MW, NetOpMargin: EVE=371 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @350MW [WEBSMS] | CVIS
8/1/2023 5:45:36 PM | [NSO Update] Luzon Grid-08/01/2023 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13856MW, PK=9414MW, RR=80MW, NetOpMargin: EVE=4362 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @170MW, MASINLOC 2 @100MW, ILIJAN B @300MW, ST. RITA 10 @161MW [WEBSMS] | CLUZ
8/1/2023 5:44:37 PM | [NSO Update] Visayas Grid-08/01/2023 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2599MW, PK=2188MW, RR=40MW, NetOpMargin: EVE=371 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @350MW [WEBSMS] | CVIS
8/1/2023 5:38:51 PM | [NSO Update] Luzon Grid-08/01/2023 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13856MW, PK=9414MW, RR=80MW, NetOpMargin: EVE=4362 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @170MW, MASINLOC 2 @100MW, ILIJAN B @300MW, ST. RITA 10 @161MW [WEBSMS] | CLUZ
8/1/2023 5:22:16 PM | [NSO Update] Luzon Grid-08/01/2023 17:15: Weather Disturbance Alert Notice (WDAN) has been lifted today, August 1, 2023 at 1700H. Typhoon ``FALCON`` is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon FALCON was estimated based on all available data at 835 km Northeast of Extreme Northern Luzon (OUTSIDE PAR) (25.1 ?N, 128.5 ?E ). [WEBSMS] | CLUZ
8/1/2023 5:17:17 PM | [NSO Update] Mindanao Grid-08/01/2023 17:17: Weather Disturbance Alert Notice (WDAN) has been lifted today, August 1, 2023 at 1700H. Typhoon "FALCON" is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon FALCON was estimated based on all available data at 835 km Northeast of Extreme Northern Luzon (OUTSIDE PAR) (25.1 ?N, 128.5 ?E ). [WEBSMS] | CMIN
8/1/2023 5:16:26 PM | [NSO Update] Visayas Grid-08/01/2023 17:16: Weather Disturbance Alert Notice (WDAN) has been lifted today, August 1, 2023 at 1700H. Typhoon ``FALCON`` is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon FALCON was estimated based on all available data at 835 km Northeast of Extreme Northern Luzon (OUTSIDE PAR) (25.1 ?N, 128.5 ?E ). [WEBSMS] | CVIS
8/1/2023 5:16:24 PM | [NSO Update] Visayas Grid-08/01/2023 17:16: Weather Disturbance Alert Notice (WDAN) has been lifted today, August 1, 2023 at 1700H. Typhoon ``FALCON`` is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon FALCON was estimated based on all available data at 835 km Northeast of Extreme Northern Luzon (OUTSIDE PAR) (25.1 ?N, 128.5 ?E ). [WEBSMS] | CVIS
8/1/2023 5:15:56 PM | [NSO Update] Mindanao Grid-08/01/2023 17:17: Weather Disturbance Alert Notice (WDAN) has been lifted today, August 1, 2023 at 1700H. Typhoon "FALCON" is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon FALCON was estimated based on all available data at 835 km Northeast of Extreme Northern Luzon (OUTSIDE PAR) (25.1 �N, 128.5 �E ). [WEBSMS] | CMIN
8/1/2023 5:15:48 PM | [NSO Update] Visayas Grid-08/01/2023 17:16: Weather Disturbance Alert Notice (WDAN) has been lifted today, August 1, 2023 at 1700H. Typhoon "FALCON" is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon FALCON was estimated based on all available data at 835 km Northeast of Extreme Northern Luzon (OUTSIDE PAR) (25.1 �N, 128.5 �E ). [WEBSMS] | CVIS
8/1/2023 5:15:44 PM | [NSO Update] Luzon Grid-08/01/2023 17:15: Weather Disturbance Alert Notice (WDAN) has been lifted today, August 1, 2023 at 1700H. Typhoon "FALCON" is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon FALCON was estimated based on all available data at 835 km Northeast of Extreme Northern Luzon (OUTSIDE PAR) (25.1 �N, 128.5 �E ). [WEBSMS] | CLUZ
8/1/2023 4:54:40 PM | Visayas Grid-08/01/2023 16:55: 230/138KV Compostela 150MVA TR# 1 energized @ 1647H. (Planned Outage) [WEBSMS] | CVIS
8/1/2023 4:53:35 PM | [NSO Update] Visayas Grid-08/01/2023 16:54: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1652H with power going to Visayas(MVIP Test). [WEBSMS] | CVIS
8/1/2023 4:53:11 PM | [NSO Update] Mindanao Grid-08/01/2023 16:54: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1652H with power going to Visayas(MVIP Test). [WEBSMS] | CMIN
8/1/2023 4:53:10 PM | [NSO Update] Mindanao Grid-08/01/2023 16:54: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1652H with power going to Visayas(MVIP Test). [WEBSMS] | CMIN
8/1/2023 4:49:13 PM | [NSO Update] Visayas Grid-08/01/2023 16:49: Weather Update: At 3:00 PM today, the center of the eye of Typhoon ``FALCON`` {KHANUN} was estimated based on all available data at 835 km Northeast of Extreme Northern Luzon (25.0?N, 128.6?E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
8/1/2023 4:49:06 PM | [NSO Update] Mindanao Grid-08/01/2023 16:50: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "FALCON" {KHANUN} was estimated based on all available data at 835 km Northeast of Extreme Northern Luzon (25.0�N, 128.6�E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
8/1/2023 4:48:56 PM | [NSO Update] Mindanao Grid-08/01/2023 16:50: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "FALCON" {KHANUN} was estimated based on all available data at 835 km Northeast of Extreme Northern Luzon (25.0?N, 128.6?E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
8/1/2023 4:48:54 PM | [NSO Update] Luzon Grid-08/01/2023 16:48: Weather Update: At 3:00 PM today, the center of the eye of Typhoon ``FALCON`` {KHANUN} was estimated based on all available data at 835 km Northeast of Extreme Northern Luzon (25.0?N, 128.6?E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
8/1/2023 4:48:48 PM | [NSO Update] Visayas Grid-08/01/2023 16:49: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "FALCON" {KHANUN} was estimated based on all available data at 835 km Northeast of Extreme Northern Luzon (25.0�N, 128.6�E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
8/1/2023 4:48:30 PM | [NSO Update] Luzon Grid-08/01/2023 16:48: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "FALCON" {KHANUN} was estimated based on all available data at 835 km Northeast of Extreme Northern Luzon (25.0�N, 128.6�E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
8/1/2023 4:34:55 PM | Mindanao Grid-08/01/2023 16:36: Baloi - Lugait 138kV Line restored at 1632H. (Planned Outage) [WEBSMS] | CMIN
8/1/2023 4:34:50 PM | Mindanao Grid-08/01/2023 16:36: Baloi - Lugait 138kV Line restored at 1632H. (Planned Outage) [WEBSMS] | CMIN
8/1/2023 4:18:55 PM | Mindanao Grid-08/01/2023 16:18: WMPC DG1 cut-out as RPS at 1614H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/1/2023 4:17:04 PM | Mindanao Grid-08/01/2023 16:18: WMPC DG1 cut-out as RPS at 1614H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/1/2023 2:29:47 PM | Mindanao Grid-08/01/2023 14:27: WMPC DG5 cut-in as RPS at 1415H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/1/2023 2:26:22 PM | Mindanao Grid-08/01/2023 14:27: WMPC DG5 cut-in as RPS at 1415H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
8/1/2023 1:03:05 PM | [NSO Update] Mindanao Grid-08/01/2023 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3383MW, PK=2258MW, RR=20MW, NetOpMargin: PM=1105, EVE=1216 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @149MW, AG7 @40MW, PG4 @90MW [WEBSMS] | CMIN
8/1/2023 1:02:45 PM | [NSO Update] Mindanao Grid-08/01/2023 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3383MW, PK=2258MW, RR=20MW, NetOpMargin: PM=1105, EVE=1216 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @149MW, AG7 @40MW, PG4 @90MW [WEBSMS] | CMIN
8/1/2023 12:57:21 PM | [NSO Update] Visayas Grid-08/01/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2817MW, PK=2252MW, RR=40MW, NetOpMargin: PM=524, EVE=438 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @340MW [WEBSMS] | CVIS
8/1/2023 12:56:13 PM | [NSO Update] Visayas Grid-08/01/2023 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2817MW, PK=2252MW, RR=40MW, NetOpMargin: PM=524, EVE=438 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @340MW [WEBSMS] | CVIS
8/1/2023 12:53:05 PM | Mindanao Grid-08/01/2023 12:52: Placer SS Bus # 1 re-energized at 1054H. From Planned Outage / Non-GOMP [WEBSMS] | CMIN
8/1/2023 12:53:03 PM | [NSO Update] Luzon Grid-08/01/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14340MW, PK=9791MW, RR=80MW, NetOpMargin: PM=4469, EVE=4344 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC2 @100MW, ILIJAN B @300MW [WEBSMS] | CLUZ
8/1/2023 12:51:09 PM | Mindanao Grid-08/01/2023 12:52: Placer SS Bus # 1 re-energized at 1054H. From Planned Outage / Non-GOMP [WEBSMS] | CMIN
8/1/2023 12:51:01 PM | [NSO Update] Luzon Grid-08/01/2023 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14340MW, PK=9791MW, RR=80MW, NetOpMargin: PM=4469, EVE=4344 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC2 @100MW, ILIJAN B @300MW [WEBSMS] | CLUZ
8/1/2023 12:20:20 PM | [NSO Update] Luzon Grid-08/01/2023 12:20: at 1101H Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1100H with power going to Visayas(MVIP Test). [WEBSMS] | CLUZ
8/1/2023 12:19:43 PM | [NSO Update] Luzon Grid-08/01/2023 12:20: at 1101H Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1100H with power going to Visayas(MVIP Test). [WEBSMS] | CLUZ
8/1/2023 11:06:23 AM | [NSO Update] Mindanao Grid-08/01/2023 11:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1101H with power going to Visayas(MVIP Test). [WEBSMS] | CMIN
8/1/2023 11:05:25 AM | [NSO Update] Mindanao Grid-08/01/2023 11:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1101H with power going to Visayas(MVIP Test). [WEBSMS] | CMIN
8/1/2023 11:05:23 AM | [NSO Update] Visayas Grid-08/01/2023 11:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1101H with power going to Visayas(MVIP Test). [WEBSMS] | CVIS
8/1/2023 11:04:07 AM | [NSO Update] Visayas Grid-08/01/2023 11:04: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1101H with power going to Visayas(MVIP Test). [WEBSMS] | CVIS
8/1/2023 10:53:28 AM | Mindanao Grid-08/01/2023 10:55: WMPC DG01 online at 1050H as RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/1/2023 10:52:58 AM | Mindanao Grid-08/01/2023 10:55: WMPC DG01 online at 1050H as RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/1/2023 10:12:57 AM | Mindanao Grid-08/01/2023 10:14: Agus 1 Unit #2 cut-out at 0923H for PMS (GOMP). Follow RTD. [WEBSMS] | CMIN
8/1/2023 10:12:53 AM | Mindanao Grid-08/01/2023 10:14: Agus 1 Unit #2 cut-out at 0923H for PMS (GOMP). Follow RTD. [WEBSMS] | CMIN
8/1/2023 9:07:23 AM | Visayas Grid-08/01/2023 09:06: 138KV Compostela 150MVA TR# 1 de-energized @ 0859H. (Planned Outage) [WEBSMS] | CVIS
8/1/2023 9:06:22 AM | Visayas Grid-08/01/2023 09:06: 138KV Compostela 150MVA TR# 1 de-energized @ 0859H. (Planned Outage) [WEBSMS] | CVIS
8/1/2023 9:06:15 AM | Mindanao Grid-08/01/2023 09:03: WMPC DG09 online at 0851H as RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/1/2023 9:06:14 AM | Mindanao Grid-08/01/2023 09:04: Baloi - Lugait 138kv Line de-energized at 0842H to conduct line maintenance activities. Planned Outage / Non-GOMP... [WEBSMS] | CMIN
8/1/2023 9:02:38 AM | Mindanao Grid-08/01/2023 09:04: Baloi - Lugait 138kv Line de-energized at 0842H to conduct line maintenance activities. Planned Outage / Non-GOMP... [WEBSMS] | CMIN
8/1/2023 9:02:20 AM | Mindanao Grid-08/01/2023 09:03: WMPC DG09 online at 0851H as RPS-System Voltage Requirement. [WEBSMS] | CMIN
8/1/2023 8:59:05 AM | Mindanao Grid-08/01/2023 09:00: STEAG Unit #1 cut-in at 0803H, from PMS (GOMP). Follow RTD. [WEBSMS] | CMIN
8/1/2023 8:56:13 AM | Mindanao Grid-08/01/2023 08:54: Placer SS Bus # 1 de-energized at 0830H. Planned Outage / Non-GOMP [WEBSMS] | CMIN
8/1/2023 8:53:12 AM | Mindanao Grid-08/01/2023 08:54: Placer SS Bus # 1 de-energized at 0830H. Planned Outage / Non-GOMP [WEBSMS] | CMIN
8/1/2023 8:51:13 AM | Mindanao Grid-08/01/2023 08:50: AGGREKO (APD) Cut-in at 0800H, to facilitate REGULATORY REQUIREMENTS : DENR EMISSION TEST. Follow RTD. [WEBSMS] | CMIN
8/1/2023 8:49:16 AM | Mindanao Grid-08/01/2023 08:50: AGGREKO (APD) Cut-in at 0800H, to facilitate REGULATORY REQUIREMENTS : DENR EMISSION TEST. Follow RTD. [WEBSMS] | CMIN
8/1/2023 5:57:49 AM | [NSO Update] Mindanao Grid-08/01/2023 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3392MW, PK=2190MW, RR=20MW, NetOpMargin: AM=1182, PM=1142, EVE=1302 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @149MW, AG7 @40MW, PG4 @90MW [WEBSMS] | CMIN
8/1/2023 5:55:17 AM | [NSO Update] Mindanao Grid-08/01/2023 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3392MW, PK=2190MW, RR=20MW, NetOpMargin: AM=1182, PM=1142, EVE=1302 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @35MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @149MW, AG7 @40MW, PG4 @90MW [WEBSMS] | CMIN
8/1/2023 5:54:00 AM | [NSO Update] Visayas Grid-08/01/2023 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2552MW, PK=2234MW, RR=40MW, NetOpMargin: AM=278, PM=225, EVE=186 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, TGPP @81.2MW, LEYTE A @340MW [WEBSMS] | CVIS
8/1/2023 5:48:21 AM | Mindanao Grid-08/01/2023 05:49: Nagamin SS 138KV Bus 1 restored at 2250H, (Planned outage) [WEBSMS] | CMIN
8/1/2023 5:47:40 AM | [NSO Update] Luzon Grid-08/01/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14467MW, PK=10085MW, RR=80MW, NetOpMargin: AM=4302, PM=3797, EVE=4129 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC2 @100MW, ILIJAN B @300MW [WEBSMS] | CLUZ
8/1/2023 5:06:09 AM | Luzon Grid-08/01/2023 05:06: SCPC 3 online at 0505H. (Unplanned Outage) [WEBSMS] | CLUZ
8/1/2023 5:06:07 AM | Luzon Grid-08/01/2023 05:06: SCPC 3 online at 0505H. (Unplanned Outage) [WEBSMS] | CLUZ
8/1/2023 4:36:07 AM | [NSO Update] Mindanao Grid-08/01/2023 04:35: Weather Update: At 3:00 AM today, the center of the eye of Typhoon FALCON was estimated based on all available data at 930 km East Northeast of Extreme Northern Luzon (24.2 N, 130.1 E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving Northwestward at 20 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
8/1/2023 4:36:06 AM | [NSO Update] Luzon Grid-08/01/2023 04:33: Weather Update: At 3:00 AM today, the center of the eye of Typhoon FALCON was estimated based on all available data at 930 km East Northeast of Extreme Northern Luzon (24.2 N, 130.1 E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving Northwestward at 20 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
8/1/2023 4:35:10 AM | [NSO Update] Visayas Grid-08/01/2023 04:34: Weather Update: At 3:00 AM today, the center of the eye of Typhoon FALCON was estimated based on all available data at 930 km East Northeast of Extreme Northern Luzon (24.2 N, 130.1 E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving Northwestward at 20 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
8/1/2023 4:34:07 AM | [NSO Update] Mindanao Grid-08/01/2023 04:35: Weather Update: At 3:00 AM today, the center of the eye of Typhoon FALCON was estimated based on all available data at 930 km East Northeast of Extreme Northern Luzon (24.2 N, 130.1 E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving Northwestward at 20 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
8/1/2023 4:33:52 AM | [NSO Update] Visayas Grid-08/01/2023 04:34: Weather Update: At 3:00 AM today, the center of the eye of Typhoon FALCON was estimated based on all available data at 930 km East Northeast of Extreme Northern Luzon (24.2 N, 130.1 E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving Northwestward at 20 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
8/1/2023 4:33:38 AM | [NSO Update] Luzon Grid-08/01/2023 04:33: Weather Update: At 3:00 AM today, the center of the eye of Typhoon FALCON was estimated based on all available data at 930 km East Northeast of Extreme Northern Luzon (24.2 N, 130.1 E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving Northwestward at 20 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
8/1/2023 2:46:02 AM | Luzon Grid-08/01/2023 02:40: SCPC U3 @110MW tripped at 0228H,Lowest frequency is 59.58Hz (Unplanned Outage) [WEBSMS] | CLUZ
8/1/2023 2:40:26 AM | Luzon Grid-08/01/2023 02:40: SCPC U3 @110MW tripped at 0228H,Lowest frequency is 59.58Hz (Unplanned Outage) [WEBSMS] | CLUZ
8/1/2023 1:42:40 AM | Luzon Grid-08/01/2023 01:38: Sta. Rita 40 online at 0134H (Unplanned Outage) [WEBSMS] | CLUZ
8/1/2023 1:38:13 AM | Luzon Grid-08/01/2023 01:38: Sta. Rita 40 online at 0134H (Unplanned Outage) [WEBSMS] | CLUZ
8/1/2023 12:21:34 AM | Mindanao Grid-08/01/2023 00:23: Matanao - DSP 69KV line tripped at 2327H. (Unplanned outage) [WEBSMS] | CMIN
8/1/2023 12:21:01 AM | Mindanao Grid-08/01/2023 00:23: Matanao - DSP 69KV line tripped at 2327H. (Unplanned outage) [WEBSMS] | CMIN
8/1/2023 12:16:20 AM | Mindanao Grid-08/01/2023 00:17: Matanao - DSP 69KV line reenergized at 0013H. (Unplanned) [WEBSMS] | CMIN
8/1/2023 12:15:22 AM | Mindanao Grid-08/01/2023 00:16: Matanao - DSP reenergized at 0013H. (Unplanned) [WEBSMS] | CMIN
7/31/2023 11:53:04 PM | Mindanao Grid-07/31/2023 23:54: Matanao - Digos Solar Power Plant tripped at 2327H. (Unplanned outage) [WEBSMS] | CMIN
7/31/2023 11:52:40 PM | Mindanao Grid-07/31/2023 23:54: Matanao - Digos Solar Power Plant tripped at 2327H. (Unplanned outage) [WEBSMS] | CMIN
7/31/2023 10:59:18 PM | Mindanao Grid-07/31/2023 23:00: Nagamin SS 138KV Bus no.1 restored at 2250H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 10:58:39 PM | Mindanao Grid-07/31/2023 23:00: Nagamin SS 138KV Bus no.1 restored at 2250H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 10:11:22 PM | Mindanao Grid-07/31/2023 22:12: Bislig SS 138KV Bus # 2 restored at 2204H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 10:11:08 PM | Mindanao Grid-07/31/2023 22:12: Bislig SS 138KV Bus # 2 restored at 2204H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 10:06:07 PM | Mindanao Grid-07/31/2023 22:06: Kidapawan - Mt. Apo 3 69kV line restored/energized 2200H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 10:04:53 PM | Mindanao Grid-07/31/2023 22:06: Kidapawan - Mt. Apo 3 69kV line restored/energized 2200H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 9:55:19 PM | Mindanao Grid-07/31/2023 21:56: WMPC DG09 cut-out at 2143H for RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2023 9:54:36 PM | [NSO Update] Mindanao Grid-07/31/2023 21:56: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2139H from forward power direction (MVIP Test). [WEBSMS] | CMIN
7/31/2023 9:54:12 PM | [NSO Update] Visayas Grid-07/31/2023 21:54: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 2139H from forward power direction (MVIP Test). [WEBSMS] | CVIS
7/31/2023 9:37:35 PM | Mindanao Grid-07/31/2023 21:37: WMPC DG05 cut-out at 2114H for RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2023 9:36:13 PM | Mindanao Grid-07/31/2023 21:37: WMPC DG05 cut-out at 2114H for RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2023 8:26:07 PM | Mindanao Grid-07/31/2023 20:27: TM1 Unit 1 cut out at 2021H. Follow RTD. [WEBSMS] | CMIN
7/31/2023 8:25:55 PM | Mindanao Grid-07/31/2023 20:27: TM1 Unit 1 cut out at 2021H. Follow RTD. [WEBSMS] | CMIN
7/31/2023 8:25:54 PM | Mindanao Grid-07/31/2023 20:27: TM2 Unit 2 cut out at 2015H. Follow RTD. [WEBSMS] | CMIN
7/31/2023 8:25:43 PM | Mindanao Grid-07/31/2023 20:27: TM2 Unit 2 cut out at 2015H. Follow RTD. [WEBSMS] | CMIN
7/31/2023 8:15:52 PM | Luzon Grid-07/31/2023 20:08: Sta. Rita 10 online at 2006H. (Unplanned Outage) [WEBSMS] | CLUZ
7/31/2023 8:07:49 PM | Luzon Grid-07/31/2023 20:08: Sta. Rita 10 online at 2006H. (Unplanned Outage) [WEBSMS] | CLUZ
7/31/2023 7:46:18 PM | Luzon Grid-07/31/2023 19:46: Sta. Rita 30 online at 1941H. (Unplanned Outage) [WEBSMS] | CLUZ
7/31/2023 7:44:57 PM | Luzon Grid-07/31/2023 19:45: Sta. Rita 30 online at 1941H. (Unplanned Outage) [WEBSMS] | CLUZ
7/31/2023 7:43:39 PM | Mindanao Grid-07/31/2023 19:45: TM2 Unit 2 cut in as energy at 1941H. Follow RTD. [WEBSMS] | CMIN
7/31/2023 7:37:37 PM | Mindanao Grid-07/31/2023 19:36: TM1 Unit 1 cut in as energy at 1851H. Follow RTD. [WEBSMS] | CMIN
7/31/2023 7:34:47 PM | Mindanao Grid-07/31/2023 19:36: TM1 Unit 1 cut in as energy at 1851H. Follow RTD. [WEBSMS] | CMIN
7/31/2023 7:27:35 PM | Mindanao Grid-07/31/2023 19:27: WMPC DG08 tripped with 8.5MW RPS at 1910H. (Unplanned outage) [WEBSMS] | CMIN
7/31/2023 7:25:54 PM | Mindanao Grid-07/31/2023 19:27: WMPC DG08 tripped with 8.5MW RPS at 1910H. (Unplanned outage) [WEBSMS] | CMIN
7/31/2023 7:22:30 PM | Luzon Grid-07/31/2023 19:17: Sta. Rita 20 online at 1859H. (Unplanned Outage) [WEBSMS] | CLUZ
7/31/2023 7:17:14 PM | Luzon Grid-07/31/2023 19:17: Sta. Rita 20 online at 1859H. (Unplanned Outage) [WEBSMS] | CLUZ
7/31/2023 6:19:59 PM | [NSO Update] Visayas Grid-07/31/2023 18:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2639MW, PK=2183MW, RR=40MW, NetOpMargin: EVE=416 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @335MW [WEBSMS] | CVIS
7/31/2023 6:18:01 PM | [NSO Update] Visayas Grid-07/31/2023 18:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2639MW, PK=2183MW, RR=40MW, NetOpMargin: EVE=416 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @335MW [WEBSMS] | CVIS
7/31/2023 6:15:52 PM | [NSO Update] Mindanao Grid-07/31/2023 18:13: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3202MW, PK=2211MW, RR=20MW, NetOpMargin: EVE=971 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @40MW, PG4 @60MW [WEBSMS] | CMIN
7/31/2023 6:15:49 PM | [NSO Update] Luzon Grid-07/31/2023 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12841MW, PK=9439MW, RR=260MW, NetOpMargin: EVE=3142 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC2 @100MW, ILIJAN B @300MW [WEBSMS] | CLUZ
7/31/2023 6:12:14 PM | [NSO Update] Mindanao Grid-07/31/2023 18:13: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3202MW, PK=2211MW, RR=20MW, NetOpMargin: EVE=971 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @40MW, PG4 @60MW [WEBSMS] | CMIN
7/31/2023 6:06:42 PM | [NSO Update] Luzon Grid-07/31/2023 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12841MW, PK=9439MW, RR=260MW, NetOpMargin: EVE=3142 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC2 @100MW, ILIJAN B @300MW [WEBSMS] | CLUZ
7/31/2023 5:45:51 PM | Luzon Grid-07/31/2023 17:46: NGCP and Meralco ALD-affected feeders were restored at 1731 and 1732H respectively. [WEBSMS] | CLUZ
7/31/2023 5:45:48 PM | Luzon Grid-07/31/2023 17:46: NGCP and Meralco ALD-affected feeders were restored at 1731 and 1732H respectively. [WEBSMS] | CLUZ
7/31/2023 5:36:48 PM | Luzon Grid-07/31/2023 17:37: ALD occurred at NGCP and Meralco feeders due to the tripping of Sta Rita 10(197MW), Sta Rita 20(197MW), Sta Rita 30(195MW) and Sta Rita 40(197MW) at 1726H. The lowest Luzon system frequency is 58.993Hz. (Unplanned Outage) [WEBSMS] | CLUZ
7/31/2023 5:32:27 PM | [NSO Update] Luzon Grid-07/31/2023 17:24: At 3:00 PM today, the center of the eye of Typhoon FALCON was estimated based on all available data at 1,015 km East Northeast of Extreme Northern Luzon (22.9 N, 131.4 E) with maximum sustained winds of 165 km/h near the center and gustiness of up to 205 km/h. It is moving North Northwestward at 15 km/h. [WEBSMS] | CLUZ
7/31/2023 5:27:31 PM | [NSO Update] Mindanao Grid-07/31/2023 17:26: At 3:00 PM today, the center of the eye of Typhoon FALCON was estimated based on all available data at 1,015 km East Northeast of Extreme Northern Luzon (22.9 N, 131.4 E) with maximum sustained winds of 165 km/h near the center and gustiness of up to 205 km/h. It is moving North Northwestward at 15 km/h. [WEBSMS] | CMIN
7/31/2023 5:25:38 PM | [NSO Update] Visayas Grid-07/31/2023 17:25: At 3:00 PM today, the center of the eye of Typhoon FALCON was estimated based on all available data at 1,015 km East Northeast of Extreme Northern Luzon (22.9 N, 131.4 E) with maximum sustained winds of 165 km/h near the center and gustiness of up to 205 km/h. It is moving North Northwestward at 15 km/h. [WEBSMS] | CVIS
7/31/2023 5:25:07 PM | [NSO Update] Mindanao Grid-07/31/2023 17:26: At 3:00 PM today, the center of the eye of Typhoon FALCON was estimated based on all available data at 1,015 km East Northeast of Extreme Northern Luzon (22.9 N, 131.4 E) with maximum sustained winds of 165 km/h near the center and gustiness of up to 205 km/h. It is moving North Northwestward at 15 km/h. [WEBSMS] | CMIN
7/31/2023 5:24:46 PM | [NSO Update] Visayas Grid-07/31/2023 17:25: At 3:00 PM today, the center of the eye of Typhoon FALCON was estimated based on all available data at 1,015 km East Northeast of Extreme Northern Luzon (22.9 N, 131.4 E) with maximum sustained winds of 165 km/h near the center and gustiness of up to 205 km/h. It is moving North Northwestward at 15 km/h. [WEBSMS] | CVIS
7/31/2023 5:24:22 PM | [NSO Update] Luzon Grid-07/31/2023 17:24: At 3:00 PM today, the center of the eye of Typhoon FALCON was estimated based on all available data at 1,015 km East Northeast of Extreme Northern Luzon (22.9 N, 131.4 E) with maximum sustained winds of 165 km/h near the center and gustiness of up to 205 km/h. It is moving North Northwestward at 15 km/h. [WEBSMS] | CLUZ
7/31/2023 5:07:33 PM | [NSO Update] Visayas Grid-07/31/2023 17:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1700H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
7/31/2023 5:07:29 PM | [NSO Update] Mindanao Grid-07/31/2023 17:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1700H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
7/31/2023 5:07:11 PM | [NSO Update] Mindanao Grid-07/31/2023 17:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1700H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
7/31/2023 5:06:46 PM | [NSO Update] Visayas Grid-07/31/2023 17:07: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 1700H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
7/31/2023 3:55:52 PM | Mindanao Grid-07/31/2023 15:54: WMPC DG01 cut-out at 1534H for RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2023 3:53:00 PM | Mindanao Grid-07/31/2023 15:54: WMPC DG01 cut-out at 1534H for RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2023 2:14:03 PM | Mindanao Grid-07/31/2023 14:12: Placer 138kV Bus 2 restored/energized 1408H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 2:10:51 PM | Mindanao Grid-07/31/2023 14:12: Placer 138kV Bus 2 restored/energized 1408H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 2:09:03 PM | [NSO Update] Mindanao Grid-07/31/2023 14:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1406H with power going to Visayas(MVIP Test). [WEBSMS] | CMIN
7/31/2023 2:08:05 PM | [NSO Update] Visayas Grid-07/31/2023 14:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1406H with power going to Visayas(MVIP Test). [WEBSMS] | CVIS
7/31/2023 2:06:45 PM | [NSO Update] Mindanao Grid-07/31/2023 14:08: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1406H with power going to Visayas(MVIP Test). [WEBSMS] | CMIN
7/31/2023 2:06:35 PM | [NSO Update] Visayas Grid-07/31/2023 14:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1406H with power going to Visayas(MVIP Test). [WEBSMS] | CVIS
7/31/2023 12:57:19 PM | Mindanao Grid-07/31/2023 12:57: TMI U1 cut out at 1236H. Follow RTD. [WEBSMS] | CMIN
7/31/2023 12:56:09 PM | Mindanao Grid-07/31/2023 12:57: TMI U1 cut out at 1236H. Follow RTD. [WEBSMS] | CMIN
7/31/2023 12:52:18 PM | [NSO Update] Luzon Grid-07/31/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14356MW, PK=10075MW, RR=260MW, NetOpMargin: PM=4020, EVE=4066 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 2 @ 101MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
7/31/2023 12:50:31 PM | [NSO Update] Luzon Grid-07/31/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14356MW, PK=10075MW, RR=260MW, NetOpMargin: PM=4020, EVE=4066 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 2 @ 101MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
7/31/2023 12:47:19 PM | [NSO Update] Mindanao Grid-07/31/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3264MW, PK=2405MW, RR=20MW, NetOpMargin: PM=839, EVE=1016 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @40MW, PG4 @60MW [WEBSMS] | CMIN
7/31/2023 12:47:18 PM | Mindanao Grid-07/31/2023 12:46: WMPC DG09cut-out at 1243H from RPS - System Voltage Requirement [WEBSMS] | CMIN
7/31/2023 12:46:55 PM | [NSO Update] Mindanao Grid-07/31/2023 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3264MW, PK=2405MW, RR=20MW, NetOpMargin: PM=839, EVE=1016 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @40MW, PG4 @60MW [WEBSMS] | CMIN
7/31/2023 12:44:49 PM | Mindanao Grid-07/31/2023 12:46: WMPC DG09cut-out at 1243H from RPS - System Voltage Requirement [WEBSMS] | CMIN
7/31/2023 12:44:33 PM | [NSO Update] Visayas Grid-07/31/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2688MW, PK=2270MW, RR=40MW, NetOpMargin: PM=378, EVE=322 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 344MW [WEBSMS] | CVIS
7/31/2023 12:44:22 PM | [NSO Update] Visayas Grid-07/31/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2688MW, PK=2270MW, RR=40MW, NetOpMargin: PM=378, EVE=322 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 344MW [WEBSMS] | CVIS
7/31/2023 12:44:21 PM | [NSO Update] Visayas Grid-07/31/2023 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2688MW, PK=2270MW, RR=40MW, NetOpMargin: PM=378, EVE=322 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 344MW [WEBSMS] | CVIS
7/31/2023 11:15:37 AM | Mindanao Grid-07/31/2023 11:15: WMPC DG09 cut-in at 1112H for RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2023 11:13:41 AM | Mindanao Grid-07/31/2023 11:15: WMPC DG09 cut-in at 1112H for RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2023 10:22:14 AM | Mindanao Grid-07/31/2023 10:21: WMPC DG01 cut-in at 1017H for RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2023 10:20:13 AM | Mindanao Grid-07/31/2023 10:21: WMPC DG01 cut-in at 1017H for RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2023 9:09:43 AM | Mindanao Grid-07/31/2023 09:11: Correction: WMPC DG05 cut-in at 0905H for RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2023 9:08:56 AM | Mindanao Grid-07/31/2023 09:10: WMPC DG08 cut-in at 0906H for RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2023 9:07:48 AM | Mindanao Grid-07/31/2023 09:08: WMPC DG05 cut-out at 0905H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2023 9:06:31 AM | Mindanao Grid-07/31/2023 09:08: WMPC DG05 cut-out at 0905H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/31/2023 9:05:33 AM | [NSO Update] Mindanao Grid-07/31/2023 09:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0904H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
7/31/2023 9:05:15 AM | [NSO Update] Mindanao Grid-07/31/2023 09:06: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0904H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
7/31/2023 9:05:08 AM | [NSO Update] Visayas Grid-07/31/2023 09:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0904H with power going to Visayas(MVIP Test). [WEBSMS] | CVIS
7/31/2023 9:04:48 AM | [NSO Update] Visayas Grid-07/31/2023 09:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) de-blocked at 0904H with power going to Visayas(MVIP Test). [WEBSMS] | CVIS
7/31/2023 8:58:02 AM | Mindanao Grid-07/31/2023 08:59: Placer 138kV Bus 2 de-energized 0856H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 8:57:47 AM | Mindanao Grid-07/31/2023 08:59: Placer 138kV Bus 2 de-energized 0856H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 8:55:33 AM | Mindanao Grid-07/31/2023 08:55: WMPC DG10 declared on FO at 0850H. (Unplanned outage) [WEBSMS] | CMIN
7/31/2023 8:53:29 AM | Mindanao Grid-07/31/2023 08:55: WMPC DG10 declared on FO at 0850H. (Unplanned outage) [WEBSMS] | CMIN
7/31/2023 8:32:46 AM | Mindanao Grid-07/31/2023 08:32: Correction: MPI - Digos Diesel Plant cut-in at 0801H for DENR emission test. [WEBSMS] | CMIN
7/31/2023 8:31:25 AM | Mindanao Grid-07/31/2023 08:32: Correction: MPI - Digos Diesel Plant cut-in at 0801H for DENR emission test. [WEBSMS] | CMIN
7/31/2023 8:07:09 AM | Mindanao Grid-07/31/2023 08:08: MPI - Digos Diesel Plant cut-in at 0800H for DENR emission test. [WEBSMS] | CMIN
7/31/2023 8:06:46 AM | Mindanao Grid-07/31/2023 08:08: MPI - Digos Diesel Plant cut-in at 0800H for DENR emission test. [WEBSMS] | CMIN
7/31/2023 6:40:40 AM | Mindanao Grid-07/31/2023 06:42: Nagamin SS 138kV Bus 1 de-energized 0639H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 6:40:26 AM | Mindanao Grid-07/31/2023 06:42: Nagamin SS 138kV Bus 1 de-energized 0639H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 6:37:43 AM | Mindanao Grid-07/31/2023 06:39: Bislig SS 138kV Bus 2 de-energized 0632H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 6:37:31 AM | Mindanao Grid-07/31/2023 06:39: Bislig SS 138kV Bus 2 de-energized 0632H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 5:53:53 AM | [NSO Update] Luzon Grid-07/31/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14318MW, PK=9631MW, RR=260MW, NetOpMargin: AM=4427, PM=4214, EVE=4055 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 2 @ 94MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
7/31/2023 5:52:18 AM | [NSO Update] Visayas Grid-07/31/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2603MW, PK=2173MW, RR=40MW, NetOpMargin: AM=390, PM=391, EVE=333 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 344MW [WEBSMS] | CVIS
7/31/2023 5:52:03 AM | [NSO Update] Mindanao Grid-07/31/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3273MW, PK=2131MW, RR=20MW, NetOpMargin: AM=1122, PM=1021, EVE=1064 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @40MW, PG4 @60MW [WEBSMS] | CMIN
7/31/2023 5:51:59 AM | [NSO Update] Mindanao Grid-07/31/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3273MW, PK=2131MW, RR=20MW, NetOpMargin: AM=1122, PM=1021, EVE=1064 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @40MW, PG4 @60MW [WEBSMS] | CMIN
7/31/2023 5:50:06 AM | [NSO Update] Visayas Grid-07/31/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2603MW, PK=2173MW, RR=40MW, NetOpMargin: AM=390, PM=391, EVE=333 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 344MW [WEBSMS] | CVIS
7/31/2023 4:09:21 AM | [NSO Update] Mindanao Grid-07/31/2023 04:09: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "FALCON" {KHANUN} was estimated based on all available data at 1,070 km East of Extreme Northern Luzon (21.3?N, 132.2?E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving North Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
7/31/2023 4:09:17 AM | Luzon Grid-07/31/2023 04:07: Masinloc U2 online at 0403H. (Planned Outage) [WEBSMS] | CLUZ
7/31/2023 4:08:20 AM | [NSO Update] Visayas Grid-07/31/2023 04:07: Weather Update: At 3:00 AM today, the center of the eye of Typhoon ``FALCON`` {KHANUN} was estimated based on all available data at 1,070 km East of Extreme Northern Luzon (21.3?N, 132.2?E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving North Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
7/31/2023 4:07:45 AM | Luzon Grid-07/31/2023 04:07: Masinloc U2 online at 0403H. (Planned Outage) [WEBSMS] | CLUZ
7/31/2023 4:07:44 AM | [NSO Update] Mindanao Grid-07/31/2023 04:09: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "FALCON" {KHANUN} was estimated based on all available data at 1,070 km East of Extreme Northern Luzon (21.3�N, 132.2�E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving North Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
7/31/2023 4:07:21 AM | [NSO Update] Visayas Grid-07/31/2023 04:07: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "FALCON" {KHANUN} was estimated based on all available data at 1,070 km East of Extreme Northern Luzon (21.3�N, 132.2�E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving North Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
7/31/2023 4:06:53 AM | [NSO Update] Luzon Grid-07/31/2023 04:07: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "FALCON" {KHANUN} was estimated based on all available data at 1,070 km East of Extreme Northern Luzon (21.3�N, 132.2�E) with maximum sustained winds of 150 km/h near the center and gustiness of up to 185 km/h. It is moving North Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
7/31/2023 12:12:38 AM | Mindanao Grid-07/31/2023 00:14: Nabunturan SS 100MVA Transformer No. 2 restored at 2348H. (Planned outage) [WEBSMS] | CMIN
7/31/2023 12:05:08 AM | Mindanao Grid-07/31/2023 00:05: Nabunturan 138kV Bus no. 2 restored at 2347H. (Planned Outage) [WEBSMS] | CMIN
7/31/2023 12:03:44 AM | Mindanao Grid-07/31/2023 00:05: Nabunturan 138kV Bus no. 2 restored at 2347H. (Planned Outage) [WEBSMS] | CMIN
7/30/2023 10:29:54 PM | [NSO Update] Luzon Grid-07/30/2023 22:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13593MW, PK=8220MW, RR=80MW, NetOpMargin: EVE=5293 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, GMEC 2 @ 150MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
7/30/2023 6:50:06 PM | Mindanao Grid-07/30/2023 18:51: Matanao - Digos Solar Plant 69KV Line rerstored at 1847H. (Planned outage) [WEBSMS] | CMIN
7/30/2023 6:49:43 PM | Mindanao Grid-07/30/2023 18:51: Matanao - Digos Solar Plant 69KV Line rerstored at 1847H. (Planned outage) [WEBSMS] | CMIN
7/30/2023 5:57:20 PM | [NSO Update] Mindanao Grid-07/30/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3202MW, PK=2001MW, RR=20MW, NetOpMargin: EVE=1181 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @40MW, PG4 @60MW [WEBSMS] | CMIN
7/30/2023 5:55:18 PM | [NSO Update] Visayas Grid-07/30/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2410MW, PK=1926MW, RR=40MW, NetOpMargin: EVE=444 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 325MW [WEBSMS] | CVIS
7/30/2023 5:54:38 PM | [NSO Update] Mindanao Grid-07/30/2023 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3202MW, PK=2001MW, RR=20MW, NetOpMargin: EVE=1181 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @40MW, PG4 @60MW [WEBSMS] | CMIN
7/30/2023 5:21:52 PM | Mindanao Grid-07/30/2023 17:20: Matanao - Digos Solar Plant 69KV Line deenergized at 1705H (Planned outage) [WEBSMS] | CMIN
7/30/2023 5:19:16 PM | Mindanao Grid-07/30/2023 17:20: Matanao - Digos Solar Plant 69KV Line deenergized at 1705H (Planned outage) [WEBSMS] | CMIN
7/30/2023 5:13:15 PM | Mindanao Grid-07/30/2023 17:11: Agus 5 - Aurora 138KV Line restored at 1703H. (Planned outage) [WEBSMS] | CMIN
7/30/2023 5:09:35 PM | Mindanao Grid-07/30/2023 17:11: Agus 5 - Aurora 138KV Line restored at 1703H. (Planned outage) [WEBSMS] | CMIN
7/30/2023 4:22:54 PM | Visayas Grid-07/30/2023 16:22: Cebu SS 100 MVA TR2 138/69/13.8 kV energized at 1617H (Planned Outage) [WEBSMS] | CVIS
7/30/2023 4:21:59 PM | Visayas Grid-07/30/2023 16:22: Cebu SS 100 MVA TR2 138/69/13.8 kV energized at 1617H (Planned Outage) [WEBSMS] | CVIS
7/30/2023 4:00:08 PM | Luzon Grid-07/30/2023 15:58: Ambuklao - Bayombong 230kV Line 2 restored at 1558H. (Planned Outage) [WEBSMS] | CLUZ
7/30/2023 3:58:46 PM | Luzon Grid-07/30/2023 15:58: Ambuklao - Bayombong 230kV Line 2 restored at 1558H. (Planned Outage) [WEBSMS] | CLUZ
7/30/2023 2:33:26 PM | Luzon Grid-07/30/2023 14:31: Tayabas S/S 9-04CB08TAY restored at 1430H. (Unplanned Outage) [WEBSMS] | CLUZ
7/30/2023 2:31:19 PM | Luzon Grid-07/30/2023 14:31: Tayabas S/S 9-04CB08TAY restored at 1430H. (Unplanned Outage) [WEBSMS] | CLUZ
7/30/2023 1:56:28 PM | Mindanao Grid-07/30/2023 13:56: Maco-Nabunturan 138kV line restored/energized 1351H. (Unplanned outage) [WEBSMS] | CMIN
7/30/2023 1:54:40 PM | Mindanao Grid-07/30/2023 13:56: Maco-Nabunturan 138kV line restored/energized 1351H. (Unplanned outage) [WEBSMS] | CMIN
7/30/2023 1:30:17 PM | Luzon Grid-07/30/2023 13:30: San Esteban SS 230kV Bus 2 restored at 1329H. (Planned Outage) [WEBSMS] | CLUZ
7/30/2023 12:52:19 PM | Luzon Grid-07/30/2023 12:52: Tayabas S/S 9-04CB08TAY emergency shutdown at 1250H. (Unplanned Outage) [WEBSMS] | CLUZ
7/30/2023 12:52:10 PM | Luzon Grid-07/30/2023 12:52: Tayabas S/S 9-04CB08TAY emergency shutdown at 1250H. (Unplanned Outage) [WEBSMS] | CLUZ
7/30/2023 12:39:42 PM | [NSO Update] Luzon Grid-07/30/2023 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14238MW, PK=8115MW, RR=80MW, NetOpMargin: PM=6043, EVE=5011 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @170MW, GMEC 2 @150MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
7/30/2023 12:37:43 PM | [NSO Update] Visayas Grid-07/30/2023 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2601MW, PK=1704MW, RR=40MW, NetOpMargin: PM=857, EVE=463 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @325MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/30/2023 12:36:02 PM | [NSO Update] Luzon Grid-07/30/2023 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14238MW, PK=8115MW, RR=80MW, NetOpMargin: PM=6043, EVE=5011 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CALACA 2 @170MW, GMEC 2 @150MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
7/30/2023 12:35:51 PM | [NSO Update] Visayas Grid-07/30/2023 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2601MW, PK=1704MW, RR=40MW, NetOpMargin: PM=857, EVE=463 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @325MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/30/2023 12:34:45 PM | [NSO Update] Mindanao Grid-07/30/2023 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3258MW, PK=1803MW, RR=20MW, NetOpMargin: PM=1435, EVE=1169 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @40MW, PG4 @60MW [WEBSMS] | CMIN
7/30/2023 12:33:25 PM | [NSO Update] Mindanao Grid-07/30/2023 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3258MW, PK=1803MW, RR=20MW, NetOpMargin: PM=1435, EVE=1169 Highest Unit O/L: GNPK 1&4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @115MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @40MW, PG4 @60MW [WEBSMS] | CMIN
7/30/2023 12:08:55 PM | Mindanao Grid-07/30/2023 12:10: Maco-Nabunturan 138kV line auto tripped 1154H. (Unplanned outage) [WEBSMS] | CMIN
7/30/2023 12:08:51 PM | Mindanao Grid-07/30/2023 12:10: Maco-Nabunturan 138kV line auto tripped 1154H. (Unplanned outage) [WEBSMS] | CMIN
7/30/2023 10:04:39 AM | Mindanao Grid-07/30/2023 10:05: Agus 5 HEP Unit no. 2 cut-in at 0847H. (Unplanned Outage) [WEBSMS] | CMIN
7/30/2023 10:03:35 AM | Mindanao Grid-07/30/2023 10:05: Agus 5 HEP Unit no. 2 cut-in at 0847H. (Unplanned Outage) [WEBSMS] | CMIN
7/30/2023 8:42:55 AM | Mindanao Grid-07/30/2023 08:43: Agus 5 HEP Unit no. 2 with 18.64 MW at 0834H. (Unplanned Outage) [WEBSMS] | CMIN
7/30/2023 8:42:22 AM | Mindanao Grid-07/30/2023 08:43: Agus 5 HEP Unit no. 2 with 18.64 MW at 0834H. (Unplanned Outage) [WEBSMS] | CMIN
7/30/2023 8:38:36 AM | Mindanao Grid-07/30/2023 08:40: Agus 5 - Aurora 138kV line de-energized 0834H. (Planned outage) [WEBSMS] | CMIN
7/30/2023 8:37:55 AM | Mindanao Grid-07/30/2023 08:40: Agus 5 - Aurora 138kV line de-energized 0834H. (Planned outage) [WEBSMS] | CMIN
7/30/2023 8:09:33 AM | Luzon Grid-07/30/2023 08:07: San Esteban SS 230kV Bus 2 de-energized at 0807H. (Planned Outage) [WEBSMS] | CLUZ
7/30/2023 8:07:20 AM | Luzon Grid-07/30/2023 08:07: San Esteban SS 230kV Bus 2 de-energized at 0807H. (Planned Outage) [WEBSMS] | CLUZ
7/30/2023 7:28:42 AM | Luzon Grid-07/30/2023 07:28: San Jose SS 750MVA T03 de-energized at 0728H. (Planned Outage) [WEBSMS] | CLUZ
7/30/2023 7:28:41 AM | Luzon Grid-07/30/2023 07:28: San Jose SS 750MVA T03 de-energized at 0728H. (Planned Outage) [WEBSMS] | CLUZ
7/30/2023 6:42:48 AM | Luzon Grid-07/30/2023 06:38: Ambuklao - Bayombong 230kV Line 2 de-energized at 0638H. (Planned Outage) [WEBSMS] | CLUZ
7/30/2023 6:38:39 AM | Luzon Grid-07/30/2023 06:38: Ambuklao - Bayombong 230kV Line 2 de-energized at 0638H. (Planned Outage) [WEBSMS] | CLUZ
7/30/2023 6:30:53 AM | Visayas Grid-07/30/2023 06:30: Cebu SS 100MVA TR2 de-energized at 0611H pre-arranged activity. ECD: 1800H. [WEBSMS] | CVIS
7/30/2023 6:29:59 AM | Visayas Grid-07/30/2023 06:30: Cebu SS 100MVA TR2 de-energized at 0611H pre-arranged activity. ECD: 1800H. [WEBSMS] | CVIS
7/30/2023 6:25:22 AM | Mindanao Grid-07/30/2023 06:26: Nabunturan SS 138kV 100MVA Transformer 2 and 138kV Bus 2 de-energized 0615H. (Planned outage). [WEBSMS] | CMIN
7/30/2023 6:24:38 AM | Mindanao Grid-07/30/2023 06:26: Nabunturan SS 138kV 100MVA Transformer 2 and 138kV Bus 2 de-energized 0615H. (Planned outage). [WEBSMS] | CMIN
7/30/2023 6:02:38 AM | [NSO Update] Mindanao Grid-07/30/2023 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3254MW, PK=1704MW, RR=20MW, NetOpMargin: AM=1530, PM=1489, EVE=1245 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @115MW, AG4 @146MW, AG5 @48MW, AG6 @124MW, AG7 @40MW, PG4 @60MW [WEBSMS] | CMIN
7/30/2023 6:02:01 AM | [NSO Update] Mindanao Grid-07/30/2023 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3254MW, PK=1704MW, RR=20MW, NetOpMargin: AM=1530, PM=1489, EVE=1245 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @115MW, AG4 @146MW, AG5 @48MW, AG6 @124MW, AG7 @40MW, PG4 @60MW [WEBSMS] | CMIN
7/30/2023 6:00:19 AM | [NSO Update] Visayas Grid-07/30/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2578MW, PK=1689MW, RR=40MW, NetOpMargin: AM=849, PM=852, EVE=542 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @325MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/30/2023 5:59:35 AM | [NSO Update] Visayas Grid-07/30/2023 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2578MW, PK=1689MW, RR=40MW, NetOpMargin: AM=849, PM=852, EVE=542 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @325MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/30/2023 5:59:26 AM | [NSO Update] Luzon Grid-07/30/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13908MW, PK=7610MW, RR=80MW, NetOpMargin: AM=6218, PM=5896, EVE=4759 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, GMEC 2 @150MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
7/30/2023 5:55:15 AM | [NSO Update] Luzon Grid-07/30/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13908MW, PK=7610MW, RR=80MW, NetOpMargin: AM=6218, PM=5896, EVE=4759 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, GMEC 2 @150MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
7/30/2023 5:26:05 AM | Luzon Grid-07/30/2023 05:23: Masinloc 3 emergency shutdown at 0522H due to coal reclaiming constraints. (Unplanned Outage) [WEBSMS] | CLUZ
7/30/2023 5:23:35 AM | Luzon Grid-07/30/2023 05:23: Masinloc 3 emergency shutdown at 0522H due to coal reclaiming constraints. (Unplanned Outage) [WEBSMS] | CLUZ
7/30/2023 4:23:26 AM | [NSO Update] Luzon Grid-07/30/2023 04:23: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm "FALCON" {KHANUN} was estimated based on all available data at 1,205 km East of Northern Luzon (17.7�N, 133.1�E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 115 km/h. It is moving North Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
7/30/2023 4:22:45 AM | [NSO Update] Mindanao Grid-07/30/2023 04:23: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm "FALCON" {KHANUN} was estimated based on all available data at 1,205 km East of Northern Luzon (17.7?N, 133.1?E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 115 km/h. It is moving North Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
7/30/2023 4:22:43 AM | [NSO Update] Luzon Grid-07/30/2023 04:23: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm ``FALCON`` {KHANUN} was estimated based on all available data at 1,205 km East of Northern Luzon (17.7?N, 133.1?E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 115 km/h. It is moving North Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
7/30/2023 4:22:08 AM | [NSO Update] Mindanao Grid-07/30/2023 04:23: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm "FALCON" {KHANUN} was estimated based on all available data at 1,205 km East of Northern Luzon (17.7�N, 133.1�E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 115 km/h. It is moving North Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
7/30/2023 4:21:14 AM | [NSO Update] Visayas Grid-07/30/2023 04:21: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm "FALCON" {KHANUN} was estimated based on all available data at 1,205 km East of Northern Luzon (17.7�N, 133.1�E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 115 km/h. It is moving North Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
7/30/2023 4:20:48 AM | [NSO Update] Visayas Grid-07/30/2023 04:21: Weather Update: At 3:00 AM today, the center of Severe Tropical Storm ``FALCON`` {KHANUN} was estimated based on all available data at 1,205 km East of Northern Luzon (17.7?N, 133.1?E) with maximum sustained winds of 95 km/h near the center and gustiness of up to 115 km/h. It is moving North Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
7/29/2023 10:40:51 PM | Mindanao Grid-07/29/2023 22:41: Lake Mainit Hydro cut in at 2236H. (Unplanned outage) [WEBSMS] | CMIN
7/29/2023 10:39:42 PM | Mindanao Grid-07/29/2023 22:41: Lake Mainit Hydro cut in at 2236H. (Unplanned outage) [WEBSMS] | CMIN
7/29/2023 10:28:30 PM | Mindanao Grid-07/29/2023 22:28: Lake Mainit Hydro tripped with 11MW load at 2222H. (Unplanned outage) [WEBSMS] | CMIN
7/29/2023 10:26:50 PM | Mindanao Grid-07/29/2023 22:28: Lake Mainit Hydro tripped with 11MW load at 2222H. (Unplanned outage) [WEBSMS] | CMIN
7/29/2023 7:47:49 PM | Mindanao Grid-07/29/2023 19:49: Baloi-Agus 5 138kv Line restored at 1759H. Planned outage. [WEBSMS] | CMIN
7/29/2023 7:47:25 PM | Mindanao Grid-07/29/2023 19:49: Baloi-Agus 5 138kv Line restored at 1759H. Planned outage. [WEBSMS] | CMIN
7/29/2023 7:01:52 PM | Luzon Grid-07/29/2023 19:01: San Esteban 230kV Bus 1 restored at 1859H (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 7:01:43 PM | Luzon Grid-07/29/2023 19:01: San Esteban 230kV Bus 1 restored at 1859H (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 6:15:42 PM | Mindanao Grid-07/29/2023 18:16: Asiga HEP cut-in at 1722H. (Unplanned Outage) [WEBSMS] | CMIN
7/29/2023 6:14:57 PM | Mindanao Grid-07/29/2023 18:16: Asiga HEP cut-in at 1722H. (Unplanned Outage) [WEBSMS] | CMIN
7/29/2023 6:14:04 PM | Mindanao Grid-07/29/2023 18:15: Lake Mainit (AGC) HEP cut-in at 1722H. (Unplanned Outage) [WEBSMS] | CMIN
7/29/2023 6:13:23 PM | Mindanao Grid-07/29/2023 18:15: Lake Mainit (AGC) HEP cut-in at 1722H. (Unplanned Outage) [WEBSMS] | CMIN
7/29/2023 5:52:52 PM | [NSO Update] Mindanao Grid-07/29/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3206MW, PK=2056MW, RR=20MW, NetOpMargin: EVE=1130 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @110MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
7/29/2023 5:52:20 PM | [NSO Update] Mindanao Grid-07/29/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3206MW, PK=2056MW, RR=20MW, NetOpMargin: EVE=1130 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @110MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
7/29/2023 5:52:17 PM | Luzon Grid-07/29/2023 17:47: Malaya 300MVA T01 energized at 1743H. Energized at 230kV side while the 115kV side associated HVE are on an ongoing upgrading project. (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 5:50:03 PM | Mindanao Grid-07/29/2023 17:51: Baloi-Tagoloan 138KV LINE restored at 1740h. Unplanned [WEBSMS] | CMIN
7/29/2023 5:50:01 PM | [NSO Update] Visayas Grid-07/29/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2553MW, PK=1928MW, RR=40MW, NetOpMargin: EVE=585 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @330MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/29/2023 5:49:57 PM | Mindanao Grid-07/29/2023 17:51: Baloi-Tagoloan 138KV LINE restored at 1740h. Unplanned [WEBSMS] | CMIN
7/29/2023 5:48:26 PM | [NSO Update] Visayas Grid-07/29/2023 17:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2553MW, PK=1928MW, RR=40MW, NetOpMargin: EVE=585 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @330MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/29/2023 5:47:52 PM | Luzon Grid-07/29/2023 17:47: Malaya 300MVA T01 energized at 1743H. Energized at 230kV side while the 115kV side associated HVE are on an ongoing upgrading project. (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 5:45:01 PM | [NSO Update] Luzon Grid-07/29/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13804MW, PK=8854MW, RR=170MW, NetOpMargin: EVE=4779 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, GMEC 2 @150MW, MSLC1 @280MW, MSLC3 @190MW, ILIJAN B @300MW [WEBSMS] | CLUZ
7/29/2023 5:43:45 PM | [NSO Update] Luzon Grid-07/29/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13804MW, PK=8854MW, RR=170MW, NetOpMargin: EVE=4779 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, GMEC 2 @150MW, MSLC1 @280MW, MSLC3 @190MW, ILIJAN B @300MW [WEBSMS] | CLUZ
7/29/2023 5:17:17 PM | Mindanao Grid-07/29/2023 17:18: BUNAWAN-DAVAO 138KV LINE 1 restored at 1649H. Planned outage. [WEBSMS] | CMIN
7/29/2023 5:16:43 PM | Mindanao Grid-07/29/2023 17:18: BUNAWAN-DAVAO 138KV LINE 1 restored at 1649H. Planned outage. [WEBSMS] | CMIN
7/29/2023 4:41:39 PM | Luzon Grid-07/29/2023 16:41: Binga 230kV Bus 1 energized at 1639H (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 4:40:56 PM | Luzon Grid-07/29/2023 16:41: Binga 230kV Bus 1 energized at 1639H (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 4:15:34 PM | Luzon Grid-07/29/2023 16:13: Bay-Makban Plant B 230kV line 2 energized at 1610H (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 4:13:19 PM | Mindanao Grid-07/29/2023 16:14: MPI - Digos cut-out at 1600H from DENR emission test. [WEBSMS] | CMIN
7/29/2023 4:13:18 PM | Mindanao Grid-07/29/2023 16:14: MPI - Digos cut-out at 1600H from DENR emission test. [WEBSMS] | CMIN
7/29/2023 4:13:01 PM | Luzon Grid-07/29/2023 16:13: Bay-Makban Plant B 230kV line 2 energized at 1610H (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 3:54:58 PM | Luzon Grid-07/29/2023 15:47: Naga - Tiwi A 230kV Line energized at 1545H (Unplanned Outage) [WEBSMS] | CLUZ
7/29/2023 3:47:48 PM | Luzon Grid-07/29/2023 15:47: Naga - Tiwi A 230kV Line energized at 1545H (Unplanned Outage) [WEBSMS] | CLUZ
7/29/2023 3:17:13 PM | Mindanao Grid-07/29/2023 15:18: WMPC DG09 cut-out at 1514H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/29/2023 3:16:54 PM | Mindanao Grid-07/29/2023 15:18: WMPC DG09 cut-out at 1514H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/29/2023 1:09:55 PM | [NSO Update] Mindanao Grid-07/29/2023 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3259MW, PK=2052MW, RR=20MW, NetOpMargin: PM=1187, EVE=1132 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @110MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
7/29/2023 1:09:29 PM | [NSO Update] Mindanao Grid-07/29/2023 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3259MW, PK=2052MW, RR=20MW, NetOpMargin: PM=1187, EVE=1132 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @110MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
7/29/2023 1:04:01 PM | [NSO Update] Visayas Grid-07/29/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2542MW, PK=1899MW, RR=40MW, NetOpMargin: PM=602, EVE=578 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @325MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/29/2023 1:03:43 PM | [NSO Update] Visayas Grid-07/29/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2542MW, PK=1899MW, RR=40MW, NetOpMargin: PM=602, EVE=578 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @325MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/29/2023 1:01:33 PM | [NSO Update] Luzon Grid-07/29/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14253MW, PK=9451MW, RR=260MW, NetOpMargin: PM=4542, EVE=4149 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, GMEC 2 @150MW, MSLC1 @280MW, MSLC3 @190MW, ILIJAN B @300MW [WEBSMS] | CLUZ
7/29/2023 1:00:39 PM | [NSO Update] Luzon Grid-07/29/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14253MW, PK=9451MW, RR=260MW, NetOpMargin: PM=4542, EVE=4149 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, GMEC 2 @150MW, MSLC1 @280MW, MSLC3 @190MW, ILIJAN B @300MW [WEBSMS] | CLUZ
7/29/2023 12:28:45 PM | Luzon Grid-07/29/2023 12:23: Naga-Tiwi A 230kV line de-energized at 1223H (Unplanned Outage) [WEBSMS] | CLUZ
7/29/2023 12:23:49 PM | Luzon Grid-07/29/2023 12:23: Naga-Tiwi A 230kV line de-energized at 1223H (Unplanned Outage) [WEBSMS] | CLUZ
7/29/2023 11:43:28 AM | Mindanao Grid-07/29/2023 11:44: BALOI - TAGOLOAN 138KV LINE tripped at 1128H. Unplanned. [WEBSMS] | CMIN
7/29/2023 10:22:01 AM | Mindanao Grid-07/29/2023 10:22: Pulangi 4 HEP Unit no. 2 cut-in at 1017H. (Unplanned Outage) [WEBSMS] | CMIN
7/29/2023 10:20:57 AM | Mindanao Grid-07/29/2023 10:22: Pulangi 4 HEP Unit no. 2 cut-in at 1017H. (Unplanned Outage) [WEBSMS] | CMIN
7/29/2023 9:53:16 AM | Mindanao Grid-07/29/2023 09:54: WMPC DG09 cut-in at 0951H for RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/29/2023 9:52:40 AM | Mindanao Grid-07/29/2023 09:54: WMPC DG09 cut-in at 0951H for RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/29/2023 8:41:05 AM | Mindanao Grid-07/29/2023 08:39: MPI - Digos Diesel Plant cut-in at 0800H for DENR emission test. [WEBSMS] | CMIN
7/29/2023 8:38:09 AM | Mindanao Grid-07/29/2023 08:39: MPI - Digos Diesel Plant cut-in at 0800H for DENR emission test. [WEBSMS] | CMIN
7/29/2023 8:08:33 AM | Luzon Grid-07/29/2023 08:04: San Esteban 230kV Bus 1 de-energized at 0802H (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 8:05:57 AM | Mindanao Grid-07/29/2023 08:06: Lake Mainit (AGC) HEP cut-out at 0802H. (Planned Outage) [WEBSMS] | CMIN
7/29/2023 8:04:54 AM | Mindanao Grid-07/29/2023 08:06: Lake Mainit (AGC) HEP cut-out at 0802H. (Planned Outage) [WEBSMS] | CMIN
7/29/2023 8:04:32 AM | Luzon Grid-07/29/2023 08:04: San Esteban 230kV Bus 1 de-energized at 0802H (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 7:35:11 AM | Luzon Grid-07/29/2023 07:32: Bay-Makban Plant B 230kV line 2 de-energized at 0730H (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 7:32:05 AM | Luzon Grid-07/29/2023 07:32: Bay-Makban Plant B 230kV line 2 de-energized at 0730H (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 7:21:50 AM | Luzon Grid-07/29/2023 07:21: Binga 230kV Bus 1 de-energized at 0721H (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 7:09:46 AM | Mindanao Grid-07/29/2023 07:10: BUNAWAN-DAVAO 138KV LINE 1 deenergized at 0702H, Planned outage. [WEBSMS] | CMIN
7/29/2023 7:09:18 AM | Mindanao Grid-07/29/2023 07:10: BUNAWAN-DAVAO 138KV LINE 1 deenergized at 0702H, Planned outage. [WEBSMS] | CMIN
7/29/2023 6:49:45 AM | Mindanao Grid-07/29/2023 06:49: BALOI-AGUS 5 138KV LINE deenergized at 0616H, Planned outage. [WEBSMS] | CMIN
7/29/2023 6:48:23 AM | Mindanao Grid-07/29/2023 06:49: BALOI-AGUS 5 138KV LINE deenergized at 0616H, Planned outage. [WEBSMS] | CMIN
7/29/2023 6:22:26 AM | Mindanao Grid-07/29/2023 06:23: BALOI-AGUS 5 138KV LINE deenergized at 0616H, Planned outage/GOMP. [WEBSMS] | CMIN
7/29/2023 5:49:25 AM | [NSO Update] Luzon Grid-07/29/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14503MW, PK=8629MW, RR=260MW, NetOpMargin: AM=5614, PM=4469, EVE=4189 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 1 @ 280MW, Masinloc 3 @ 190MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
7/29/2023 5:48:35 AM | [NSO Update] Visayas Grid-07/29/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2585MW, PK=1907MW, RR=40MW, NetOpMargin: AM=638, PM=564, EVE=404 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 325MW [WEBSMS] | CVIS
7/29/2023 5:47:48 AM | [NSO Update] Mindanao Grid-07/29/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3219MW, PK=1841MW, RR=20MW, NetOpMargin: AM=1358, PM=1244, EVE=1182 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @110MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
7/29/2023 5:47:34 AM | [NSO Update] Mindanao Grid-07/29/2023 05:49: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3219MW, PK=1841MW, RR=20MW, NetOpMargin: AM=1358, PM=1244, EVE=1182 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @110MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
7/29/2023 5:47:31 AM | Luzon Grid-07/29/2023 05:42: Malaya SS 300MVA T01 de-energized at 0541H. (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 5:46:40 AM | [NSO Update] Visayas Grid-07/29/2023 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2585MW, PK=1907MW, RR=40MW, NetOpMargin: AM=638, PM=564, EVE=404 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 325MW [WEBSMS] | CVIS
7/29/2023 5:42:30 AM | Luzon Grid-07/29/2023 05:42: Malaya SS 300MVA T01 de-energized at 0541H. (Planned Outage) [WEBSMS] | CLUZ
7/29/2023 4:41:44 AM | [NSO Update] Luzon Grid-07/29/2023 04:38: Weather Disturbance Alert Notice (WDAN) is issued at 0400H. Tropical Storm FALCON has entered the Philippine Area of Responsibility (PAR). The center was estimated based on all available data at 1,395 km East of Central Luzon (15.1?N, 134.6?E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CLUZ
7/29/2023 4:39:22 AM | [NSO Update] Mindanao Grid-07/29/2023 04:40: Weather Disturbance Alert Notice (WDAN) is issued at 0400H. Tropical Storm FALCON has entered the Philippine Area of Responsibility (PAR). The center was estimated based on all available data at 1,395 km East of Central Luzon (15.1�N, 134.6�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CMIN
7/29/2023 4:39:11 AM | [NSO Update] Mindanao Grid-07/29/2023 04:40: Weather Disturbance Alert Notice (WDAN) is issued at 0400H. Tropical Storm FALCON has entered the Philippine Area of Responsibility (PAR). The center was estimated based on all available data at 1,395 km East of Central Luzon (15.1?N, 134.6?E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CMIN
7/29/2023 4:38:59 AM | [NSO Update] Visayas Grid-07/29/2023 04:39: Weather Disturbance Alert Notice (WDAN) is issued at 0400H. Tropical Storm FALCON has entered the Philippine Area of Responsibility (PAR). The center was estimated based on all available data at 1,395 km East of Central Luzon (15.1�N, 134.6�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CVIS
7/29/2023 4:38:52 AM | [NSO Update] Visayas Grid-07/29/2023 04:39: Weather Disturbance Alert Notice (WDAN) is issued at 0400H. Tropical Storm FALCON has entered the Philippine Area of Responsibility (PAR). The center was estimated based on all available data at 1,395 km East of Central Luzon (15.1?N, 134.6?E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CVIS
7/29/2023 4:38:51 AM | [NSO Update] Visayas Grid-07/29/2023 04:37: Weather Update: At 3:00 AM today, the center of Tropical Storm ``FALCON`` {KHANUN} was estimated based on all available data at 1,395 km East of Central Luzon (15.1?N, 134.6?E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
7/29/2023 4:38:23 AM | [NSO Update] Luzon Grid-07/29/2023 04:38: Weather Disturbance Alert Notice (WDAN) is issued at 0400H. Tropical Storm FALCON has entered the Philippine Area of Responsibility (PAR). The center was estimated based on all available data at 1,395 km East of Central Luzon (15.1�N, 134.6�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CLUZ
7/29/2023 4:37:24 AM | [NSO Update] Mindanao Grid-07/29/2023 04:38: Weather Update: At 3:00 AM today, the center of Tropical Storm "FALCON" {KHANUN} was estimated based on all available data at 1,395 km East of Central Luzon (15.1�N, 134.6�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
7/29/2023 4:37:10 AM | [NSO Update] Visayas Grid-07/29/2023 04:37: Weather Update: At 3:00 AM today, the center of Tropical Storm "FALCON" {KHANUN} was estimated based on all available data at 1,395 km East of Central Luzon (15.1�N, 134.6�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
7/29/2023 4:36:45 AM | [NSO Update] Mindanao Grid-07/29/2023 04:38: Weather Update: At 3:00 AM today, the center of Tropical Storm "FALCON" {KHANUN} was estimated based on all available data at 1,395 km East of Central Luzon (15.1?N, 134.6?E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
7/29/2023 4:36:19 AM | [NSO Update] Luzon Grid-07/29/2023 04:36: Weather Update: At 3:00 AM today, the center of Tropical Storm "FALCON" {KHANUN} was estimated based on all available data at 1,395 km East of Central Luzon (15.1�N, 134.6�E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwestward at 15 km/h. Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
7/28/2023 9:18:15 PM | Mindanao Grid-07/28/2023 21:19: WMPC DG09 cut-out at 2111H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/28/2023 9:18:07 PM | Mindanao Grid-07/28/2023 21:19: WMPC DG09 cut-out at 2111H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/28/2023 6:22:13 PM | [NSO Update] Mindanao Grid-07/28/2023 18:23: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3220MW, PK=1960MW, RR=20MW, NetOpMargin: EVE=1239 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MCO @270MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @110MW, AG4 @146MW, AG5 @50MW, AG6 @134MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
7/28/2023 6:22:03 PM | [NSO Update] Mindanao Grid-07/28/2023 18:23: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3220MW, PK=1960MW, RR=20MW, NetOpMargin: EVE=1239 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MCO @270MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @110MW, AG4 @146MW, AG5 @50MW, AG6 @134MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
7/28/2023 6:13:51 PM | [NSO Update] Luzon Grid-07/28/2023 18:12: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13832MW, PK=9552MW, RR=260MW, NetOpMargin: EVE=4021 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 3 @ 175MW, Pagbilao 1 @ 340MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
7/28/2023 6:12:13 PM | [NSO Update] Luzon Grid-07/28/2023 18:12: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13832MW, PK=9552MW, RR=260MW, NetOpMargin: EVE=4021 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 3 @ 175MW, Pagbilao 1 @ 340MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
7/28/2023 6:11:56 PM | [NSO Update] Visayas Grid-07/28/2023 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2638MW, PK=1993MW, RR=40MW, NetOpMargin: EVE=605 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 312MW [WEBSMS] | CVIS
7/28/2023 4:19:03 PM | Visayas Grid-07/28/2023 16:19: Colon-Sibonga 69 KV line restored at 1618H. (unplanned outage). [WEBSMS] | CVIS
7/28/2023 4:18:41 PM | Visayas Grid-07/28/2023 16:19: Colon-Sibonga 69 KV line restored at 1618H. (unplanned outage). [WEBSMS] | CVIS
7/28/2023 3:50:26 PM | Visayas Grid-07/28/2023 15:50: Colon-Sibonga 69 KV line isolated at 1539H due to tripping of 100 MVA transformer 2. (Unplanned outage). [WEBSMS] | CVIS
7/28/2023 3:49:54 PM | Visayas Grid-07/28/2023 15:50: Colon-Sibonga 69 KV line isolated at 1539H due to tripping of 100 MVA transformer 2. (Unplanned outage). [WEBSMS] | CVIS
7/28/2023 3:34:13 PM | [NSO Update] Mindanao Grid-07/28/2023 15:35: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1530H from forward power direction (MVIP Test) [WEBSMS] | CMIN
7/28/2023 3:33:49 PM | [NSO Update] Visayas Grid-07/28/2023 15:34: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) blocked at 1530H from forward power direction (MVIP Test) [WEBSMS] | CVIS
7/28/2023 3:26:12 PM | Mindanao Grid-07/28/2023 15:26: Agus 6 HEP Unit no. 4 cut-in at 1507H. (Planned Outage) [WEBSMS] | CMIN
7/28/2023 3:25:09 PM | Mindanao Grid-07/28/2023 15:26: Agus 6 HEP Unit no. 4 cut-in at 1507H. (Planned Outage) [WEBSMS] | CMIN
7/28/2023 3:20:28 PM | Mindanao Grid-07/28/2023 15:18: Therma Marine 1 Unit 1 (Hybrid) cut-out at 1425H from energy (RTD) dispatch. [WEBSMS] | CMIN
7/28/2023 3:17:11 PM | Mindanao Grid-07/28/2023 15:18: Therma Marine 1 Unit 1 (Hybrid) cut-out at 1425H from energy (RTD) dispatch. [WEBSMS] | CMIN
7/28/2023 2:48:15 PM | Mindanao Grid-07/28/2023 14:49: WMPC DG07 cut-out at 1434H from energy (RTD) dispatch. [WEBSMS] | CMIN
7/28/2023 2:47:50 PM | Mindanao Grid-07/28/2023 14:49: WMPC DG07 cut-out at 1434H from energy (RTD) dispatch. [WEBSMS] | CMIN
7/28/2023 2:47:49 PM | Mindanao Grid-07/28/2023 14:48: King Energy Jimenez Unit 1 cut-out at 1436H from (RTD) energy dispatch. [WEBSMS] | CMIN
7/28/2023 2:47:18 PM | Mindanao Grid-07/28/2023 14:48: King Energy Jimenez Unit 1 cut-out at 1436H from (RTD) energy dispatch. [WEBSMS] | CMIN
7/28/2023 1:38:46 PM | Mindanao Grid-07/28/2023 13:39: TM1 Unit 1 cut-in as Energy at 1336H. Follow RTD [WEBSMS] | CMIN
7/28/2023 1:38:05 PM | Mindanao Grid-07/28/2023 13:39: TM1 Unit 1 cut-in as Energy at 1336H. Follow RTD [WEBSMS] | CMIN
7/28/2023 12:50:22 PM | [NSO Update] Luzon Grid-07/28/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14263MW, PK=10067MW, RR=260MW, NetOpMargin: PM=3937, EVE=4291 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC3 @175MW, ILIJAN B @300MW [WEBSMS] | CLUZ
7/28/2023 12:49:58 PM | [NSO Update] Luzon Grid-07/28/2023 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14263MW, PK=10067MW, RR=260MW, NetOpMargin: PM=3937, EVE=4291 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC3 @175MW, ILIJAN B @300MW [WEBSMS] | CLUZ
7/28/2023 12:40:46 PM | [NSO Update] Visayas Grid-07/28/2023 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2554MW, PK=2137MW, RR=40MW, NetOpMargin: PM=376, EVE=308 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @304MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/28/2023 12:40:24 PM | [NSO Update] Mindanao Grid-07/28/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3267MW, PK=2128MW, RR=20MW, NetOpMargin: PM=1118, EVE=1220 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @110MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
7/28/2023 12:40:12 PM | [NSO Update] Mindanao Grid-07/28/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3267MW, PK=2128MW, RR=20MW, NetOpMargin: PM=1118, EVE=1220 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @110MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @30MW, PG4 @90MW [WEBSMS] | CMIN
7/28/2023 12:38:50 PM | [NSO Update] Visayas Grid-07/28/2023 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2554MW, PK=2137MW, RR=40MW, NetOpMargin: PM=376, EVE=308 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @304MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/28/2023 12:22:04 PM | Mindanao Grid-07/28/2023 12:21: WMPC DG05 cut-in as Energy at 1218H. Follow RTD. [WEBSMS] | CMIN
7/28/2023 12:20:19 PM | Mindanao Grid-07/28/2023 12:21: WMPC DG05 cut-in as Energy at 1218H. Follow RTD. [WEBSMS] | CMIN
7/28/2023 12:17:55 PM | Mindanao Grid-07/28/2023 12:19: WMPC DG07 cut-in as Energy at 1216H. Follow RTD. [WEBSMS] | CMIN
7/28/2023 12:17:42 PM | Mindanao Grid-07/28/2023 12:19: WMPC DG07 cut-in as Energy at 1216H. Follow RTD. [WEBSMS] | CMIN
7/28/2023 11:47:02 AM | Mindanao Grid-07/28/2023 11:47: BISLIG SS 138KV BUS 1 restored at 1141H, Planned outage. [WEBSMS] | CMIN
7/28/2023 11:45:54 AM | Mindanao Grid-07/28/2023 11:47: BISLIG SS 138KV BUS 1 restored at 1141H, Planned outage. [WEBSMS] | CMIN
7/28/2023 11:43:43 AM | [NSO Update] Mindanao Grid-07/28/2023 11:45: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1130H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
7/28/2023 11:43:35 AM | [NSO Update] Mindanao Grid-07/28/2023 11:45: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1130H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
7/28/2023 11:42:52 AM | [NSO Update] Visayas Grid-07/28/2023 11:42: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1130H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
7/28/2023 11:42:17 AM | [NSO Update] Visayas Grid-07/28/2023 11:42: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1130H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
7/28/2023 9:13:18 AM | Mindanao Grid-07/28/2023 09:14: WMPC DG02 cut-in as RPS at 0901H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/28/2023 8:58:37 AM | Mindanao Grid-07/28/2023 08:58: WMPC DG09 cut-in as RPS at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/28/2023 8:57:22 AM | Mindanao Grid-07/28/2023 08:58: WMPC DG09 cut-in as RPS at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/28/2023 8:37:33 AM | Mindanao Grid-07/28/2023 08:38: BISLIG SS 138KV BUS 1 deenergized at 0834H, Planned outage. [WEBSMS] | CMIN
7/28/2023 8:37:07 AM | Mindanao Grid-07/28/2023 08:38: BISLIG SS 138KV BUS 1 deenergized at 0834H, Planned outage. [WEBSMS] | CMIN
7/28/2023 8:06:54 AM | Mindanao Grid-07/28/2023 08:08: AGREKO DIG cut in at 0801H (DENR EMISSION TEST) [WEBSMS] | CMIN
7/28/2023 8:06:50 AM | Mindanao Grid-07/28/2023 08:08: AGREKO DIG cut in at 0801H (DENR EMISSION TEST) [WEBSMS] | CMIN
7/28/2023 7:56:19 AM | Visayas Grid-07/28/2023 07:55: Frequency reaches up to 61.068_Hz at 0743H due to sudden loss of load at VECO, CEBU SUBGRID with estimated total load of 29 MW. [WEBSMS] | CVIS
7/28/2023 7:55:09 AM | Visayas Grid-07/28/2023 07:55: Frequency reaches up to 61.068_Hz at 0743H due to sudden loss of load at VECO, CEBU SUBGRID with estimated total load of 29 MW. [WEBSMS] | CVIS
7/28/2023 5:47:11 AM | Mindanao Grid-07/28/2023 05:48: Filinvest Development Corp. (FDC) U3 cut-out at 0533H on reserve shutdown. (Unplanned Outage) [WEBSMS] | CMIN
7/28/2023 5:46:49 AM | [NSO Update] Mindanao Grid-07/28/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3198MW, PK=2181MW, RR=20MW, NetOpMargin: AM=997, PM=981, EVE=1172 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @110MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @30MW, PG4 @65MW [WEBSMS] | CMIN
7/28/2023 5:46:48 AM | Mindanao Grid-07/28/2023 05:48: Filinvest Development Corp. (FDC) U3 cut-out at 0533H on reserve shutdown. (Unplanned Outage) [WEBSMS] | CMIN
7/28/2023 5:46:39 AM | [NSO Update] Mindanao Grid-07/28/2023 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3198MW, PK=2181MW, RR=20MW, NetOpMargin: AM=997, PM=981, EVE=1172 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @100MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @110MW, AG4 @146MW, AG5 @50MW, AG6 @124MW, AG7 @30MW, PG4 @65MW [WEBSMS] | CMIN
7/28/2023 5:45:43 AM | [NSO Update] Visayas Grid-07/28/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2624MW, PK=2095MW, RR=40MW, NetOpMargin: AM=489, PM=427, EVE=353 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @304MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/28/2023 5:44:03 AM | [NSO Update] Luzon Grid-07/28/2023 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14208MW, PK=9766MW, RR=260MW, NetOpMargin: AM=4182, PM=4058, EVE=4216 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC2 @170MW, MSLC3 @175MW, PBL1 @240MW, ILIJAN A @600MW, ILIJAN B @300MW, [WEBSMS] | CLUZ
7/28/2023 5:43:14 AM | [NSO Update] Visayas Grid-07/28/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2624MW, PK=2095MW, RR=40MW, NetOpMargin: AM=489, PM=427, EVE=353 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @304MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/28/2023 5:39:16 AM | [NSO Update] Luzon Grid-07/28/2023 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14208MW, PK=9766MW, RR=260MW, NetOpMargin: AM=4182, PM=4058, EVE=4216 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC2 @170MW, MSLC3 @175MW, PBL1 @240MW, ILIJAN A @600MW, ILIJAN B @300MW, [WEBSMS] | CLUZ
7/28/2023 5:16:47 AM | Mindanao Grid-07/28/2023 05:17: Tudaya 2 HEP emergency shutdown at 0440H due to insufficient water supply. (Unplanned Outage) [WEBSMS] | CMIN
7/28/2023 5:15:34 AM | Mindanao Grid-07/28/2023 05:17: Tudaya 2 HEP emergency shutdown at 0440H due to insufficient water supply. (Unplanned Outage) [WEBSMS] | CMIN
7/28/2023 5:13:53 AM | Mindanao Grid-07/28/2023 05:15: Sibulan A/B and Tudaya 1 HEP tripped with 24.5 MW total load at 0439H due to outage of DLPCs Puan Switching Station. (Unplanned Outage). [WEBSMS] | CMIN
7/28/2023 5:13:28 AM | Mindanao Grid-07/28/2023 05:15: Sibulan A/B and Tudaya 1 HEP tripped with 24.5 MW total load at 0439H due to outage of DLPCs Puan Switching Station. (Unplanned Outage). [WEBSMS] | CMIN
7/28/2023 4:26:25 AM | [NSO Update] Mindanao Grid-07/28/2023 04:27: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
7/28/2023 4:26:12 AM | [NSO Update] Visayas Grid-07/28/2023 04:25: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
7/28/2023 4:25:43 AM | [NSO Update] Mindanao Grid-07/28/2023 04:27: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CMIN
7/28/2023 4:25:41 AM | [NSO Update] Visayas Grid-07/28/2023 04:25: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CVIS
7/28/2023 4:25:07 AM | [NSO Update] Luzon Grid-07/28/2023 04:25: Weather Update: Southwest Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
7/28/2023 4:24:03 AM | Visayas Grid-07/28/2023 04:24: 138KV Calung-calung-Daanlungsod Line 1 energized at 0403H, refilling of SF6 gas on PCB CB04 (7LI1CGC-DNU) at Daanlungsod SS activity completed. [WEBSMS] | CVIS
7/28/2023 4:23:44 AM | Visayas Grid-07/28/2023 04:24: 138KV Calung-calung-Daanlungsod Line 1 energized at 0403H, refilling of SF6 gas on PCB CB04 (7LI1CGC-DNU) at Daanlungsod SS activity completed. [WEBSMS] | CVIS
7/28/2023 12:46:27 AM | Visayas Grid-07/28/2023 00:45: 138KV Calung-calung-Daanlungsod Line 1 de-energized at 0039H, to facilitate refilling of SF6 gas on PCB CB04 (7LI1CGC-DNU) at Daanlungsod SS. ECD: 0200H. [WEBSMS] | CVIS
7/28/2023 12:45:07 AM | Visayas Grid-07/28/2023 00:45: 138KV Calung-calung-Daanlungsod Line 1 de-energized at 0039H, to facilitate refilling of SF6 gas on PCB CB04 (7LI1CGC-DNU) at Daanlungsod SS. ECD: 0200H. [WEBSMS] | CVIS
7/28/2023 12:30:41 AM | Visayas Grid-07/28/2023 00:30: Magdugo SS, 138KV Daanlungsod-Magdugo Line de-energized at 0018H to prevent overloading of 138KV Daanlungsod-Calung-calung Line 2 during maintenance of 138KV Daanlungsod-Calung-calung Line 1, refilling of SF6 gas at PCB 7LI1 CGC-DNU breaker. [WEBSMS] | CVIS
7/28/2023 12:30:39 AM | Visayas Grid-07/28/2023 00:30: Magdugo SS, 138KV Daanlungsod-Magdugo Line de-energized at 0018H to prevent overloading of 138KV Daanlungsod-Calung-calung Line 2 during maintenance of 138KV Daanlungsod-Calung-calung Line 1, refilling of SF6 gas at PCB 7LI1 CGC-DNU breaker. [WEBSMS] | CVIS
7/28/2023 12:13:20 AM | Mindanao Grid-07/28/2023 00:13: Pulangi 4 HEP Unit no. 2 emergency shutdown at 0010H due to insufficient water supply. (Unplanned Outage) [WEBSMS] | CMIN
7/28/2023 12:11:49 AM | Mindanao Grid-07/28/2023 00:13: Pulangi 4 HEP Unit no. 2 emergency shutdown at 0010H due to insufficient water supply. (Unplanned Outage) [WEBSMS] | CMIN
7/27/2023 11:16:38 PM | Mindanao Grid-07/27/2023 23:17: Minergy Coal Balingasag Plant U1 emergency shutdown at 2159H due to coal feeder problem. (Unplanned Outage). [WEBSMS] | CMIN
7/27/2023 11:16:13 PM | Mindanao Grid-07/27/2023 23:17: Minergy Coal Balingasag Plant U1 emergency shutdown at 2159H due to coal feeder problem. (Unplanned Outage). [WEBSMS] | CMIN
7/27/2023 10:03:17 PM | Mindanao Grid-07/27/2023 22:03: Lake Mainit Hydro online at 2155H. (Unplanned Outage) [WEBSMS] | CMIN
7/27/2023 10:01:55 PM | Mindanao Grid-07/27/2023 22:03: Lake Mainit Hydro online at 2155H. (Unplanned Outage) [WEBSMS] | CMIN
7/27/2023 9:20:41 PM | Mindanao Grid-07/27/2023 21:22: WMPC DG09 cut-out at 2113H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/27/2023 9:19:56 PM | Mindanao Grid-07/27/2023 21:22: WMPC DG09 cut-out at 2113H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/27/2023 9:05:39 PM | Mindanao Grid-07/27/2023 21:07: Lake Mainit Hydro tripped with 11MW load at 2058H(Unplanned Outage) [WEBSMS] | CMIN
7/27/2023 6:43:40 PM | Luzon Grid-07/27/2023 18:42: Laoag - Caparispisan (Pagudpud Wind Farm) 115kV line looped at Caparispisan side at 1839H. (Unplanned Outage) [WEBSMS] | CLUZ
7/27/2023 6:42:07 PM | Luzon Grid-07/27/2023 18:42: Laoag - Caparispisan (Pagudpud Wind Farm) 115kV line looped at Caparispisan side at 1839H. (Unplanned Outage) [WEBSMS] | CLUZ
7/27/2023 6:05:25 PM | [NSO Update] Mindanao Grid-07/27/2023 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3224MW, PK=2123MW, RR=20MW, NetOpMargin: EVE=1081 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @135MW, AG4 @140MW, AG5 @48MW, AG6 @74MW, AG7 @35MW, PG4 @125MW [WEBSMS] | CMIN
7/27/2023 6:05:20 PM | [NSO Update] Mindanao Grid-07/27/2023 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3224MW, PK=2123MW, RR=20MW, NetOpMargin: EVE=1081 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @135MW, AG4 @140MW, AG5 @48MW, AG6 @74MW, AG7 @35MW, PG4 @125MW [WEBSMS] | CMIN
7/27/2023 6:02:04 PM | [NSO Update] Visayas Grid-07/27/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2627MW, PK=2043MW, RR=40MW, NetOpMargin: EVE=545 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @301MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/27/2023 6:00:27 PM | [NSO Update] Visayas Grid-07/27/2023 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2627MW, PK=2043MW, RR=40MW, NetOpMargin: EVE=545 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @301MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/27/2023 5:53:53 PM | [NSO Update] Luzon Grid-07/27/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12993MW, PK=9321MW, RR=260MW, NetOpMargin: EVE=3412 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC2 @170MW, MSLC3 @180MW, ILIJAN A @340MW, ILIJAN B @165MW [WEBSMS] | CLUZ
7/27/2023 5:53:09 PM | [NSO Update] Luzon Grid-07/27/2023 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12993MW, PK=9321MW, RR=260MW, NetOpMargin: EVE=3412 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CLC2 @170MW, MSLC3 @180MW, ILIJAN A @340MW, ILIJAN B @165MW [WEBSMS] | CLUZ
7/27/2023 5:16:59 PM | Mindanao Grid-07/27/2023 17:17: Aurora SS 138kV Bus 2 energized at 1631H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
7/27/2023 5:16:01 PM | Mindanao Grid-07/27/2023 17:17: Aurora SS 138kV Bus 2 energized at 1631H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
7/27/2023 4:41:31 PM | Mindanao Grid-07/27/2023 16:42: WMPC DG05 cut-out at 1614H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/27/2023 4:41:30 PM | Mindanao Grid-07/27/2023 16:42: WMPC DG05 cut-out at 1614H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/27/2023 4:26:25 PM | Luzon Grid-07/27/2023 16:24: San Esteban-Bantay 115kV line restored at 1622H (Unplanned Outage) [WEBSMS] | CLUZ
7/27/2023 4:24:46 PM | Luzon Grid-07/27/2023 16:24: San Esteban-Bantay 115kV line restored at 1622H (Unplanned Outage) [WEBSMS] | CLUZ
7/27/2023 4:00:13 PM | Luzon Grid-07/27/2023 15:54: Naga-Tayabas 230kV line 1 restored at 1552H (Planned Outage) [WEBSMS] | CLUZ
7/27/2023 3:54:08 PM | Luzon Grid-07/27/2023 15:54: Naga-Tayabas 230kV line 1 restored at 1552H (Planned Outage) [WEBSMS] | CLUZ
7/27/2023 3:24:45 PM | [NSO Update] Mindanao Grid-07/27/2023 15:24: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1519H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
7/27/2023 3:22:56 PM | [NSO Update] Visayas Grid-07/27/2023 15:22: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1519H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
7/27/2023 3:22:38 PM | [NSO Update] Mindanao Grid-07/27/2023 15:24: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1519H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
7/27/2023 3:22:07 PM | [NSO Update] Visayas Grid-07/27/2023 15:22: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1519H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
7/27/2023 2:49:44 PM | [NSO Update] Mindanao Grid-07/27/2023 14:49: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked/ de-blocked at 1445H with power going to Visayas from Mindanao (MVIP Test). [WEBSMS] | CMIN
7/27/2023 2:48:40 PM | [NSO Update] Visayas Grid-07/27/2023 14:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked/ de-blocked at 1445H with power going to Visayas from Mindanao (MVIP Test). [WEBSMS] | CVIS
7/27/2023 2:47:57 PM | [NSO Update] Mindanao Grid-07/27/2023 14:49: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked/ de-blocked at 1445H with power going to Visayas from Mindanao (MVIP Test). [WEBSMS] | CMIN
7/27/2023 2:47:38 PM | [NSO Update] Visayas Grid-07/27/2023 14:47: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked/ de-blocked at 1445H with power going to Visayas from Mindanao (MVIP Test). [WEBSMS] | CVIS
7/27/2023 2:18:57 PM | [NSO Update] Mindanao Grid-07/27/2023 14:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked/ de-blocked at 1415H with power going to Mindanao from Visayas (MVIP Test). [WEBSMS] | CMIN
7/27/2023 2:18:31 PM | [NSO Update] Mindanao Grid-07/27/2023 14:20: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked/ de-blocked at 1415H with power going to Mindanao from Visayas (MVIP Test). [WEBSMS] | CMIN
7/27/2023 2:18:17 PM | [NSO Update] Visayas Grid-07/27/2023 14:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked/ de-blocked at 1415H with power going to Mindanao from Visayas (MVIP Test). [WEBSMS] | CVIS
7/27/2023 2:17:51 PM | [NSO Update] Visayas Grid-07/27/2023 14:18: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked/ de-blocked at 1415H with power going to Mindanao from Visayas (MVIP Test). [WEBSMS] | CVIS
7/27/2023 1:33:02 PM | [NSO Update] Mindanao Grid-07/27/2023 13:32: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1331H with power going to Visayas (MVIP Test) [WEBSMS] | CMIN
7/27/2023 1:31:34 PM | [NSO Update] Mindanao Grid-07/27/2023 13:32: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1331H with power going to Visayas (MVIP Test) [WEBSMS] | CMIN
7/27/2023 1:31:23 PM | [NSO Update] Visayas Grid-07/27/2023 13:31: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1331H with power going to Visayas (MVIP Test) [WEBSMS] | CVIS
7/27/2023 1:31:20 PM | [NSO Update] Visayas Grid-07/27/2023 13:31: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1331H with power going to Visayas (MVIP Test) [WEBSMS] | CVIS
7/27/2023 1:15:13 PM | Mindanao Grid-07/27/2023 13:16: Agus 7 Unit 1 cut in at 1312H from PMS(Non-GOMP) [WEBSMS] | CMIN
7/27/2023 1:14:40 PM | Mindanao Grid-07/27/2023 13:16: Agus 7 Unit 1 cut in at 1312H from PMS(Non-GOMP) [WEBSMS] | CMIN
7/27/2023 1:06:40 PM | Luzon Grid-07/27/2023 13:06: Currimao-Paguludan 69kV line(Customer owned and maintained) restored at 1304H (Unplanned Outage) [WEBSMS] | CLUZ
7/27/2023 1:06:26 PM | Luzon Grid-07/27/2023 13:06: Currimao-Paguludan 69kV line(Customer owned and maintained) restored at 1304H (Unplanned Outage) [WEBSMS] | CLUZ
7/27/2023 1:00:58 PM | [NSO Update] Luzon Grid-07/27/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13278MW, PK=10324MW, RR=260MW, NetOpMargin: PM=2694, EVE=3097 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 3 @ 180MW, Ilijan A @ 340MW, Ilijan B @ 165MW [WEBSMS] | CLUZ
7/27/2023 1:00:47 PM | [NSO Update] Visayas Grid-07/27/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2586MW, PK=2118MW, RR=40MW, NetOpMargin: PM=428, EVE=578 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 301MW [WEBSMS] | CVIS
7/27/2023 12:59:55 PM | [NSO Update] Mindanao Grid-07/27/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3256MW, PK=2288MW, RR=20MW, NetOpMargin: PM=948, EVE=989 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MCO @270MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @50MW, AG2 @135MW, AG4 @140MW, AG5 @70MW, AG6 @74MW, AG7 @15MW, PG4 @125MW [WEBSMS] | CMIN
7/27/2023 12:59:52 PM | [NSO Update] Visayas Grid-07/27/2023 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2586MW, PK=2118MW, RR=40MW, NetOpMargin: PM=428, EVE=578 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 301MW [WEBSMS] | CVIS
7/27/2023 12:59:39 PM | [NSO Update] Mindanao Grid-07/27/2023 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3256MW, PK=2288MW, RR=20MW, NetOpMargin: PM=948, EVE=989 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MCO @270MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @50MW, AG2 @135MW, AG4 @140MW, AG5 @70MW, AG6 @74MW, AG7 @15MW, PG4 @125MW [WEBSMS] | CMIN
7/27/2023 11:22:56 AM | [NSO Update] Mindanao Grid-07/27/2023 11:22: Weather Disturbance Alert Notice (WDAN) has been lifted today, July 27, 2023 at 1100H. Typhoon ?EGAY? maintains its strength and is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon EGAY was estimated based on all available data at 255 km West of Itbayat, Batanes (OUTSIDE PAR) (20.9 ?N, 119.4 ?E ) [WEBSMS] | CMIN
7/27/2023 11:21:12 AM | [NSO Update] Mindanao Grid-07/27/2023 11:22: Weather Disturbance Alert Notice (WDAN) has been lifted today, July 27, 2023 at 1100H. Typhoon �EGAY� maintains its strength and is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon EGAY was estimated based on all available data at 255 km West of Itbayat, Batanes (OUTSIDE PAR) (20.9 �N, 119.4 �E ) [WEBSMS] | CMIN
7/27/2023 11:21:07 AM | [NSO Update] Visayas Grid-07/27/2023 11:21: Weather Disturbance Alert Notice (WDAN) has been lifted today, July 27, 2023 at 1100H. Typhoon ?EGAY? maintains its strength and is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon EGAY was estimated based on all available data at 255 km West of Itbayat, Batanes (OUTSIDE PAR) (20.9 ?N, 119.4 ?E ) [WEBSMS] | CVIS
7/27/2023 11:20:54 AM | [NSO Update] Visayas Grid-07/27/2023 11:21: Weather Disturbance Alert Notice (WDAN) has been lifted today, July 27, 2023 at 1100H. Typhoon �EGAY� maintains its strength and is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon EGAY was estimated based on all available data at 255 km West of Itbayat, Batanes (OUTSIDE PAR) (20.9 �N, 119.4 �E ) [WEBSMS] | CVIS
7/27/2023 11:20:13 AM | [NSO Update] Luzon Grid-07/27/2023 11:20: Weather Disturbance Alert Notice (WDAN) has been lifted today, July 27, 2023 at 1100H. Typhoon �EGAY� maintains its strength and is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon EGAY was estimated based on all available data at 255 km West of Itbayat, Batanes (OUTSIDE PAR) (20.9 �N, 119.4 �E ) [WEBSMS] | CLUZ
7/27/2023 11:19:55 AM | [NSO Update] Luzon Grid-07/27/2023 11:20: Weather Disturbance Alert Notice (WDAN) has been lifted today, July 27, 2023 at 1100H. Typhoon ?EGAY? maintains its strength and is now outside the Philippine Area of Responsibility (PAR). The center of the eye of Typhoon EGAY was estimated based on all available data at 255 km West of Itbayat, Batanes (OUTSIDE PAR) (20.9 ?N, 119.4 ?E ) [WEBSMS] | CLUZ
7/27/2023 10:54:36 AM | Mindanao Grid-07/27/2023 10:54: WMPC DG05 cut-in as RPS at 1051H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/27/2023 10:53:35 AM | Mindanao Grid-07/27/2023 10:54: WMPC DG05 cut-in as RPS at 1051H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/27/2023 10:49:36 AM | Mindanao Grid-07/27/2023 10:49: FDC Unit 1 cut in at 1046H. [WEBSMS] | CMIN
7/27/2023 10:48:02 AM | Mindanao Grid-07/27/2023 10:49: FDC Unit 1 cut in at 1046H. [WEBSMS] | CMIN
7/27/2023 10:26:13 AM | Luzon Grid-07/27/2023 10:25: Pagbilao Unit 1 online at 1024H (Planned Outage) [WEBSMS] | CLUZ
7/27/2023 10:25:46 AM | Luzon Grid-07/27/2023 10:25: Pagbilao Unit 1 online at 1024H (Planned Outage) [WEBSMS] | CLUZ
7/27/2023 9:09:52 AM | Mindanao Grid-07/27/2023 09:10: WMPC DG09 cut-in as RPS at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/27/2023 9:09:01 AM | Mindanao Grid-07/27/2023 09:10: WMPC DG09 cut-in as RPS at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/27/2023 9:02:53 AM | Mindanao Grid-07/27/2023 09:02: FDC Unit 1 tripped at 0856H with generation of 7.45MW. [WEBSMS] | CMIN
7/27/2023 9:01:27 AM | Mindanao Grid-07/27/2023 09:02: FDC Unit 1 tripped at 0856H with generation of 7.45MW. [WEBSMS] | CMIN
7/27/2023 8:49:35 AM | Mindanao Grid-07/27/2023 08:49: Aurora SS 138kV Bus 2 deenergized at 0807H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
7/27/2023 8:47:40 AM | Mindanao Grid-07/27/2023 08:49: Aurora SS 138kV Bus 2 deenergized at 0807H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
7/27/2023 8:40:20 AM | Mindanao Grid-07/27/2023 08:41: FDC Unit 1 cut in at 0823H from reserved shutdown. [WEBSMS] | CMIN
7/27/2023 8:39:34 AM | Mindanao Grid-07/27/2023 08:41: FDC Unit 1 cut in at 0823H from reserved shutdown. [WEBSMS] | CMIN
7/27/2023 8:29:34 AM | Mindanao Grid-07/27/2023 08:28: Kauswagan-Lala 230kV L2 deenergized 0728H. P & E emergency shutdown request to undertake stringing works for the conversion from single conductor to bundle of four (4). [WEBSMS] | CMIN
7/27/2023 8:27:21 AM | Mindanao Grid-07/27/2023 08:28: Kauswagan-Lala 230kV L2 deenergized 0728H. P & E emergency shutdown request to undertake stringing works for the conversion from single conductor to bundle of four (4). [WEBSMS] | CMIN
7/27/2023 8:11:13 AM | Mindanao Grid-07/27/2023 08:08: Aggreko Digos (APD) sync at 0800H for DENR emission testing. [WEBSMS] | CMIN
7/27/2023 8:07:28 AM | Mindanao Grid-07/27/2023 08:08: Aggreko Digos (APD) sync at 0800H for DENR emission testing. [WEBSMS] | CMIN
7/27/2023 6:39:28 AM | Luzon Grid-07/27/2023 06:37: Tayabas-Naga 230kV line 1 de-energized at 0635H (Planned Outage) [WEBSMS] | CLUZ
7/27/2023 6:37:45 AM | Luzon Grid-07/27/2023 06:37: Tayabas-Naga 230kV line 1 de-energized at 0635H (Planned Outage) [WEBSMS] | CLUZ
7/27/2023 5:53:06 AM | [NSO Update] Mindanao Grid-07/27/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3254MW, PK=2215MW, RR=20MW, NetOpMargin: AM=1019, PM=993, EVE=1141 Highest Unit O/L: GNPK 1& 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @50MW, AG2 @135MW, AG4 @140MW, AG5 @50MW, AG6 @74MW, AG7 @15MW, PG4 @125MW [WEBSMS] | CMIN
7/27/2023 5:52:09 AM | [NSO Update] Mindanao Grid-07/27/2023 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3254MW, PK=2215MW, RR=20MW, NetOpMargin: AM=1019, PM=993, EVE=1141 Highest Unit O/L: GNPK 1& 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @50MW, AG2 @135MW, AG4 @140MW, AG5 @50MW, AG6 @74MW, AG7 @15MW, PG4 @125MW [WEBSMS] | CMIN
7/27/2023 5:43:23 AM | [NSO Update] Visayas Grid-07/27/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2451MW, PK=2000MW, RR=40MW, NetOpMargin: AM=411, PM=301, EVE=271 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @301MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/27/2023 5:43:03 AM | [NSO Update] Luzon Grid-07/27/2023 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13466MW, PK=9871MW, RR=260MW, NetOpMargin: AM=3335, PM=3092, EVE=3505 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @170MW, MASINLOC 3 @180MW, ILIJAN A @340MW, ILIJAN B @165MW [WEBSMS] | CLUZ
7/27/2023 5:41:11 AM | [NSO Update] Visayas Grid-07/27/2023 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2451MW, PK=2000MW, RR=40MW, NetOpMargin: AM=411, PM=301, EVE=271 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @301MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/27/2023 5:38:49 AM | [NSO Update] Luzon Grid-07/27/2023 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13466MW, PK=9871MW, RR=260MW, NetOpMargin: AM=3335, PM=3092, EVE=3505 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @170MW, MASINLOC 3 @180MW, ILIJAN A @340MW, ILIJAN B @165MW [WEBSMS] | CLUZ
7/27/2023 5:12:22 AM | Luzon Grid-07/27/2023 05:12: San Jose-Camarin 115kV L restored at 0511H (Planned Outage) [WEBSMS] | CLUZ
7/27/2023 4:16:21 AM | [NSO Update] Luzon Grid-07/27/2023 04:11: Weather Update: At 3:00 AM today, the center of the eye of Typhoon ``EGAY`` {DOKSURI} was estimated based on all available data at 200 km West Southwest of Basco, Batanes (20.0?N, 120.1?E) with max. sustained winds of 150 km/h near the center & gustiness of up to 185 km/h. It is moving Northwestward at 15 km/h. Southwest Monsoon affecting Southern Luzon & Visayas. [WEBSMS] | CLUZ
7/27/2023 4:14:26 AM | [NSO Update] Mindanao Grid-07/27/2023 04:14: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "EGAY" {DOKSURI} was estimated based on all available data at 200 km West Southwest of Basco, Batanes (20.0?N, 120.1?E) with max. sustained winds of 150 km/h near the center & gustiness of up to 185 km/h. It is moving Northwestward at 15 km/h. Southwest Monsoon affecting Southern Luzon & Visayas. [WEBSMS] | CMIN
7/27/2023 4:12:45 AM | [NSO Update] Mindanao Grid-07/27/2023 04:14: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "EGAY" {DOKSURI} was estimated based on all available data at 200 km West Southwest of Basco, Batanes (20.0�N, 120.1�E) with max. sustained winds of 150 km/h near the center & gustiness of up to 185 km/h. It is moving Northwestward at 15 km/h. Southwest Monsoon affecting Southern Luzon & Visayas. [WEBSMS] | CMIN
7/27/2023 4:11:46 AM | [NSO Update] Visayas Grid-07/27/2023 04:12: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "EGAY" {DOKSURI} was estimated based on all available data at 200 km West Southwest of Basco, Batanes (20.0�N, 120.1�E) with max. sustained winds of 150 km/h near the center & gustiness of up to 185 km/h. It is moving Northwestward at 15 km/h. Southwest Monsoon affecting Southern Luzon & Visayas. [WEBSMS] | CVIS
7/27/2023 4:11:16 AM | [NSO Update] Luzon Grid-07/27/2023 04:11: Weather Update: At 3:00 AM today, the center of the eye of Typhoon "EGAY" {DOKSURI} was estimated based on all available data at 200 km West Southwest of Basco, Batanes (20.0�N, 120.1�E) with max. sustained winds of 150 km/h near the center & gustiness of up to 185 km/h. It is moving Northwestward at 15 km/h. Southwest Monsoon affecting Southern Luzon & Visayas. [WEBSMS] | CLUZ
7/27/2023 12:39:32 AM | Luzon Grid-07/27/2023 00:35: San Jose-Camarin 115kV L de-energized at 0034H (Planned Outage) [WEBSMS] | CLUZ
7/27/2023 12:35:04 AM | Luzon Grid-07/27/2023 00:35: San Jose-Camarin 115kV L de-energized at 0034H (Planned Outage) [WEBSMS] | CLUZ
7/26/2023 11:59:18 PM | Luzon Grid-07/26/2023 23:58: MPGC 1 shutdown at 2357H (Commissioning Test) [WEBSMS] | CLUZ
7/26/2023 11:58:09 PM | Luzon Grid-07/26/2023 23:58: MPGC 1 shutdown at 2357H (Commissioning Test) [WEBSMS] | CLUZ
7/26/2023 10:32:47 PM | Luzon Grid-07/26/2023 22:33: Concepcion-Concepcion 1 Solar PP 69kV Line restored at 2230H (Planned Outage) [WEBSMS] | CLUZ
7/26/2023 10:32:36 PM | Luzon Grid-07/26/2023 22:33: Concepcion-Concepcion 1 Solar PP 69kV Line restored at 2230H (Planned Outage) [WEBSMS] | CLUZ
7/26/2023 9:20:57 PM | Mindanao Grid-07/26/2023 21:21: WMPC DG09 cut-out at 2114H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/26/2023 9:19:07 PM | Mindanao Grid-07/26/2023 21:21: WMPC DG09 cut-out at 2114H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/26/2023 7:36:02 PM | Luzon Grid-07/26/2023 19:36: Concepcion-Concepcion 1 Solar PP 69kV Line de-energized at 1933H (Planned Outage) [WEBSMS] | CLUZ
7/26/2023 7:35:40 PM | Luzon Grid-07/26/2023 19:36: Concepcion-Concepcion 1 Solar PP 69kV Line de-energized at 1933H (Planned Outage) [WEBSMS] | CLUZ
7/26/2023 7:02:42 PM | Luzon Grid-07/26/2023 19:03: GNPD 2 online at 1901H (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 7:02:29 PM | Luzon Grid-07/26/2023 19:03: GNPD 2 online at 1901H (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 6:07:39 PM | [NSO Update] Mindanao Grid-07/26/2023 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3199MW, PK=2147MW, RR=20MW, NetOpMargin: EVE=1032 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @52MW, AG2 @105MW, AG4 @140MW, AG5 @48MW, AG6 @121MW, AG7 @15MW, PG4 @120MW [WEBSMS] | CMIN
7/26/2023 6:07:34 PM | [NSO Update] Mindanao Grid-07/26/2023 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3199MW, PK=2147MW, RR=20MW, NetOpMargin: EVE=1032 Highest Unit O/L: GNPK 1 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @52MW, AG2 @105MW, AG4 @140MW, AG5 @48MW, AG6 @121MW, AG7 @15MW, PG4 @120MW [WEBSMS] | CMIN
7/26/2023 6:02:33 PM | Luzon Grid-07/26/2023 18:01: San Esteban-Bantay 115kV line tripped at 1752H (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 6:01:03 PM | Luzon Grid-07/26/2023 18:01: San Esteban-Bantay 115kV line tripped at 1752H (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 5:59:19 PM | Luzon Grid-07/26/2023 17:56: San Jose - Tayabas 500kV Line 2 re-energized @Tayabas side at 1755H (Planned Outage) [WEBSMS] | CLUZ
7/26/2023 5:55:30 PM | Luzon Grid-07/26/2023 17:56: San Jose - Tayabas 500kV Line 2 re-energized @Tayabas side at 1755H (Planned Outage) [WEBSMS] | CLUZ
7/26/2023 5:55:25 PM | [NSO Update] Visayas Grid-07/26/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2361MW, PK=1940MW, RR=40MW, NetOpMargin: EVE=381 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 280MW [WEBSMS] | CVIS
7/26/2023 5:54:24 PM | [NSO Update] Visayas Grid-07/26/2023 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2361MW, PK=1940MW, RR=40MW, NetOpMargin: EVE=381 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 280MW [WEBSMS] | CVIS
7/26/2023 5:52:30 PM | Luzon Grid-07/26/2023 17:51: Correction: San Esteban-Bantay 115kV line restored at 1742H (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 5:50:27 PM | Luzon Grid-07/26/2023 17:51: Correction: San Esteban-Bantay 115kV line restored at 1742H (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 5:49:10 PM | Luzon Grid-07/26/2023 17:49: San Esteban-Bantay 115kV line restored at 1748H (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 5:48:29 PM | Luzon Grid-07/26/2023 17:49: San Esteban-Bantay 115kV line restored at 1748H (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 5:46:40 PM | Luzon Grid-07/26/2023 17:47: San Esteban-Bantay 115kV line tripped at 1742H (Planned Outage) [WEBSMS] | CLUZ
7/26/2023 5:41:16 PM | [NSO Update] Luzon Grid-07/26/2023 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12351MW, PK=9120MW, RR=260MW, NetOpMargin: EVE=3151 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Calaca 2 @170MW, Masinloc 3 @ 185MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
7/26/2023 5:39:12 PM | [NSO Update] Mindanao Grid-07/26/2023 17:40: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1702H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
7/26/2023 5:38:09 PM | [NSO Update] Visayas Grid-07/26/2023 17:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1702H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
7/26/2023 5:38:08 PM | [NSO Update] Mindanao Grid-07/26/2023 17:40: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1702H with power going to Visayas (MVIP Test). [WEBSMS] | CMIN
7/26/2023 5:37:04 PM | [NSO Update] Visayas Grid-07/26/2023 17:37: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1702H with power going to Visayas (MVIP Test). [WEBSMS] | CVIS
7/26/2023 4:52:37 PM | Luzon Grid-07/26/2023 16:52: San Esteban-Bantay 115kV line auto-tripped at 1644H. Auto-reclosing was successful at Bantay side. The line was looped at San Esteban at 1652H. [WEBSMS] | CLUZ
7/26/2023 4:51:59 PM | Luzon Grid-07/26/2023 16:52: San Esteban-Bantay 115kV line auto-tripped at 1644H. Auto-reclosing was successful at Bantay side. The line was looped at San Esteban at 1652H. [WEBSMS] | CLUZ
7/26/2023 4:47:26 PM | Luzon Grid-07/26/2023 16:48: Currimao - Paguludan 69kV Line tripped at 1639H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 4:42:37 PM | Luzon Grid-07/26/2023 16:38: Hermosa - BCCPP 230kV Line 3 restored at 1637H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 4:38:00 PM | Luzon Grid-07/26/2023 16:38: Hermosa - BCCPP 230kV Line 3 restored at 1637H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 4:31:04 PM | [NSO Update] Mindanao Grid-07/26/2023 16:33: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1610H and de-blocked at 1611 with power going to Visayas from Mindanao (MVIP Test). [WEBSMS] | CMIN
7/26/2023 4:30:51 PM | [NSO Update] Mindanao Grid-07/26/2023 16:33: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1610H and de-blocked at 1611 with power going to Visayas from Mindanao (MVIP Test). [WEBSMS] | CMIN
7/26/2023 4:30:50 PM | [NSO Update] Mindanao Grid-07/26/2023 16:32: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked/ de-blocked at 1533H with power going to Mindanao from Visayas(MVIP Test). [WEBSMS] | CMIN
7/26/2023 4:30:48 PM | Visayas Grid-07/26/2023 16:31: Visayas grid experience large load reduction at Lapu-Lapu SS MECO feeders @1623H, High frequency of 61.5Hz. [WEBSMS] | CVIS
7/26/2023 4:30:26 PM | Visayas Grid-07/26/2023 16:31: Visayas grid experience large load reduction at Lapu-Lapu SS MECO feeders @1623H, High frequency of 61.5Hz. [WEBSMS] | CVIS
7/26/2023 4:30:08 PM | [NSO Update] Mindanao Grid-07/26/2023 16:32: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked/ de-blocked at 1533H with power going to Mindanao from Visayas(MVIP Test). [WEBSMS] | CMIN
7/26/2023 4:25:48 PM | Luzon Grid-07/26/2023 16:24: Hermosa - BCCPP 230kV Line 3 tripped at 1623H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 4:24:23 PM | Luzon Grid-07/26/2023 16:24: Hermosa - BCCPP 230kV Line 3 tripped at 1623H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 4:17:29 PM | Mindanao Grid-07/26/2023 16:17: WMPC DG05 cut-out at 1614H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/26/2023 4:15:45 PM | Mindanao Grid-07/26/2023 16:17: WMPC DG05 cut-out at 1614H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/26/2023 4:15:40 PM | [NSO Update] Visayas Grid-07/26/2023 16:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1610H and de-blocked at 1611 with power going to Visayas from Mindanao (MVIP Test). [WEBSMS] | CVIS
7/26/2023 4:14:34 PM | [NSO Update] Visayas Grid-07/26/2023 16:15: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked at 1610H and de-blocked at 1611 with power going to Visayas from Mindanao (MVIP Test). [WEBSMS] | CVIS
7/26/2023 4:05:33 PM | [NSO Update] Visayas Grid-07/26/2023 16:05: Correction: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked/ de-blocked at 1533H with power going to Mindanao from Visayas(MVIP Test). [WEBSMS] | CVIS
7/26/2023 4:04:17 PM | [NSO Update] Visayas Grid-07/26/2023 16:05: Correction: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was blocked/ de-blocked at 1533H with power going to Mindanao from Visayas(MVIP Test). [WEBSMS] | CVIS
7/26/2023 4:00:41 PM | [NSO Update] Visayas Grid-07/26/2023 16:01: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked/blocked at 1533H with power going to Mindanao from Visayas(MVIP Test). [WEBSMS] | CVIS
7/26/2023 4:00:34 PM | [NSO Update] Visayas Grid-07/26/2023 16:01: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked/blocked at 1533H with power going to Mindanao from Visayas(MVIP Test). [WEBSMS] | CVIS
7/26/2023 3:29:15 PM | Luzon Grid-07/26/2023 15:29: San Esteban-Laoag 230kV line 1 restored at 1529H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 3:29:07 PM | Luzon Grid-07/26/2023 15:29: San Esteban-Laoag 230kV line 1 restored at 1529H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 3:24:30 PM | Luzon Grid-07/26/2023 15:25: San Esteban-Laoag 230kV line 1 tripped at 1523H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 3:19:07 PM | Luzon Grid-07/26/2023 15:17: San Esteban-Laoag 230kV line 1 restored at 1516H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 3:16:33 PM | Luzon Grid-07/26/2023 15:17: San Esteban-Laoag 230kV line 1 restored at 1516H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 3:15:52 PM | Luzon Grid-07/26/2023 15:12: San Esteban-Laoag 230kV line 1 tripped at 1508H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 3:11:56 PM | Luzon Grid-07/26/2023 15:12: San Esteban-Laoag 230kV line 1 tripped at 1508H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 2:18:42 PM | Mindanao Grid-07/26/2023 14:20: NACSUR Diesel Plant cut-in at 1404H. Follow RTD. [WEBSMS] | CMIN
7/26/2023 2:15:46 PM | Mindanao Grid-07/26/2023 14:17: Kibawe-Davao 138kV Line 2 restored at 1413H from Unplanned Outage. [WEBSMS] | CMIN
7/26/2023 2:15:37 PM | Mindanao Grid-07/26/2023 14:17: Kibawe-Davao 138kV Line 2 restored at 1413H from Unplanned Outage. [WEBSMS] | CMIN
7/26/2023 1:05:47 PM | Luzon Grid-07/26/2023 13:03: San Esteban-Laoag 230kV line 1 auto-tripped at 1301H. Auto-reclosing was successful at Laoag side. The line was looped at San Esteban at 1303H. [WEBSMS] | CLUZ
7/26/2023 1:04:15 PM | [NSO Update] Visayas Grid-07/26/2023 13:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1304H with power going to Visayas (MVIP Test) [WEBSMS] | CVIS
7/26/2023 1:04:08 PM | [NSO Update] Visayas Grid-07/26/2023 13:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1304H with power going to Visayas (MVIP Test) [WEBSMS] | CVIS
7/26/2023 1:04:02 PM | [NSO Update] Mindanao Grid-07/26/2023 13:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1304H with power going to Visayas (MVIP Test) [WEBSMS] | CMIN
7/26/2023 1:04:00 PM | [NSO Update] Mindanao Grid-07/26/2023 13:05: Lala-Dumanjug 350kV HVDC (Mindanao-Visayas) was de-blocked at 1304H with power going to Visayas (MVIP Test) [WEBSMS] | CMIN
7/26/2023 1:03:10 PM | Luzon Grid-07/26/2023 13:03: San Esteban-Laoag 230kV line 1 auto-tripped at 1301H. Auto-reclosing was successful at Laoag side. The line was looped at San Esteban at 1303H. [WEBSMS] | CLUZ
7/26/2023 12:44:16 PM | [NSO Update] Luzon Grid-07/26/2023 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12915MW, PK=10033MW, RR=260MW, NetOpMargin: PM=2622, EVE=2727 Highest Unit O/L: GNPD 1 @ 668MW Derated Plant: Calaca 2 @ 170MW, Masinloc 3 @ 185MW, Ilijan B @ 300MW [WEBSMS] | CLUZ
7/26/2023 12:42:51 PM | [NSO Update] Visayas Grid-07/26/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2493MW, PK=2039MW, RR=40MW, NetOpMargin: PM=414, EVE=326 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 284MW [WEBSMS] | CVIS
7/26/2023 12:42:09 PM | [NSO Update] Mindanao Grid-07/26/2023 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3205MW, PK=2181MW, RR=20MW, NetOpMargin: PM=1005, EVE=1070 Highest Unit O/L: GNPK 1 & 2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @52MW, AG2 @105MW, AG4 @90MW, AG5 @50MW, AG6 @121MW, AG7 @15MW, PG4 @120MW [WEBSMS] | CMIN
7/26/2023 12:41:54 PM | [NSO Update] Visayas Grid-07/26/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2493MW, PK=2039MW, RR=40MW, NetOpMargin: PM=414, EVE=326 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 284MW [WEBSMS] | CVIS
7/26/2023 12:41:52 PM | [NSO Update] Visayas Grid-07/26/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2493MW, PK=2039MW, RR=40MW, NetOpMargin: PM=414, EVE=326 Highest Unit O/L: THVI 1 & 2 @ 169MW Derated Plant: TPC Thermal @ 82MW, TPC Carmen @ 30MW, Leyte A @ 284MW [WEBSMS] | CVIS
7/26/2023 12:35:38 PM | Luzon Grid-07/26/2023 12:35: San Esteban-Laoag 230kV line 1 auto-tripped/auto-reclosed at 1228H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 12:34:36 PM | Luzon Grid-07/26/2023 12:35: San Esteban-Laoag 230kV line 1 auto-tripped/auto-reclosed at 1228H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 11:48:57 AM | Luzon Grid-07/26/2023 11:46: Hermosa - BCCPP 230kV Line 1 looped BCCPP at 1145H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 11:46:19 AM | Luzon Grid-07/26/2023 11:46: Hermosa - BCCPP 230kV Line 1 looped BCCPP at 1145H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 11:38:27 AM | Luzon Grid-07/26/2023 11:39: Hermosa - BCCPP 230kV Line 1 tripped at 1135H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 11:37:05 AM | Luzon Grid-07/26/2023 11:37: San Jose - Tayabas 500kV Line 1 restored at 1137H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 11:22:15 AM | Luzon Grid-07/26/2023 11:20: La Trinidad - Binga 230kV Line 2 looped at Binga side at 1119H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 11:19:33 AM | Luzon Grid-07/26/2023 11:20: La Trinidad - Binga 230kV Line 2 looped at Binga side at 1119H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 11:18:54 AM | Luzon Grid-07/26/2023 11:18: Nagsaag - Binga 230kV Line 2 restored at 1117H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 11:18:53 AM | Luzon Grid-07/26/2023 11:14: San Jose - Tayabas 500kV Line 1 tripped at 1108H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 11:17:46 AM | Luzon Grid-07/26/2023 11:18: Nagsaag - Binga 230kV Line 2 restored at 1117H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 11:13:28 AM | Luzon Grid-07/26/2023 11:14: San Jose - Tayabas 500kV Line 1 tripped at 1108H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 11:12:17 AM | Luzon Grid-07/26/2023 11:12: La Trinidad - Binga 230kV Line 2 on-floating status (affected by the tripping of Nagsaag - Binga 230kV Line 2). [WEBSMS] | CLUZ
7/26/2023 11:10:22 AM | Luzon Grid-07/26/2023 11:10: Nagsaag - Binga 230kV Line 2 tripped at 1106H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 10:58:57 AM | Mindanao Grid-07/26/2023 10:59: WMPC DG05 cut-in as RPS at 1051H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/26/2023 10:57:48 AM | Mindanao Grid-07/26/2023 10:59: WMPC DG05 cut-in as RPS at 1051H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/26/2023 10:03:51 AM | Luzon Grid-07/26/2023 10:04: Binga - Ambuklao 230KV line 1 auto-tripped/auto-reclosed at 0956H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 10:02:26 AM | Luzon Grid-07/26/2023 10:03: La Trinidad - Binga 230KV line 2 auto-tripped/auto-reclosed at 0956H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 10:02:11 AM | Luzon Grid-07/26/2023 10:03: La Trinidad - Binga 230KV line 2 auto-tripped/auto-reclosed at 0956H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 10:00:01 AM | Luzon Grid-07/26/2023 10:00: Correction: ALD occurred at NGCP and MERALCO feeders at 0929H due to tripping of GNPD 2 @356MW. Lowest Frequency is 59.008Hz [WEBSMS] | CLUZ
7/26/2023 9:52:10 AM | Luzon Grid-07/26/2023 09:50: San Esteban-Laoag 230kV line 1 auto-tripped at 0944H. Auto-reclosing was successful at Laoag side. The line was looped at San Esteban at 0949H. [WEBSMS] | CLUZ
7/26/2023 9:49:42 AM | Luzon Grid-07/26/2023 09:50: San Esteban-Laoag 230kV line 1 auto-tripped at 0944H. Auto-reclosing was successful at Laoag side. The line was looped at San Esteban at 0949H. [WEBSMS] | CLUZ
7/26/2023 9:43:31 AM | Luzon Grid-07/26/2023 09:44: Affected ALD feeders of MERALCO and NGCP restored at 0940H and 0942H, respectively. [WEBSMS] | CLUZ
7/26/2023 9:38:49 AM | Luzon Grid-07/26/2023 09:36: Correction: ALD occurred at NGCP and MERALCO feeders at 0929H due to tripping of GNPD 2 @400MW. Lowest Frequency is 59.008Hz (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 9:38:48 AM | Luzon Grid-07/26/2023 09:34: ALD occurred at NGCP and MERALCO feeders at 0929H due to tripping of GNPD 2 @400MW. Lowest Frequency is 59.03Hz (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 9:36:22 AM | Luzon Grid-07/26/2023 09:36: Correction: ALD occurred at NGCP and MERALCO feeders at 0929H due to tripping of GNPD 2 @400MW. Lowest Frequency is 59.008Hz (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 9:33:55 AM | Luzon Grid-07/26/2023 09:34: ALD occurred at NGCP and MERALCO feeders at 0929H due to tripping of GNPD 2 @400MW. Lowest Frequency is 59.03Hz (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 9:22:12 AM | Mindanao Grid-07/26/2023 09:22: Agus 7 Unit 1 shutdown at 0902H. Non-GOMP [WEBSMS] | CMIN
7/26/2023 9:20:31 AM | Mindanao Grid-07/26/2023 09:22: Agus 7 Unit 1 shutdown at 0902H. Non-GOMP [WEBSMS] | CMIN
7/26/2023 9:08:47 AM | Luzon Grid-07/26/2023 09:08: San Esteban-Laoag 230kV line 1 auto-tripped at 0902H. Auto-reclosing was successful at Laoag side. The line was looped at San Esteban at 0907H. (Unplanned Outage). [WEBSMS] | CLUZ
7/26/2023 9:07:30 AM | Luzon Grid-07/26/2023 09:08: San Esteban-Laoag 230kV line 1 auto-tripped at 0902H. Auto-reclosing was successful at Laoag side. The line was looped at San Esteban at 0907H. (Unplanned Outage). [WEBSMS] | CLUZ
7/26/2023 8:58:49 AM | Mindanao Grid-07/26/2023 08:58: WMPC DG09 cut-in as RPS at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/26/2023 8:56:48 AM | Mindanao Grid-07/26/2023 08:58: WMPC DG09 cut-in as RPS at 0851H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/26/2023 8:55:28 AM | Luzon Grid-07/26/2023 08:52: Currimao - Laoag 115kV Line restored at 0852H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 8:52:20 AM | Luzon Grid-07/26/2023 08:52: Currimao - Laoag 115kV Line restored at 0852H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 8:45:27 AM | Luzon Grid-07/26/2023 08:40: Currimao - Laoag 115kV Line tripped at 0837H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 8:40:27 AM | Mindanao Grid-07/26/2023 08:41: Aggreko Digos (APD) sync at 0800H for DENR emission testing. [WEBSMS] | CMIN
7/26/2023 8:39:47 AM | Mindanao Grid-07/26/2023 08:41: Aggreko Digos (APD) sync at 0800H for DENR emission testing. [WEBSMS] | CMIN
7/26/2023 8:39:32 AM | Luzon Grid-07/26/2023 08:40: Currimao - Laoag 115kV Line tripped at 0837H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 8:33:50 AM | Mindanao Grid-07/26/2023 08:35: Aurora SS 138kV Bus 2 deenergized at 0812H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
7/26/2023 8:33:27 AM | Mindanao Grid-07/26/2023 08:35: Aurora SS 138kV Bus 2 deenergized at 0812H. Planned Outage/Non-GOMP. [WEBSMS] | CMIN
7/26/2023 8:12:05 AM | Luzon Grid-07/26/2023 08:07: La Trinidad - Binga 230KV line 2 restored at 0806H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 8:06:39 AM | Luzon Grid-07/26/2023 08:07: La Trinidad - Binga 230KV line 2 restored at 0806H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 7:59:21 AM | Luzon Grid-07/26/2023 07:59: Binga - Ambuklao 230kV Line 1 auto tripped - auto reclosed at 0734H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 7:42:04 AM | Luzon Grid-07/26/2023 07:35: La Trinidad - Binga 230KV line 2 auto-tripped at 0734H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 7:35:13 AM | Luzon Grid-07/26/2023 07:35: La Trinidad - Binga 230KV line 2 auto-tripped at 0734H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 7:18:43 AM | Luzon Grid-07/26/2023 07:16: San Jose - Tayabas 500kV Line 2 de-energized at 0716H. (Planned Outage) [WEBSMS] | CLUZ
7/26/2023 7:15:56 AM | Luzon Grid-07/26/2023 07:16: San Jose - Tayabas 500kV Line 2 de-energized at 0716H. (Planned Outage) [WEBSMS] | CLUZ
7/26/2023 6:58:42 AM | Luzon Grid-07/26/2023 06:54: Bacnotan - San Esteban 230kV Line restored at 0653H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 6:53:30 AM | Luzon Grid-07/26/2023 06:54: Bacnotan - San Esteban 230kV Line restored at 0653H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 6:24:14 AM | Luzon Grid-07/26/2023 06:24: San Esteban - Laoag 230kV Line 1 auto tripped - auto reclosed at 0618H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 6:15:21 AM | Luzon Grid-07/26/2023 06:13: Bacnotan - San Esteban 230kV Line tripped at 0608H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 6:12:41 AM | Luzon Grid-07/26/2023 06:13: Bacnotan - San Esteban 230kV Line tripped at 0608H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 6:02:01 AM | Luzon Grid-07/26/2023 05:59: La Trinidad-Binga 230kV line 2 - restored at 0556H (Unplanned Outage during the passage of Typhoon Egay) [WEBSMS] | CLUZ
7/26/2023 5:59:08 AM | Luzon Grid-07/26/2023 05:59: La Trinidad-Binga 230kV line 2 - restored at 0556H (Unplanned Outage during the passage of Typhoon Egay) [WEBSMS] | CLUZ
7/26/2023 5:48:15 AM | [NSO Update] Visayas Grid-07/26/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2588MW, PK=1897MW, RR=40MW, NetOpMargin: AM=651, PM=622, EVE=512 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @307MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/26/2023 5:48:06 AM | [NSO Update] Mindanao Grid-07/26/2023 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3220MW, PK=2034MW, RR=20MW, NetOpMargin: AM=1166, PM=992, EVE=1046 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @52MW, AG2 @105MW, AG4 @90MW, AG5 @50MW, AG6 @121MW, AG7 @15MW, PG4 @120MW [WEBSMS] | CMIN
7/26/2023 5:47:51 AM | Luzon Grid-07/26/2023 05:48: San Esteban-Laoag 230kV line 1 auto-tripped at 0542H. Auto-reclosing was successful at Laoag side. The line was looped at San Esteban at 0544H. (Unplanned Outage due to Typhoon Egay) [WEBSMS] | CLUZ
7/26/2023 5:46:09 AM | [NSO Update] Visayas Grid-07/26/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2588MW, PK=1897MW, RR=40MW, NetOpMargin: AM=651, PM=622, EVE=512 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @307MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/26/2023 5:45:24 AM | [NSO Update] Luzon Grid-07/26/2023 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13628MW, PK=10237MW, RR=260MW, NetOpMargin: AM=3131, PM=2343, EVE=2681 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC3 @185MW, ILIJAN A @340MW, ILIJAN B @165MW [WEBSMS] | CLUZ
7/26/2023 5:44:52 AM | [NSO Update] Luzon Grid-07/26/2023 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13628MW, PK=10237MW, RR=260MW, NetOpMargin: AM=3131, PM=2343, EVE=2681 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC3 @185MW, ILIJAN A @340MW, ILIJAN B @165MW [WEBSMS] | CLUZ
7/26/2023 5:42:00 AM | Luzon Grid-07/26/2023 05:41: La Trinidad-Binga 230KV line 2 - auto-tripped at 0537H (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 5:40:30 AM | Luzon Grid-07/26/2023 05:41: La Trinidad-Binga 230KV line 2 - auto-tripped at 0537H (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 5:32:00 AM | [NSO Update] Luzon Grid-07/26/2023 05:27: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data including Aparri Doppler Weather Radar in the vicinity of Aparri, Cagayan (18.9N, 121.4E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 240 km/h. It is moving Westward at 20 km/h. [WEBSMS] | CLUZ
7/26/2023 5:28:03 AM | [NSO Update] Visayas Grid-07/26/2023 05:28: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data including Aparri Doppler Weather Radar in the vicinity of Aparri, Cagayan (18.9N, 121.4E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 240 km/h. It is moving Westward at 20 km/h. [WEBSMS] | CVIS
7/26/2023 5:27:58 AM | [NSO Update] Mindanao Grid-07/26/2023 05:29: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data including Aparri Doppler Weather Radar in the vicinity of Aparri, Cagayan (18.9N, 121.4E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 240 km/h. It is moving Westward at 20 km/h. [WEBSMS] | CMIN
7/26/2023 5:27:34 AM | [NSO Update] Visayas Grid-07/26/2023 05:28: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data including Aparri Doppler Weather Radar in the vicinity of Aparri, Cagayan (18.9N, 121.4E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 240 km/h. It is moving Westward at 20 km/h. [WEBSMS] | CVIS
7/26/2023 5:26:47 AM | [NSO Update] Luzon Grid-07/26/2023 05:27: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data including Aparri Doppler Weather Radar in the vicinity of Aparri, Cagayan (18.9N, 121.4E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 240 km/h. It is moving Westward at 20 km/h. [WEBSMS] | CLUZ
7/26/2023 2:38:41 AM | Luzon Grid-07/26/2023 02:39: For info: Sta Rita Module 30 fuel changeover from oil to gas was completed at 0234H. [WEBSMS] | CLUZ
7/26/2023 2:38:32 AM | Luzon Grid-07/26/2023 02:39: For info: Sta Rita Module 30 fuel changeover from oil to gas was completed at 0234H. [WEBSMS] | CLUZ
7/26/2023 2:15:11 AM | Luzon Grid-07/26/2023 02:09: Laoag-Caparispisan(Pagudpud Wind Farm) 115kV line - auto-tripped at Laoag side at 0203H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 2:09:05 AM | Luzon Grid-07/26/2023 02:09: Laoag-Caparispisan(Pagudpud Wind Farm) 115kV line - auto-tripped at Laoag side at 0203H. (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 1:21:50 AM | Luzon Grid-07/26/2023 01:22: Laoag-Caparispisan 115kV line - unlooped at Caparispisan side at 0120H due to unbalanced 115kV Bus 2 Voltage(Unplanned Outage). [WEBSMS] | CLUZ
7/26/2023 1:21:27 AM | Luzon Grid-07/26/2023 01:22: Laoag-Caparispisan 115kV line - unlooped at Caparispisan side at 0120H due to unbalanced 115kV Bus 2 Voltage(Unplanned Outage). [WEBSMS] | CLUZ
7/26/2023 1:16:18 AM | Luzon Grid-07/26/2023 01:16: Laoag-Caparispisan 115kV line - looped at Caparispisan side at 0115H (Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 12:37:51 AM | Luzon Grid-07/26/2023 00:38: Laoag-Caparispisan 115kV line auto-tripped and auto-reclosed at Laoag side at 0031H.(Unplanned Outage) [WEBSMS] | CLUZ
7/26/2023 12:31:57 AM | Luzon Grid-07/26/2023 00:31: SLTEC Unit 1 - shutdown at 0030H (Planned Outage). [WEBSMS] | CLUZ
7/26/2023 12:31:07 AM | Luzon Grid-07/26/2023 00:31: SLTEC Unit 1 - shutdown at 0030H (Planned Outage). [WEBSMS] | CLUZ
7/25/2023 9:15:14 PM | Mindanao Grid-07/25/2023 21:14: WMPC DG10 cut-out at 2111H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/25/2023 9:12:34 PM | Mindanao Grid-07/25/2023 21:14: WMPC DG10 cut-out at 2111H from RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/25/2023 7:24:58 PM | Mindanao Grid-07/25/2023 19:24: Mt. Apo 3 Binary Plant cut-in at 1920H from forced outage. [WEBSMS] | CMIN
7/25/2023 7:23:03 PM | Mindanao Grid-07/25/2023 19:24: Mt. Apo 3 Binary Plant cut-in at 1920H from forced outage. [WEBSMS] | CMIN
7/25/2023 7:20:23 PM | Mindanao Grid-07/25/2023 19:22: Agus 1 HEP Unit no. 1 cut-in at 1600H from forced outage. [WEBSMS] | CMIN
7/25/2023 7:20:11 PM | Mindanao Grid-07/25/2023 19:22: Agus 1 HEP Unit no. 1 cut-in at 1600H from forced outage. [WEBSMS] | CMIN
7/25/2023 5:53:14 PM | Mindanao Grid-07/25/2023 17:53: Mapalad Power Inc. - Digos Power Plant cut-out at 1746H from DENR emission test. [WEBSMS] | CMIN
7/25/2023 5:51:16 PM | Mindanao Grid-07/25/2023 17:53: Mapalad Power Inc. - Digos Power Plant cut-out at 1746H from DENR emission test. [WEBSMS] | CMIN
7/25/2023 5:43:16 PM | [NSO Update] Mindanao Grid-07/25/2023 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3257MW, PK=1866MW, RR=20MW, NetOpMargin: EVE=1371 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @105MW, AG4 @140MW, AG5 @48MW, AG6 @121MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
7/25/2023 5:41:21 PM | [NSO Update] Visayas Grid-07/25/2023 17:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2328MW, PK=1873MW, RR=40MW, NetOpMargin: EVE=415 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @302MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/25/2023 5:38:27 PM | [NSO Update] Luzon Grid-07/25/2023 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13202MW, PK=9999MW, RR=260MW, NetOpMargin: EVE=2943 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @170MW, MASINLOC 3 @290MW, ILIJAN A @340MW, ILIJAN B @165MW [WEBSMS] | CLUZ
7/25/2023 5:37:26 PM | [NSO Update] Luzon Grid-07/25/2023 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13202MW, PK=9999MW, RR=260MW, NetOpMargin: EVE=2943 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @170MW, MASINLOC 3 @290MW, ILIJAN A @340MW, ILIJAN B @165MW [WEBSMS] | CLUZ
7/25/2023 5:33:29 PM | Mindanao Grid-07/25/2023 17:32: Bislig-Nabunturan 138kV Line restored at 1729H from Unplanned Outage. [WEBSMS] | CMIN
7/25/2023 5:30:57 PM | Mindanao Grid-07/25/2023 17:32: Bislig-Nabunturan 138kV Line restored at 1729H from Unplanned Outage. [WEBSMS] | CMIN
7/25/2023 5:14:55 PM | [NSO Update] Mindanao Grid-07/25/2023 17:12: Weather Update: At 3:00 PM today, the center of the eye of Super Typhoon "EGAY" {DOKSURI} was estimated based on all available data at 210 km East of Aparri, Cagayan (18.4N, 123.6?E) with maximum sustained winds of 185 km/h near the center & gustiness of up to 230 kmh. It is moving Northwestward at 20 kmh. Southwest Monsoon affecting Visayas, Mindanao, & the western section of Southern Luzon. [WEBSMS] | CMIN
7/25/2023 5:14:53 PM | [NSO Update] Luzon Grid-07/25/2023 17:10: Weather Update: At 3:00 PM today, the center of the eye of Super Typhoon ``EGAY`` {DOKSURI} was estimated based on all available data at 210 km East of Aparri, Cagayan (18.4N, 123.6?E) with maximum sustained winds of 185 km/h near the center & gustiness of up to 230 kmh. It is moving Northwestward at 20 kmh. Southwest Monsoon affecting Visayas, Mindanao, & the western section of Southern Luzon. [WEBSMS] | CLUZ
7/25/2023 5:10:56 PM | [NSO Update] Mindanao Grid-07/25/2023 17:12: Weather Update: At 3:00 PM today, the center of the eye of Super Typhoon "EGAY" {DOKSURI} was estimated based on all available data at 210 km East of Aparri, Cagayan (18.4N, 123.6�E) with maximum sustained winds of 185 km/h near the center & gustiness of up to 230 kmh. It is moving Northwestward at 20 kmh. Southwest Monsoon affecting Visayas, Mindanao, & the western section of Southern Luzon. [WEBSMS] | CMIN
7/25/2023 5:10:39 PM | [NSO Update] Visayas Grid-07/25/2023 17:11: Weather Update: At 3:00 PM today, the center of the eye of Super Typhoon "EGAY" {DOKSURI} was estimated based on all available data at 210 km East of Aparri, Cagayan (18.4N, 123.6�E) with maximum sustained winds of 185 km/h near the center & gustiness of up to 230 kmh. It is moving Northwestward at 20 kmh. Southwest Monsoon affecting Visayas, Mindanao, & the western section of Southern Luzon. [WEBSMS] | CVIS
7/25/2023 5:10:12 PM | [NSO Update] Luzon Grid-07/25/2023 17:10: Weather Update: At 3:00 PM today, the center of the eye of Super Typhoon "EGAY" {DOKSURI} was estimated based on all available data at 210 km East of Aparri, Cagayan (18.4N, 123.6�E) with maximum sustained winds of 185 km/h near the center & gustiness of up to 230 kmh. It is moving Northwestward at 20 kmh. Southwest Monsoon affecting Visayas, Mindanao, & the western section of Southern Luzon. [WEBSMS] | CLUZ
7/25/2023 5:04:52 PM | Luzon Grid-07/25/2023 17:04: Laoag - Caparispisan (Pagudpud NLREC Wind Farm) 115kV Line successfully commissioned from Bay 66 to Bay 65 at 1616H. (End of commissioning). [WEBSMS] | CLUZ
7/25/2023 5:04:04 PM | Luzon Grid-07/25/2023 17:04: Laoag - Caparispisan (Pagudpud NLREC Wind Farm) 115kV Line successfully commissioned from Bay 66 to Bay 65 at 1616H. (End of commissioning). [WEBSMS] | CLUZ
7/25/2023 4:35:08 PM | Mindanao Grid-07/25/2023 16:35: Aurora SS 138kV Bus no.2 restored at 1620H from Planned Outage. [WEBSMS] | CMIN
7/25/2023 4:33:27 PM | Mindanao Grid-07/25/2023 16:35: Aurora SS 138kV Bus no.2 restored at 1620H from Planned Outage. [WEBSMS] | CMIN
7/25/2023 3:58:08 PM | Luzon Grid-07/25/2023 15:58: Laoag - Caparispisan 115kV restored at 1554H. (On-going commissioning) [WEBSMS] | CLUZ
7/25/2023 3:57:54 PM | Luzon Grid-07/25/2023 15:58: Laoag - Caparispisan 115kV restored at 1554H. (On-going commissioning) [WEBSMS] | CLUZ
7/25/2023 3:48:09 PM | Mindanao Grid-07/25/2023 15:46: Bislig-Nabunturan 138kV Line tripped at 1540H. (Unplanned outage) [WEBSMS] | CMIN
7/25/2023 3:48:08 PM | Luzon Grid-07/25/2023 15:43: Bacman - Daraga 230kV Line 2 restored at 1542H. (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2023 3:44:37 PM | Mindanao Grid-07/25/2023 15:46: Bislig-Nabunturan 138kV Line tripped at 1540H. (Unplanned outage) [WEBSMS] | CMIN
7/25/2023 3:43:18 PM | Luzon Grid-07/25/2023 15:43: Bacman - Daraga 230kV Line 2 restored at 1542H. (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2023 3:24:47 PM | Luzon Grid-07/25/2023 15:23: Bacman 230kV Bus 2 and Bacman - Daraga 230kV Line 2 tripped (at Daraga side) at 1516H. (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2023 3:23:24 PM | Luzon Grid-07/25/2023 15:23: Bacman 230kV Bus 2 and Bacman - Daraga 230kV Line 2 tripped (at Daraga side) at 1516H. (Unplanned Outage) [WEBSMS] | CLUZ
7/25/2023 2:26:26 PM | Mindanao Grid-07/25/2023 14:27: Tudaya 2 HEP Unit 1 and Unit 2 cut-out both at 1306H affected by the emergency shutdown of Toril - Digos 69kV line. Restored by 1331H and 1338H, respectively. [WEBSMS] | CMIN
7/25/2023 2:25:49 PM | Mindanao Grid-07/25/2023 14:27: Tudaya 2 HEP Unit 1 and Unit 2 cut-out both at 1306H affected by the emergency shutdown of Toril - Digos 69kV line. Restored by 1331H and 1338H, respectively. [WEBSMS] | CMIN
7/25/2023 2:11:24 PM | Mindanao Grid-07/25/2023 14:11: Kibawe-Davao 138kV Line 2 tripped at 1401H. Unplanned Outage. [WEBSMS] | CMIN
7/25/2023 2:10:03 PM | Mindanao Grid-07/25/2023 14:11: Kibawe-Davao 138kV Line 2 tripped at 1401H. Unplanned Outage. [WEBSMS] | CMIN
7/25/2023 1:33:03 PM | Mindanao Grid-07/25/2023 13:31: Kibawe-Sultan Kudarat 138kV Line restored at 1316H from tripping. [WEBSMS] | CMIN
7/25/2023 1:29:37 PM | Mindanao Grid-07/25/2023 13:31: Kibawe-Sultan Kudarat 138kV Line restored at 1316H from tripping. [WEBSMS] | CMIN
7/25/2023 1:24:43 PM | Mindanao Grid-07/25/2023 13:25: Kibawe-Sultan Kudarat 138kV Line tripped at 1302H. Unplanned Outage. [WEBSMS] | CMIN
7/25/2023 1:23:51 PM | Mindanao Grid-07/25/2023 13:25: Kibawe-Sultan Kudarat 138kV Line tripped at 1302H. Unplanned Outage. [WEBSMS] | CMIN
7/25/2023 1:04:43 PM | [NSO Update] Mindanao Grid-07/25/2023 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3312MW, PK=2199MW, RR=20MW, NetOpMargin: PM=1092, EVE=1152 Highest Unit O/L: GNPK 1& 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @105MW, AG4 @140MW, AG5 @50MW, AG6 @121MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
7/25/2023 1:04:41 PM | [NSO Update] Luzon Grid-07/25/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14095MW, PK=11223MW, RR=260MW, NetOpMargin: PM=2612, EVE=2952 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @170MW, MASINLOC 3 @290MW, ILIJAN A @470MW, ILIJAN B @230MW [WEBSMS] | CLUZ
7/25/2023 1:04:09 PM | [NSO Update] Mindanao Grid-07/25/2023 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3312MW, PK=2199MW, RR=20MW, NetOpMargin: PM=1092, EVE=1152 Highest Unit O/L: GNPK 1& 4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @105MW, AG4 @140MW, AG5 @50MW, AG6 @121MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
7/25/2023 1:01:51 PM | [NSO Update] Luzon Grid-07/25/2023 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14095MW, PK=11223MW, RR=260MW, NetOpMargin: PM=2612, EVE=2952 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @170MW, MASINLOC 3 @290MW, ILIJAN A @470MW, ILIJAN B @230MW [WEBSMS] | CLUZ
7/25/2023 1:01:35 PM | [NSO Update] Visayas Grid-07/25/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2443MW, PK=1908MW, RR=40MW, NetOpMargin: PM=494, EVE=369 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @302MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/25/2023 12:59:46 PM | [NSO Update] Visayas Grid-07/25/2023 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2443MW, PK=1908MW, RR=40MW, NetOpMargin: PM=494, EVE=369 Highest Unit O/L: THVI 1&2 @ 169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @302MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/25/2023 11:17:58 AM | Mindanao Grid-07/25/2023 11:17: Agus 1 HEP Unit no. 2 cut-out at 1113H on emergency shutdown to replace two broken shear pins. ETC: 1300H. [WEBSMS] | CMIN
7/25/2023 11:15:05 AM | Mindanao Grid-07/25/2023 11:17: Agus 1 HEP Unit no. 2 cut-out at 1113H on emergency shutdown to replace two broken shear pins. ETC: 1300H. [WEBSMS] | CMIN
7/25/2023 11:09:49 AM | Mindanao Grid-07/25/2023 11:11: Nickle Asia Diesel Plant cut-out at 1100H from energy dispatch. [WEBSMS] | CMIN
7/25/2023 11:09:39 AM | Mindanao Grid-07/25/2023 11:11: Nickle Asia Diesel Plant cut-out at 1100H from energy dispatch. [WEBSMS] | CMIN
7/25/2023 10:54:38 AM | Mindanao Grid-07/25/2023 10:55: WMPC DG10 and DG05 cut-in at 0900H and 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/25/2023 10:53:49 AM | Mindanao Grid-07/25/2023 10:55: WMPC DG10 and DG05 cut-in at 0900H and 1050H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/25/2023 10:51:34 AM | Mindanao Grid-07/25/2023 10:53: Tudaya 2 HEP U1 and U2 tripped at 0945H due to outage of Toril - Digos 69kV line. Restored at 1012H. [WEBSMS] | CMIN
7/25/2023 10:19:56 AM | Mindanao Grid-07/25/2023 10:19: Nickle Asia Diesel Plant cut-in at 1000H. Follow RTD. [WEBSMS] | CMIN
7/25/2023 10:17:12 AM | Mindanao Grid-07/25/2023 10:19: Nickle Asia Diesel Plant cut-in at 1000H. Follow RTD. [WEBSMS] | CMIN
7/25/2023 8:59:34 AM | Mindanao Grid-07/25/2023 09:01: Mapalad Power Inc. - Digos Power Plant cut-in at 0801H for DENR emission test. [WEBSMS] | CMIN
7/25/2023 8:59:31 AM | Mindanao Grid-07/25/2023 09:01: Mapalad Power Inc. - Digos Power Plant cut-in at 0801H for DENR emission test. [WEBSMS] | CMIN
7/25/2023 8:11:18 AM | Mindanao Grid-07/25/2023 08:13: Aurora SS 138kV Bus no.2 de-energized at 0805H. Planned Outage / Non-GOMP. [WEBSMS] | CMIN
7/25/2023 7:12:46 AM | Mindanao Grid-07/25/2023 07:14: Lake Mainit HEP (AGC) tripped at 0703H with gen. loss of 11 MW. Indication: G3 power signal fault. [WEBSMS] | CMIN
7/25/2023 7:12:22 AM | Mindanao Grid-07/25/2023 07:14: Lake Mainit HEP (AGC) tripped at 0703H with gen. loss of 11 MW. Indication: G3 power signal fault. [WEBSMS] | CMIN
7/25/2023 6:28:10 AM | Mindanao Grid-07/25/2023 06:29: Lake Mainit HEP (AGC) cut-in at 0602H from forced outage. [WEBSMS] | CMIN
7/25/2023 6:27:54 AM | Mindanao Grid-07/25/2023 06:29: Lake Mainit HEP (AGC) cut-in at 0602H from forced outage. [WEBSMS] | CMIN
7/25/2023 5:54:49 AM | Mindanao Grid-07/25/2023 05:55: AGC(Lake Mainit) HEP Auto trip at 0549H. Gen. Loss of 11MW. Relay Indication: 50BF- CB FAIL TRIP. Force Outage. [WEBSMS] | CMIN
7/25/2023 5:53:08 AM | Mindanao Grid-07/25/2023 05:55: AGC(Lake Mainit) HEP Auto trip at 0549H. Gen. Loss of 11MW. Relay Indication: 50BF- CB FAIL TRIP. Force Outage. [WEBSMS] | CMIN
7/25/2023 5:46:03 AM | [NSO Update] Mindanao Grid-07/25/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3320MW, PK=2059MW, RR=20MW, NetOpMargin: AM=1241, PM=1142, EVE=1218 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @105MW, AG4 @140MW, AG5 @50MW, AG6 @121MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
7/25/2023 5:45:28 AM | [NSO Update] Visayas Grid-07/25/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2561MW, PK=2053MW, RR=40MW, NetOpMargin: AM=468, PM=377, EVE=304 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @310MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/25/2023 5:45:21 AM | [NSO Update] Mindanao Grid-07/25/2023 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3320MW, PK=2059MW, RR=20MW, NetOpMargin: AM=1241, PM=1142, EVE=1218 Highest Unit O/L: GNPK 1&4 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @45.5MW, MA2 @31MW, AG1 @70MW, AG2 @105MW, AG4 @140MW, AG5 @50MW, AG6 @121MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
7/25/2023 5:43:40 AM | [NSO Update] Visayas Grid-07/25/2023 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2561MW, PK=2053MW, RR=40MW, NetOpMargin: AM=468, PM=377, EVE=304 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @310MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/25/2023 5:41:53 AM | [NSO Update] Luzon Grid-07/25/2023 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14215MW, PK=10688MW, RR=260MW, NetOpMargin: AM=3268, PM=2607, EVE=3052 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC3 @290MW, ILIJAN A @420MW, ILIJAN B @215MW [WEBSMS] | CLUZ
7/25/2023 5:41:39 AM | [NSO Update] Luzon Grid-07/25/2023 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14215MW, PK=10688MW, RR=260MW, NetOpMargin: AM=3268, PM=2607, EVE=3052 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC3 @290MW, ILIJAN A @420MW, ILIJAN B @215MW [WEBSMS] | CLUZ
7/25/2023 5:41:02 AM | [NSO Update] Luzon Grid-07/25/2023 05:38: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data including Daet Doppler Weather Radar at 320 km East Northeast of Casiguran, Aurora or 350 km East Southeast of Tuguegarao City, Cagayan (17.1N, 125.0E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CLUZ
7/25/2023 5:38:04 AM | [NSO Update] Luzon Grid-07/25/2023 05:38: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data including Daet Doppler Weather Radar at 320 km East Northeast of Casiguran, Aurora or 350 km East Southeast of Tuguegarao City, Cagayan (17.1N, 125.0E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CLUZ
7/25/2023 5:06:28 AM | [NSO Update] Mindanao Grid-07/25/2023 05:06: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data including Daet Doppler Weather Radar at 320 km East Northeast of Casiguran, Aurora or 350 km East Southeast of Tuguegarao City, Cagayan (17.1N, 125.0E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CMIN
7/25/2023 5:04:58 AM | [NSO Update] Mindanao Grid-07/25/2023 05:06: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data including Daet Doppler Weather Radar at 320 km East Northeast of Casiguran, Aurora or 350 km East Southeast of Tuguegarao City, Cagayan (17.1N, 125.0E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CMIN
7/25/2023 5:04:43 AM | [NSO Update] Visayas Grid-07/25/2023 05:05: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data including Daet Doppler Weather Radar at 320 km East Northeast of Casiguran, Aurora or 350 km East Southeast of Tuguegarao City, Cagayan (17.1N, 125.0E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CVIS
7/25/2023 5:04:29 AM | [NSO Update] Visayas Grid-07/25/2023 05:05: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data including Daet Doppler Weather Radar at 320 km East Northeast of Casiguran, Aurora or 350 km East Southeast of Tuguegarao City, Cagayan (17.1N, 125.0E) with maximum sustained winds of 175 km/h near the center and gustiness of up to 215 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CVIS
7/24/2023 11:20:50 PM | Mindanao Grid-07/24/2023 23:21: Lala- Kauswagan 230 kV L1 energized at 1817H, and looped at Kauswagan SS 2315H. [WEBSMS] | CMIN
7/24/2023 11:20:01 PM | Mindanao Grid-07/24/2023 23:21: Lala- Kauswagan 230 kV L1 energized at 1817H, and looped at Kauswagan SS 2315H. [WEBSMS] | CMIN
7/24/2023 9:31:59 PM | Mindanao Grid-07/24/2023 21:33: GN Power (GKP) Unit 2 cut-out at 2130H - reserve shutdown. [WEBSMS] | CMIN
7/24/2023 9:19:39 PM | Mindanao Grid-07/24/2023 21:20: Correction: WMPC DG10 cut-out as RPS at 2109H. From RPS - System Voltage Requirement, not WMPC DG02. [WEBSMS] | CMIN
7/24/2023 9:18:35 PM | Mindanao Grid-07/24/2023 21:20: Correction: WMPC DG10 cut-out as RPS at 2109H. From RPS - System Voltage Requirement, not WMPC DG02. [WEBSMS] | CMIN
7/24/2023 9:16:02 PM | Mindanao Grid-07/24/2023 21:17: WMPC DG2 cut-out as RPS at 2109H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2023 9:15:45 PM | Mindanao Grid-07/24/2023 21:17: WMPC DG2 cut-out as RPS at 2109H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2023 6:21:11 PM | Mindanao Grid-07/24/2023 18:21: Lala- Kauswagan 230 kV L1 energized at 1817H, open at Kauswagan 230kV SS side. [WEBSMS] | CMIN
7/24/2023 6:19:31 PM | Mindanao Grid-07/24/2023 18:21: Lala- Kauswagan 230 kV L1 energized at 1817H, open at Kauswagan 230kV SS side. [WEBSMS] | CMIN
7/24/2023 5:43:54 PM | [NSO Update] Luzon Grid-07/24/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13519MW, PK=9811MW, RR=260MW, NetOpMargin: EVE=3448 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @170MW, MASINLOC 3 @280MW, ILIJAN A @420MW, ILIJAN B @215MW [WEBSMS] | CLUZ
7/24/2023 5:42:52 PM | [NSO Update] Luzon Grid-07/24/2023 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13519MW, PK=9811MW, RR=260MW, NetOpMargin: EVE=3448 Highest Unit O/L: GNPD 1 & 2 @ 668MW Derated Plant: CALACA 2 @170MW, MASINLOC 3 @280MW, ILIJAN A @420MW, ILIJAN B @215MW [WEBSMS] | CLUZ
7/24/2023 5:37:15 PM | [NSO Update] Visayas Grid-07/24/2023 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2338MW, PK=1959MW, RR=40MW, NetOpMargin: EVE=339 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @296MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/24/2023 5:35:00 PM | [NSO Update] Visayas Grid-07/24/2023 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2338MW, PK=1959MW, RR=40MW, NetOpMargin: EVE=339 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @296MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/24/2023 5:29:04 PM | [NSO Update] Mindanao Grid-07/24/2023 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3264MW, PK=2021MW, RR=20MW, NetOpMargin: EVE=1223 Highest Unit O/L: GNPK 1,2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @70MW, AG2 @105MW, AG4 @140MW, AG5 @49MW, AG6 @121MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
7/24/2023 5:28:56 PM | [NSO Update] Mindanao Grid-07/24/2023 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3264MW, PK=2021MW, RR=20MW, NetOpMargin: EVE=1223 Highest Unit O/L: GNPK 1,2 & 4 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @70MW, AG2 @105MW, AG4 @140MW, AG5 @49MW, AG6 @121MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
7/24/2023 5:13:56 PM | Mindanao Grid-07/24/2023 17:13: AGGREKODIG (APD) cut out 1700H. - REGULATORY REQUIREMENTS : DENR EMISSION TEST. [WEBSMS] | CMIN
7/24/2023 5:11:31 PM | Mindanao Grid-07/24/2023 17:13: AGGREKODIG (APD) cut out 1700H. - REGULATORY REQUIREMENTS : DENR EMISSION TEST. [WEBSMS] | CMIN
7/24/2023 5:10:51 PM | [NSO Update] Luzon Grid-07/24/2023 17:11: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "EGAY" {DOKSURI} was estimated based on all available data at 500km East of Baler, Aurora (15.8�N, 126.3�E) with max. sustained winds of 155 kmh near the center & gustiness of up to 190 kmh. It is moving North Northwestward at 10 kmh. Southwest Monsoon affecting Visayas, Mindanao, & the western section of Southern Luzon. [WEBSMS] | CLUZ
7/24/2023 5:10:33 PM | [NSO Update] Luzon Grid-07/24/2023 17:11: Weather Update: At 3:00 PM today, the center of the eye of Typhoon ``EGAY`` {DOKSURI} was estimated based on all available data at 500km East of Baler, Aurora (15.8?N, 126.3?E) with max. sustained winds of 155 kmh near the center & gustiness of up to 190 kmh. It is moving North Northwestward at 10 kmh. Southwest Monsoon affecting Visayas, Mindanao, & the western section of Southern Luzon. [WEBSMS] | CLUZ
7/24/2023 5:09:30 PM | [NSO Update] Mindanao Grid-07/24/2023 17:10: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "EGAY" {DOKSURI} was estimated based on all available data at 500km East of Baler, Aurora (15.8?N, 126.3?E) with max. sustained winds of 155 kmh near the center & gustiness of up to 190 kmh. It is moving North Northwestward at 10 kmh. Southwest Monsoon affecting Visayas, Mindanao, & the western section of Southern Luzon. [WEBSMS] | CMIN
7/24/2023 5:08:41 PM | [NSO Update] Mindanao Grid-07/24/2023 17:10: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "EGAY" {DOKSURI} was estimated based on all available data at 500km East of Baler, Aurora (15.8�N, 126.3�E) with max. sustained winds of 155 kmh near the center & gustiness of up to 190 kmh. It is moving North Northwestward at 10 kmh. Southwest Monsoon affecting Visayas, Mindanao, & the western section of Southern Luzon. [WEBSMS] | CMIN
7/24/2023 5:08:35 PM | [NSO Update] Visayas Grid-07/24/2023 17:09: Weather Update: At 3:00 PM today, the center of the eye of Typhoon ``EGAY`` {DOKSURI} was estimated based on all available data at 500km East of Baler, Aurora (15.8?N, 126.3?E) with max. sustained winds of 155 kmh near the center & gustiness of up to 190 kmh. It is moving North Northwestward at 10 kmh. Southwest Monsoon affecting Visayas, Mindanao, & the western section of Southern Luzon. [WEBSMS] | CVIS
7/24/2023 5:08:28 PM | [NSO Update] Visayas Grid-07/24/2023 17:09: Weather Update: At 3:00 PM today, the center of the eye of Typhoon "EGAY" {DOKSURI} was estimated based on all available data at 500km East of Baler, Aurora (15.8�N, 126.3�E) with max. sustained winds of 155 kmh near the center & gustiness of up to 190 kmh. It is moving North Northwestward at 10 kmh. Southwest Monsoon affecting Visayas, Mindanao, & the western section of Southern Luzon. [WEBSMS] | CVIS
7/24/2023 4:26:10 PM | Mindanao Grid-07/24/2023 16:25: WMPC DG5 declared available at 1610H. [WEBSMS] | CMIN
7/24/2023 4:26:09 PM | Mindanao Grid-07/24/2023 16:26: WMPC DG2 cut-out as RPS at 1614H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2023 4:24:41 PM | Mindanao Grid-07/24/2023 16:26: WMPC DG2 cut-out as RPS at 1614H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2023 4:23:44 PM | Mindanao Grid-07/24/2023 16:25: WMPC DG5 declared available at 1610H. [WEBSMS] | CMIN
7/24/2023 3:43:00 PM | Visayas Grid-07/24/2023 15:43: 138 kV Colon - Magdugo Line energized at 1506H, pre-arranged VPD-A activity, equipment parameters testing on-going. [WEBSMS] | CVIS
7/24/2023 3:42:25 PM | Visayas Grid-07/24/2023 15:43: 138 kV Colon - Magdugo Line energized at 1506H, pre-arranged VPD-A activity, equipment parameters testing on-going. [WEBSMS] | CVIS
7/24/2023 3:33:49 PM | Luzon Grid-07/24/2023 15:31: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1531H. (Planned Outage) [WEBSMS] | CLUZ
7/24/2023 3:30:52 PM | Luzon Grid-07/24/2023 15:31: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1531H. (Planned Outage) [WEBSMS] | CLUZ
7/24/2023 2:49:27 PM | Mindanao Grid-07/24/2023 14:48: AGC(Lake Mainit) HEP cut in at 1441H from forced outage. [WEBSMS] | CMIN
7/24/2023 2:46:41 PM | Mindanao Grid-07/24/2023 14:48: AGC(Lake Mainit) HEP cut in at 1441H from forced outage. [WEBSMS] | CMIN
7/24/2023 2:35:45 PM | Mindanao Grid-07/24/2023 14:37: GN Power (GKP) cut-in at 1430H from economic shutdown. [WEBSMS] | CMIN
7/24/2023 2:35:28 PM | Mindanao Grid-07/24/2023 14:37: GN Power (GKP) cut-in at 1430H from economic shutdown. [WEBSMS] | CMIN
7/24/2023 12:50:22 PM | [NSO Update] Luzon Grid-07/24/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14056MW, PK=10855MW, RR=260MW, NetOpMargin: PM=2941, EVE=3443 Highest Unit O/L: GNPD 1 & 2 @668MW Derated Plant: CALACA 2 @170MW, MASINLOC 3 @280MW, ILIJAN A @420MW, ILIJAN B @215MW [WEBSMS] | CLUZ
7/24/2023 12:45:24 PM | [NSO Update] Luzon Grid-07/24/2023 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14056MW, PK=10855MW, RR=260MW, NetOpMargin: PM=2941, EVE=3443 Highest Unit O/L: GNPD 1 & 2 @668MW Derated Plant: CALACA 2 @170MW, MASINLOC 3 @280MW, ILIJAN A @420MW, ILIJAN B @215MW [WEBSMS] | CLUZ
7/24/2023 12:44:15 PM | [NSO Update] Visayas Grid-07/24/2023 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2455MW, PK=2060MW, RR=40MW, NetOpMargin: PM=355, EVE=363 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @296MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/24/2023 12:42:26 PM | [NSO Update] Visayas Grid-07/24/2023 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2455MW, PK=2060MW, RR=40MW, NetOpMargin: PM=355, EVE=363 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @296MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/24/2023 12:40:24 PM | [NSO Update] Mindanao Grid-07/24/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3308MW, PK=2186MW, RR=20MW, NetOpMargin: PM=1102, EVE=1182 Highest Unit O/L: GNPK 1&2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @70MW, AG2 @105MW, AG4 @140MW, AG5 @49MW, AG6 @121MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
7/24/2023 12:39:44 PM | [NSO Update] Mindanao Grid-07/24/2023 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3308MW, PK=2186MW, RR=20MW, NetOpMargin: PM=1102, EVE=1182 Highest Unit O/L: GNPK 1&2 @ 138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @70MW, AG2 @105MW, AG4 @140MW, AG5 @49MW, AG6 @121MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
7/24/2023 11:13:39 AM | Mindanao Grid-07/24/2023 11:15: WMPC DG10 cut-in as RPS at 1052H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2023 11:13:21 AM | Mindanao Grid-07/24/2023 11:15: WMPC DG10 cut-in as RPS at 1052H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2023 11:12:40 AM | Mindanao Grid-07/24/2023 11:11: WMPC DG5 cut-out as RPS at 1100H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2023 11:09:07 AM | Mindanao Grid-07/24/2023 11:11: WMPC DG5 cut-out as RPS at 1100H. From RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2023 11:07:52 AM | Mindanao Grid-07/24/2023 11:09: NACSUR cut-in at 1100H [WEBSMS] | CMIN
7/24/2023 11:07:39 AM | Mindanao Grid-07/24/2023 11:09: NACSUR cut-in at 1100H [WEBSMS] | CMIN
7/24/2023 10:53:39 AM | Mindanao Grid-07/24/2023 10:53: WMPC DG2 cut-in as RPS at 1044H, as replacement for DG5. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2023 10:51:21 AM | Mindanao Grid-07/24/2023 10:53: WMPC DG2 cut-in as RPS at 1044H, as replacement for DG5. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2023 10:10:17 AM | Mindanao Grid-07/24/2023 10:08: NACSUR cut-in at 1003H . Follow RTD. [WEBSMS] | CMIN
7/24/2023 10:06:59 AM | Mindanao Grid-07/24/2023 10:08: NACSUR cut-in at 1003H . Follow RTD. [WEBSMS] | CMIN
7/24/2023 9:07:34 AM | Luzon Grid-07/24/2023 09:05: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0901H. (Planned Outage) [WEBSMS] | CLUZ
7/24/2023 9:05:07 AM | Luzon Grid-07/24/2023 09:05: Dasmarinas-TMC II (Ternate) 115kV Line de-energized at 0901H. (Planned Outage) [WEBSMS] | CLUZ
7/24/2023 9:02:36 AM | Mindanao Grid-07/24/2023 09:01: WMPC DG5 cut-in as RPS at 0857H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2023 9:00:00 AM | Mindanao Grid-07/24/2023 09:01: WMPC DG5 cut-in as RPS at 0857H. RPS - System Voltage Requirement. [WEBSMS] | CMIN
7/24/2023 8:57:35 AM | Mindanao Grid-07/24/2023 08:58: AGC(Lake Mainit) HEP Auto trip at 0851H. Gen. Loss of 11MW. Relay Indication: Earth Directional Trip phase B-N. Force Outage. [WEBSMS] | CMIN
7/24/2023 8:56:10 AM | Mindanao Grid-07/24/2023 08:58: AGC(Lake Mainit) HEP Auto trip at 0851H. Gen. Loss of 11MW. Relay Indication: Earth Directional Trip phase B-N. Force Outage. [WEBSMS] | CMIN
7/24/2023 8:24:18 AM | Mindanao Grid-07/24/2023 08:25: AGGREKODIG (APD) cut in at 0801H with 1.07MW Load. [WEBSMS] | CMIN
7/24/2023 8:23:26 AM | Mindanao Grid-07/24/2023 08:25: AGGREKODIG (APD) cut in at 0801H with 1.07MW Load. [WEBSMS] | CMIN
7/24/2023 6:00:07 AM | [NSO Update] Mindanao Grid-07/24/2023 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3325MW, PK=2102MW, RR=20MW, NetOpMargin: AM=1203, PM=1132, EVE=1245 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @47.5MW, MA2 @31MW, AG1 @70MW, AG2 @105MW, AG4 @140MW, AG5 @49MW, AG6 @121MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
7/24/2023 5:57:04 AM | [NSO Update] Visayas Grid-07/24/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2514MW, PK=2035MW, RR=40MW, NetOpMargin: AM=439, PM=380, EVE=334 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @296MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/24/2023 5:55:10 AM | [NSO Update] Visayas Grid-07/24/2023 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2514MW, PK=2035MW, RR=40MW, NetOpMargin: AM=439, PM=380, EVE=334 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal @82MW, LEYTE A @296MW, TPC-Carmen @30MW [WEBSMS] | CVIS
7/24/2023 5:54:09 AM | [NSO Update] Luzon Grid-07/24/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14153MW, PK=10120MW, RR=260MW, NetOpMargin: AM=3773, PM=2706, EVE=3171 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC3 @275MW, ILIJAN A @470MW, ILIJAN B @230MW [WEBSMS] | CLUZ
7/24/2023 5:53:44 AM | [NSO Update] Luzon Grid-07/24/2023 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14153MW, PK=10120MW, RR=260MW, NetOpMargin: AM=3773, PM=2706, EVE=3171 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC3 @275MW, ILIJAN A @470MW, ILIJAN B @230MW [WEBSMS] | CLUZ
7/24/2023 5:06:43 AM | [NSO Update] Luzon Grid-07/24/2023 04:59: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data at 570 km East of Baler, Aurora (15.2N, 126.9E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/24/2023 5:01:45 AM | [NSO Update] Mindanao Grid-07/24/2023 05:01: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data at 570 km East of Baler, Aurora (15.2N, 126.9E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
7/24/2023 4:59:46 AM | [NSO Update] Visayas Grid-07/24/2023 04:59: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data at 570 km East of Baler, Aurora (15.2N, 126.9E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
7/24/2023 4:59:15 AM | [NSO Update] Mindanao Grid-07/24/2023 05:01: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data at 570 km East of Baler, Aurora (15.2N, 126.9E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
7/24/2023 4:59:01 AM | [NSO Update] Visayas Grid-07/24/2023 04:59: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data at 570 km East of Baler, Aurora (15.2N, 126.9E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
7/24/2023 4:58:33 AM | [NSO Update] Luzon Grid-07/24/2023 04:59: Weather Update: At 3:00 AM today, the center of the eye of Typhoon EGAY was estimated based on all available data at 570 km East of Baler, Aurora (15.2N, 126.9E) with maximum sustained winds of 140 km/h near the center and gustiness of up to 170 km/h. It is moving Westward at 15 km/h. Southwest Monsoon affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/24/2023 3:21:53 AM | Mindanao Grid-07/24/2023 03:23: Sultan Kudarat 138/69/13.8 KV T3 (75MVA) energized 0210H. Affected by tripping of Kibawe-SKU 138 kV L. [WEBSMS] | CMIN
7/24/2023 3:21:40 AM | Mindanao Grid-07/24/2023 03:23: Sultan Kudarat 138/69/13.8 KV T3 (75MVA) energized 0210H. Affected by tripping of Kibawe-SKU 138 kV L. [WEBSMS] | CMIN
7/24/2023 3:15:47 AM | Mindanao Grid-07/24/2023 03:15: Kibawe-SKU 138 kV L energized at 0207H and looped at Sultan Kudarat 0210H. After repair works on the detached 138 kV line conductor at tower #107 completed. Unplanned Outage. [WEBSMS] | CMIN
7/24/2023 3:13:21 AM | Mindanao Grid-07/24/2023 03:15: Kibawe-SKU 138 kV L energized at 0207H and looped at Sultan Kudarat 0210H. After repair works on the detached 138 kV line conductor at tower #107 completed. Unplanned Outage. [WEBSMS] | CMIN
7/23/2023 11:39:51 PM | Luzon Grid-07/23/2023 23:39: Lumban-Malaya 230kV L energized at 2337H (Planned Outage) [WEBSMS] | CLUZ
7/23/2023 11:38:43 PM | Luzon Grid-07/23/2023 23:39: Lumban-Malaya 230kV L energized at 2337H (Planned Outage) [WEBSMS] | CLUZ
7/23/2023 9:57:36 PM | Mindanao Grid-07/23/2023 21:59: Bunawan - Toril 230kV Line 2 rrestored 2155H. Planned outage/N-GOMP P&E related activity [WEBSMS] | CMIN
7/23/2023 9:57:18 PM | Mindanao Grid-07/23/2023 21:59: Bunawan - Toril 230kV Line 2 rrestored 2155H. Planned outage/N-GOMP P&E related activity [WEBSMS] | CMIN
7/23/2023 8:35:36 PM | Mindanao Grid-07/23/2023 20:33: Lala-Kauswagan 230 kV L1( open at Kauswagan side) tripped at 2020H with indication CN,14.7 Km from Lala 230kV SS. The said line was energized at 1932H. [WEBSMS] | CMIN
7/23/2023 8:32:03 PM | Mindanao Grid-07/23/2023 20:33: Lala-Kauswagan 230 kV L1( open at Kauswagan side) tripped at 2020H with indication CN,14.7 Km from Lala 230kV SS. The said line was energized at 1932H. [WEBSMS] | CMIN
7/23/2023 7:43:02 PM | Mindanao Grid-07/23/2023 19:41: Lala- Kauswagan 230 kV L1 energized at 1932H, open at Kauswagan 230 SS side. [WEBSMS] | CMIN
7/23/2023 7:40:05 PM | Mindanao Grid-07/23/2023 19:41: Lala- Kauswagan 230 kV L1 energized at 1932H, open at Kauswagan 230 SS side. [WEBSMS] | CMIN
7/23/2023 7:01:16 PM | Luzon Grid-07/23/2023 19:01: Masinloc-Bolo 230kV Line 1 restored at 1900H (Planned Outage) [WEBSMS] | CLUZ
7/23/2023 6:30:31 PM | Luzon Grid-07/23/2023 18:10: Lumban-Malaya 230kV Line 2 de-energized at 1808H (Planned Outage) [WEBSMS] | CLUZ
7/23/2023 6:10:20 PM | Luzon Grid-07/23/2023 18:10: Lumban-Malaya 230kV Line 2 de-energized at 1808H (Planned Outage) [WEBSMS] | CLUZ
7/23/2023 6:06:18 PM | [NSO Update] Mindanao Grid-07/23/2023 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3219MW, PK=1855MW, RR=20MW, NetOpMargin: EVE=1344 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46.5MW, MA2 @31MW, AG1 @70MW, AG2 @65MW, AG4 @140MW, AG5 @49MW, AG6 @121MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
7/23/2023 6:05:10 PM | [NSO Update] Mindanao Grid-07/23/2023 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3219MW, PK=1855MW, RR=20MW, NetOpMargin: EVE=1344 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46.5MW, MA2 @31MW, AG1 @70MW, AG2 @65MW, AG4 @140MW, AG5 @49MW, AG6 @121MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN
7/23/2023 6:05:10 PM | [NSO Update] Visayas Grid-07/23/2023 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2318MW, PK=1839MW, RR=40MW, NetOpMargin: EVE=439 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @293MW [WEBSMS] | CVIS
7/23/2023 6:03:47 PM | [NSO Update] Visayas Grid-07/23/2023 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2318MW, PK=1839MW, RR=40MW, NetOpMargin: EVE=439 Highest Unit O/L: THVI 1&2 @169MW Derated Plant: TPC-Thermal 1A @82MW, LEYTE A @293MW [WEBSMS] | CVIS
7/23/2023 6:02:57 PM | [NSO Update] Luzon Grid-07/23/2023 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13617MW, PK=9380MW, RR=80MW, NetOpMargin: EVE=4157 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC3 @290MW, ILIJAN A @470MW, ILIJAN B @230MW [WEBSMS] | CLUZ
7/23/2023 6:01:39 PM | [NSO Update] Luzon Grid-07/23/2023 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13617MW, PK=9380MW, RR=80MW, NetOpMargin: EVE=4157 Highest Unit O/L: GNPD 1&2 @668MW Derated Plant: CLC2 @170MW, MSLC3 @290MW, ILIJAN A @470MW, ILIJAN B @230MW [WEBSMS] | CLUZ
7/23/2023 5:58:12 PM | Luzon Grid-07/23/2023 17:58: Lumban-Malaya 230kV Line 1 restored at 1758H. (Planned Outage) [WEBSMS] | CLUZ
7/23/2023 5:22:57 PM | Mindanao Grid-07/23/2023 17:24: Updates: Kibawe-SKU 138 kV Line and Kibawe SS 138 KV Bus 1 simultaneously tripped at 1617H. As per info from SKU SEOD, there was a detached 138 kV line conductor at tower # 107 located at Barangay Gumaga, Libungan, North Cotabato. D6 Linemen proceeding to the said location to conduct the repair. [WEBSMS] | CMIN
7/23/2023 5:22:56 PM | Mindanao Grid-07/23/2023 17:24: Updates: Kibawe-SKU 138 kV Line and Kibawe SS 138 KV Bus 1 simultaneously tripped at 1617H. As per info from SKU SEOD, there was a detached 138 kV line conductor at tower # 107 located at Barangay Gumaga, Libungan, North Cotabato. D6 Linemen proceeding to the said location to conduct the repair. [WEBSMS] | CMIN
7/23/2023 4:49:36 PM | Mindanao Grid-07/23/2023 16:47: Kibawe SS 138 KV Bus 1 energized back at 1644H [WEBSMS] | CMIN
7/23/2023 4:45:24 PM | Mindanao Grid-07/23/2023 16:47: Kibawe SS 138 KV Bus 1 energized back at 1644H [WEBSMS] | CMIN
7/23/2023 4:39:35 PM | Mindanao Grid-07/23/2023 16:40: Kibawe-SKU 138 kV Line and Kibawe SS 138 KV Bus 1 simultaneously tripped at 1617H. Reclosed after 2 sec but failed due to SOTF indication. Note : said Line was energized at 1531H from P.O /GOMP. Indication: M1: Z1, AN, 93.9 Km. M2: Z1, A, 82.6 Km. [WEBSMS] | CMIN
7/23/2023 4:38:50 PM | Mindanao Grid-07/23/2023 16:40: Kibawe-SKU 138 kV Line and Kibawe SS 138 KV Bus 1 simultaneously tripped at 1617H. Reclosed after 2 sec but failed due to SOTF indication. Note : said Line was energized at 1531H from P.O /GOMP. Indication: M1: Z1, AN, 93.9 Km. M2: Z1, A, 82.6 Km. [WEBSMS] | CMIN
7/23/2023 4:36:13 PM | [NSO Update] Luzon Grid-07/23/2023 16:31: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm EGAY was estimated based on all available data at 570 km East of Daet, Camarines Norte (14.9 N, 128.4 E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/23/2023 4:31:28 PM | [NSO Update] Mindanao Grid-07/23/2023 16:33: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm EGAY was estimated based on all available data at 570 km East of Daet, Camarines Norte (14.9 N, 128.4 E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
7/23/2023 4:31:16 PM | [NSO Update] Visayas Grid-07/23/2023 16:32: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm EGAY was estimated based on all available data at 570 km East of Daet, Camarines Norte (14.9 N, 128.4 E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
7/23/2023 4:31:15 PM | Mindanao Grid-07/23/2023 16:33: AGC(Lake Mainit) HEP cut in at 1626H from forced outage. [WEBSMS] | CMIN
7/23/2023 4:31:14 PM | [NSO Update] Mindanao Grid-07/23/2023 16:33: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm EGAY was estimated based on all available data at 570 km East of Daet, Camarines Norte (14.9 N, 128.4 E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CMIN
7/23/2023 4:31:04 PM | [NSO Update] Visayas Grid-07/23/2023 16:32: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm EGAY was estimated based on all available data at 570 km East of Daet, Camarines Norte (14.9 N, 128.4 E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CVIS
7/23/2023 4:30:57 PM | [NSO Update] Luzon Grid-07/23/2023 16:31: Weather Update: At 3:00 PM today, the center of Severe Tropical Storm EGAY was estimated based on all available data at 570 km East of Daet, Camarines Norte (14.9 N, 128.4 E) with maximum sustained winds of 110 km/h near the center and gustiness of up to 135 km/h. It is moving West Northwestward at 10 km/h. Southwest Monsoon affecting the western sections of Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
7/23/2023 4:30:11 PM | Mindanao Grid-07/23/2023 16:32: AGC(Lake Mainit) HEP Unit 2 and Unit 3 Auto trip at 1603H. Gen. Loss of 11MW. Relay Indication: 50BF CB Fail Relay. [WEBSMS] | CMIN
7/23/2023 4:26:12 PM | Luzon Grid-07/23/2023 16:24: San Rafael-Cabanatuan 230kV Line restored at 1624H. (Planned Outage) [WEBSMS] | CLUZ
7/23/2023 4:24:01 PM | Luzon Grid-07/23/2023 16:24: San Rafael-Cabanatuan 230kV Line restored at 1624H. (Planned Outage) [WEBSMS] | CLUZ
7/23/2023 3:53:33 PM | Luzon Grid-07/23/2023 15:54: Laoag - San Esteban 230kV Line 2 restored at 1553H. (Planned Outage) [WEBSMS] | CLUZ
7/23/2023 3:37:51 PM | Mindanao Grid-07/23/2023 15:39: Kibawe- Sultan Kudarat 138kV line restored 1531H. Planned outage / N-GOMP. [WEBSMS] | CMIN
7/23/2023 3:37:33 PM | Mindanao Grid-07/23/2023 15:39: Kibawe- Sultan Kudarat 138kV line restored 1531H. Planned outage / N-GOMP. [WEBSMS] | CMIN
7/23/2023 2:59:30 PM | Luzon Grid-07/23/2023 14:58: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1457H. (Planned Outage) [WEBSMS] | CLUZ
7/23/2023 2:58:31 PM | Luzon Grid-07/23/2023 14:58: Dasmarinas-TMC II (Ternate) 115kV Line restored at 1457H. (Planned Outage) [WEBSMS] | CLUZ
7/23/2023 1:42:46 PM | Luzon Grid-07/23/2023 13:42: Daraga-Bacman 230kV Line 2 energized at 1341H (Planned Outage) [WEBSMS] | CLUZ
7/23/2023 1:42:02 PM | Luzon Grid-07/23/2023 13:42: Daraga-Bacman 230kV Line 2 energized at 1341H (Planned Outage) [WEBSMS] | CLUZ
7/23/2023 1:03:26 PM | [NSO Update] Mindanao Grid-07/23/2023 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3266MW, PK=1638MW, RR=20MW, NetOpMargin: PM=1607, EVE=1370 Highest Unit O/L: GNPK 1&2 @138MW Derated Plant: MCC @150MW, MPC @40MW, MA1 @46.5MW, MA2 @31MW, AG1 @70MW, AG2 @65MW, AG4 @140MW, AG5 @49MW, AG6 @121MW, AG7 @30MW, PG4 @140MW [WEBSMS] | CMIN