5/26/2022 1:46:48 AM | LEYTE ACC-05/26/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 0128H/0138H, on reverse flow per RTD | CVIS
5/26/2022 1:46:47 AM | LEYTE ACC-05/26/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 0128H/0138H, on reverse flow per RTD | CVIS
5/26/2022 1:03:13 AM | LRCC-05/26/2022 01:01: Muntinlupa(Sucat) - Sun Valley 115kV Line de-energized at 0059H (Planned Outage) [WEBSMS] | CLUZ
5/26/2022 12:12:20 AM | LEYTE ACC-05/26/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 2358H/0008H, on normal flow per RTD | CVIS
5/26/2022 12:12:19 AM | LEYTE ACC-05/26/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 2358H/0008H, on normal flow per RTD | CVIS
5/26/2022 12:12:18 AM | VRCC-05/26/2022 00:09: 69KV Naga-Sibonga line auto trip @2330H with load=31.89MW OCR indication. [WEBSMS] | CVIS
5/25/2022 10:22:19 PM | LRCC-05/25/2022 22:20: Araneta-Sta. Mesa 115kV L1 de-energized at 2217H (Planned Outage). [WEBSMS] | CLUZ
5/25/2022 9:01:41 PM | LEYTE ACC-05/25/22: CALBAYOG SS, 69kV Calbayog-Bliss Line energized/de-energized to facilitate normalization, TIME OUT: 20:39:00, TIME IN: 20:57:00, LOAD=3.6MW, WEATHER: FAIR | CVIS
5/25/2022 9:01:40 PM | LEYTE ACC-05/25/22: CALBAYOG SS, 69kV Calbayog-Bliss Line energized/de-energized to facilitate normalization, TIME OUT: 20:39:00, TIME IN: 20:57:00, LOAD=3.6MW, WEATHER: FAIR | CVIS
5/25/2022 6:37:40 PM | PANAY ACC-05/25/22 18:30: BAROTAC VIEJO SS, Barotac Viejo-Dingle 138 kV Line 2 (7LI2BAR-DIN), TIME IN: 06:25:00, Pre arranged maintenance | CVIS
5/25/2022 6:37:37 PM | LRCC-05/25/2022 18:30: Tayabas-Naga 230kV Line 2 restored at 1826H. (Planned Outage) [WEBSMS] | CLUZ
5/25/2022 6:15:25 PM | VRCC-05/25/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2359MW, PK=2175MW, RR=40MW, NetOpMargin: EVE=144 Highest Unit O/L: TVI U1 at 169MW Derated Plant: TVI at 169MW, EDC at 345MW, TPC at 82MW, Luzon to augment Visayas [WEBSMS] | CVIS
5/25/2022 5:49:26 PM | LRCC-05/25/2022 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13203MW, PK=10545MW, RR=372MW, NetOpMargin: EVE=2286 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLPGC 1 @135MW, GMEC 2 @ 280MW, & Ilijan @540MW [WEBSMS] | CLUZ
5/25/2022 5:36:00 PM | PANAY ACC-05/25/22 17:26: BAROTAC VIEJO SS, Barotac Viejo-Dingle 138 kV Line 2 (7LI2BAR-DIN), TIME OUT: 05:24:00, Pre arranged maintenance | CVIS
5/25/2022 5:25:27 PM | MRCC-05/25/2022 17:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2873MW, PK=1980MW, RR=79MW, NetOpMargin: EVE=0 Highest Unit O/L: GNPOWER U1&U4@138MW each Derated Plant: Ag1@55MW, Ag2@70MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@25MW, Pul4@142MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@246MW, MCC@100MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/25/2022 5:11:47 PM | PANAY ACC-05/25/22 16:56: NABAS SS, Nabas-Culasi 69KV L1 (5LI1NBS-CSI), TIME OUT: 04:44:00, TIME IN: 04:51:00, Manually open to facilitate closing of ABS 357 after clearing of bamboo at str. 123, Brgy. Tigis, Tib-iao, Antique. WEATHER: FAIR | CVIS
5/25/2022 5:01:44 PM | LEYTE ACC-05/25/22: CALBAYOG SS, 69kV Calbayog-Bliss Line re-energized up to Str # 228-D at 1654H, customer re-energized while tripper is being corrected. | CVIS
5/25/2022 5:01:43 PM | LEYTE ACC-05/25/22: CALBAYOG SS, 69kV Calbayog-Bliss Line re-energized up to Str # 228-D at 1654H, customer re-energized while tripper is being corrected. | CVIS
5/25/2022 3:38:01 PM | PANAY ACC-05/25/22 15:32: NABAS SS, Nabas-Culasi 69KV L1 (5LI1NBS-CSI), TIME IN: 03:27:00 | CVIS
5/25/2022 2:29:00 PM | LEYTE ACC-05/25/22: CALBAYOG SS, 69kV Calbayog-Bliss Line, TIME OUT: 14:13:00, RELAY: phase BN, 26.03kms, load=3MW, WEATHER: FAIR | CVIS
5/25/2022 2:28:58 PM | LEYTE ACC-05/25/22: CALBAYOG SS, 69kV Calbayog-Bliss Line, TIME OUT: 14:13:00, RELAY: phase BN, 26.03kms, load=3MW, WEATHER: FAIR | CVIS
5/25/2022 2:28:56 PM | LRCC-05/25/2022 14:22: Bauang-La Trinidad 230kV Line 2 tripped & reclosed at 1400H (Unplanned Outage) [WEBSMS] | CLUZ
5/25/2022 2:28:53 PM | LRCC-05/25/2022 14:22: Bauang-La Trinidad 230kV Line 2 tripped & reclosed at 1400H (Planned Outage) [WEBSMS] | CLUZ
5/25/2022 1:38:22 PM | PANAY ACC-05/25/22 13:22: NABAS SS, Nabas-Culasi 69KV L1 (5LI1NBS-CSI), Test energized at 13:19H but failed , RELAY: Started A-B, Phase A, 56.19km., WEATHER: FAIR. Sustained fault. | CVIS
5/25/2022 1:28:19 PM | PANAY ACC-05/25/22 13:18: NABAS SS, Nabas-Culasi 69KV L1 (5LI1NBS-CSI), TIME OUT: 13:15:00, RELAY: Started A-B, Phase A, 56.19km., WEATHER: FAIR. Cause under investigation. | CVIS
5/25/2022 1:14:27 PM | LRCC-05/25/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13555MW, PK=11578MW, RR=425MW, NetOpMargin: PM=1552, EVE=2282 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLPGC 1 @130MW, GMEC 2 @ 280MW, & Ilijan @540MW [WEBSMS] | CLUZ
5/25/2022 1:04:23 PM | VRCC-05/25/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2571MW, PK=2254MW, RR=40MW, NetOpMargin: PM=277, EVE=139 Highest Unit O/L: TVI U1 at 169 MW Derated Plant: TVI at 169MW, EDC = 340 MW, TPC = 82 MW [WEBSMS] | CVIS
5/25/2022 11:27:52 AM | MRCC-05/25/2022 11:16: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2947MW, PK=2120MW, RR=85MW, NetOpMargin: PM=742, EVE=814 Highest Unit O/L: GNPOWER U1&U4@138MW each Derated Plant: Ag1@55MW, Ag2@70MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@25MW, Pul4@142MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@246MW, MCC@100MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/25/2022 9:39:39 AM | PANAY ACC-05/25/22 09:32: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME IN: 09:30:00, RELAY: Phase A, Gen. Start, Forward Fault, 49.31km., WEATHER: FAIR. Cause under investigation. | CVIS
5/25/2022 9:39:37 AM | PANAY ACC-05/25/22 09:23: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 09:21:00, RELAY: A, Gen. Start, Forward Fault, 49.31km., WEATHER: FAIR. Cause under investigatio. | CVIS
5/25/2022 9:02:39 AM | LEYTE ACC-05/25/22 08:22: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 0810H/0820H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
5/25/2022 8:29:23 AM | LEYTE ACC-05/25/22 08:18: ORMOC SS, 69kV Ormoc-Simangan-Baybay line tripped at 0802H, EF Inverse trip, load=27.2MW. Restored per clearance from Line Engineer at 0808H. WEATHER: FAIR | CVIS
5/25/2022 6:45:13 AM | VRCC-05/25/2022 06:40: TVI unit# 2 auto tripped @0636H with load=164MW, cause possible boiler tube leak. [WEBSMS] | CVIS
5/25/2022 6:45:11 AM | LRCC-05/25/2022 06:44: Tayabas-Naga 230kV Line 2 de-energized at 0643H. (Planned Outage) [WEBSMS] | CLUZ
5/25/2022 5:30:48 AM | LRCC-05/25/2022 05:22: San Jose - Taytay 230kV Line 1 restored at 0518H (Planned Outage) [WEBSMS] | CLUZ
5/25/2022 4:57:06 AM | LRCC-05/25/2022 04:53: Binan-San Pedro 115kV Line restored at 0446H (Planned Outage) [WEBSMS] | CLUZ
5/25/2022 4:40:01 AM | MRCC-05/25/2022 04:31: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2944MW, PK=1990MW, RR=57MW, NetOpMargin: AM=875, PM=746, EVE=817 Highest Unit O/L: GNPOWER U1&U4@138MW each. Derated Plant: Ag1@55MW, Ag2@70MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@25MW, Pul4@148MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@245.5MW, SMCPC@270MW, GNPOWER@276MW, SEC1@105MW, SEC2@105MW & MCC@100MW. [WEBSMS] | CMIN
5/25/2022 12:24:34 AM | LRCC-05/25/2022 00:24: San Jose - Taytay 230kV Line 1 de-energized at 0015H (Planned Outage) [WEBSMS] | CLUZ
5/25/2022 12:24:33 AM | LRCC-05/25/2022 00:23: Binan-San Pedro 115kV Line de-energized at 2359H (Planned Outage) [WEBSMS] | CLUZ
5/24/2022 8:25:50 PM | LEYTE ACC-05/24/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 2011H/2021H, on normal flow per RTD | CVIS
5/24/2022 8:25:49 PM | LEYTE ACC-05/24/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 2011H/2021H, on normal flow per RTD | CVIS
5/24/2022 6:23:25 PM | LRCC-05/24/2022 18:16: Tayabas-Naga 230kV Line 2 restored at 1807H. (Planned Outage) [WEBSMS] | CLUZ
5/24/2022 5:49:49 PM | LRCC-05/24/2022 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13142MW, PK=10643MW, RR=374MW, NetOpMargin: EVE=2125 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A at 540MW, GMEC 2 at 280MW, SLPGC 1 at 140MW [WEBSMS] | CLUZ
5/24/2022 5:39:50 PM | VRCC-05/24/2022 17:39: Samboan 30MVA Transformer no, 1energized at 1733H. Pre-arranged activity completed. [WEBSMS] | CVIS
5/24/2022 2:15:46 PM | LRCC-05/24/2022 14:13: Limay-Limay BESS 69kV Line restored at 1411H. (Planned Outage) [WEBSMS] | CLUZ
5/24/2022 2:05:49 PM | NEGROS ACC: 05/24/2022, PGPP1 U1 re-online at 1358H. | CVIS
5/24/2022 1:55:47 PM | NEGROS ACC: 05/24/2022, PGPP1 U1 (36.54 MW) auto-tripped at 1344H.Ongoing investigation on cause of tripping. | CVIS
5/24/2022 1:41:32 PM | PANAY ACC-05/24/22 13:30: DINGLE SS, Dingle-Calinog 69KV (5LI1DIN-CLI), TIME IN: 13:26:00, RELAY: Z1, B-N, WEATHER: FAIR. Detached conductor structure 142 type B at Bgy. Dalid, Calinog, Iloilo. | CVIS
5/24/2022 1:41:30 PM | PANAY ACC-05/24/22 13:30: DINGLE SS, Dingle-Calinog 69KV (5LI1DIN-CLI), TIME IN: 01:26:00, RELAY: Z1, B-N, WEATHER: FAIR. Detached conductor structure 142 type B at Bgy. Dalid, Calinog, Iloilo. | CVIS
5/24/2022 1:06:17 PM | VRCC-05/24/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2735MW, PK=2254MW, RR=39MW, NetOpMargin: PM=486, EVE=343 Highest Unit O/L: TVI U at 169MW each Derated Plant: EDC at 335MW, TPC at 82MW [WEBSMS] | CVIS
5/24/2022 12:31:07 PM | LRCC-05/24/2022 12:28: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13512MW, PK=11107MW, RR=365MW, NetOpMargin: PM=2040, EVE=2832 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A at 540MW, GMEC 2 at 280MW, SLPGC 1 at 140MW [WEBSMS] | CLUZ
5/24/2022 11:57:40 AM | MRCC-05/24/2022 11:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2949MW, PK=2100MW, RR=59MW, NetOpMargin: PM=765, EVE=823 Highest Unit O/L: GNPOWER U1&U4@138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@25MW, Pul4@149MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@245.5MW, SMCPC@270MW, GNPOWER@276MW, SEC1@105MW, SEC2@105MW & MCC@100MW. [WEBSMS] | CMIN
5/24/2022 11:57:27 AM | PANAY ACC-05/24/22 11:48: DINGLE SS, Dingle-Calinog 69KV (5LI1DIN-CLI), TIME OUT: 11:41:00, RELAY: Z1, B-N, WEATHER: FAIR. Test energized at 1146H but failed with ind.: A-B-N. Sustained Fault. Customers owned and maintained line. | CVIS
5/24/2022 11:51:39 AM | PANAY ACC-05/24/22 11:45: DINGLE SS, Dingle-Calinog 69KV (5LI1DIN-CLI), TIME OUT: 11:41:00, RELAY: Z1, B-N, WEATHER: FAIR, Customers Owned and maintained line. | CVIS
5/24/2022 10:53:55 AM | LEYTE ACC-05/24/22: EDC-Leyte A, UMPP Unit #1 cut-in at 1017H | CVIS
5/24/2022 10:53:54 AM | LEYTE ACC-05/24/22: EDC-Leyte A, UMPP Unit #1 cut-in at 1017H | CVIS
5/24/2022 8:56:39 AM | LEYTE ACC-05/24/22: PARANAS SS, 69kV Paranas-Borongan-Quinapondan Line, TIME OUT: 08:42:00, TIME IN: 08:44:00, RELAY: z1, phase BN, 16.55kms, load=11.5MW, WEATHER: FAIR | CVIS
5/24/2022 8:56:37 AM | LEYTE ACC-05/24/22: PARANAS SS, 69kV Paranas-Borongan-Quinapondan Line, TIME OUT: 08:42:00, TIME IN: 08:44:00, RELAY: z1, phase BN, 16.55kms, load=11.5MW, WEATHER: FAIR | CVIS
5/24/2022 7:32:50 AM | LEYTE ACC-05/24/22: ORMOC SS, 138kV Ormoc-Maasin Line 2 pre-arranged activity, TIME OUT: 07:21:00, WEATHER: FAIR | CVIS
5/24/2022 7:32:48 AM | LEYTE ACC-05/24/22: ORMOC SS, 138kV Ormoc-Maasin Line 2 pre-arranged activity, TIME OUT: 07:21:00, WEATHER: FAIR | CVIS
5/24/2022 6:25:31 AM | LRCC-05/24/2022 06:21: Tayabas-Naga 230kV Line 2 de-energized at 0618H. (Planned Outage) [WEBSMS] | CLUZ
5/24/2022 6:18:52 AM | VRCC-05/24/2022 06:16: Samboan 30MVA Transformer #1manually open @0604H for PMS. [WEBSMS] | CVIS
5/24/2022 6:18:50 AM | LRCC-05/24/2022 06:15: Limay-Limay BESS 69kV Line de-energized at 0602H. (Planned Outage) [WEBSMS] | CLUZ
5/24/2022 5:58:49 AM | VRCC-05/24/2022 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2796MW, PK=2247MW, RR=40MW, NetOpMargin: AM=509, PM=441, EVE=342 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 335 MW, TPC = 82 MW [WEBSMS] | CVIS
5/24/2022 5:35:12 AM | LRCC-05/24/2022 05:32: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13542MW, PK=10877MW, RR=315MW, NetOpMargin: AM=2350, PM=2108, EVE=2987 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLPGC 1 @135MW, GMEC 2 @ 280MW, & Ilijan @540MW [WEBSMS] | CLUZ
5/24/2022 4:46:55 AM | MRCC-05/24/2022 04:33: GRID UPDATE AS OF 6:00 AM System Condition: CAP=2939MW, PK=2015MW, RR=81MW, NetOpMargin: AM=843, PM=761, EVE=811 Highest Unit O/L: GNPOWER U1&U4@138MW each Derated Plant: Ag1@55MW, Ag2@65MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@25MW, Pul4@108MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@246MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/24/2022 4:18:25 AM | LRCC-05/24/2022 04:18: Weather Update: Southwest Monsoon affecting the western section of Luzon. [WEBSMS] | CLUZ
5/24/2022 2:07:16 AM | NEGROS ACC: 05/24/2022, PGPP2 SOG1 re-online at 0145H. | CVIS
5/24/2022 12:10:50 AM | LRCC-05/24/2022 00:06: San Gabriel online at 2359H. (Maintenance Outage) [WEBSMS] | CLUZ
5/23/2022 11:36:23 PM | (Correction)NEGROS ACC: 05/23/2022, PGPP2 SOG1 (19.3 MW) auto-tripped at 2309H with indication condenser level high | CVIS
5/23/2022 11:23:31 PM | LEYTE ACC-05/23/22 23:23: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked on normal flow per RTD. WEATHER: FAIR | CVIS
5/23/2022 11:23:30 PM | NEGROS ACC: 05/23/2022, PGPP2 SOG1 (17.58MW) auto-tripped at 1121H with indication condenser level high | CVIS
5/23/2022 11:23:28 PM | NEGROS ACC: 03/23/2022, PGPP2 SOG1 (19.37 MW) auto-tripped at 2309H due to condenser level high | CVIS
5/23/2022 11:09:29 PM | LRCC-05/23/2022 23:01: For info: Sta Rita-San Lorenzo 230kV Bus A & B tie Breakers were opened at 2252H, unlooping Sta Rita CCPP and San Lorenzo CCPP. This is in preparation for the synchronization of San Gabriel CCPP. Paralleling of Batangas 300MVA T04 and T05 was completed at 2300H. [WEBSMS] | CLUZ
5/23/2022 6:16:58 PM | LRCC-05/23/2022 18:16: Tayabas-Naga 230kV Line 2 restored at 1816H. (Planned Outage) [WEBSMS] | CLUZ
5/23/2022 6:03:25 PM | VRCC-05/23/2022 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2518MW, PK=2220MW, RR=40MW, NetOpMargin: EVE=258 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 335 MW, TPC = 82 MW [WEBSMS] | CVIS
5/23/2022 5:31:00 PM | LRCC-05/23/2022 17:27: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12777MW, PK=9890MW, RR=392MW, NetOpMargin: EVE=2495 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLPGC 1 @130MW; SLPGC 2 @140MW; ILIJAN A @540MW [WEBSMS] | CLUZ
5/23/2022 4:32:10 PM | MRCC-05/23/2022 16:20: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2854MW, PK=2020MW, RR=81MW, NetOpMargin: EVE=753 Highest Unit O/L: GNPOWER U1&U4@138MW each Derated Plant: Ag1@55MW, Ag2@65MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@25MW, Pul4@145MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@246MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/23/2022 1:00:26 PM | VRCC-05/23/2022 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2735MW, PK=2245MW, RR=40MW, NetOpMargin: PM=450, EVE=258 Highest Unit O/L: TVI U @ 169 MW EDC = 335 MW Derated Plant: EDC = 335 MW, TPC = 82 MW [WEBSMS] | CVIS
5/23/2022 12:31:20 PM | MRCC-05/23/2022 12:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2926MW, PK=2160MW, RR=86MW, NetOpMargin: PM=680, EVE=753 Highest Unit O/L: GNPOWER U1&U4@138MW each Derated Plant: Ag1@55MW, Ag2@65MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@25MW, Pul4@142MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@246MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/23/2022 6:31:06 AM | LRCC-05/23/2022 06:21: Tayabas-Naga 230kV Line 2 de-energized at 0621H. (Planned Outage) [WEBSMS] | CLUZ
5/23/2022 6:07:46 AM | VRCC-05/23/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2796MW, PK=2169MW, RR=63MW, NetOpMargin: AM=564, PM=450, EVE=258 Highest Unit O/L: TVI U at 169MW each Derated Plant: EDC at 335MW, TPC at 82MW [WEBSMS] | CVIS
5/23/2022 5:41:58 AM | LRCC-05/23/2022 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13005MW, PK=10553MW, RR=437MW, NetOpMargin: AM=2015, PM=1693, EVE=2664 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLPGC 1 @140MW; SLPGC 2 @60MW; ILIJAN A @540MW [WEBSMS] | CLUZ
5/23/2022 5:14:30 AM | MRCC-05/23/2022 05:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2926MW, PK=2100MW, RR=56MW, NetOpMargin: AM=742, PM=688, EVE=762 Highest Unit O/L: GNPOWER U1&U4@138MW each. Derated Plant: Ag1@55MW, Ag2@70MW, Ag4@156MW, Ag5@47MW, Ag6@65MW, Ag7@25MW, Pul4@148MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@245.5MW, SMCPC@270MW, GNPOWER@276MW, SEC1@105MW, SEC2@105MW & MCC@100MW. [WEBSMS] | CMIN
5/23/2022 12:59:38 AM | NEGROS ACC: 05/23/2022, 69kV Dauin-Siaton Line section restored at 0050H. | CVIS
5/23/2022 12:59:37 AM | NEGROS ACC: 05/23/2022, 69kV Dauin-Siaton Line section restored at 0050H. | CVIS
5/22/2022 10:27:41 PM | LRCC-05/22/2022 22:18: Laoag 115kV Bus 1 restored at 2213H (Planned Outage) [WEBSMS] | CLUZ
5/22/2022 9:16:27 PM | NEGROS ACC: 05/12/2022, 69kV Dauin-Siaton Line section auto-tripped at 2109H with indication Z3 CA Start, 32.37 km. | CVIS
5/22/2022 9:16:26 PM | NEGROS ACC: 05/22/2022, 69kV Dauin-Siaton Line section restored at 2104H. | CVIS
5/22/2022 9:02:55 PM | NEGROS ACC: 05/22/2022, 69kV Dauin-Siaton Line section (9.26MW) auto-tripped at 2049H with indication Z3 CA Start, 32.63 km. | CVIS
5/22/2022 9:02:54 PM | VRCC-05/22/2022 21:02: Cebu SS Transformer No. 3 energized at 2051H. Pre-arranged activity completed. [WEBSMS] | CVIS
5/22/2022 8:38:58 PM | VRCC-05/22/2022 20:34: 138KV Cebu-Colon line 1 energized at 2030H. Pre-arranged activity completed. [WEBSMS] | CVIS
5/22/2022 8:15:12 PM | VRCC-05/22/2022 20:12: Cebu SS CB 7-04CB24CEB manually closed at 2009H. [WEBSMS] | CVIS
5/22/2022 6:40:27 PM | LEYTE ACC-05/22/22 18:42: CALBAYOG SS, Calbayog Bliss 69kVL,Deenergized/Energized 1751H/1757H,while Catbalogan feeder energized at 1818H,load=12.8mw, back to Normal configuration per PANR VRCC-2022-05-0040,WEATHER: FAIR | CVIS
5/22/2022 6:30:22 PM | LEYTE ACC-05/22/22 18:37:PARANAS SS, Paranas 138/69/13.8 kV T2 (50MVA),Energized at 1744H,pre arranged completed per PANR VRCC-2022-05-0040, WEATHER: FAIR | CVIS
5/22/2022 6:06:38 PM | VRCC-05/22/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2501MW, PK=1995MW, RR=40MW, NetOpMargin: EVE=466 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 335, TPC at 82 MW [WEBSMS] | CVIS
5/22/2022 5:33:06 PM | LRCC-05/22/2022 17:29: Tayabas-Naga 230kV Line 2 restored at 1728H. (Planned Outage) [WEBSMS] | CLUZ
5/22/2022 5:27:00 PM | LEYTE ACC-05/22/22 17:19:ORMOC SS,Tolosa-San Isidro 69 kV L/PCB Nasaug Deenergized/Energized at 1639,1641H/1654/1641H, respectively,while Soleq ABS#2 closed at 1653H, Tunga feeder back to normal configuration,load=26.3mw,Per PANR No.TLOS V_LEY-2022-05-0007, WEATHER: FAIR | CVIS
5/22/2022 5:06:57 PM | NEGROS ACC: 05/22/2022, PGPP1 U1 re-online at 1659H | CVIS
5/22/2022 5:03:31 PM | NEGROS ACC: 05/22/2022, 69kV Mabinay-Bayawan Sub T/L energized at 1658H after completion of maintenance activities | CVIS
5/22/2022 4:53:28 PM | NEGROS ACC: 05/22/2022, 69kV Kabankalan-La Castellana Sub T/L (10.45 MW) auto-tripped at 1638H with indication Z1 BC-N, 36.0 km. Restored at 1641H. Customer-owned and maintained line. | CVIS
5/22/2022 4:29:47 PM | LRCC-05/22/2022 16:20: Las Pinas (Zapote) 300MVA T04 restored at 1619H (Planned Outage). [WEBSMS] | CLUZ
5/22/2022 4:16:53 PM | LRCC-05/22/2022 16:16: Las Pinas(Zapote)-Dasmarinas 230kV Line 2 restored at 1615H (Planned Outage). [WEBSMS] | CLUZ
5/22/2022 4:06:03 PM | PANAY ACC-05/22/22 15:55: PANIT-AN SS, Panit-an 138/69/13.8 kV T2 (30MVA) (7XF02PNT), TIME IN: 15:52, Pre-arranged maintenance | CVIS
5/22/2022 3:32:37 PM | MRCC-05/22/2022 15:17: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2874MW, PK=1750MW, RR=57MW, NetOpMargin: EVE=1054 Highest Unit O/L: GNPOWER U1&U4@138MW each. Derated Plant: Ag1@55MW, Ag2@70MW, Ag4@156MW, Ag5@47MW, Ag6@65MW, Ag7@25MW, Pul4@145MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@245.5MW, SMCPC@270MW, GNPOWER@276MW, SEC1@105MW, SEC2@105MW & MCC@100MW. [WEBSMS] | CMIN
5/22/2022 3:32:26 PM | LEYTE ACC-05/22/22 15:33:ORMOC SS, Ormoc-Lemon-Tolosa-San Isidro 69 kV L,Energized at 1510H while Soleq Solar PP cut-in at 1515H, WEATHER: FAIR . | CVIS
5/22/2022 3:32:24 PM | LRCC-05/22/2022 15:21: Calamba 230kV Bus 1 restored at 1520H (Planned Outage). [WEBSMS] | CLUZ
5/22/2022 3:21:31 PM | MRCC-05/22/2022 15:13: GRID UPDATE AS OF 6:00 PM System Condition: CAP=2874MW, PK=1750MW, RR=57MW, NetOpMargin: EVE=1054 Highest Unit O/L: GNPOWER U1&U4@138MW each. Derated Plant: Ag1@55MW, Ag2@70MW, Ag4@156MW, Ag5@47MW, Ag6@65MW, Ag7@25MW, Pul4@145MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@245.5MW, SMCPC@270MW, GNPOWER@276MW, SEC1@105MW, SEC2@105MW & MCC@100MW. [WEBSMS] | CMIN
5/22/2022 3:21:15 PM | NEGROS ACC: 05/22/2022, PGPP1 U1 (12.08 MW) auto-tripped at 1459H due to condenser level very low | CVIS
5/22/2022 2:49:56 PM | NEGROS ACC: 05/22/2022, PGPP1 U1 re-online at 1434H. | CVIS
5/22/2022 2:26:31 PM | LEYTE ACC-05/22/22 14:30: ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69 kV L ,Deenergized at 1409H Per Customers request Soleq Solar PP to effect emergency correction of Phase B contact finger of Soleq ABS #2 (ECT at 1500H) WEATHER: FAIR | CVIS
5/22/2022 1:56:57 PM | NEGROS ACC: 05/22/2022, PGPP1 U1 (37.09MW) auto-tripped at 1339H. On going investigation on cause of tripping. | CVIS
5/22/2022 1:56:56 PM | NEGROS ACC: 05/22/2022, PGPP1 U1 (37.09MW) auto-tripped at 1339H. On going investigation on cause of tripping. | CVIS
5/22/2022 1:33:22 PM | PANAY ACC-05/22/22 06:45: PANIT-AN SS, Panit-an 138/69/13.8 kV T2 (30MVA) (7XF02PNT), TIME OUT: 06:39:00, Pre arranged maintenance, ETR: 1800H, WEATHER: FAIR | CVIS
5/22/2022 1:09:25 PM | VRCC-05/22/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2731MW, PK=1965MW, RR=29MW, NetOpMargin: PM=737, EVE=466 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 335, TPC at 82 MW [WEBSMS] | CVIS
5/22/2022 12:32:32 PM | LRCC-05/22/2022 12:31: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13305MW, PK=8678MW, RR=352MW, NetOpMargin: PM=4275, EVE=3433 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; ILIJAN A @540MW [WEBSMS] | CLUZ
5/22/2022 11:56:39 AM | LEYTE ACC-05/22/22 12:00: MAASIN SS,69kV PCB Soleco closed at 1138H,while Sepalco Solar PP cut-in at 1140H, with clearance from O&M, WEATHER: Cloudy. | CVIS
5/22/2022 11:44:12 AM | LEYTE ACC-05/22/22 11:46: MAASIN SS, PCB Soleco Tripped at 1120H,under assestment, WEATHER: FAIR | CVIS
5/22/2022 11:34:10 AM | NEGROS ACC: 05/22/2022, 69kV Bacolod-Reclamation Sub T/L restored at 1123H. Customer owned and maintained line. | CVIS
5/22/2022 11:34:09 AM | NEGROS ACC: 05/22/2022, 69kV Bacolod-Reclamation Sub T/L (25.57 MW) auto tripped at 1118H with indication: Z1 L3-E, 0.6 km. Customer owned and maintained line. | CVIS
5/22/2022 11:34:07 AM | NEGROS ACC: 05/22/2022, 69kV Bacolod-Reclamation Sub T/L (25.57 MW) auto tripped at 1118H with indication: Z1 L3-E, 0.6 km. Customer owned and maintained line. | CVIS
5/22/2022 10:55:42 AM | MRCC-05/22/2022 10:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2931MW, PK=1615MW, RR=58MW, NetOpMargin: PM=1251, EVE=1054 Highest Unit O/L: GNPOWER U1&U4@138MW each. Derated Plant: Ag1@55MW, Ag2@70MW, Ag4@156MW, Ag5@47MW, Ag6@65MW, Ag7@25MW, Pul4@145MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@245.5MW, SMCPC@270MW, GNPOWER@276MW, SEC1@105MW, SEC2@105MW & MCC@100MW. [WEBSMS] | CMIN
5/22/2022 8:23:56 AM | LRCC-05/22/2022 08:18: Sta. Rita-San Lorenzo Tie Line 1 & 2 looped at 0816H. [WEBSMS] | CLUZ
5/22/2022 7:46:37 AM | LEYTE ACC-05/22/22 07:48:PARANAS SS, Paranas 138/69/13.8 kV T2(50MVA),Deenergized at 0732H,pre arranged per PANR No.VRCC-2022-05-0040,(6am-6pm) WEATHER: FAIR . | CVIS
5/22/2022 7:12:51 AM | LRCC-05/22/2022 07:08: Calamba 230kV Bus 1 de-energized at 0707H (Planned Outage). [WEBSMS] | CLUZ
5/22/2022 6:59:12 AM | LRCC-05/22/2022 06:55: Laoag 115kV Bus 1 de-energized at 0654H (Planned Outage). [WEBSMS] | CLUZ
5/22/2022 6:49:14 AM | VRCC-05/22/2022 06:48: 138KV Colon-Samboan Line 2 manually open @0642H for APMS. [WEBSMS] | CVIS
5/22/2022 6:39:10 AM | LRCC-05/22/2022 06:39: Tayabas-Naga 230kV Line 2 de-energized at 0638H. (Planned Outage) [WEBSMS] | CLUZ
5/22/2022 6:15:44 AM | NEGROS ACC: 05/22/2022, 69kV Mabinay-Bayawan Sub T/L (5.7MW) de-energized at 0609H to conduct wood pole replacement and correction of defects on affected HVE and protection devices. | CVIS
5/22/2022 6:15:43 AM | NEGROS ACC: 05/22/2022, 69kV Mabinay-Bayawan Sub T/L (5.7MW) de-energized at 0609H to conduct wood pole replacement and correction of defects on affected HVE and protection devices. | CVIS
5/22/2022 6:12:07 AM | LEYTE ACC-05/22/22 05:45: ORMOC SS, Ormoc-Tolosa-San Isidro 69 kV line de-energized at 0505H, pre arranged activity. Leyeco 3 & DORELCO loads were transferred to Maasin Ss. WEATHER: FAIR | CVIS
5/22/2022 6:02:05 AM | VRCC-05/22/2022 06:00: 138KV Cebu-Colon line 1 manually open @0553H for maintenance activity. [WEBSMS] | CVIS
5/22/2022 6:02:03 AM | VRCC-05/22/2022 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2778MW, PK=1839MW, RR=40MW, NetOpMargin: AM=899, PM=724, EVE=466 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 335 MW, TPC = 82 MW [WEBSMS] | CVIS
5/22/2022 5:49:36 AM | VRCC-05/22/2022 05:45: Cebu SS Transformer #3 manually open @0541H for maintenance activity. [WEBSMS] | CVIS
5/22/2022 5:49:20 AM | LRCC-05/22/2022 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13203MW, PK=8355MW, RR=339MW, NetOpMargin: AM=4509, PM=4146, EVE=3421 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; ILIJAN A @540MW [WEBSMS] | CLUZ
5/22/2022 5:25:16 AM | MRCC-05/22/2022 05:11: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2939MW, PK=1575MW, RR=63MW, NetOpMargin: AM=1301, PM=1261, EVE=1064 Highest Unit O/L: GNPOWER U1&U4@138MW each Derated Plant: Ag1@55MW, Ag2@70MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@25MW, Pul4@145MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@246MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/22/2022 5:24:53 AM | LRCC-05/22/2022 05:24: Las Pinas (Zapote)-Dasmarinas 230kV Line 1, Las Pinas (Zapote) 300MVA T02 and Las Pinas (Zapote) 300MVA T03 de-enerized at 0523H (Planned Outage). [WEBSMS] | CLUZ
5/22/2022 5:24:52 AM | LRCC-05/22/2022 05:19: Las Pinas(Zapote)-Dasmarinas 230kV Line 2 de-energized at 0518H (Planned Outage). [WEBSMS] | CLUZ
5/22/2022 12:33:03 AM | LRCC-05/22/2022 00:26: Hermosa - BCCPP 230kV L3 tripped and autoreclosed at 0022H (Unplanned Outage). [WEBSMS] | CLUZ
5/21/2022 9:34:59 PM | LEYTE ACC-05/21/22 21:30: 350kV HVDC manually blocked/deblocked at 2117H/2127H, on normal power flow per RTD. WEATHER: FAIR | CVIS
5/21/2022 6:39:29 PM | VRCC-05/21/2022 18:38: Cebu SS 138 kV Bus 2 energized at 1835H, pre-arranged activity completed [WEBSMS] | CVIS
5/21/2022 6:01:29 PM | VRCC-05/21/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2500MW, PK=2124MW, RR=39MW, NetOpMargin: EVE=337 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 335, TPC at 82 MW [WEBSMS] | CVIS
5/21/2022 5:40:36 PM | PANAY ACC-05/21/22 17:32: PANIT-AN SS, Panit-an 138/69/13.8 kV T3 (30MVA) (7XF03PNT), TIME IN: 17:31:00, Pre-arranged Maintenance activity, Paralleled to TR#2 at 1732H. | CVIS
5/21/2022 5:40:34 PM | LRCC-05/21/2022 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12428MW, PK=8719MW, RR=381MW, NetOpMargin: EVE=3328 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, San Lorenzo 60 at 260MW, Ilijan at 540MW [WEBSMS] | CLUZ
5/21/2022 5:40:32 PM | LRCC-05/21/2022 17:36: Tayabas-Naga 230kV Line 2 restored at 1733H. (Planned Outage) [WEBSMS] | CLUZ
5/21/2022 5:17:35 PM | VRCC-05/21/2022 17:17: 138kV Colon-Samboan Line 1 energized at 1715H, pre-arranged activity completed [WEBSMS] | CVIS
5/21/2022 5:17:32 PM | LRCC-05/21/2022 17:17: San Jose 115kV Bus 1 restored at 1716H (Planned Outage). [WEBSMS] | CLUZ
5/21/2022 4:53:39 PM | LRCC-05/21/2022 16:50: GMEC 1 on line at 1642H (Unplanned Outage). [WEBSMS] | CLUZ
5/21/2022 4:50:00 PM | LEYTE ACC-05/21/22 16:40: ORMOC SS, Ormoc-Simangan-Baybay 69 kV L normalized at 1636H, completed pre arranged activity along 69kV Ormoc-Talisayan portion. WEATHER: FAIR | CVIS
5/21/2022 4:28:50 PM | MRCC-05/21/2022 16:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2927MW, PK=1870MW, RR=75MW, NetOpMargin: EVE=2417 Highest Unit O/L: GNPOWER U1&U4@138MW each Derated Plant: Ag1@55MW, Ag2@60MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@25MW, Pul4@143MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@246MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/21/2022 3:29:22 PM | LRCC-05/21/2022 15:25: Ambuklao-Ambuklao HEPP 230kV Tie Line restored at 1524H (Planned Outage). [WEBSMS] | CLUZ
5/21/2022 2:28:47 PM | LRCC-05/21/2022 14:23: Mexico-Quezon 230kV Line restored at 1422H (Planned Outage). [WEBSMS] | CLUZ
5/21/2022 12:58:25 PM | LRCC-05/21/2022 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12473MW, PK=9797MW, RR=385MW, NetOpMargin: PM=2291, EVE=1985 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, San Lorenzo 60 at 260MW, Ilijan at 540MW [WEBSMS] | CLUZ
5/21/2022 12:34:59 PM | LEYTE ACC-05/21/22 12:44:ORMOC CONVERTER STATION SS,350kV Leyte-Luzon,Blocked/Deblocked at 1218H/1228H,on reverse power flow per RTD. WEATHER: FAIR | CVIS
5/21/2022 11:21:40 AM | MRCC-05/21/2022 11:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2957MW, PK=1840MW, RR=74MW, NetOpMargin: PM=1043, EVE=972 Highest Unit O/L: GNPOWER U1&U4@138MW each Derated Plant: Ag1@55MW, Ag2@60MW, Ag4@156MW, Ag5@47MW, Ag6@65MW, Ag7@25MW, Pul4@131MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@246MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/21/2022 10:58:39 AM | LRCC-05/21/2022 10:58: GNPD 2 on line at 1057H, on commissioning. [WEBSMS] | CLUZ
5/21/2022 10:11:43 AM | LRCC-05/21/2022 10:10: GNPD 2 shutdown at 1009H, on commissioning. [WEBSMS] | CLUZ
5/21/2022 10:08:21 AM | LRCC-05/21/2022 10:04: GNPD 2 on line at 0956H, on commissioning. [WEBSMS] | CLUZ
5/21/2022 7:40:22 AM | LEYTE ACC-05/21/22 07:40: ORMOC SS,Ormoc-Simangan-Baybay 69 kV L,Deenergized at 0702H,Pre arranged per PANR No.TLOS V_LEY-2022-05-0005,load=18.6mw,while VOMI,SPMI,Sc Global & Leyeco IV load transferred via Maasin SS at 0715H,(0701-1800H). | CVIS
5/21/2022 7:14:05 AM | LRCC-05/21/2022 07:09: Calaca 1 on line at 0704H (Unplanned Outage). [WEBSMS] | CLUZ
5/21/2022 6:50:35 AM | LRCC-05/21/2022 06:47: Mexico-Quezon 230kV Line de-energized at 0645H (Planned Outage). [WEBSMS] | CLUZ
5/21/2022 6:40:34 AM | PANAY ACC-05/21/22 06:27: PANIT-AN SS, Panit-an 138/69/13.8 kV T3 (30MVA) (7XF03PNT), TIME OUT: 06:23, Pre-arranged Maintenance, load transferred to TR#2; ETR:1800H | CVIS
5/21/2022 6:40:32 AM | LRCC-05/21/2022 06:40: San Jose 750MVA T02 de-energized at 0633H (Planned Outage). [WEBSMS] | CLUZ
5/21/2022 6:37:09 AM | VRCC-05/21/2022 06:30: 138kV Bus 2 Cebu SS de-energized at 0617H. Pre-arranged activity [WEBSMS] | CVIS
5/21/2022 6:27:07 AM | VRCC-05/21/2022 06:21: 138kV Colon-Samboan Line 1 de-energized at 0609H. Pre-arranged activity [WEBSMS] | CVIS
5/21/2022 6:27:05 AM | LRCC-05/21/2022 06:17: Tayabas-Naga 230kV Line 2 de-energized at 0612H. (Planned Outage) [WEBSMS] | CLUZ
5/21/2022 6:05:42 AM | VRCC-05/21/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2778MW, PK=2105MW, RR=59.5MW, NetOpMargin: AM=614, PM=553, EVE=337 Highest Unit O/L: TVI U @169 MW each Derated Plant: EDC = 335 MW, TPC = 82 MW [WEBSMS] | CVIS
5/21/2022 5:40:48 AM | LRCC-05/21/2022 05:33: Weather Update: Southwest Monsoon affecting Northern Luzon. Metro Manila, Ilocos Region, Cordillera Administrative Region, CALABARZON, MIMAROPA, Western Visayas, Zamboanga Peninsula, Batanes, Cagayan, Zambales, and Bataan will have cloudy skies with scattered rainshowers and thunderstorms. The rest of the country will have partly cloudy to cloudy skies with isolated rainshowers or thunderstorms. [WEBSMS] | CLUZ
5/21/2022 4:39:58 AM | MRCC-05/21/2022 04:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2955MW, PK=1750MW, RR=50MW, NetOpMargin: AM=1135, PM=1044, EVE=972 Highest Unit O/L: GNPOWER U1 & U4 @ 138MW each unit. Derated Plant: Ag1@55MW, Ag2@60MW, Ag4@156MW, Ag5@47MW, Ag6@65MW, Ag7@25MW, Pul4@131MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@246MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/21/2022 1:08:48 AM | PANAY ACC-05/21/22 00:40: BUENAVISTA SS, Buenavista-GUIMELCO 69kV Line (CO (5LI1BVI-GUI), TIME IN: 12:35:00, RELAY: NONE, WEATHER: FAIR. Affected by the tripping of 69kV Sta. Barbara-Ingore 69kV TL. | CVIS
5/21/2022 12:58:46 AM | PANAY ACC-05/21/22 00:39: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW), TIME IN: 12:36:00, RELAY: NONE, WEATHER: FAIR. Affected by the tripping of 69kV Sta. Barbara-Ingore 69kV TL. | CVIS
5/21/2022 12:58:44 AM | PANAY ACC-05/21/22 00:35: BUENAVISTA SS, Buenavista-Ingore 69kV Line (5LI1BVI-INR), TIME IN: 12:32:00, RELAY: C-N, 1.4km., WEATHER: FAIR. Affected by the tripping of 69kV Sta. Barbara-Ingore 69kV TL. | CVIS
5/21/2022 12:58:43 AM | PANAY ACC-05/21/22 00:34: STA. BARBARA SS, Sta. Barbara-Ingore 69 kV Line (5LI1SBA-INR), TIME IN: 12:29:00, RELAY: M1: Z2, L3-E, 16.8km.; M2: Z2, C-N,1.4km., WEATHER: FAIR. Affected by the tripping of 69kV Sta. Barbara-Ingore 69kV TL. | CVIS
5/21/2022 12:58:42 AM | PANAY ACC-05/21/22 00:30: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW), TIME OUT: 12:25:00, RELAY: NONE, WEATHER: FAIR. Affected by the tripping of 69kV Sta. Barbara-Ingore 69kV TL. | CVIS
5/21/2022 12:58:40 AM | PANAY ACC-05/21/22 00:29: BUENAVISTA SS, Buenavista-Ingore 69kV Line (5LI1BVI-INR), TIME OUT: 12:25:00, RELAY: C-N, 1.4km., WEATHER: FAIR. Affected by the tripping of 69kV Sta. Barbara-Ingore 69kV TL. | CVIS
5/20/2022 11:34:22 PM | LRCC-05/20/2022 23:34: San Gabriel offline at 2331H. (Maintenance Outage) [WEBSMS] | CLUZ
5/20/2022 10:47:29 PM | LEYTE ACC-05/20/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 2233H/2245H, on normal flow per RTD | CVIS
5/20/2022 8:14:57 PM | LRCC-05/20/2022 20:08: GMEC 1 tripped at 2003H from 264MW load. The system frequency dipped to 59.395Hz. [WEBSMS] | CLUZ
5/20/2022 7:04:37 PM | LRCC-05/20/2022 19:01: Tayabas-Naga 230kV Line 2 restored at 1859H. (Planned Outage) [WEBSMS] | CLUZ
5/20/2022 6:51:01 PM | LRCC-05/20/2022 18:42: Ambuklao S/S - Ambuklao HEPP 230kV Tie Line restored at 1842H (Planned Outage). [WEBSMS] | CLUZ
5/20/2022 6:04:41 PM | VRCC-05/20/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2504MW, PK=2062MW, RR=77MW, NetOpMargin: EVE=365 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 335 MW, TPC = 82 MW [WEBSMS] | CVIS
5/20/2022 6:04:35 PM | LRCC-05/20/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12876MW, PK=9881MW, RR=385MW, NetOpMargin: EVE=2610 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; ILIJAN A @540MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
5/20/2022 5:54:17 PM | LEYTE ACC-05/20/22 17:59: MAASIN SS, 69kV Tunga and Nasaug Feeders normalized at 1739H & 1742H respectively, pre-arranged activity completed. Weather: Fair. | CVIS
5/20/2022 5:20:33 PM | LEYTE ACC-05/20/22 17:29: ORMOC SS, Correction: Ormoc 138/69kV 100MVA TR No. 1 re-energized on parallel operation at 1705H, pre-arranged activity completed. Weather: Fair. | CVIS
5/20/2022 4:51:54 PM | MRCC-05/20/2022 16:40: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2903MW, PK=2020MW, RR=56MW, NetOpMargin: EVE=802 Highest Unit O/L: GNPOWER U1 & U4 @ 138MW each unit. Derated Plant: Ag1@55MW, Ag2@70MW, Ag4@156MW, Ag5@47MW, Ag6@65MW, Ag7@25MW, Pul4@135MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@245.5MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/20/2022 4:41:38 PM | NEGROS ACC: 05/20/2022, 69kV Cadiz-VMC Sub T/L restored at 1631H. Customer owned and maintained line. | CVIS
5/20/2022 4:41:37 PM | NEGROS ACC: 05/20/2022, 69kV Cadiz-VMC Sub T/L restored at 1631H. Customer owned and maintained line. | CVIS
5/20/2022 4:31:32 PM | NEGROS ACC: 05/20/2022, 69kV Cadiz-VMC Sub T/L (12.08MW) auto-tripped at 1622H with indication: Z1 BN, 13.62km. VMCI & NNBP isolated. Customer owned and maintained line. | CVIS
5/20/2022 4:31:31 PM | NEGROS ACC: 05/20/2022, 69kV Cadiz-VMC Sub T/L (12.08MW) auto-tripped at 1622H with indication: Z1 BN, 13.62km. VMCI & NNBP isolated. Customer owned and maintained line. | CVIS
5/20/2022 12:58:57 PM | VRCC-05/20/2022 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2669MW, PK=2242MW, RR=40MW, NetOpMargin: PM=387, EVE=365 Highest Unit O/L: TVI U @ 169 MW Derated Plant: EDC = 335 MW, TPC = 82 MW [WEBSMS] | CVIS
5/20/2022 12:58:55 PM | LRCC-05/20/2022 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13144MW, PK=11019MW, RR=436MW, NetOpMargin: PM=1689, EVE=2610 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; ILIJAN A @540MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
5/20/2022 9:27:59 AM | LEYTE ACC-05/20/22 09:33: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 0909H/0919H on reverse power flow per RTD. Weather: Fair. | CVIS
5/20/2022 8:51:03 AM | LRCC-05/20/2022 08:48: San Jose-Angat 115kV Line 3 looped at Angat side at 0847H (Testing and commissioning after line reconfiguration) [WEBSMS] | CLUZ
5/20/2022 8:51:01 AM | LRCC-05/20/2022 08:46: San Jose-Angat 115kV Line 3 energized at San Jose side at 0836H (Testing and commissioning after line reconfiguration) [WEBSMS] | CLUZ
5/20/2022 8:27:32 AM | PANAY ACC-05/20/22 08:12: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD),Load:40.3MW, TIME IN: 08:07, RELAY: Z2 BN at 1.5kms, WEATHER: FAIR; Sustained fault | CVIS
5/20/2022 8:07:27 AM | PANAY ACC-05/20/22 08:00: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD) Load:40MW, TIME OUT: 07:57:00, RELAY: Z2 BN at 1.5kms, Sustained Fault | CVIS
5/20/2022 8:07:25 AM | PANAY ACC-05/20/22 08:00: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD) Load:40MW, TIME OUT: 07:57:00, RELAY: Z2 BN at 1.5kms, Sustained Fault | CVIS
5/20/2022 6:30:19 AM | LEYTE ACC-05/20/22 06:40: ORMOC SS, Ormoc 150MVA 230/138kV TR No. 1 isolated at 0624H, pre-arranged activity (0601H-1800H). Weather: Fair. | CVIS
5/20/2022 6:30:17 AM | LEYTE ACC-05/20/22 06:38: MAASIN SS, Nasaug - San Isidro 69kV Line de-energized at 0604H, pre-arranged activity (0601H-1800H). Load=6.4MW. Weather: Fair. | CVIS
5/20/2022 6:30:15 AM | LRCC-05/20/2022 06:21: Tayabas-Naga 230kV Line 2 de-energized at 0614H. (Planned Outage) [WEBSMS] | CLUZ
5/20/2022 6:08:54 AM | VRCC-05/20/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2762MW, PK=2192MW, RR=40MW, NetOpMargin: AM=530, PM=387, EVE=365 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 335, TPC at 82 MW [WEBSMS] | CVIS
5/20/2022 5:56:36 AM | LRCC-05/20/2022 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13259MW, PK=10834MW, RR=435MW, NetOpMargin: AM=1990, PM=1987, EVE=2785 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, San Lorenzo 60 at 260MW, San Gabriel at 210MW, Ilijan A at 540MW [WEBSMS] | CLUZ
5/20/2022 5:46:33 AM | PANAY ACC-05/20/22 05:25: STA. BARBARA SS, 69kV 5BS01SBA BUS 1, TIME IN: 05:18:00 | CVIS
5/20/2022 5:43:14 AM | LRCC-05/20/2022 05:34: Weather Update: Southwesterly Surface Windflow affecting the western sections of Northern and Central Luzon. Ilocos Region, Cordillera Administrative Region, Batanes, Cagayan, Zambales, Bataan, Tarlac, and Pampanga will have cloudy skies with scattered rainshowers and thunderstorms. Metro Manila and the rest of the country will be partly cloudy to cloudy skies with isolated rainshowers or thunderstorms. [WEBSMS] | CLUZ
5/20/2022 4:35:51 AM | MRCC-05/20/2022 04:25: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2958MW, PK=2030MW, RR=81MW, NetOpMargin: AM=847, PM=730, EVE=792 Highest Unit O/L: GNPOWER U1&U4@138MW each Derated Plant: Ag1@55MW, Ag2@60MW, Ag4@156MW, Ag5@37MW, Ag6@65MW, Ag7@25MW, Pul4@167MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@245.5MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/20/2022 4:35:41 AM | LRCC-05/20/2022 04:24: Dona Imelda-Quezon 230kV line was energized at 0422H. (Planned Outage) [WEBSMS] | CLUZ
5/20/2022 4:22:36 AM | PANAY ACC-05/20/22 04:12: STA. BARBARA SS, 69kV 5BS01SBA BUS 1, TIME OUT: 04:04:00, Reconnection of TR# 3 69kV loop connection towards gantry, ETR: 06:00:OO, WEATHER: FAIR | CVIS
5/19/2022 11:27:42 PM | LEYTE ACC-05/19/22 23:30:ORMOC CONVERTER STATION SS,350kV HVDC manually blocked/deblocked at 2305H/2315H,on normal power flow per RTD. WEATHER: FAIR | CVIS
5/19/2022 11:07:36 PM | LRCC-05/19/2022 23:04: Dona Imelda-Quezon 230kV line was de-energized at 2303H. (Planned Outage) [WEBSMS] | CLUZ
5/19/2022 9:33:45 PM | LRCC-05/19/2022 21:32: Ilijan GT1-2 synchronized at 2129H. (Dependent on SPEX Malampaya gas supply) [WEBSMS] | CLUZ
5/19/2022 6:47:42 PM | LRCC-05/19/2022 18:40: Tayabas-Naga 230kV Line 2 was restored at 1840H. (Planned Outage) [WEBSMS] | CLUZ
5/19/2022 5:59:34 PM | LEYTE ACC-05/19/22: MAASIN SS, 69kV Maasin-Baybay back to normal configuration at 1750H after pre-arranged activity , WEATHER: FAIR | CVIS
5/19/2022 5:59:33 PM | LEYTE ACC-05/19/22: MAASIN SS, 69kV Maasin-Baybay back to normal configuration at 1750H after pre-arranged activity , WEATHER: FAIR | CVIS
5/19/2022 5:59:32 PM | VRCC-05/19/2022 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2530MW, PK=2077MW, RR=38MW, NetOpMargin: EVE=415 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 365 MW, TPC = 82 MW [WEBSMS] | CVIS
5/19/2022 5:49:29 PM | LEYTE ACC-05/19/22: ORMOC SS, 69kV Ormoc-Simangan-Baybay opened/closed, TIME OUT: 17:38:00, TIME IN: 17:40, load=37.1MW, WEATHER: FAIR | CVIS
5/19/2022 5:49:28 PM | LEYTE ACC-05/19/22: ORMOC SS, 69kV Ormoc-Simangan-Baybay opened/closed, TIME OUT: 17:38:00, TIME IN: 17:40, load=37.1MW, WEATHER: FAIR | CVIS
5/19/2022 5:35:12 PM | LRCC-05/19/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12615MW, PK=9843MW, RR=385MW, NetOpMargin: EVE=2387 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A at 300MW, GMEC 2 at 300MW, San Lorenzo 60 at 260MW, San Gabriel at 210MW [WEBSMS] | CLUZ
5/19/2022 4:51:20 PM | MRCC-05/19/2022 16:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2946MW, PK=1970MW, RR=79MW, NetOpMargin: EVE=897 Highest Unit O/L: GNPOWER U1&U4@138MW each Derated Plant: Ag1@30MW, Ag2@50MW, Ag4@107MW, Ag5@37MW, Ag6@65MW, Ag7@25MW, Pul4@198MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@245.5MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/19/2022 4:06:45 PM | LEYTE ACC-05/19/22: PARANAS SS, 69kV Paranas-Borongan-Quinapondan Line, TIME OUT: 15:55:00, RELAY: z2, phase BCN, 81.61kms, load=11.8MW, WEATHER: FAIR | CVIS
5/19/2022 4:06:43 PM | LEYTE ACC-05/19/22: PARANAS SS, 69kV Paranas-Borongan-Quinapondan Line, TIME OUT: 15:55:00, RELAY: z2, phase BCN, 81.61kms, load=11.8MW, WEATHER: FAIR | CVIS
5/19/2022 4:06:42 PM | LEYTE ACC-05/19/22: PARANAS SS, 69kV Paranas-Borongan-Quinapondan Line, TIME OUT: 15:55:00, RELAY: z2, phase BCN, 81.61kms, load=11.8MW, WEATHER: FAIR | CVIS
5/19/2022 3:00:50 PM | LRCC-05/19/2022 14:51: San Jose-Nagsaag 500kV Line 1 auto-tripped and auto-reclosed at 1430H. [WEBSMS] | CLUZ
5/19/2022 12:57:40 PM | VRCC-05/19/2022 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2756MW, PK=2252MW, RR=38MW, NetOpMargin: PM=466, EVE=415 Highest Unit O/L: TVI U @ 169 MW Derated Plant: EDC = 365 MW, TPC = 82 MW [WEBSMS] | CVIS
5/19/2022 12:43:05 PM | LRCC-05/19/2022 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12860MW, PK=11107MW, RR=445MW, NetOpMargin: PM=1308, EVE=2249 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A at 300MW, GMEC 2 at 300MW, San Lorenzo 60 at 260MW, San Gabriel at 210MW [WEBSMS] | CLUZ
5/19/2022 12:33:14 PM | MRCC-05/19/2022 12:15: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3020MW, PK=2120MW, RR=85MW, NetOpMargin: PM=815, EVE=897 Highest Unit O/L: GNPOWER U1&U4@138MW each Derated Plant: Ag1@55MW, Ag2@50MW, Ag4@156MW, Ag5@37MW, Ag6@65MW, Ag7@25MW, Pul4@152MW, MGPP@78MW, STEAG@204MW, TSI@270MW, SMCPC@270MW, FDC@245.5MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/19/2022 10:46:54 AM | PANAY ACC-05/19/22 10:43: SAN JOSE SS, San Jose-Hamtic 69 kV L (5LI1SJB-HAM), TIME OUT: 10:37:00, TIME IN: 10:42:00, RELAY: Z1 Trip CN, 9.361kms., Ld:2.69MW; WEATHER: FAIR; Momentary line fault. | CVIS
5/19/2022 6:27:09 AM | LEYTE ACC-05/19/22 06:30: MAASIN SS, Maasin - Baybay 69kV Line de-energized at 0602H, pre-arranged activity (0601H-1800H). Load=5.4MW. Weather: Fair. | CVIS
5/19/2022 6:27:07 AM | LRCC-05/19/2022 06:19: Tayabas-Naga 230kV Line 2 de-energized at 0618H. (Planned Outage) [WEBSMS] | CLUZ
5/19/2022 6:12:26 AM | LRCC-05/19/2022 06:10: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13046MW, PK=10908MW, RR=442MW, NetOpMargin: AM=1696, PM=1318, EVE=2355 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, San Lorenzo 60 at 260MW, San Gabriel at 210MW and Ilijan at 300MW [WEBSMS] | CLUZ
5/19/2022 6:02:26 AM | VRCC-05/19/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2802MW, PK=2212MW, RR=38MW, NetOpMargin: AM=552, PM=466, EVE=415 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 365, TPC at 82 MW [WEBSMS] | CVIS
5/19/2022 5:25:06 AM | LRCC-05/19/2022 05:18: Weather Update: Frontal System affecting Extreme Northern Luzon. Metro Manila and the rest of the country will have partly cloudy to cloudy skies with isolated rainshowers or thunderstorms. [WEBSMS] | CLUZ
5/19/2022 5:15:00 AM | LRCC-05/19/2022 05:10: Quezon-Dona Imelda 230kV line was restored at 0506H. (Planned Outage) [WEBSMS] | CLUZ
5/19/2022 4:38:03 AM | MRCC-05/19/2022 04:31: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3012MW, PK=2010MW, RR=57MW, NetOpMargin: AM=921, PM=816, EVE=898 Highest Unit O/L: GNPOWER U1 & U4 @ 138MW each unit. Derated Plant: Ag1@55MW, Ag2@90MW, Ag4@156MW, Ag5@47MW, Ag6@65MW, Ag7@25MW, Pul4@202MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@246MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/19/2022 12:42:15 AM | LEYTE ACC-05/19/22 00:43:GCGI POWER PLANT,TGPP unit 1 cut-in at 2243H,Capability increased back to 113.5MW, WEATHER: FAIR | CVIS
5/18/2022 11:36:03 PM | LRCC-05/18/2022 23:35: Ilijan GT 1-2 offline at 2333H. (Due to SPEX Malampaya gas supply restriction) [WEBSMS] | CLUZ
5/18/2022 11:16:02 PM | LEYTE ACC-05/18/22 23:25:ORMOC CONVERTER STATION SS, 350kV Leyte Luzon,Blocked/Deblocked at 2259H/2309H, on normal power flow per RTD. WEATHER: FAIR | CVIS
5/18/2022 11:16:00 PM | LRCC-05/18/2022 23:12: Quezon-Dona Imelda 230kV line was de-energized at 2312H. (Planned Outage) [WEBSMS] | CLUZ
5/18/2022 11:02:40 PM | LRCC-05/18/2022 23:01: Ilijan GT 2-2 offline at 2259H. (Due to SPEX Malampaya gas supply restriction) [WEBSMS] | CLUZ
5/18/2022 10:52:30 PM | LRCC-05/18/2022 22:49: Ilijan ST-2 offline at 2246H. (Due to SPEX Malampaya gas supply restriction) [WEBSMS] | CLUZ
5/18/2022 6:44:14 PM | LRCC-05/18/2022 18:34: Tayabas-Naga 230kV Line 2 restored at 1833H. (Planned Outage) [WEBSMS] | CLUZ
5/18/2022 6:07:16 PM | VRCC-05/18/2022 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2521MW, PK=2077MW, RR=40MW, NetOpMargin: EVE=404 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 355 MW, TPC = 82 MW [WEBSMS] | CVIS
5/18/2022 5:37:47 PM | LRCC-05/18/2022 17:27: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13376MW, PK=9928MW, RR=410MW, NetOpMargin: EVE=3038 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sta. Rita 40 at 260MW, San Lorenzo 60 at 260MW, San Gabriel at 210MW [WEBSMS] | CLUZ
5/18/2022 4:56:43 PM | LRCC-05/18/2022 16:52: Malaya 2 shutdown at 1642H. (Planned Outage) [WEBSMS] | CLUZ
5/18/2022 1:38:48 PM | LEYTE ACC-05/18/22 13:44:GCGI POWER PLANT,TGPP unit 1 cut-out at 1328H to effect Steam leak repair ,ETC 8hrs, WEATHER: FAIR | CVIS
5/18/2022 1:15:20 PM | VRCC-05/18/2022 13:08: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2727MW, PK=2252MW, RR=40MW, NetOpMargin: PM=435, EVE=404 Highest Unit O/L: TVI U @ 169 MW Derated Plant: EDC = 355 MW, TPC = 82 MW [WEBSMS] | CVIS
5/18/2022 12:51:48 PM | NEGROS ACC: 05/18/2022, 69kV Panaogao -Silay Line Section(11.0MW) de-energized at 1222H to facilitate load shifting from Cadiz Substation back to Bacolod Substation.Restored at 1231H. Customer owned and maintained line. | CVIS
5/18/2022 12:08:42 PM | PANAY ACC-05/18/22 11:58: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 11:57:00, WEATHER: FAIR; Ld: 6.9MW; As per emergency shutdown request by AKELCO. | CVIS
5/18/2022 12:08:41 PM | PANAY ACC-05/18/22 11:58: NABAS SS, Caticlan-Malay 69kV L (5LI1CTC-MLA), TIME OUT: 11:57:00, WEATHER: FAIR; Ld: 15.5MW; As per emergency shutdown request by AKELCO. | CVIS
5/18/2022 11:40:40 AM | LEYTE ACC-05/18/22 11:47: ORMOC CONVERTER STATION SS,350kV HVDC Leyte-Luzon,Blocked/Deblocked at 1119H/1130H on reverse power flow per RTD.WEATHER: FAIR | CVIS
5/18/2022 10:50:31 AM | NEGROS ACC: 05/18/2022, 69kV Amlan-San Carlos Sub T/L (24.0 MW) auto-tripped at 1027H with indication Z2 BN DELAY,27.03km.SACASUN, MONTESOL and CABI isolated.Restored at 1039H. | CVIS
5/18/2022 10:40:37 AM | MRCC-05/18/2022 10:33: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3068MW, PK=2030MW, RR=59MW, NetOpMargin: PM=957, EVE=1060 Highest Unit O/L: GNPOWER U1 & U4 @ 138MW each unit Derated Plant: Ag1@55MW, Ag2@90MW, Ag4@156MW, Ag5@47MW, Ag6@65MW, Ag7@26MW, Pul4@204MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@245.5MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/18/2022 6:36:11 AM | NEGROS ACC: 05/18/2022, 69kV Talisay-Silay Line Section(6.0MW) de-energized at 0616H as per customers(CENECO) request to conduct preventive maintenance along 69KV Talisay-Panaogao line section. FFHC(7.0MW), HPCo and Silay Solar(1.0MW) isolated. Customer owned and maintained line. | CVIS
5/18/2022 6:36:09 AM | LRCC-05/18/2022 06:26: Tayabas-Naga 230kV Line 2 de-energized at 0622H. (Planned Outage) [WEBSMS] | CLUZ
5/18/2022 6:09:51 AM | VRCC-05/18/2022 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2733MW, PK=2248MW, RR=59MW, NetOpMargin: AM=425, PM=435, EVE=404 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 355, TPC at 82 MW [WEBSMS] | CVIS
5/18/2022 6:09:49 AM | VRCC-05/18/2022 06:02: 69KV Compostela- Consolacion fdr. tripped at 0510H auto-reclosed. indication overcurrent AN load 9.0MW . [WEBSMS] | CVIS
5/18/2022 5:57:27 AM | LRCC-05/18/2022 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13670MW, PK=10981MW, RR=441MW, NetOpMargin: AM=2248, PM=1868, EVE=2403 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, Ilijan A/B at 851MW, San Lorenzo 60 at 260MW, Sta Rita 40 at 260MW, San Gabriel at 210MW [WEBSMS] | CLUZ
5/18/2022 5:30:39 AM | LRCC-05/18/2022 05:30: Weather Update: Frontal System affecting Extreme Northern Luzon. Metro Manila and the rest of the country will have partly cloudy to cloudy skies with isolated rainshowers or thunderstorms. [WEBSMS] | CLUZ
5/18/2022 4:47:06 AM | MRCC-05/18/2022 04:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3057MW, PK=1950MW, RR=78MW, NetOpMargin: AM=1029, PM=952, EVE=1049 Highest Unit O/L: GNPOWER U1&U4@138MW each Derated Plant: Ag1@55MW, Ag2@90MW, Ag4@156MW, Ag5@47MW, Ag6@65MW, Ag7@26MW, Pul4@152MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@245.5MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/18/2022 3:45:49 AM | LRCC-05/18/2022 03:36: Sual Unit 2 synchronized at 0328H. (Maintenance Outage) [WEBSMS] | CLUZ
5/17/2022 10:31:05 PM | LEYTE ACC-05/17/22 22:34: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2157H/2207H on normal power flow per RTD. Weather: Fair. | CVIS
5/17/2022 10:07:37 PM | LEYTE ACC-05/17/22 22:08: MARSHALLING SS,Mahanagdong B Emergency cut-out/cut-in at 2112H/2155H, replacement of Generator Circuit breaker, WEATHER: FAIR | CVIS
5/17/2022 6:35:04 PM | LRCC-05/17/2022 18:32: Tayabas-Naga 230kV Line 2 restored at 1832H. (Planned Outage) [WEBSMS] | CLUZ
5/17/2022 6:01:36 PM | VRCC-05/17/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2518MW, PK=2145MW, RR=39MW, NetOpMargin: EVE=334 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 355, TPC at 82 MW [WEBSMS] | CVIS
5/17/2022 5:38:05 PM | LRCC-05/17/2022 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12778MW, PK=10008MW, RR=405MW, NetOpMargin: EVE=2365 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sta. Rita 40 at 260MW, San Lorenzo 60 at 260MW, San Gabriel at 250MW [WEBSMS] | CLUZ
5/17/2022 1:05:47 PM | VRCC-05/17/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2746MW, PK=2278MW, RR=40MW, NetOpMargin: PM=428, EVE=334 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 355, TPC at 82 MW [WEBSMS] | CVIS
5/17/2022 12:31:03 PM | LRCC-05/17/2022 12:30: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13134MW, PK=11094MW, RR=464MW, NetOpMargin: PM=1576, EVE=2077 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, San Gabriel at 270MW, Sta. Rita 40 at 260MW, San Lorenzo 60 at 260MW [WEBSMS] | CLUZ
5/17/2022 11:37:21 AM | MRCC-05/17/2022 11:24: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3084MW, PK=2030MW, RR=81MW, NetOpMargin: PM=973, EVE=1055 Highest Unit O/L: GNPOWER U3 & U4@138MW each Derated Plant: Ag1@30MW, Ag2@55MW, Ag4@107MW, Ag5@37MW, Ag6@65MW, Ag7@21MW, Pul4@115MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@245.5MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/17/2022 10:20:40 AM | VRCC-05/17/2022 10:16: Quiot SS 69 kV Ermita Feeder (CO) re-energized at 1009H [WEBSMS] | CVIS
5/17/2022 10:20:38 AM | LEYTE ACC-05/17/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 0947H/0957H, on reverse flow per RTD | CVIS
5/17/2022 10:20:37 AM | LEYTE ACC-05/17/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 0947H/0957H, on reverse flow per RTD | CVIS
5/17/2022 10:20:35 AM | VRCC-05/17/2022 10:07: Quiot SS 69 kV Ermita Feeder (CO) auto-tripped at 1000H with 96 MW load [WEBSMS] | CVIS
5/17/2022 6:21:09 AM | LRCC-05/17/2022 06:13: Tayabas-Naga 230kV Line 2 de-energized at 0613H. (Planned Outage) [WEBSMS] | CLUZ
5/17/2022 6:11:00 AM | VRCC-05/17/2022 06:10: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2808MW, PK=2256MW, RR=40MW, NetOpMargin: AM=512, PM=479, EVE=339 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 355 MW, TPC = 82 MW [WEBSMS] | CVIS
5/17/2022 5:47:26 AM | LRCC-05/17/2022 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13227MW, PK=10950MW, RR=445MW, NetOpMargin: AM=1832, PM=1412, EVE=2154 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; ILIJAN A / B @851MW; SAN GABRIEL @270MW [WEBSMS] | CLUZ
5/17/2022 4:40:16 AM | MRCC-05/17/2022 04:31: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3073MW, PK=2020MW, RR=57MW, NetOpMargin: AM=973, PM=968, EVE=1050 Highest Unit O/L: GNPOWER U1 & U4 @ 138MW each unit. Derated Plant: Ag1@55MW, Ag2@100MW, Ag4@156MW, Ag5@47MW, Ag6@65MW, Ag7@26MW, Pul4@200MW, MGPP@80MW, STEAG@200MW, FMP@246MW, GNPK@276MW, DCP@270MW, and SMCPC@270MW. [WEBSMS] | CMIN
5/16/2022 11:45:06 PM | LRCC-05/16/2022 23:36: Sual Unit 2 offline at 2327h (Maintenance Outage) [WEBSMS] | CLUZ
5/16/2022 9:40:39 PM | LEYTE ACC-05/16/22 21:42:ORMOC CONVERTER STATION SS,350kV HVDC blocked/deblocked at 2104H/2115H,on normal power flow per RTD. WEATHER: FAIR | CVIS
5/16/2022 6:09:23 PM | VRCC-05/16/2022 18:05: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2539MW, PK=2095MW, RR=40MW, NetOpMargin: EVE=404 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 355, TPC at 82 MW [WEBSMS] | CVIS
5/16/2022 5:59:18 PM | LRCC-05/16/2022 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13199MW, PK=9841MW, RR=418MW, NetOpMargin: EVE=2940 Highest Unit O/L: GNPD Unit 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sta. Rita 40 at 250MW, San Lorenzo 60 at 260MW, San Gabriel at 270MW, Calaca 1 at 50MW [WEBSMS] | CLUZ
5/16/2022 2:14:03 PM | LEYTE ACC-05/16/22 14:21:ORMOC CONVERTER STATION SS,350kV HVDC blocked/deblocked at 1352H/1404H,on reverse power flow per RTD,WEATHER: FAIR | CVIS
5/16/2022 12:53:36 PM | LRCC-05/16/2022 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13486MW, PK=11407MW, RR=459MW, NetOpMargin: PM=1620, EVE=2991 Highest Unit O/L: GNPD Unit 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sta. Rita 40 at 250MW, San Lorenzo 60 at 260MW, San Gabriel at 270MW [WEBSMS] | CLUZ
5/16/2022 11:09:11 AM | MRCC-05/16/2022 11:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3142MW, PK=2050MW, RR=59MW, NetOpMargin: PM=1010, EVE=1057 Highest Unit O/L: GNPOWER U1 & U4 @ 138MW each unit> Derated Plant: Ag1@55MW, Ag2@111MW, Ag4@156MW, Ag5@47MW, Ag6@70MW, Ag7@26MW, Pul4@198MW, MGPP@80MW, STEAG@200MW, FMP@246MW, GNPK@276MW, DCP@270MW, and SMCPC@270MW. [WEBSMS] | CMIN
5/16/2022 10:52:53 AM | LRCC-05/16/2022 10:51: Calaca Unit 1 tripped at 1045H from 235MW load. The Luzon system frequency dipped to 59.505Hz. [WEBSMS] | CLUZ
5/16/2022 9:01:25 AM | MRCC-05/16/2022 05:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2948MW, PK=2010MW, RR=57MW, NetOpMargin: AM=881, PM=983, EVE=1033 Highest Unit O/L: GNPKU1&U4@138MW each; Derated Plant: Ag1@55MW, Ag2@111MW, Ag4@156MW, Ag5@47MW, Ag6@70MW, Ag7@26MW, Pul4@198MW, MGPP@80MW, STEAG@200MW, FMP@246MW, GNPK@276MW, and SMCPC@135MW. [WEBSMS] | CMIN
5/16/2022 9:01:13 AM | VRCC-05/16/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2808MW, PK=2226MW, RR=40MW, NetOpMargin: AM=542, PM=540, EVE=362 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 355, TPC at 82 MW [WEBSMS] | CVIS
5/16/2022 9:01:09 AM | LRCC-05/16/2022 07:18: Taytay-Malaya 230kV line 1 auto-tripped at 0707H, auto-reclosing was successful on Taytay side. The line was looped at Malaya side at 0713H. (Unplanned Outage) [WEBSMS] | CLUZ
5/16/2022 9:01:08 AM | LRCC-05/16/2022 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13700MW, PK=10179MW, RR=435MW, NetOpMargin: AM=3085, PM=2559, EVE=3145 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sta. Rita 40 at 250MW, San Lorenzo 60 at 260MW, San Gabriel at 270MW, Calaca 1 at 180MW [WEBSMS] | CLUZ
5/15/2022 9:31:52 PM | LEYTE ACC-05/15/22 21:40: MAASIN SS, 69kV Hilongos Feeder tripped/restored at 2122H/2130H, ind.: Phase-A & 11.2kms. Load=7.3MW. Weather: Cloudy. | CVIS
5/15/2022 9:08:23 PM | PANAY ACC-05/15/22 20:55: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME IN: 08:51:00 | CVIS
5/15/2022 8:44:58 PM | PANAY ACC-05/15/22 20:33: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 08:30:00, RELAY: Z1 BN 54.49KMS, Load: 27.1mw, Sustained fault, WEATHER: FAIR | CVIS
5/15/2022 6:11:45 PM | VRCC-05/15/2022 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2531MW, PK=1920MW, RR=40MW, NetOpMargin: EVE=571 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 362 MW, TPC = 82 MW [WEBSMS] | CVIS
5/15/2022 5:47:30 PM | LRCC-05/15/2022 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13257MW, PK=9984MW, RR=392MW, NetOpMargin: EVE=2881 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW; ILIJAN A / B at 851MW; STA RITA 40 at 250MW; SAN GABRIEL at 270MW [WEBSMS] | CLUZ
5/15/2022 5:02:47 PM | MRCC-05/15/2022 16:48: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2895MW, PK=1720MW, RR=59MW, NetOpMargin: EVE=1116 Highest Unit O/L: GNPKU1&U4@138MW each; Derated Plant: Ag1@55MW, Ag2@108MW, Ag4@156MW, Ag5@47MW, Ag6@70MW, Ag7@26MW, Pul4@200MW, MGPP@80MW, STEAG@200MW, FMP@246MW, GNPK@276MW, and SMCPC@135MW. [WEBSMS] | CMIN
5/15/2022 1:31:37 PM | LRCC-05/15/2022 13:26: San Jose-Quezon 230kV line 2 auto-tripped/auto-reclosed at 1321H. (Unplanned Outage) [WEBSMS] | CLUZ
5/15/2022 1:17:50 PM | VRCC-05/15/2022 13:16: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2770MW, PK=1819MW, RR=60MW, NetOpMargin: PM=891, EVE=571 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 362 MW, TPC = 82 MW [WEBSMS] | CVIS
5/15/2022 12:45:17 PM | LRCC-05/15/2022 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13884MW, PK=9598MW, RR=366MW, NetOpMargin: PM=3920, EVE=2881 Highest Unit O/L: GNPD Unit 1 at 668MW Derated Plant: GMEC 2 at 300MW; ILIJAN A / B at 851MW; STA RITA 40 at 250MW; SAN GABRIEL at 270MW [WEBSMS] | CLUZ
5/15/2022 12:18:16 PM | LRCC-05/15/2022 12:09: Bolo-Balingueo 230kV line 1 was restored at 1207H. (Unplanned Outage) [WEBSMS] | CLUZ
5/15/2022 12:07:46 PM | LRCC-05/15/2022 11:58: Bolo-Balingueo 230kV line 1 auto-tripped at 1153H. (Unplanned Outage) [WEBSMS] | CLUZ
5/15/2022 11:57:06 AM | MRCC-05/15/2022 11:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2939MW, PK=1620MW, RR=50MW, NetOpMargin: PM=1269, EVE=1116 Highest Unit O/L: GNPKU3&U4@138MW each; Derated Plant: Ag1@55MW, Ag2@111MW, Ag4@156MW, Ag5@47MW, Ag6@70MW, Ag7@26MW, Pul4@188MW, MGPP@80MW, STEAG@200MW, FMP@246MW, GNPK@276MW, and SMCPC@135MW. [WEBSMS] | CMIN
5/15/2022 11:37:50 AM | VRCC-05/15/2022 11:32: 69KV Mandaue GIS Fdr 5. tripped at 1059H, restored at 1154H load 31MW, customer owned line (Veco). Indication. NEF 1 LOW. [WEBSMS] | CVIS
5/15/2022 6:04:43 AM | VRCC-05/15/2022 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2805MW, PK=1789MW, RR=40MW, NetOpMargin: AM=976, PM=891, EVE=571 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 362 MW, TPC = 82 MW [WEBSMS] | CVIS
5/15/2022 5:41:12 AM | LRCC-05/15/2022 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13893MW, PK=9194MW, RR=350MW, NetOpMargin: AM=4349, PM=3810, EVE=3016 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; ILIJAN A / B @851MW; STA RITA 40 @250MW; SAN GABRIEL @270MW [WEBSMS] | CLUZ
5/15/2022 4:57:26 AM | MRCC-05/15/2022 04:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2939MW, PK=1580MW, RR=63MW, NetOpMargin: AM=1294, PM=1254, EVE=1106 Highest Unit O/L: GNPOWER U3 & U4@138MW each Derated Plant: Ag1@30MW, Ag2@75MW, Ag4@108MW, Ag5@37MW, Ag6@51MW, Ag7@21MW, Pul4@85MW, MGPP@78MW, STEAG@200MW, TSI@270MW, SMCPC@270MW, FDC@245.5MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/14/2022 6:06:14 PM | VRCC-05/14/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: CAP=2532MW, PK=2060MW, RR=40MW, NetOpMargin: EVE=432 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 360, TPC at 82 MW [WEBSMS] | CVIS
5/14/2022 5:56:02 PM | LRCC-05/14/2022 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13163MW, PK=10560MW, RR=402MW, NetOpMargin: EVE=2201 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; ILIJAN A / B @851MW; STA RITA 40 @240MW; SAN GABRIEL @270MW [WEBSMS] | CLUZ
5/14/2022 5:56:01 PM | LRCC-05/14/2022 17:51: Nagsaag-Casecnan 230kV L1 auto tripped and reclosed at Nagsaag at 1645H (Unplanned Outage). [WEBSMS] | CLUZ
5/14/2022 5:18:08 PM | LRCC-05/14/2022 17:10: Cabanatuan-Pantabangan 230kV Line auto tripped and auto reclosed at 1630H (Unplanned Outage). [WEBSMS] | CLUZ
5/14/2022 4:49:51 PM | MRCC-05/14/2022 16:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2932MW, PK=1840MW, RR=74MW, NetOpMargin: EVE=1018 Highest Unit O/L: GNPOWER U3&U4@138MW each Derated Plant: [WEBSMS] | CMIN
5/14/2022 1:09:28 PM | VRCC-05/14/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2746MW, PK=2059MW, RR=40MW, NetOpMargin: PM=647, EVE=432 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 360, TPC at 82 MW [WEBSMS] | CVIS
5/14/2022 12:55:11 PM | LRCC-05/14/2022 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13540MW, PK=11025MW, RR=417MW, NetOpMargin: PM=2098, EVE=2604 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; ILIJAN A / B @851MW; STA RITA 40 @240MW; SAN GABRIEL @270MW [WEBSMS] | CLUZ
5/14/2022 11:42:31 AM | MRCC-05/14/2022 11:29: GRID UPDATE AS OF 1:00 PM System Condition: CAP=3005MW, PK=1820MW, RR=73MW, NetOpMargin: PM=1112, EVE=1018 Highest Unit O/L: GNPOWER U3&U4@138MW each Derated Plant: Ag1@30MW, Ag2@75MW, Ag4@107MW, Ag5@37MW, Ag6@75MW, Ag7@21MW, Pul4@116MW, MGPP@78MW, STEAG@200MW, TSI@135MW, SMCPC@270MW, FDC@245.5MW, MCC@150MW, GNPOWER@276MW. [WEBSMS] | CMIN
5/14/2022 7:43:00 AM | PANAY ACC-05/14/22 07:39: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME OUT: 07:26:00, TIME IN: 07:31:00, RELAY: L 3 E 9.1kms / TRIP C N 9.07kms, Load: 37.6mw, Momentary line fault, WEATHER: FAIR | CVIS
5/14/2022 6:04:33 AM | VRCC-05/14/2022 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2808MW, PK=2013MW, RR=40MW, NetOpMargin: AM=755, PM=656, EVE=439 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 360 MW, TPC = 82 MW [WEBSMS] | CVIS
5/14/2022 5:54:29 AM | LRCC-05/14/2022 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13635MW, PK=10166MW, RR=395MW, NetOpMargin: AM=3074, PM=2613, EVE=2579 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; ILIJAN A / B @851MW; STA RITA 40 @240MW; SAN GABRIEL @270MW [WEBSMS] | CLUZ
5/14/2022 4:43:42 AM | MRCC-05/14/2022 04:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3001MW, PK=1815MW, RR=58MW, NetOpMargin: AM=1113, PM=1113, EVE=1018 Highest Unit O/L: GNPOWER U3 & U4 @ 138MW each unit. Derated Plant: Ag1@55MW, Ag2@108MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@202MW, MGPP@78MW, STEAG@200MW, FMP@246MW, GNPK@276MW, and DCP@135MW [WEBSMS] | CMIN
5/13/2022 9:29:04 PM | PANAY ACC-05/13/22 21:25: PANIT-AN SS, Sigma-Dao 69 kV L (CO) (5LI1SGM-DAX), TIME IN: 21:24:00, RELAY: Z2, CN, 16.24kms., WEATHER: FAIR; Restored as per request by CAPELCO. | CVIS
5/13/2022 8:27:22 PM | LEYTE ACC-05/13/22 20:29:ORMOC CONVERTER STATION SS,350kV HVDC Leyte-Luzon,Blocked/Deblocked at 2004H/2014H,on normal power flow per RTD,WEATHER: FAIR | CVIS
5/13/2022 8:03:33 PM | PANAY ACC-05/13/22 19:43: PANIT-AN SS, Sigma-Dao 69 kV L (CO) (5LI1SGM-DAX), TIME OUT: 19:36:00, RELAY: Z2, CN, 16.24kms., Ld: 8.74MW; WEATHER: FAIR; Customer owned and maintained line. | CVIS
5/13/2022 8:03:31 PM | PANAY ACC-05/13/22 19:43: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN), TIME OUT: 19:36:00, TIME IN: 19:43:00, Load: 4MW, RELAY: Z2, CN, 16.24kms., WEATHER: FAIR; Affected by a line fault along Sigma-Dao 69kV TL (CO). | CVIS
5/13/2022 8:03:30 PM | PANAY ACC-05/13/22 19:43: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN), TIME OUT: 19:36:00, TIME IN: 19:43:00, Load: 4MW, RELAY: Z2, CN, 16.24kms., WEATHER: FAIR; Affected by a line fault along Sigma-Dao 69kV TL (CO). | CVIS
5/13/2022 2:29:46 PM | LRCC-05/13/2022 14:23: Dasmarinas-TMC II (Ternate) 115kV Line restored at Dasmarinas side at 1421H (Planned Outage) [WEBSMS] | CLUZ
5/13/2022 1:04:42 PM | VRCC-05/13/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2754MW, PK=2272MW, RR=39MW, NetOpMargin: PM=443, EVE=404 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 360, TPC at 82 MW [WEBSMS] | CVIS
5/13/2022 12:53:54 PM | LRCC-05/13/2022 12:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13689MW, PK=11915MW, RR=466MW, NetOpMargin: PM=1308, EVE=2026 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Sta Rita 40 @240MW, San Gabriel @300MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/13/2022 11:21:26 AM | MRCC-05/13/2022 11:13: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2993MW, PK=2000MW, RR=59MW, NetOpMargin: PM=913, EVE=964 Highest Unit O/L: GNPOWER U3 & U4 @ 138MW each unit. Derated Plant: Ag1@55MW, Ag2@108MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@200MW, MGPP@78MW, STEAG@200MW, FMP@246MW, GNPK@276MW, and DCP@135MW. [WEBSMS] | CMIN
5/13/2022 10:33:03 AM | LEYTE ACC-05/13/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1012H/1022H, on reverse flow per RTD | CVIS
5/13/2022 10:33:01 AM | LEYTE ACC-05/13/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1012H/1022H, on reverse flow per RTD | CVIS
5/13/2022 9:08:09 AM | LRCC-05/13/2022 09:02: Dasmarinas-TMC II (Ternate_ 115kV Line de-energized at Dasmarinas side at 0852H (Planned Outage). [WEBSMS] | CLUZ
5/13/2022 8:31:45 AM | PANAY ACC-05/13/22 07:25: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME IN: 07:23:00, Affected by the tripping AKELCOs feeder 10 | CVIS
5/13/2022 7:56:20 AM | PANAY ACC-05/13/22 07:08: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME OUT: 07:05, Load:5MW; Affected by the tripping AKELCOs feeder 10 | CVIS
5/13/2022 6:16:44 AM | VRCC-05/13/2022 06:10: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2808MW, PK=2283MW, RR=59MW, NetOpMargin: AM=466, PM=443, EVE=404 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 360, TPC at 82 MW [WEBSMS] | CVIS
5/13/2022 6:16:41 AM | LRCC-05/13/2022 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13850MW, PK=11466MW, RR=435MW, NetOpMargin: AM=1949, PM=1262, EVE=2094 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Sta Rita 40 @220MW, San Gabriel @300MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/13/2022 5:08:41 AM | MRCC-05/13/2022 04:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2997MW, PK=1910MW, RR=57MW, NetOpMargin: AM=1030, PM=944, EVE=993 Highest Unit O/L: GNPKU3&U4@138MW each; Derated Plant: Ag1@55MW, Ag2@108MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@200MW, MGPP@78MW, STEAG@200MW, FMP@246MW, GNPK@276MW, and DCP@135MW. [WEBSMS] | CMIN
5/13/2022 1:22:31 AM | LRCC-05/13/2022 01:12: SLPGC 2 emergency shutdown at 0106H (Unplanned Outage) [WEBSMS] | CLUZ
5/12/2022 9:49:25 PM | LEYTE ACC-05/12/22 21:56:ORMOC CONVERTER STATION SS,350kV Leyte Luzon,Blocked/Deblocked at 2122H/2139H,on normal power flow per Visayas requirement,WEATHER: FAIR | CVIS
5/12/2022 9:26:50 PM | LRCC-05/12/2022 21:20: Hermosa-San Jose 230kV Line tripped at 2051H & restored at 2108H (Unplanned Outage) [WEBSMS] | CLUZ
5/12/2022 6:09:13 PM | VRCC-05/12/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2546MW, PK=2103MW, RR=40MW, NetOpMargin: EVE=403 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 360, TPC at 82 MW [WEBSMS] | CVIS
5/12/2022 5:52:49 PM | LRCC-05/12/2022 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13609MW, PK=11056MW, RR=416MW, NetOpMargin: EVE=1668 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLPGC 2 @75MW; ILIJAN A / B @851MW; STA RITA 40 @220MW; SAN GABRIEL @300MW [WEBSMS] | CLUZ
5/12/2022 5:27:07 PM | MRCC-05/12/2022 17:15: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2932MW, PK=1880MW, RR=56MW, NetOpMargin: EVE=996 Highest Unit O/L: GNPKU3&U4@138MW each; Derated Plant: Ag1@55MW, Ag2@103MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@193MW, MGPP@76MW, STEAG@200MW, FMP@246MW, GNPK@276MW, and DCP@135MW. [WEBSMS] | CMIN
5/12/2022 4:52:17 PM | LRCC-05/12/2022 16:52: Hermosa - Malolos 230kV Line restored at 1646H (Unplanned Outage). [WEBSMS] | CLUZ
5/12/2022 4:52:15 PM | LRCC-05/12/2022 16:51: Hermosa - Malolos 230kV Line tripped at 1638H (Unplanned Outage). [WEBSMS] | CLUZ
5/12/2022 4:04:44 PM | LRCC-05/12/2022 15:56: System Advisory: Luzon Grid Highest Peak Load for this year 2022 at 12,113MW occurred at 1428H today, Thursday, May 12, 2022. Previous highest peak is 11,863MW (May 11, 2022, Wednesday at 1436H). [WEBSMS] | CLUZ
5/12/2022 1:03:48 PM | VRCC-05/12/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2788MW, PK=2160MW, RR=40MW, NetOpMargin: PM=588, EVE=403 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 360, TPC at 82 MW [WEBSMS] | CVIS
5/12/2022 1:03:46 PM | LRCC-05/12/2022 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13993MW, PK=11790MW, RR=465MW, NetOpMargin: PM=1778, EVE=2250 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLPGC 2 @75MW; ILIJAN A / B @851MW; STA RITA 40 @220MW; SAN GABRIEL @300MW [WEBSMS] | CLUZ
5/12/2022 12:07:51 PM | LEYTE ACC-05/12/22 12:06:ORMOC CONVERTER STATION SS, 350kV HVDC Leyte-Luzon,Blocked/Deblocked at 1137H/1147H, on reverse power flow per RTD,WEATHER: FAIR | CVIS
5/12/2022 11:53:51 AM | MRCC-05/12/2022 11:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2995MW, PK=2020MW, RR=59MW, NetOpMargin: PM=916, EVE=996 Highest Unit O/L: GNPKU3&U4@138MW each; Derated Plant: Ag1@55MW, Ag2@103MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@204MW, MGPP@76MW, STEAG@200MW, FMP@246MW, GNPK@276MW, and DCP@135MW. [WEBSMS] | CMIN
5/12/2022 10:36:15 AM | LRCC-05/12/2022 10:25: GNPD 2 online at 1024H (Commissioning Test). [WEBSMS] | CLUZ
5/12/2022 7:29:15 AM | NEGROS ACC: 05/12/2022, 69kV Dauin-Siaton Line section restored at 0723H. | CVIS
5/12/2022 7:29:14 AM | NEGROS ACC: 05/12/2022, 69kV Dauin-Siaton Line section restored at 0723H. | CVIS
5/12/2022 7:17:27 AM | NEGROS ACC: 05/12/2022, 69kV Dauin-Siaton Line section (3.11MW) auto-tripped at 0649H with indication Z3 DEF Start, BN, 58.08km. | CVIS
5/12/2022 7:17:25 AM | NEGROS ACC: 05/12/2022, 69kV Dauin-Siaton Line section (3.11MW) auto-tripped at 0649H with indication Z3 DEF Start, BN, 58.08km. | CVIS
5/12/2022 6:03:38 AM | VRCC-05/12/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2849MW, PK=2136MW, RR=40MW, NetOpMargin: AM=673, PM=588, EVE=403 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 360MW, TPC at 82MW [WEBSMS] | CVIS
5/12/2022 5:43:10 AM | LRCC-05/12/2022 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14079MW, PK=11303MW, RR=434MW, NetOpMargin: AM=2342, PM=1603, EVE=2281 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLPGC 2 @75MW; ILIJAN A / B @851MW; STA RITA 40 @220MW; SAN GABRIEL @340MW [WEBSMS] | CLUZ
5/12/2022 5:29:05 AM | LRCC-05/12/2022 05:19: Weather Update: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 490 km East of Davao City (6.5 N, 130.2 E). It is embedded along the Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CLUZ
5/12/2022 4:18:49 AM | MRCC-05/12/2022 04:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3124MW, PK=1960MW, RR=57MW, NetOpMargin: AM=1085, PM=1029, EVE=1111 Highest Unit O/L: GNPOWER U3 & U4 @ 138MW each unit. Derated Plant: Ag1@55MW, Ag2@103MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@202MW, MGPP@78MW, STEAG@200MW, FMP@246MW, and GNPK@276MW. [WEBSMS] | CMIN
5/11/2022 11:18:46 PM | LEYTE ACC-05/11/22: PARANAS SS, 69kV Paranas-Borongan-Quinapondan Line, TIME OUT: 23:11:00, TIME IN: 23:12:00, RELAY: phase AN, 156.85kms, load=11.9MW, WEATHER: FAIR | CVIS
5/11/2022 11:18:44 PM | LEYTE ACC-05/11/22: PARANAS SS, 69kV Paranas-Borongan-Quinapondan Line, TIME OUT: 23:11:00, TIME IN: 23:12:00, RELAY: phase AN, 156.85kms, load=11.9MW, WEATHER: FAIR | CVIS
5/11/2022 9:18:51 PM | LEYTE ACC-05/11/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 2005H/2016H, on normal flow per RTD | CVIS
5/11/2022 6:05:42 PM | VRCC-05/11/2022 18:05: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2529MW, PK=2227MW, RR=36MW, NetOpMargin: EVE=352 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 352, TPC at 82 MW [WEBSMS] | CVIS
5/11/2022 6:00:39 PM | LRCC-05/11/2022 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13480MW, PK=11028MW, RR=414MW, NetOpMargin: EVE=2038 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLPGC 2 @75MW; ILIJAN A / B @851MW; STA RITA 40 @220MW; SAN GABRIEL @340MW [WEBSMS] | CLUZ
5/11/2022 4:40:44 PM | MRCC-05/11/2022 16:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3072MW, PK=1890MW, RR=56MW, NetOpMargin: EVE=1107 Highest Unit O/L: GNPOWER U3 & U4 @ 138MW each unit. Derated Plant: Ag1@55MW, Ag2@105MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@196MW, MGPP@78MW, STEAG@200MW, FMP@246MW, and GNPK@276MW. [WEBSMS] | CMIN
5/11/2022 4:40:34 PM | LEYTE ACC-05/11/22 16:38:ORMOC CONVERTER STATION SS,350kV Leyte-Luzon, Blocked/Deblocked at 1607H/1617H,on reverse power flow per RTD. WEATHER: FAIR | CVIS
5/11/2022 4:40:31 PM | LRCC-05/11/2022 16:30: Calaca - Malamig (Sta. Rosa) 230kV Line tripped at Calaca side only at 1555H. Manually looped/restored at 1622H (Unplanned Outage) [WEBSMS] | CLUZ
5/11/2022 3:45:13 PM | LRCC-05/11/2022 15:40: System Advisory: Luzon Grid Highest Peak Load for this year 2022 at 11,863MW occurred at 1436H today, Wednesday, May 11, 2022. Previous highest peak is 11,727MWMW (May 6, 2022, Friday at 1429H). [WEBSMS] | CLUZ
5/11/2022 3:19:35 PM | VRCC-05/11/2022 15:13: Toledo SS. 30 MVA TR 1 energized at 1504. with clearance from MTD-A. [WEBSMS] | CVIS
5/11/2022 1:04:29 PM | VRCC-05/11/2022 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2788MW, PK=2227MW, RR=36.0MW, NetOpMargin: PM=525, EVE=325 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 352, TPC at 82 MW [WEBSMS] | CVIS
5/11/2022 1:04:27 PM | LRCC-05/11/2022 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14033MW, PK=11572MW, RR=464MW, NetOpMargin: PM=1997, EVE=2390 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLPGC 2 @75MW; ILIJAN A / B @851MW; STA RITA 40 @220MW; SAN GABRIEL @340MW [WEBSMS] | CLUZ
5/11/2022 11:51:25 AM | MRCC-05/11/2022 11:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3135MW, PK=1970MW, RR=59MW, NetOpMargin: PM=1086, EVE=1107 Highest Unit O/L: GNPOWER U3 & U4 @ 138MW each unit. Derated Plant: Ag1@55MW, Ag2@105MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@206MW, MGPP@78MW, STEAG@200MW, FMP@246MW, and GNPK@276MW. [WEBSMS] | CMIN
5/11/2022 6:08:05 AM | VRCC-05/11/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2831MW, PK=2188MW, RR=36MW, NetOpMargin: AM=606, PM=525, EVE=325 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 352, TPC at 82 MW [WEBSMS] | CVIS
5/11/2022 5:46:13 AM | LRCC-05/11/2022 05:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14131MW, PK=11261MW, RR=434MW, NetOpMargin: AM=2436, PM=1949, EVE=2504 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLPGC 2 @70MW, Sta Rita 40 @220MW, San Gabriel @340MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/11/2022 5:46:10 AM | LRCC-05/11/2022 05:36: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
5/11/2022 12:36:38 AM | LRCC-05/11/2022 00:27: San Lorenzo 50 online at 0005H (Unplanned Outage) [WEBSMS] | CLUZ
5/11/2022 12:26:32 AM | LRCC-05/11/2022 00:22: San Lorenzo 50 online at 0005H (Planned Outage) [WEBSMS] | CLUZ
5/10/2022 6:02:28 PM | VRCC-05/10/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2538MW, PK=2148MW, RR=40MW, NetOpMargin: EVE=350 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 355MW, TPC at 82MW [WEBSMS] | CVIS
5/10/2022 5:52:21 PM | LRCC-05/10/2022 17:42: Correction: San Lorenzo 50 (166MW) tripped at 1732H (Unplanned Outage). Lowest freq = 59.527Hz). [WEBSMS] | CLUZ
5/10/2022 5:41:52 PM | LRCC-05/10/2022 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13458MW, PK=10716MW, RR=405MW, NetOpMargin: EVE=2337 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLPGC 2 @60MW; ILJJAN A / B @851MW; STA RITA 40 @200MW; SAN GABRIEL @340MW [WEBSMS] | CLUZ
5/10/2022 5:38:56 PM | LRCC-05/10/2022 17:35: San Lorenzo 60 (166MW) tripped at 1732H (Unplanned Outage). Lowest freq = 59.527Hz). [WEBSMS] | CLUZ
5/10/2022 5:14:09 PM | MRCC-05/10/2022 17:05: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3081MW, PK=1850MW, RR=56MW, NetOpMargin: EVE=1175 Highest Unit O/L: GNPKU3&U4@138MW each; Derated Plant: Ag1@55MW, Ag2@105MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@196MW, MGPP@78MW, STEAG@200MW, FMP@246MW, and GNPK@276MW. [WEBSMS] | CMIN
5/10/2022 4:17:44 PM | NEGROS ACC: 05/10/2022, PGPP1 U2 re-online at 1606H. | CVIS
5/10/2022 1:56:07 PM | VRCC-05/10/2022 13:47: 138 KV Magdugo-Colon line energized at 1346H. [WEBSMS] | CVIS
5/10/2022 1:46:04 PM | VRCC-05/10/2022 13:44: Toledo SS. 30 MVA TR 1 tripped w/a load of 10 MW at 1333H, Differential, phase C. [WEBSMS] | CVIS
5/10/2022 1:43:15 PM | VRCC-05/10/2022 13:40: 138 KV Magdugo-Colon line tripped w/a load of 196MW at1333H, under assessment. [WEBSMS] | CVIS
5/10/2022 1:20:00 PM | LRCC-05/10/2022 13:17: Quezon -Mexico 230kV Line restored at 1316H (Unplanned Outage). [WEBSMS] | CLUZ
5/10/2022 1:09:34 PM | VRCC-05/10/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2729MW, PK=2297MW, RR=40MW, NetOpMargin: PM=392, EVE=320 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 355MW, TPC at 82MW, PGPP 1 at 75MW [WEBSMS] | CVIS
5/10/2022 12:56:36 PM | NEGROS ACC: 05/10/2022, PGPP1 U2(6.24MW) auto tripped at 1245H. On going investigation. | CVIS
5/10/2022 12:46:31 PM | NEGROS ACC: 05/10/2022, PGPP1 U2(36.48MW) auto tripped at 1136H due to turbine governor fault. Re-online at 1241H. | CVIS
5/10/2022 12:46:24 PM | LRCC-05/10/2022 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14057MW, PK=11436MW, RR=464MW, NetOpMargin: PM=2157, EVE=2775 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLPGC 2 @60MW; ILIJAN A / B @851MW; STA RITA 40 @200MW; SAN GABRIEL @340MW [WEBSMS] | CLUZ
5/10/2022 11:56:23 AM | MRCC-05/10/2022 11:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3148MW, PK=1950MW, RR=59MW, NetOpMargin: PM=1139, EVE=1175 Highest Unit O/L: GNPKU3&U4@138ME each; Derated Plant: Ag1@55MW, Ag2@105MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@202MW, MGPP@78MW, STEAG@200MW, FMP@246MW, and GNPK@276MW. [WEBSMS] | CMIN
5/10/2022 6:09:18 AM | VRCC-05/10/2022 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2811MW, PK=2261MW, RR=70MW, NetOpMargin: AM=480, PM=416, EVE=324 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 355MW, TPC at 82MW [WEBSMS] | CVIS
5/10/2022 6:09:16 AM | LRCC-05/10/2022 06:07: Malaya 2 online at 0601H (Planned Outage) [WEBSMS] | CLUZ
5/10/2022 5:25:19 AM | LRCC-05/10/2022 05:20: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13869MW, PK=10691MW, RR=454MW, NetOpMargin: AM=2724, PM=2340, EVE=2561 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLPGC 2 @60MW, Calaca 2 @200MW, Sta Rita 40 @200MW, San Gabriel @330MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/10/2022 4:57:25 AM | LRCC-05/10/2022 04:48: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
5/10/2022 4:47:08 AM | MRCC-05/10/2022 04:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3115MW, PK=1890MW, RR=56MW, NetOpMargin: AM=1149, PM=1095, EVE=1141 Highest Unit O/L: GNPOWER U3 & U4 @ 138MW each unit. Derated Plant: Ag!@55MW, Ag2@105MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@198MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW. [WEBSMS] | CMIN
5/10/2022 4:09:11 AM | LEYTE ACC-05/10/22 04:11: ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69 kV L,tripped/restored at 0350H/0401H,EF Inverse trip,load=28.7mw, WEATHER: FAIR | CVIS
5/9/2022 7:28:44 PM | LEYTE ACC-05/09/22 19:25: MARSHALLING SS, EDC-MAHA A unit 1 cut-in to the system at 1921H. Total plant capability = 355MW. WEATHER: FAIR | CVIS
5/9/2022 6:13:10 PM | VRCC-05/09/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2507MW, PK=1962MW, RR=40MW, NetOpMargin: EVE=505 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 323MW, TPC at 82MW [WEBSMS] | CVIS
5/9/2022 6:13:03 PM | LRCC-05/09/2022 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13566MW, PK=9572MW, RR=375MW, NetOpMargin: EVE=3619 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLPGC 2 @75MW, Sta Rita 40 @200MW, San Gabriel @330MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/9/2022 5:26:55 PM | LEYTE ACC-05/09/22: CALBAYOG SS, 69kV Palanas-Allen-Lao-ang Line tripped/restored, TIME OUT: 17:21:00, TIME IN: 17:24:00, RELAY: z2, phase BN, 91.89kms, load=14.4MW, WEATHER: FAIR | CVIS
5/9/2022 5:26:54 PM | LEYTE ACC-05/09/22: CALBAYOG SS, 69kV Palanas-Allen-Lao-ang Line tripped/restored, TIME OUT: 17:21:00, TIME IN: 17:24:00, RELAY: z2, phase BN, 91.89kms, load=14.4MW, WEATHER: FAIR | CVIS
5/9/2022 4:39:51 PM | MRCC-05/09/2022 16:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2915MW, PK=1730MW, RR=56MW, NetOpMargin: EVE=1115 Highest Unit O/L: GNPOWER U3 & U4 @ 138MW each unit. Derated Plant: Ag1@55MW, Ag2@105MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@196MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW. [WEBSMS] | CMIN
5/9/2022 1:44:47 PM | LEYTE ACC-05/09/22 13:51: KANANGA CS, EDC-Mahanagdong A unit #1 tripped at 1336H, under assessment. Gen Loaad=45.0MW. Weather: Fair. | CVIS
5/9/2022 1:17:48 PM | LRCC-05/09/2022 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13969MW, PK=8728MW, RR=377MW, NetOpMargin: PM=4864, EVE=3232 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLPGC 2 @60MW, Sta Rita 40 @200MW, San Gabriel @350MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/9/2022 1:03:46 PM | VRCC-05/09/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2821MW, PK=2059MW, RR=60MW, NetOpMargin: PM=703, EVE=217 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 345MW, TPC at 82MW [WEBSMS] | CVIS
5/9/2022 11:43:58 AM | MRCC-05/09/2022 11:33: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2959MW, PK=1550MW, RR=54MW, NetOpMargin: PM=1347, EVE=1115 Highest Unit O/L: GNPOWER U3 & U4 @ 138MW each unit. Derated Plant: Ag1@55MW, Ag2@105MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@202MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW. [WEBSMS] | CMIN
5/9/2022 6:09:50 AM | VRCC-05/09/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2836MW, PK=1997MW, RR=60MW, NetOpMargin: AM=780, PM=702, EVE=217 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 345, TPC at 82 MW [WEBSMS] | CVIS
5/9/2022 5:32:13 AM | LRCC-05/09/2022 05:28: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14043MW, PK=9553MW, RR=350MW, NetOpMargin: AM=4140, PM=3571, EVE=3178 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLPGC 2 @75MW, Sta Rita 40 @200MW, San Gabriel @350MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/9/2022 5:09:07 AM | LRCC-05/09/2022 04:58: Weather Update: Issued at 0400H, Intertropical Convergence Zone (ITCZ) affecting Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
5/9/2022 3:06:21 AM | MRCC-05/09/2022 02:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3115MW, PK=1440MW, RR=56MW, NetOpMargin: AM=1917, PM=1482, EVE=1251 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@105MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@196MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW. [WEBSMS] | CMIN
5/8/2022 6:10:58 PM | VRCC-05/08/2022 18:07: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2538MW, PK=2027MW, RR=40MW, NetOpMargin: EVE=471 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 355MW, TPC at 82MW [WEBSMS] | CVIS
5/8/2022 6:07:35 PM | LRCC-05/08/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13490MW, PK=9930MW, RR=390MW, NetOpMargin: EVE=3170 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLPGC 2 @75MW, Sta Rita 40 @200MW, San Gabriel @350MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/8/2022 4:34:34 PM | MRCC-05/08/2022 16:22: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3056MW, PK=1670MW, RR=59MW, NetOpMargin: EVE=1319 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@105MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@202MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW [WEBSMS] | CMIN
5/8/2022 3:33:25 PM | LRCC-05/08/2022 15:26: GNPD 2 shutdown at 1522H. On commissioning test (Planned Outage) [WEBSMS] | CLUZ
5/8/2022 1:22:46 PM | VRCC-05/08/2022 13:20: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2810MW, PK=1844MW, RR=40MW, NetOpMargin: PM=926, EVE=471 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 355MW, TPC at 82MW [WEBSMS] | CVIS
5/8/2022 12:36:59 PM | LRCC-05/08/2022 12:36: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13990MW, PK=9568MW, RR=373MW, NetOpMargin: PM=4049, EVE=3408 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLPGC 2 @40MW, Sta Rita 40 @200MW, San Gabriel @350MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/8/2022 12:10:25 PM | MRCC-05/08/2022 11:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3090MW, PK=1520MW, RR=52MW, NetOpMargin: PM=1509, EVE=1319 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@105MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@202MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW [WEBSMS] | CMIN
5/8/2022 12:04:57 PM | LRCC-05/08/2022 11:59: Mexico-Quezon 230kV Line restored at 1159H (Unplanned Outage) [WEBSMS] | CLUZ
5/8/2022 12:04:52 PM | LRCC-05/08/2022 11:58: Mexico-Quezon 230kV Line tripped at 1150H (Unplanned Outage) [WEBSMS] | CLUZ
5/8/2022 10:25:03 AM | LRCC-05/08/2022 10:13: Mexico-Quezon 230kV Line restored at 1011H (Unplanned Outage) [WEBSMS] | CLUZ
5/8/2022 10:24:58 AM | LRCC-05/08/2022 10:11: Mexico-Quezon 230kV Line tripped at 1003H (Unplanned Outage) [WEBSMS] | CLUZ
5/8/2022 7:34:42 AM | LEYTE ACC-05/08/22 07:38: SOLEQ SS,Soleq Solar Farm tripped/cut-in,0639H/0643H,affected by the tripping OF 69kV Ormoc-Simangan-Baybay 69 kV L,WEATHER: FAIR | CVIS
5/8/2022 6:51:01 AM | LEYTE ACC-05/08/22 06:59:ORMOC SS, Ormoc-Simangan-Baybay 69 kV L ,tripped/restored at 0639H/0644H,Phase CN, fd=7.7kms,load=20.1mw, WEATHER: FAIR | CVIS
5/8/2022 6:14:08 AM | LRCC-05/08/2022 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14157MW, PK=9017MW, RR=343MW, NetOpMargin: AM=4797, PM=4264, EVE=3369 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; MASINLOC 3 @250MW; ILIJAN A / B @851MW; STA RITA 40 @180MW; SAN GABRIEL @370MW [WEBSMS] | CLUZ
5/8/2022 6:04:09 AM | VRCC-05/08/2022 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2834MW, PK=1906MW, RR=76MW, NetOpMargin: AM=852, PM=907, EVE=471 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 355MW, TPC at 82MW [WEBSMS] | CVIS
5/7/2022 6:31:35 PM | VRCC-05/07/2022 18:28: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2492MW, PK=2106MW, RR=40MW, NetOpMargin: EVE=346 Highest Unit O/L: TVI U at 169MW/unit. Derated Plant: EDC at 305MW, TPC at 82MW [WEBSMS] | CVIS
5/7/2022 5:37:47 PM | LRCC-05/07/2022 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13381MW, PK=10305MW, RR=390MW, NetOpMargin: EVE=2686 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLPGC 2 @60MW, Sta Rita 40 @180MW, San Gabriel @370MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/7/2022 2:33:48 PM | VRCC-05/07/2022 14:28: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2717MW, PK=1987MW, RR=40MW, NetOpMargin: PM=690, EVE=346 Highest Unit O/L: TVI U at 169MW/unit. Derated Plant: EDC at 305MW, TPC at 82MW [WEBSMS] | CVIS
5/7/2022 2:09:10 PM | LRCC-05/07/2022 14:02: Dasmarinas-TMC 2 115kV Line tripped at 1353H. (Unplanned Outage) [WEBSMS] | CLUZ
5/7/2022 1:19:35 PM | LRCC-05/07/2022 13:09: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13937MW, PK=10440MW, RR=435MW, NetOpMargin: PM=3062, EVE=3035 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Sta Rita 40 @180MW, San Gabriel @370MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/7/2022 12:22:11 PM | LRCC-05/07/2022 12:17: Dasmarinas-MEC-Rosario 115kV Line restored at 1217H (Unplanned Outage) [WEBSMS] | CLUZ
5/7/2022 11:57:21 AM | MRCC-05/07/2022 11:48: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2934MW, PK=1665MW, RR=59MW, NetOpMargin: PM=1210, EVE=1140 Highest Unit O/L: GNPKU3&U4@138MW each; Derated Plant: Ag1@30MW, Ag2@85MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@194MW, MGPP@77MW, STEAG@200MW, FMP@246MW, GNPK@276MW and DCP@135MW. [WEBSMS] | CMIN
5/7/2022 11:04:09 AM | LEYTE ACC-05/07/22 11:11: ORMOC SS, Tolosa-Mabuhay-San Isidro 69kV Line tripped/restored at 1050H/1056H, ind.: Zone-2, Phase-B/C & F.D.=54.97kms. Load=5.4MW. Weather: Fair. | CVIS
5/7/2022 8:41:45 AM | LRCC-05/07/2022 08:36: Dasmarinas-MEC-Rosario 115kV Line de-energized at 0833H (Unplanned Outage) [WEBSMS] | CLUZ
5/7/2022 6:07:31 AM | VRCC-05/07/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2797MW, PK=1964MW, RR=40MW, NetOpMargin: AM=793, PM=690, EVE=346 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 305MW, TPC at 82MW [WEBSMS] | CVIS
5/7/2022 5:34:01 AM | LRCC-05/07/2022 05:24: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14031MW, PK=10019MW, RR=395MW, NetOpMargin: AM=3617, PM=3327, EVE=3075 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Sta Rita 40 @180MW, San Gabriel @380MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/7/2022 5:09:59 AM | LRCC-05/07/2022 05:00: Weather Update: Issued at 0400H, Easterlies affecting the country. [WEBSMS] | CLUZ
5/7/2022 4:11:52 AM | MRCC-05/07/2022 04:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2930MW, PK=1630MW, RR=58MW, NetOpMargin: AM=1235, PM=1202, EVE=989 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@75MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@188MW, MGPP@79MW, STEAG@200MW, TSI@135MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW. [WEBSMS] | CMIN
5/7/2022 2:24:52 AM | PANAY ACC-05/07/22 02:13 NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 02:02:00, TIME IN: 02:12:00, RELAY: Z1, Trip, AN, 77.1kms., WEATHER: FAIR, Momentary line fault. | CVIS
5/6/2022 9:50:17 PM | VRCC-05/06/2022 21:47: DaanBantayan SS. 69 KV DaanBantayan-Medellin line energized at 2146H. [WEBSMS] | CVIS
5/6/2022 9:50:15 PM | VRCC-05/06/2022 21:40: DaanBantayan SS. 69 KV DaanBantayan-Medellin line tripped w/a load of 26MW at 2130H, ind: 3Ph OCR. [WEBSMS] | CVIS
5/6/2022 7:05:25 PM | NEGROS ACC: 05/06/2022, 69kV Amlan-San Carlos restored at 1859H. | CVIS
5/6/2022 6:06:53 PM | VRCC-05/06/2022 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2540MW, PK=2149MW, RR=40MW, NetOpMargin: EVE=351 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 350MW, TPC at 82MW [WEBSMS] | CVIS
5/6/2022 5:56:49 PM | LRCC-05/06/2022 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13511MW, PK=10636MW, RR=395MW, NetOpMargin: EVE=2480 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Sta Rita 40 @180MW, San Gabriel @380MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/6/2022 3:52:18 PM | MRCC-05/06/2022 15:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2900MW, PK=1900MW, RR=56MW, NetOpMargin: EVE=924 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@47MW, Ag2@85MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@194MW, MGPP@79MW, STEAG@200MW, TSI@135MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW [WEBSMS] | CMIN
5/6/2022 3:52:09 PM | LRCC-05/06/2022 15:34: System Advisory: Luzon Grid Highest Peak Load for this year 2022 at 11,727MW occurred at 1429H today, Friday, May 6, 2022. Previous highest peak is 11,654MW (March 23, 2022, Wednesday at 1437H). [WEBSMS] | CLUZ
5/6/2022 1:52:15 PM | LRCC-05/06/2022 13:42: System Advisory: May 6, 2022: Market intervention initiated by Market Operator is lifted at 1339H, Market will resume starting 1345H trading interval. [WEBSMS] | CLUZ
5/6/2022 1:52:14 PM | VRCC-05/06/2022 13:49: MO initiated Market Intervention lifted at interval 1340H back to normal operation. [WEBSMS] | CVIS
5/6/2022 1:18:57 PM | LRCC-05/06/2022 13:09: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=14034MW, PK=11549MW, RR=460MW, NetOpMargin: PM=2025, EVE=2542 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Sta Rita 30/40 @240MW/180MW, San Gabriel @400MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/6/2022 10:38:45 AM | MRCC-05/06/2022 10:28: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2962MW, PK=2030MW, RR=59MW, NetOpMargin: PM=851, EVE=924 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@47MW, Ag2@85MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@194MW, MGPP@79MW, STEAG@200MW, TSI@135MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW [WEBSMS] | CMIN
5/6/2022 6:07:42 AM | VRCC-05/06/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2833MW, PK=2170MW, RR=40MW, NetOpMargin: AM=623, PM=581, EVE=351 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 350MW, TPC at 82MW [WEBSMS] | CVIS
5/6/2022 6:07:39 AM | LRCC-05/06/2022 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13924MW, PK=11289MW, RR=451MW, NetOpMargin: AM=2184, PM=1829, EVE=2515 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; ILIJAN A / B @851MW; STA RITA 30 @240MW; STA RITA 40 @161MW [WEBSMS] | CLUZ
5/6/2022 5:13:10 AM | MRCC-05/06/2022 05:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3059MW, PK=1930MW, RR=57MW, NetOpMargin: AM=1072, PM=976, EVE=1053 Highest Unit O/L: GNPKU3&U4@138MW each; Derated Plant: Ag1@30MW, Ag2@85MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@190MW, MGPP@77MW, STEAG@200MW, FMP@246MW, and GNPK@276MW. [WEBSMS] | CMIN
5/6/2022 3:22:53 AM | PANAY ACC-05/06/22 03:15: DINGLE SS, Dingle-Dumangas 69KV (5LI1DIN-DUM), TIME IN: 03:11:00, RELAY: B - N, WEATHER: FAIR. Customers owned and maintained line. | CVIS
5/6/2022 3:22:52 AM | PANAY ACC-05/06/22 03:15: DINGLE SS, Dingle-Dumangas 69KV (5LI1DIN-DUM), TIME IN: 03:11:00, RELAY: B - N, WEATHER: FAIR. Customers owned and maintained line. | CVIS
5/6/2022 3:22:50 AM | PANAY ACC-05/06/22 03:07: DINGLE SS, Dingle-Dumangas 69KV (5LI1DIN-DUM), TIME OUT: 03:04:00, RELAY: B - N, WEATHER: FAIR. Customers owned and maintained line. | CVIS
5/6/2022 3:22:49 AM | PANAY ACC-05/06/22 03:07: DINGLE SS, Dingle-Dumangas 69KV (5LI1DIN-DUM), TIME OUT: 03:04:00, RELAY: B - N, WEATHER: FAIR. Customers owned and maintained line. | CVIS
5/5/2022 8:40:05 PM | VRCC-05/05/2022 20:37: CEDC U1 synchronized at 2032H with 8MW initial load. [WEBSMS] | CVIS
5/5/2022 6:05:22 PM | VRCC-05/05/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2443MW, PK=2165MW, RR=40MW, NetOpMargin: EVE=238 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 350MW, CEDC at 164MW, TPC at 82MW [WEBSMS] | CVIS
5/5/2022 5:53:03 PM | NEGROS ACC: 05/05/2022, 69kV Bacolod-Reclamation Sub T/L (32.4MW) auto tripped at 1741H with indication: Z1 L3E, 0.6km. Customer owned and maintained line. Restored at 1747H. | CVIS
5/5/2022 5:31:35 PM | LRCC-05/05/2022 17:27: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13466MW, PK=10775MW, RR=395MW, NetOpMargin: EVE=2296 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Sta Rita 30/40 @240MW/161MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/5/2022 5:23:29 PM | MRCC-05/05/2022 17:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3022MW, PK=1860MW, RR=56MW, NetOpMargin: EVE=1106 Highest Unit O/L: GNPKU3&U4@138MW each; Derated Plant: Ag1@30MW, Ag2@85MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@188MW, MGPP@79MW, STEAG@200MW, FMP@246MW, and GNPK@276MW. [WEBSMS] | CMIN
5/5/2022 4:09:59 PM | LEYTE ACC-05/05/22 16:17: PARANAS SS, 69kV Taft Feeder tripped/restored at 1602H/1604H, ind.: Phase-A/N & F.D.=156.72kms. Load=11.6MW. Weather: Fair. | CVIS
5/5/2022 3:56:12 PM | LEYTE ACC-05/05/22 16:05: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1542H/1552H on reverse power per RTD. Weather: Fair. | CVIS
5/5/2022 3:42:51 PM | LEYTE ACC-05/05/22 15:41: CALBAYOG SS, Palanas Cara-Catarman-Allen/Lao-ang 69kV Line tripped/restored at 1525H/1528H, ind.: Z1, CN & 14.67kms. Load=18.5MW. Weather: Fair. | CVIS
5/5/2022 3:42:49 PM | VRCC-05/05/2022 15:37: 34.5 KV Sangi-Toledo line energized at 1518H. [WEBSMS] | CVIS
5/5/2022 3:14:40 PM | LEYTE ACC-05/05/22 15:13: ORMOC SS, 69kV PCB Tolosa manually opened/closed at 1450H/1455H, for normalization along Tolosa-Mabuhay-San Isidro 69kV Line. Load=5.7MW. Weather: Fair. | CVIS
5/5/2022 3:14:38 PM | VRCC-05/05/2022 14:59: 34.5 KV Sangi-Carcon L3 energized at 1457H at Carcon side only, since Sangi CB not affected. [WEBSMS] | CVIS
5/5/2022 2:52:19 PM | VRCC-05/05/2022 14:47: 34.5 KV Sangi-Toledo line tripped w/a load of 13.53MW at 1427H, under assessment. [WEBSMS] | CVIS
5/5/2022 2:52:17 PM | VRCC-05/05/2022 14:37: 34.5 KV Sangi-Carcon L3 tripped w/a load 16.87MW at 1427H, under assessment. [WEBSMS] | CVIS
5/5/2022 1:31:07 PM | PANAY ACC-05/05/22 13:20: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 13:18, Facilitated emergency request of ILECO1 to conduct hotspot correction of their San Miguel SS. | CVIS
5/5/2022 1:31:06 PM | PANAY ACC-05/05/22 13:20: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 13:18, Facilitated emergency request of ILECO1 to conduct hotspot correction of their San Miguel SS. | CVIS
5/5/2022 1:18:04 PM | PANAY ACC-05/05/22 13:15: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD),Load:49.98MW TIME OUT: 13:10, Facilitated emergency request of ILECO1 to conduct hotspot correction at their San Miguel SS. | CVIS
5/5/2022 1:07:57 PM | VRCC-05/05/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2742MW, PK=2223MW, RR=40MW, NetOpMargin: PM=479, EVE=238 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 350MW, CEDC at 164MW, TPC at 82MW [WEBSMS] | CVIS
5/5/2022 1:07:55 PM | LRCC-05/05/2022 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13874MW, PK=11570MW, RR=435MW, NetOpMargin: PM=1869, EVE=2619 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Sta Rita 30/40 @240MW/161MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
5/5/2022 12:00:31 PM | MRCC-05/05/2022 11:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3078MW, PK=1950MW, RR=59MW, NetOpMargin: PM=1069, EVE=1106 Highest Unit O/L: GNPKU3&U4@138MW each; Derated Plant: Ag1@30MW, Ag2@85MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@194MW, MGPP@79MW, STEAG@200MW, FMP@246MW, and GNPK@276MW. [WEBSMS] | CMIN
5/5/2022 7:07:50 AM | LRCC-05/05/2022 07:00: Malaya 2 shutdown at 0657H (Planned Outage) [WEBSMS] | CLUZ
5/5/2022 6:21:16 AM | VRCC-05/05/2022 06:13: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2618MW, PK=2223MW, RR=40MW, NetOpMargin: AM=395, PM=379, EVE=209 Highest Unit O/L: TVI Units at 169MW/Unit Derated Plant: EDC at 350MW, TPC at 82MW [WEBSMS] | CVIS
5/5/2022 6:07:26 AM | LRCC-05/05/2022 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=14131MW, PK=11088MW, RR=440MW, NetOpMargin: AM=2603, PM=2202, EVE=2820 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; ILJJAN A / B @851MW; STA RITA 30 @240MW; STA RITA 40 @161MW [WEBSMS] | CLUZ
5/5/2022 5:20:38 AM | LEYTE ACC-05/05/22 05:12: MAASIN SS, 69kV Maasin-Baybay line tripped at 0506H, phase A, 11.1kms., load=4.2MW. Restored at 0509H. WEATHER: FAIR | CVIS
5/5/2022 4:33:28 AM | PANAY ACC-05/05/22 04:24: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD)(41.0MW), TIME IN: 04:21:00, RELAY: M1: Z2, 11.4km.; M2: C - N, Z2, 11.39km, WEATHER: FAIR. Cause under investigation. | CVIS
5/5/2022 4:33:27 AM | PANAY ACC-05/05/22 04:24: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD)(41.0MW), TIME IN: 04:21:00, RELAY: M1: Z2, 11.4km.; M2: C - N, Z2, 11.39km, WEATHER: FAIR. Cause under investigation. | CVIS
5/5/2022 4:12:02 AM | PANAY ACC-05/05/22 03:51: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME OUT: 03:48:00, RELAY: M1: Z2, 11.4km.; M2: Z2, 11.39km, WEATHER: FAIR. Under investigation. | CVIS
5/5/2022 4:12:00 AM | PANAY ACC-05/05/22 03:51: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME OUT: 03:48:00, RELAY: M1: Z2, 11.4km.; M2: Z2, 11.39km, WEATHER: FAIR. Under investigation. | CVIS
5/5/2022 3:48:36 AM | MRCC-05/05/2022 03:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3063MW, PK=1915MW, RR=58MW, NetOpMargin: AM=1071, PM=1039, EVE=1077 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@85MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@194MW, MGPP@79MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW [WEBSMS] | CMIN
5/5/2022 12:36:26 AM | LRCC-05/05/2022 00:27: Sual 2 online at 0025H (Planned Outage) . [WEBSMS] | CLUZ
5/5/2022 12:13:01 AM | LEYTE ACC-05/04/22 00:00: ORMOC SS, 69kV Tolosa-San Isidro restored at 2355H, still isolated 69kV Javier ABS 2 up to San Isidro portion. | CVIS
5/4/2022 11:25:58 PM | VRCC-05/04/2022 23:16: CEDC unit # 1 tripped at 2304H with a load of 72.2MW under assessment. [WEBSMS] | CVIS
5/4/2022 11:15:27 PM | LEYTE ACC-05/04/22 23:00: ORMOC SS, 69kV Tolosa-San Isidro line tripped at 2233H, phase BN, Z2, 34.53Kms., load=7.2MW. Reclosed attempt failed with same indications. Sustained. | CVIS
5/4/2022 9:24:57 PM | LEYTE ACC-05/04/22 21:31: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2107H/2117H on normal power flow per RTD. Weather: Fair. | CVIS
5/4/2022 6:05:31 PM | VRCC-05/04/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2512MW, PK=2112MW, RR=40MW, NetOpMargin: EVE=360 Highest Unit O/L: TVI Units at 169MW/Unit Derated Plant: EDC at 321MW, TPC at 82MW [WEBSMS] | CVIS
5/4/2022 5:55:28 PM | LEYTE ACC-05/04/22 18:04: KANANGA CS, EDC-Mahanagdong unit #2 emergency cut-out from the system at 1744H. Weather: Fair. | CVIS
5/4/2022 5:51:21 PM | LRCC-05/04/2022 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12925MW, PK=10511MW, RR=399MW, NetOpMargin: EVE=2015 Highest Unit O/L: GNPD 2 at 668MW Derated Plant: GMEC 2 at 300MW, Sta Rita 30 at 240MW, Sta Rita 40 at 161MW and Ilijan at 851MW [WEBSMS] | CLUZ
5/4/2022 5:18:13 PM | LEYTE ACC-05/04/22 17:24: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1650H/1708H on reverse power flow per RTD. Weather: Cloudy. | CVIS
5/4/2022 4:20:14 PM | MRCC-05/04/2022 16:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3044MW, PK=1915MW, RR=56MW, NetOpMargin: EVE=1053 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@120MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@206MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW [WEBSMS] | CMIN
5/4/2022 1:32:28 PM | MRCC-05/04/2022 10:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3080MW, PK=2015MW, RR=59MW, NetOpMargin: PM=984, EVE=1053 Highest Unit O/L: GNPK U3&U4 @138MW each Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@120MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@206MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW. [WEBSMS] | CMIN
5/4/2022 1:32:08 PM | VRCC-05/04/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2764MW, PK=2219MW, RR=40MW, NetOpMargin: PM=505, EVE=389 Highest Unit O/L: TVI Units at 169MW/Unit Derated Plant: EDC at 350MW, TPC at 82MW [WEBSMS] | CVIS
5/4/2022 1:14:01 PM | LRCC-05/04/2022 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13462MW, PK=11310MW, RR=423MW, NetOpMargin: PM=1729, EVE=2236 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, Sta Rita 30 at 240MW, Sta Rita 40 at 161MW and Ilijan at 851MW [WEBSMS] | CLUZ
5/4/2022 6:06:54 AM | LRCC-05/04/2022 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13380MW, PK=10590MW, RR=423MW, NetOpMargin: AM=2368, PM=1955, EVE=2160 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sta. Rita 30 at 240MW, Sta. Rita 40 at 161MW [WEBSMS] | CLUZ
5/4/2022 6:04:51 AM | VRCC-05/04/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2875MW, PK=2203MW, RR=40MW, NetOpMargin: AM=632, PM=505, EVE=389 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 350MW, TPC at 82MW [WEBSMS] | CVIS
5/4/2022 5:06:09 AM | MRCC-05/04/2022 04:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3095MW, PK=1940MW, RR=56MW, NetOpMargin: AM=1078, PM=1012, EVE=1054 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@206MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW. [WEBSMS] | CMIN
5/4/2022 5:05:50 AM | LRCC-05/04/2022 05:02: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 185 km East of General Santos City (5.8?N, 126.8?E). Frontal System affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
5/3/2022 10:27:08 PM | NEGROS ACC: 05/03/2022: 69kV Mabinay-Kabankalan Sub T/L(0.66MW) auto-tripped at 2212H with indication Z1 AN, 10.36km. URC isolated.Restored at 2214H. | CVIS
5/3/2022 6:04:46 PM | VRCC-05/03/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2526MW, PK=1992MW, RR=40MW, NetOpMargin: EVE=494 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 345MW, TPC at 82MW [WEBSMS] | CVIS
5/3/2022 5:40:24 PM | LRCC-05/03/2022 17:33: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12837MW, PK=10047MW, RR=371MW, NetOpMargin: EVE=2419 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Sta Rita 30/40 @240MW/161MW, GMEC 2 @ 300MW & Ilijan @851MW [WEBSMS] | CLUZ
5/3/2022 4:41:51 PM | MRCC-05/03/2022 16:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3045MW, PK=1830MW, RR=56MW, NetOpMargin: EVE=1142 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@196MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW. [WEBSMS] | CMIN
5/3/2022 1:05:23 PM | VRCC-05/03/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2686MW, PK=2170MW, RR=40MW, NetOpMargin: PM=476, EVE=494 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 345MW, TPC at 82MW [WEBSMS] | CVIS
5/3/2022 1:05:21 PM | LRCC-05/03/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13158MW, PK=10326MW, RR=373MW, NetOpMargin: PM=2459, EVE=2565 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Calaca 1 @220MW, Sta Rita 30/40 @240MW/161MW, GMEC 2 @ 300MW & Ilijan @851MW [WEBSMS] | CLUZ
5/3/2022 12:44:14 PM | MRCC-05/03/2022 12:31: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3108MW, PK=1740MW, RR=59MW, NetOpMargin: PM=1298, EVE=1142 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@196MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW. [WEBSMS] | CMIN
5/3/2022 6:10:08 AM | VRCC-05/03/2022 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2666MW, PK=2159MW, RR=40MW, NetOpMargin: AM=467, PM=341, EVE=359 Highest Unit O/L: TVI U at 169MW/unit. Derated Plant: EDC at 345MW, TPC at 82MW [WEBSMS] | CVIS
5/3/2022 6:00:04 AM | LRCC-05/03/2022 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13223MW, PK=8766MW, RR=373MW, NetOpMargin: AM=4084, PM=3655, EVE=2988 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Calaca 1 @220MW, Sta Rita 30/40 @240MW/161MW, GMEC 2 @ 300MW & Ilijan @851MW [WEBSMS] | CLUZ
5/3/2022 5:22:46 AM | LRCC-05/03/2022 05:18: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 230 km East Southeast of General Santos City (5.6?N, 127.2?E). It is embedded along the Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CLUZ
5/3/2022 2:36:48 AM | MRCC-05/03/2022 02:24: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3099MW, PK=1733MW, RR=57MW, NetOpMargin: AM=1297, PM=1298, EVE=1142 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@156MW, Ag5@47MW, Ag6@75MW, Ag7@26MW, Pul4@196MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW. [WEBSMS] | CMIN
5/2/2022 11:28:07 PM | VRCC-05/02/2022 23:24: Toledo SS. 40 MVA TR 1 energized at 2317H with clearance from MTD-A. [WEBSMS] | CVIS
5/2/2022 8:30:01 PM | LEYTE ACC-05/02/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 2009H/2019H, on normal flow per RTD | CVIS
5/2/2022 8:30:00 PM | LEYTE ACC-05/02/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 2009H/2019H, on normal flow per RTD | CVIS
5/2/2022 8:15:17 PM | LRCC-05/02/2022 20:14: Ilijan GT2-1 shutdown at 2008H (Unplanned Outage) [WEBSMS] | CLUZ
5/2/2022 6:42:13 PM | LRCC-05/02/2022 18:40: Ilijan GT1-1 online at 1755H (Planned Outage) [WEBSMS] | CLUZ
5/2/2022 6:04:13 PM | VRCC-05/02/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2534MW, PK=2067MW, RR=40MW, NetOpMargin: EVE=427 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 345MW, TPC at 82MW [WEBSMS] | CVIS
5/2/2022 5:29:53 PM | LRCC-05/02/2022 17:27: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12631MW, PK=10222MW, RR=411MW, NetOpMargin: EVE=1998 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sta. Rita 30 at 240MW, Sta. Rita 40 at 161MW [WEBSMS] | CLUZ
5/2/2022 5:26:52 PM | LEYTE ACC-05/02/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1651H/1702H, on reverse flow per RTD | CVIS
5/2/2022 5:26:51 PM | LEYTE ACC-05/02/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1651H/1702H, on reverse flow per RTD | CVIS
5/2/2022 4:14:30 PM | MRCC-05/02/2022 16:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3047MW, PK=14970MW, RR=56MW, NetOpMargin: EVE=998 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@156MW, Ag5@47MW, Ag6@85MW, Ag7@26MW, Pul4@194MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@150MW. [WEBSMS] | CMIN
5/2/2022 3:55:54 PM | VRCC-05/02/2022 15:51: Toledo SS. 40 MVA TR 1 tripped at 1531H w/a load of 12.98 MW, under assessment. [WEBSMS] | CVIS
5/2/2022 1:47:44 PM | LRCC-05/02/2022 13:44: Kalayaan 2 (135MW) tripped as generator at 1338H. Lowest Frequency is 59.781Hz. (Unplanned Outage) [WEBSMS] | CLUZ
5/2/2022 1:00:06 PM | VRCC-05/02/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2762MW, PK=2169MW, RR=40MW, NetOpMargin: PM=553, EVE=427 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 345MW, TPC at 82MW [WEBSMS] | CVIS
5/2/2022 12:47:22 PM | LRCC-05/02/2022 12:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12930MW, PK=10839MW, RR=443MW, NetOpMargin: PM=1648, EVE=1744 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sta. Rita 30 at 240MW, Sta. Rita 40 at 161MW [WEBSMS] | CLUZ
5/2/2022 11:58:04 AM | MRCC-05/02/2022 11:43: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3105MW, PK=2090MW, RR=59MW, NetOpMargin: PM=932, EVE=998 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@156MW, Ag5@47MW, Ag6@85MW, Ag7@26MW, Pul4@194MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@0MW & MCC@150MW. [WEBSMS] | CMIN
5/2/2022 6:06:33 AM | LRCC-05/02/2022 06:05: Malaya 2 online at 0601H (Planned Outage) [WEBSMS] | CLUZ
5/2/2022 6:03:14 AM | VRCC-05/02/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2822MW, PK=2159MW, RR=40MW, NetOpMargin: AM=623, PM=553, EVE=427 Highest Unit O/L: TVI Units at 169 MW each Derated Plant: EDC at 345MW, TPC at 82MW [WEBSMS] | CVIS
5/2/2022 5:53:10 AM | LRCC-05/02/2022 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12983MW, PK=10665MW, RR=423MW, NetOpMargin: AM=1895, PM=1409, EVE=1614 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 2 @270MW, Sta Rita 40 @161MW, GMEC 2 @ 300MW, & Ilijan @603MW [WEBSMS] | CLUZ
5/2/2022 5:18:05 AM | MRCC-05/02/2022 05:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3096MW, PK=2015MW, RR=56MW, NetOpMargin: AM=1025, PM=955, EVE=1020 Highest Unit O/L: GNPKU3&U4@138MW each; Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@156MW, Ag5@47MW, Ag6@85MW, Ag7@26MW, Pul4@188MW, MGPP@78MW, STEAG@200MW, FMP@246MW, and GNPK@276MW. [WEBSMS] | CMIN
5/2/2022 4:35:46 AM | LRCC-05/02/2022 04:32: Las Pinas-Dasmarinas 230kV Line 2 restored at 0432H (Unplanned Outage) [WEBSMS] | CLUZ
5/2/2022 4:11:56 AM | LRCC-05/02/2022 04:04: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 40 km South Southwest of General Santos City (5.8?N, 125.0?E). It is embedded along the Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CLUZ
5/2/2022 12:49:52 AM | LRCC-05/02/2022 00:39: Las Pinas 300MVA T03 & T02 de-energized at 0035H & 0036H, respectively. (Unplanned Outage) [WEBSMS] | CLUZ
5/2/2022 12:29:05 AM | LRCC-05/02/2022 00:28: Las Pinas-Dasmarinas 230kV Line 1 de-energized at 0027H (Unplanned Outage) [WEBSMS] | CLUZ
5/2/2022 12:26:04 AM | LRCC-05/02/2022 00:25: Las Pinas-Dasmarinas 230kV Line 2 de-energized at 0022H (Unplanned Outage) [WEBSMS] | CLUZ
5/1/2022 6:03:44 PM | VRCC-05/01/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2529MW, PK=1912MW, RR=40MW, NetOpMargin: EVE=577 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 340MW, TPC at 82MW [WEBSMS] | CVIS
5/1/2022 5:51:37 PM | LRCC-05/01/2022 17:47: Botolan-Subic(Hanjin) 230kV Line restored at 1746H. (Planned Outage) [WEBSMS] | CLUZ
5/1/2022 5:30:25 PM | MRCC-05/01/2022 17:22: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3036MW, PK=1750MW, RR=59MW, NetOpMargin: EVE=1227 Highest Unit O/L: GNPKU3&U4@138MW each; Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@156MW, Ag5@47MW, Ag6@85MW, Ag7@26MW, Pul4@194MW, MGPP@78MW, STEAG@200MW, FMP@246MW, and GNPK@276MW. [WEBSMS] | CMIN
5/1/2022 5:30:16 PM | LRCC-05/01/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12587MW, PK=9934MW, RR=373MW, NetOpMargin: EVE=2280 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 603MW, GMEC 2 at 300MW, Sta. Rita 40 at 161MW [WEBSMS] | CLUZ
5/1/2022 1:05:32 PM | NEGROS ACC: 05/01/2022, 69kV Kabankalan-La Castellana Sub T/L energized at 1300H after replacement of rotten poles by NOCECO. Customer owned and maintained line. | CVIS
5/1/2022 1:05:30 PM | VRCC-05/01/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2773MW, PK=1619MW, RR=40MW, NetOpMargin: PM=1114, EVE=577 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 340MW, TPC at 82MW [WEBSMS] | CVIS
5/1/2022 12:51:09 PM | LRCC-05/01/2022 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13022MW, PK=9087MW, RR=357MW, NetOpMargin: PM=3578, EVE=2569 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 603MW, GMEC 2 at 300MW, Sta. Rita 40 at 161MW [WEBSMS] | CLUZ
5/1/2022 12:20:22 PM | MRCC-05/01/2022 12:08: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3072MW, PK=1570MW, RR=52MW, NetOpMargin: PM=1450, EVE=1227 Highest Unit O/L: GNPKU3&U4@138MW each; Derated Plant: Ag1@25MW, Ag2@110MW, Ag4@156MW, Ag5@47MW, Ag6@85MW, Ag7@26MW, Pul4@181MW, MGPP@76MW, STEAG@200MW, FMP@246MW, and GNPK@276MW. [WEBSMS] | CMIN
5/1/2022 11:17:41 AM | LRCC-05/01/2022 11:14: Kalayaan 2 tripped as pump (-150MW) at 1110H. Highest Frequency is 60.403Hz (Unplanned Outage) [WEBSMS] | CLUZ
5/1/2022 10:19:33 AM | LRCC-05/01/2022 10:13: Botolan-Subic(Hanjin) 230kV Line de-energized at 1003H. (Planned Outage) [WEBSMS] | CLUZ
5/1/2022 9:18:28 AM | LRCC-05/01/2022 09:12: Olongapo-Subic(Hanjin) 230kV line restored at 0911H. (Planned Outage) [WEBSMS] | CLUZ
5/1/2022 7:36:20 AM | NEGROS ACC: 05/01/2022, 69kV Kabankalan-La Castellana Sub T/L (10.0MW) de-energized at 0726H , due to customers request(NOCECO) to conduct replacement of rotten poles at strs. 16HT, 102B & 116E. Customer owned and maintained line. | CVIS
5/1/2022 6:39:04 AM | LRCC-05/01/2022 06:33: Olongapo-Subic(Hanjin) 230kV line de-energized at 0633H. (Planned Outage) [WEBSMS] | CLUZ
5/1/2022 6:05:07 AM | VRCC-05/01/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2802MW, PK=1616MW, RR=65MW, NetOpMargin: AM=1121, PM=1119, EVE=582 Highest Unit O/L: TVI Units at 169MW each Derated Plant: EDC at 340MW, TPC at 82MW [WEBSMS] | CVIS
5/1/2022 6:05:05 AM | LRCC-05/01/2022 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13090MW, PK=8648MW, RR=335MW, NetOpMargin: AM=4107, PM=3485, EVE=2518 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, Sta Rita 40 at 161MW and Ilijan at 603MW [WEBSMS] | CLUZ
5/1/2022 5:25:59 AM | LRCC-05/01/2022 05:17: Weather Update: Issued at 0400H of May 1, 2022, At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 315 km Southeast of Davao City (5.7N, 128.2E). It is embedded along the Intertropical Convergence Zone (ITCZ) affecting Mindanao. [WEBSMS] | CLUZ
5/1/2022 4:42:17 AM | MRCC-05/01/2022 04:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3083MW, PK=1530MW, RR=50MW, NetOpMargin: AM=1492, PM=1439, EVE=1216 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@156MW, Ag5@47MW, Ag6@85MW, Ag7@26MW, Pul4@194MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@0MW & MCC@150MW. [WEBSMS] | CMIN
5/1/2022 3:36:46 AM | LRCC-05/01/2022 03:32: Nagsaag - San Manuel 230kV Line 2 restored at 0324H. (Planned Outage) [WEBSMS] | CLUZ
4/30/2022 9:43:11 PM | LRCC-04/30/2022 21:41: Hermosa-Marilao(Duhat) 230kV Line restored at 2140H. (Planned Outage) [WEBSMS] | CLUZ
4/30/2022 8:59:19 PM | LEYTE ACC-04/30/22 19:36: Marshalling Ss, EDC-Malitbog unit 1 cut-in to the system at 1930H. WEATHER: FAIR | CVIS
4/30/2022 8:35:29 PM | LRCC-04/30/2022 20:34: For info: Meralco Sector 3 was normalized at 2015H. (Pamplona Bank 1 remain shifted to Laguna Sector via San Pedro) [WEBSMS] | CLUZ
4/30/2022 8:07:54 PM | LRCC-04/30/2022 20:07: Las Pinas 300MVA T02 and T03 was looped at 115kV side at 2003h and 2004h respectively. [WEBSMS] | CLUZ
4/30/2022 7:57:53 PM | LRCC-04/30/2022 19:49: Dasmarinas-Las Pinas 230kV line 1 and Las Pinas 230kV Bus 1 was looped at the New GIS via Las Pinas 230kV Bus 4 at 1943H. (On-going energization of Dasmarinas-Las Pinas 230kV line 1 temporary reconfiguration at Las Pinas SS.) [WEBSMS] | CLUZ
4/30/2022 7:43:56 PM | LEYTE ACC-04/30/22 19:42: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1927H/1937H, on normal flow per RTD. WEATHER: FAIR | CVIS
4/30/2022 7:43:54 PM | LRCC-04/30/2022 19:37: Dasmarinas-Las Pinas 230kV line 1, Las Pinas 300MVA T02 and Las Pinas 300MVA T03 were energized at 1932H. (On-going energization of Dasmarinas-Las Pinas 230kV line 1 thru temporary reconfiguration at Las Pinas SS.) [WEBSMS] | CLUZ
4/30/2022 6:46:07 PM | PANAY ACC-04/30/22 18:07: DINGLE SS, Dingle-Sta. Barbara 138 kV L1 (7LI1DIN-SBA), TIME IN: 06:02:00, Pre arranged maintenance | CVIS
4/30/2022 6:46:04 PM | LRCC-04/30/2022 18:42: Nagsaag - San Manuel 230kV Line 2 de-energized at 1836H. (Planned Outage) [WEBSMS] | CLUZ
4/30/2022 6:32:47 PM | LRCC-04/30/2022 18:31: Hermosa-Marilao(Duhat) 230kV Line de-energized at 1831H. (Planned Outage) [WEBSMS] | CLUZ
4/30/2022 6:10:41 PM | NEGROS ACC: 04/30/2022, 69kV Kabankalan-Sipalay Sub T/L restored at 1748H. | CVIS
4/30/2022 6:10:39 PM | VRCC-04/30/2022 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2471MW, PK=1912MW, RR=40MW, NetOpMargin: EVE=519 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 295MW, TPC at 82MW [WEBSMS] | CVIS
4/30/2022 6:00:19 PM | LEYTE ACC-04/30/22 18:00: MARSHALLING SS, EDC-Malitbog unit 1 tripped at 1741H, load=40MW. Under assessment. WEATHER: FAIR | CVIS
4/30/2022 6:00:17 PM | LEYTE ACC-04/30/22 18:00: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1735H/1745H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
4/30/2022 6:00:16 PM | NEGROS ACC: 04/30/2022 1st level ALD activation in Negros area at 1741H isolating 69kV Kabankalan-Sipalay Sub T/L(17.8MW) due to tripping of Malitbog U1(40MW) while on process of de-blocking of HVDC. | CVIS
4/30/2022 6:00:15 PM | VRCC-04/30/2022 17:53: Visayas grid first level UFR activated at 1741H due to tripping of Malitbog U1 during HVDC at block mode in preparation for reverse, load affected at 17.8MW. [WEBSMS] | CVIS
4/30/2022 5:46:15 PM | LRCC-04/30/2022 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12331MW, PK=9820MW, RR=341MW, NetOpMargin: EVE=2170 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 603MW, GMEC 2 at 300MW, Sta. Rita 40 at 161MW [WEBSMS] | CLUZ
4/30/2022 5:21:45 PM | LRCC-04/30/2022 17:18: Lumban-Malaya 230kV Line 1 restored at 1716H. (Planned Outage) [WEBSMS] | CLUZ
4/30/2022 4:50:18 PM | MRCC-04/30/2022 16:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3054MW, PK=1810MW, RR=56MW, NetOpMargin: EVE=1172 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@157MW, Ag5@47MW, Ag6@108MW, Ag7@26MW, Pul4@178MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@0MW & MCC@150MW. [WEBSMS] | CMIN
4/30/2022 4:50:10 PM | PANAY ACC-04/30/22 16:42: CONCEPCION S/S SS, Concepcion-Sara 69 kV Line (5LI1CNE-SAR), TIME OUT: 04:27:00, TIME IN: 04:30:00, Load: 6.4mw, facilitate restoration of 69kV Sara-Estancia TL. | CVIS
4/30/2022 4:50:08 PM | PANAY ACC-04/30/22 16:41: CONCEPCION S/S SS, Sara-Estancia 69 kV Line, TIME OUT: 11:55:00, TIME IN: 04:30:00 | CVIS
4/30/2022 4:50:05 PM | LRCC-04/30/2022 16:47: Hermosa - Malolos 230kV Line restored at 1645H. (Planned Outage) [WEBSMS] | CLUZ
4/30/2022 2:37:12 PM | LEYTE ACC-04/30/22 14:22: ORMOC SS, Ormoc 230 kV 150MVA T3 re-energized at 1415H, completed pre arranged activity. WEATHER: FAIR | CVIS
4/30/2022 1:36:09 PM | LRCC-04/30/2022 13:29: Ilijan B2 online at 1324H. (Unplanned Outage) [WEBSMS] | CLUZ
4/30/2022 1:12:29 PM | PANAY ACC-04/30/22 13:03: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST), TIME IN: 01:01:00, RELAY: B - N, WEATHER: FAIR. Sectionalized with Concepcion - Sara 69kV Line energized. | CVIS
4/30/2022 1:12:27 PM | PANAY ACC-04/30/22 13:03: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST), TIME IN: 01:01:00, RELAY: B - N, WEATHER: FAIR. Sectionalized with Concepcion - Sara 69kV Line energized. | CVIS
4/30/2022 1:02:22 PM | VRCC-04/30/2022 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2761MW, PK=1714MW, RR=40MW, NetOpMargin: PM=1007, EVE=559 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 335MW, TPC at 82MW [WEBSMS] | CVIS
4/30/2022 12:46:24 PM | LRCC-04/30/2022 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12772MW, PK=10241MW, RR=398MW, NetOpMargin: PM=2133, EVE=2244 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 540MW, San Gabriel at 400MW, GMEC 2 at 300MW, Sta. Rita 40 at 80MW [WEBSMS] | CLUZ
4/30/2022 12:32:25 PM | PANAY ACC-04/30/22 12:10: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST), TIME OUT: 11:55:00, Test Energized at 1206H but failed, RELAY ind.: A - B - N, WEATHER: FAIR. Sustained Fault. | CVIS
4/30/2022 12:32:24 PM | PANAY ACC-04/30/22 12:10: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST), TIME OUT: 11:55:00, Test Energized at 1206H but failed, RELAY ind.: A - B - N, WEATHER: FAIR. Sustained Fault. | CVIS
4/30/2022 12:11:56 PM | MRCC-04/30/2022 11:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3121MW, PK=1670MW, RR=59MW, NetOpMargin: PM=1384, EVE=1172 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@157MW, Ag5@47MW, Ag6@108MW, Ag7@26MW, Pul4@178MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@0MW & MCC@150MW. [WEBSMS] | CMIN
4/30/2022 12:11:23 PM | PANAY ACC-04/30/22 11:58: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST)(14.7), TIME OUT: 11:55:00, RELAY: B - N, WEATHER: FAIR. Cause under investigation. | CVIS
4/30/2022 12:11:22 PM | NEGROS ACC: 04/30/2022, 69kV Cadiz-VMC Sub T/L normalized at 1151H after customers request(NONECO). Customer owned and maintained line. | CVIS
4/30/2022 9:51:03 AM | LEYTE ACC-04/30/22 09:52: ORMOC SS, Ormoc 138kV BUS 1 re-energized at 0933H, pre-arranged activity completed. Weather: Fair. | CVIS
4/30/2022 8:12:41 AM | LRCC-04/30/2022 08:04: Hermosa - Malolos 230kV Line de-energized at 0802H. (Planned Outage) [WEBSMS] | CLUZ
4/30/2022 7:24:18 AM | LRCC-04/30/2022 07:18: Weather Update: Issued at 0400H, Intertropical Convergence Zone (ITCZ) affecting Mindanao and Palawan. [WEBSMS] | CLUZ
4/30/2022 7:11:34 AM | NEGROS ACC: 04/30/2022, NONECO VMC S/S load shifted to 69kV Bacolod-Silay-VMC Line at 0700H. | CVIS
4/30/2022 7:01:08 AM | LRCC-04/30/2022 06:57: Lumban-Malaya 230kV Line 1 de-energized at 0653H (Planned Outage). [WEBSMS] | CLUZ
4/30/2022 6:50:47 AM | NEGROS ACC: 04/30/2022, Emergency shutdown of 69kV Cadiz-VMC Sub T/L(9.4MW)at 0641H as per customers(NONECO) request due to installation of wedge connectors and additional conductors. | CVIS
4/30/2022 6:50:45 AM | PANAY ACC-04/30/22 06:39: DINGLE SS, Dingle-Sta. Barbara 138 kV L1 (7LI1DIN-SBA), TIME OUT: 06:35:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance Activities. | CVIS
4/30/2022 6:50:44 AM | PANAY ACC-04/30/22 06:39: DINGLE SS, Dingle-Sta. Barbara 138 kV L1 (7LI1DIN-SBA), TIME OUT: 06:35:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance Activities. | CVIS
4/30/2022 6:13:40 AM | VRCC-04/30/2022 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2828MW, PK=1692MW, RR=40MW, NetOpMargin: AM=1096, PM=1031, EVE=567 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 335 MW, TPC = 82 MW [WEBSMS] | CVIS
4/30/2022 6:00:27 AM | LRCC-04/30/2022 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12684MW, PK=9646MW, RR=391MW, NetOpMargin: AM=2647, PM=2401, EVE=2136 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 514MW, San Gabriel at 400MW, GMEC 2 at 300MW, SCPC 3 at 120MW [WEBSMS] | CLUZ
4/30/2022 5:49:38 AM | LEYTE ACC-04/30/22 05:53: ORMOC SS,Ormoc 230kV 150MVA T3 ,TIME OUT:05:22:00,Pre arranged per PANR No.VRCC-22-04-0082,8Am-12Noon.Weather:fair | CVIS
4/30/2022 4:50:25 AM | MRCC-04/30/2022 04:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3112MW, PK=1570MW, RR=63MW, NetOpMargin: AM=1479, PM=1384, EVE=1172 Highest Unit O/L: GNPK U3 and U4 @ 138 MW each. Derated Plant: Ag1@20MW, Ag2@85MW, Ag4@108MW, Ag5@37MW, Ag6@98MW, Ag7@21MW, Pul4@71MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@245.5MW, GNPK@276MW, SMCPC@270MW, MCC@150MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
4/30/2022 3:45:58 AM | LRCC-04/30/2022 03:41: Sta. Rita 40 online at 0339H (Unplanned Outage) [WEBSMS] | CLUZ
4/30/2022 2:12:16 AM | LRCC-04/30/2022 02:08: Sta. Rita 40 shutdown at 0204H (Unplanned Outage). [WEBSMS] | CLUZ
4/30/2022 1:25:05 AM | LRCC-04/30/2022 01:21: Sta. Rita 40 online at 0114H (Unplanned Outage). [WEBSMS] | CLUZ
4/29/2022 10:41:25 PM | LRCC-04/29/2022 22:40: Zapote 300MVA T02 and T03 de-energized at 2229H (Planned Outage) [WEBSMS] | CLUZ
4/29/2022 8:09:05 PM | LRCC-04/29/2022 20:05: Malaya 2 shutdown at 1940H (Planned Outage). [WEBSMS] | CLUZ
4/29/2022 6:07:35 PM | VRCC-04/29/2022 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2489MW, PK=2023MW, RR=40MW, NetOpMargin: EVE=426 Highest Unit O/L: TVI units at 169MW/unit Derated Plant: EDC at 335MW, TPC at 82MW [WEBSMS] | CVIS
4/29/2022 5:56:08 PM | LRCC-04/29/2022 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12461MW, PK=10498MW, RR=421MW, NetOpMargin: EVE=12461 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 540MW, San Gabriel at 400MW, GMEC 2 at 300MW, SCPC 3 at 110MW, SLPGC 1 at 135MW [WEBSMS] | CLUZ
4/29/2022 4:33:30 PM | MRCC-04/29/2022 16:22: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=3043MW, PK=1870MW, RR=75MW, NetOpMargin: EVE=1098 Highest Unit O/L: GNPK U3 and U4 @ 138 MW each. Derated Plant: Ag1@20MW, Ag2@100MW, Ag4@108MW, Ag5@37MW, Ag6@78MW, Ag7@21MW, Pul4@94MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@245.5MW, GNPK@276MW, SMCPC@270MW, MCC@150MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
4/29/2022 1:56:15 PM | MRCC-04/29/2022 13:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=3112MW, PK=2000MW, RR=80MW, NetOpMargin: PM=472, EVE=550 Highest Unit O/L: GNPK U3 and U4 @ 138 MW each. Derated Plant: Ag1@20MW, Ag2@100MW, Ag4@108MW, Ag5@37MW, Ag6@78MW, Ag7@21MW, Pul4@99MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@245.5MW, GNPK@276MW, SMCPC@270MW, MCC@150MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
4/29/2022 1:12:01 PM | VRCC-04/29/2022 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2755MW, PK=2166MW, RR=40MW, NetOpMargin: PM=549, EVE=426 Highest Unit O/L: TVI units at 169MW/unit Derated Plant: EDC at 335MW, TPC at 82MW [WEBSMS] | CVIS
4/29/2022 12:56:07 PM | LRCC-04/29/2022 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12941MW, PK=11337MW, RR=454MW, NetOpMargin: PM=1150, EVE=1276 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 540MW, San Gabriel at 400MW, GMEC 2 at 300MW, SCPC 3 at 110MW, SLPGC 1 at 90MW [WEBSMS] | CLUZ
4/29/2022 10:21:45 AM | LEYTE ACC-04/29/22 10:23: BABATNGON SS, BABATNGON 7.5MVAr Cap. Bank #1 ready for operation at 1000H, emergency hotspot correction completed. Weather: Cloudy. | CVIS
4/29/2022 9:11:07 AM | PANAY ACC-04/29/22 09:05: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST), TIME IN: 08:56:00, WEATHER: FAIR | CVIS
4/29/2022 8:55:19 AM | LEYTE ACC-04/29/22 09:02: BABATNGON SS, Isolated Babatngon 7.5MVAr Cap. Bank #1 at 0846H to facilitate emergency hotspot correction. Weaher: Cloudy. | CVIS
4/29/2022 6:13:14 AM | LRCC-04/29/2022 06:10: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12962MW, PK=11022MW, RR=441MW, NetOpMargin: AM=1499, PM=1130, EVE=1298 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, Ilijan at 540MW, San Gabriel at 400MW and SLPGC 1 at 75MW [WEBSMS] | CLUZ
4/29/2022 6:03:36 AM | MRCC-04/29/2022 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=3088MW, PK=1930MW, RR=56MW, NetOpMargin: AM=1081, PM=1020, EVE=1086 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@157MW, Ag5@47MW, Ag6@88MW, Ag7@26MW, Pul4@186MW, MGPP@78MW, STEAG@200MW, TSI@270MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@0MW & MCC@150MW. [WEBSMS] | CMIN
4/29/2022 6:03:26 AM | VRCC-04/29/2022 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2798MW, PK=2159MW, RR=40MW, NetOpMargin: AM=599, PM=549, EVE=426 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 335Mw, TPC at 82MW [WEBSMS] | CVIS
4/29/2022 5:35:39 AM | LRCC-04/29/2022 05:32: Binan-San Pedro 115kV line was restored at 0532H. (Planned Outage) [WEBSMS] | CLUZ
4/29/2022 5:22:57 AM | PANAY ACC-04/29/22 05:16: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST), TIME OUT: 05:15:00, Ld: 12.3MW; WEATHER: FAIR; Facilitated Emergency shutdown request for insulator replacement along 69kV Concepcion - Sara - Estancia Line. | CVIS
4/29/2022 5:22:55 AM | LRCC-04/29/2022 05:17: Weather Update: April 29, 2022; Intertropical Convergence Zone (ITCZ) affecting Mindanao. Northern Mindanao, Caraga, and Davao Region will experience cloudy skies with scattered rainshowers and thunderstorms. Metro Manila and the rest of the country will have partly cloudy to cloudy skies with isolated rainshowers or thunderstorms. [WEBSMS] | CLUZ
4/29/2022 4:01:20 AM | NEGROS ACC: 04/29/2022, 69kV Kabankalan-Sipalay Sub T/L energized at 0344H after completion of activity. | CVIS
4/29/2022 3:48:12 AM | NEGROS ACC: 04/29/2022, 69kV Naga-Overflow line section(8.0MW) de-energized at 0335H to facilitate load shifting back to 69KV Kabankalan-Sipalay Sub TL. | CVIS
4/29/2022 2:17:14 AM | PANAY ACC-04/29/22 02:13: DINGLE SS, Dingle-Natividad 69 kV L (5LI1DIN-NTV), TIME OUT: 02:08:00, TIME IN: 02:12:00, RELAY: Z1, BN, WEATHER: FAIR; Momentary line fault. | CVIS
4/29/2022 12:15:37 AM | LRCC-04/29/2022 00:05: Binan - San Pedro 115kV Line de-energized at 0002H. (Planned Outage) [WEBSMS] | CLUZ
4/29/2022 12:05:39 AM | NEGROS ACC: 04/28/2022, 69kV Naga-Overflow line sections load shifted to 69kV Mabinay-Kabankalan Sub T/L at 2350H. Naga DSW facing Kabankalan opened and Overflow DSW facing Mabinay closed. | CVIS
4/28/2022 11:28:32 PM | NEGROS ACC: 04/28/2022, Emergency shut down of 69kV Kabankalan-Sipalay Sub T/L (16.7MW) at 2324H to conduct L.A. replacement of A-LA(7LI2KAB-SIP)SIP due to sudden increase of leakage current. | CVIS
4/28/2022 7:22:14 PM | PANAY ACC-04/28/22 18:40:PEDC U1 synchronized to the grid at 1836H with an initial load of 8MW | CVIS
4/28/2022 7:09:16 PM | LEYTE ACC-04/28/22: CALBAYOG SS, 69kV Calbayog-Bliss Line re-energized back at 1901H | CVIS
4/28/2022 6:59:13 PM | LEYTE ACC-04/28/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1838H/1848H, on normal flow per RTD | CVIS
4/28/2022 6:59:12 PM | LEYTE ACC-04/28/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1838H/1848H, on normal flow per RTD | CVIS
4/28/2022 6:24:51 PM | NEGROS ACC: 04/28/2022, 69kV Amlan-San Carlos Sub T/L restored at 1814H. | CVIS
4/28/2022 6:24:49 PM | NEGROS ACC: 04/28/2022, 69kV Amlan-San Carlos Sub T/L restored at 1814H. | CVIS
4/28/2022 6:24:48 PM | VRCC-04/28/2022 18:19: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2446MW, PK=2024MW, RR=40MW, NetOpMargin: EVE=382 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 335 MW, TPC = 82 MW [WEBSMS] | CVIS
4/28/2022 6:01:56 PM | LEYTE ACC-04/28/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1750H/1800H, on reverse flow per RTD | CVIS
4/28/2022 5:49:53 PM | NEGROS ACC: 04/28/2022, 69kV Bacolod-San Enrique Sub T/L restored at 1739H . | CVIS
4/28/2022 5:49:51 PM | NEGROS ACC: 04/28/2022, 69kV Bacolod-San Enrique Sub T/L restored at 1739H . | CVIS
4/28/2022 5:37:03 PM | PANAY ACC-04/28/22 17:09: PEDC U1 (83MW), auto-tripped at 1705H, load prior to the tripping: 63MW; cause: under investigation | CVIS
4/28/2022 5:37:01 PM | LRCC-04/28/2022 17:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12342MW, PK=10319MW, RR=396MW, NetOpMargin: EVE=1627 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 540MW, San Gabriel at 400MW, GMEC 2 at 300MW, SCPC 3 at 110MW [WEBSMS] | CLUZ
4/28/2022 5:26:41 PM | NEGROS ACC: 04/28/2022: SIPS activation in Negros area at 1705H, isolating 69kV Bacolod-San Enrique Sub TL(-2.35MW) and 69kV Amlan-San Carlos Sub TL(10.84MW) to prevent overloading of 138kV Cebu-Negros Submarine Cable L2 due to tripping of PEDC U1. CENPRI, ISLASOL II, MONTESOL and SACASUN isolated. | CVIS
4/28/2022 5:26:39 PM | NEGROS ACC: 04/28/2022: SIPS activation in Negros area at 1705H, isolating 69kV Bacolod-San Enrique Sub TL(-2.35MW) and 69kV Amlan-San Carlos Sub TL(10.84MW) to prevent overloading of 138kV Cebu-Negros Submarine Cable L2 due to tripping of PEDC U1. CENPRI, ISLASOL II, MONTESOL and SACASUN isolated. | CVIS
4/28/2022 5:12:45 PM | LRCC-04/28/2022 17:05: Naga-Tayabas 230kV Line 2 restored at 1704H. (Planned Outage) [WEBSMS] | CLUZ
4/28/2022 4:15:14 PM | MRCC-04/28/2022 16:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2842MW, PK=1900MW, RR=56MW, NetOpMargin: EVE=886 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@150MW, Ag5@47MW, Ag6@108MW, Ag7@26MW, Pul4@156MW, MGPP@78MW, STEAG@200MW, TSI@203MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@0MW & MCC@150MW. [WEBSMS] | CMIN
4/28/2022 3:40:08 PM | LEYTE ACC-04/28/22: CALBAYOG SS, 69kV Calbayog-Bliss Line, TIME OUT: 15:22:00, RELAY: NEF1 Low:Trip, phase CN, 21.57kms, load=2.26MW, WEATHER: FAIR | CVIS
4/28/2022 3:40:07 PM | LEYTE ACC-04/28/22: CALBAYOG SS, 69kV Calbayog-Bliss Line, TIME OUT: 15:22:00, RELAY: NEF1 Low:Trip, phase CN, 21.57kms, load=2.26MW, WEATHER: FAIR | CVIS
4/28/2022 3:16:40 PM | PANAY ACC-04/28/22 15:10: PCPC U1 synchronized to the grid at 1508H | CVIS
4/28/2022 3:16:39 PM | PANAY ACC-04/28/22 15:10: PCPC U1 synchronized to the grid at 1508H | CVIS
4/28/2022 3:16:37 PM | PANAY ACC-04/28/22 14:45: Panitan SS, Panitan-Nabas 138kV L2 energized at 1444H | CVIS
4/28/2022 1:02:20 PM | VRCC-04/28/2022 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2596MW, PK=2000MW, RR=40MW, NetOpMargin: PM=556, EVE=331 Highest Unit O/L: TVI U @ 169 MW Derated Plant: EDC = 335 MW, TPC = 82 MW [WEBSMS] | CVIS
4/28/2022 1:02:18 PM | LRCC-04/28/2022 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12686MW, PK=11363MW, RR=433MW, NetOpMargin: PM=890, EVE=1662 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 540MW, San Gabriel at 400MW, GMEC 2 at 300MW, SCPC 3 at 108MW [WEBSMS] | CLUZ
4/28/2022 11:37:30 AM | MRCC-04/28/2022 11:29: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2910MW, PK=2055MW, RR=59MW, NetOpMargin: PM=796, EVE=886 Highest Unit O/L: GNPK U3&U4 @138MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@150MW, Ag5@47MW, Ag6@108MW, Ag7@26MW, Pul4@156MW, MGPP@78MW, STEAG@200MW, TSI@203MW, FDC@ 245.5MW, SMCP@270MW, GNPK@276MW, SEC1@105MW, SEC2@0MW & MCC@150MW. [WEBSMS] | CMIN
4/28/2022 10:49:01 AM | NEGROS ACC: 04/28/2022, 34.5kV Amlan-AHEP line restored at 1039H. | CVIS
4/28/2022 8:49:30 AM | LRCC-04/28/2022 08:48: Malaya Unit 2 online at 0829H. (Unplanned Outage) [WEBSMS] | CLUZ
4/28/2022 6:52:19 AM | LRCC-04/28/2022 06:50: Malaya Unit 2 (75MW) tripped at 0641H. (Unplanned Outage) [WEBSMS] | CLUZ
4/28/2022 6:28:34 AM | LRCC-04/28/2022 06:19: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12924MW, PK=11202MW, RR=433MW, NetOpMargin: AM=1289, PM=1032, EVE=1816 Highest Unit O/L: GNPD 2 at 668MW Derated Plant: GMEC 2 at 300MW, Ilijan at 540MW [WEBSMS] | CLUZ
4/28/2022 6:18:26 AM | LRCC-04/28/2022 06:13: Naga-Tayabas 230kV Line 2 de-energized at 0609H. (Planned Outage) [WEBSMS] | CLUZ
4/28/2022 6:07:29 AM | VRCC-04/28/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2636MW, PK=2168MW, RR=0MW, NetOpMargin: AM=468, PM=596, EVE=371 Highest Unit O/L: TVI Units at 169MW each Derated Plant: EDC at 335MW, TPC at 82MW [WEBSMS] | CVIS
4/28/2022 5:41:56 AM | LRCC-04/28/2022 05:39: Weather Update: April 28, 2022: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 220 km Southwest of Zamboanga City (5.4N, 120.8E). It is embedded along the Intertropical Convergence Zone (ITCZ) affecting Palawan, Visayas and Mindanao. [WEBSMS] | CLUZ
4/28/2022 4:34:45 AM | MRCC-04/28/2022 04:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2948MW, PK=2005MW, RR=80MW, NetOpMargin: AM=863, PM=810, EVE=905 Highest Unit O/L: GNPK U3 and U4 @ 138 MW each. Derated Plant: Ag1@20MW, Ag2@85MW, Ag4@96MW, Ag5@37MW, Ag6@98MW, Ag7@21MW, Pul4@71MW, MGPP@78MW, STEAG@200MW, TSI@135MW, FDC@245.5MW, GNPK@276MW, SMCPC@270MW, MCC@150MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
4/28/2022 1:11:53 AM | NEGROS ACC: 04/28/2022, 34.5kV Amlan-AHEP Line(0.78MW)auto tripped at 0057H with ind.; Z1 BN 16.02KM | CVIS
4/28/2022 1:00:29 AM | NEGROS ACC: 04/28/2022, 69kV Amlan-Siaton Sub T/L restored at 0055H. | CVIS
4/28/2022 12:50:24 AM | NEGROS ACC: 04/28/2022, 69kV Amlan-Siaton Sub T/L (22.87MW) auto-tripped at 0039H with indication Z2, BCN, 28.59km. | CVIS
4/28/2022 12:50:19 AM | LRCC-04/28/2022 00:48: NGCP Calamba-Meralco Calamba 230kV tie line 2 was energized at 0046H. (Planned Outage) [WEBSMS] | CLUZ
4/28/2022 12:25:22 AM | PANAY ACC-04/27/2022: 11:59:00 Nabas SS: 69kv CULASI TL, TIME OUT: 23:56:00, TIME IN: 23:59:00, Load: 2.3mw, TRIP B N 18.78kms, Momentary fault, Weather: Fair | CVIS
4/28/2022 12:01:22 AM | VRCC-04/27/2022 23:53: 69kV Compostela-Consolacion Feeder tripped/restored at 2337H/2349H with 9.8MW load and 50/51 FD 14.3kms phase A indication. [WEBSMS] | CVIS
4/28/2022 12:01:20 AM | LRCC-04/27/2022 23:56: Sual U2 offline 2349H (planned Outage) [WEBSMS] | CLUZ
4/27/2022 10:37:13 PM | LRCC-04/27/2022 22:33: NGCP Calamba-Meralco Calamba 230kV tie line 2 was de-energized at 2232H. (Planned Outage) [WEBSMS] | CLUZ
4/27/2022 8:39:14 PM | LEYTE ACC-04/27/22 20:49:ORMOC CONVERTER STATION SS,350kV Leyte Luzon,Blocked/Deblocked at 2024H/2034H,on normal power flow per RTD. WEATHER: FAIR | CVIS
4/27/2022 6:54:06 PM | LRCC-04/27/2022 18:49: NGCP Calamba-Meralco Calamba 230kV tie line 1 was de-energized at 1847H. (Planned Outage) [WEBSMS] | CLUZ
4/27/2022 6:17:41 PM | LEYTE ACC-04/27/22 18:24:ORMOC CONVERTER STATION SS, 350kV HVDC Leyte-Luzon,Blocked/Deblocked at 1739H/1749H, on reverse power flow per RTD, WEATHER: FAIR | CVIS
4/27/2022 5:57:16 PM | VRCC-04/27/2022 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2372MW, PK=2008MW, RR=40MW, NetOpMargin: EVE=324 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 335 MW, TPC = 82 MW [WEBSMS] | CVIS
4/27/2022 5:43:36 PM | LRCC-04/27/2022 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12326MW, PK=10553MW, RR=417MW, NetOpMargin: EVE=1356 Highest Unit O/L: Sual 1 at 600MW Derated Plant: Ilijan A/B at 540MW, GMEC 2 at 300MW, Sual 2 at 230MW, Pagbilao 2 at 300MW, San Gabriel at 400MW [WEBSMS] | CLUZ
4/27/2022 4:22:22 PM | MRCC-04/27/2022 16:13: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2792MW, PK=1900MW, RR=76MW, NetOpMargin: EVE=816 Highest Unit O/L: GNPK U3 and U4 @ 138 MW each. Derated Plant: Ag1@20MW, Ag2@100MW, Ag4@72MW, Ag5@35MW, Ag6@98MW, Ag7@21MW, Pul4@104MW, MGPP@73MW, STEAG@200MW, TSI@112MW, FDC@245.5MW, GNPK@276MW, SMCPC@270MW, MCC@100MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
4/27/2022 3:38:57 PM | LRCC-04/27/2022 15:36: Balsik 230kV Bus 2 restored at 1534H. (Unplanned Outage) [WEBSMS] | CLUZ
4/27/2022 1:27:51 PM | VRCC-04/27/2022 13:24: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2587MW, PK=2142MW, RR=40MW, NetOpMargin: PM=405, EVE=324 Highest Unit O/L: TVI U @ 169 MW Derated Plant: EDC = 335 MW, TPC = 82 MW [WEBSMS] | CVIS
4/27/2022 1:17:48 PM | LEYTE ACC-04/27/22 13:19:ISABEL SS,Isabel-Tongonan 138 kV L,Energized at 1259H,Pre arranged per PANR No.VRCC-2022-04-0055,WEATHER: FAIR | CVIS
4/27/2022 1:03:26 PM | LRCC-04/27/2022 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12632MW, PK=11450MW, RR=455MW, NetOpMargin: PM=727, EVE=1312 Highest Unit O/L: Sual 1 at 600MW Derated Plant: Ilijan A/B at 540MW, GMEC 2 at 300MW, Sual 2 at 350MW, Dinginin 1 at 501MW, San Gabriel at 400MW [WEBSMS] | CLUZ
4/27/2022 11:43:27 AM | LEYTE ACC-04/27/22 11:53:ORMOC CONVERTER STATION SS,350kV Leyte Luzon, Blocked/Deblocked at 1118H/1129H,on normal power flow per RTD, WEATHER: FAIR | CVIS
4/27/2022 11:32:29 AM | MRCC-04/27/2022 11:22: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2840MW, PK=2025MW, RR=81MW, NetOpMargin: PM=0, EVE=0 Highest Unit O/L: GNPK U3 and U4 @ 138 MW each. Derated Plant: Ag1@20MW, Ag2@100MW, Ag4@72MW, Ag5@35MW, Ag6@98MW, Ag7@21MW, Pul4@107MW, MGPP@73MW, STEAG@200MW, TSI@112MW, FDC@245.5MW, GNPK@276MW, SMCPC@270MW, MCC@100MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
4/27/2022 11:06:14 AM | LEYTE ACC-04/27/22 11:13:ORMOC CONVERTER STATION SS,350kV HVDC Leyte-Luzon, Blocked/Deblocked at 1023H/1033H,on reverse power flow per Visayas requirement,weather:fair | CVIS
4/27/2022 11:06:13 AM | LEYTE ACC-04/27/22 11:07: MARSHALLING SS,EDC-Mahanagdong A unit 1 tripped at 1048H,under assessment WEATHER: FAIR | CVIS
4/27/2022 9:54:42 AM | LRCC-04/27/2022 09:47: Ilijan A1 offline at 0941H. (Unplanned Outage) [WEBSMS] | CLUZ
4/27/2022 9:32:35 AM | LEYTE ACC-04/27/22 09:39: ISABEL SS,Isabel-Tongonan 138 kV L,Deenergized at 0905H,Pre arranged per PANR No.VRCC-2022-04-0055,ETC April 29,2022(0601H/1800H) WEATHER: FAIR | CVIS
4/27/2022 8:25:32 AM | LRCC-04/27/2022 08:24: Balsik 230kV Bus 2 de-energized at 0821H. (Unplanned Outage) [WEBSMS] | CLUZ
4/27/2022 7:58:44 AM | PANAY ACC-04/27/22 07:32: NABAS SS, Caticlan-Malay 69kV L (5LI1CTC-MLA),Load:10MW; TIME OUT: 07:26, TIME IN: 07:32, Emergency isolation due to toppled bamboo pole at 69kV bus of Malay SS | CVIS
4/27/2022 7:58:42 AM | PANAY ACC-04/27/22 07:04: BUENAVISTA SS, Buenavista-GUIMELCO 69kV Line (CO (5LI1BVI-GUI), TIME IN: 06:59:00, Conducted emergency corrective line maintenance along Sta. Barbara- Ingore 69kV Line | CVIS
4/27/2022 7:35:54 AM | PANAY ACC-04/27/22 07:05: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW), TIME IN: 07:00:00, Conducted emergency corrective line maintenance along Sta. Barbara- Ingore 69kV Line | CVIS
4/27/2022 7:35:53 AM | PANAY ACC-04/27/22 07:00: STA. BARBARA SS, Sta. Barbara-Ingore 69 kV Line (5LI1SBA-INR), TIME IN: 06:56:00, Conducted emergency corrective line maintenance. | CVIS
4/27/2022 7:35:51 AM | PANAY ACC-04/27/22 07:00: STA. BARBARA SS, Sta. Barbara-Ingore 69 kV Line (5LI1SBA-INR), TIME IN: 06:56:00, Conducted emergency corrective line maintenance. | CVIS
4/27/2022 6:37:38 AM | LRCC-04/27/2022 06:30: Tayabas-Naga 230kV Line 2 de-energized at 0629H. (Planned Outage) [WEBSMS] | CLUZ
4/27/2022 6:24:11 AM | LRCC-04/27/2022 06:14: Binan - San Pedro 115kV Line restored at 0613H. (Planned Outage) [WEBSMS] | CLUZ
4/27/2022 6:14:09 AM | LRCC-04/27/2022 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13170MW, PK=11141MW, RR=448MW, NetOpMargin: AM=1581, PM=1059, EVE=1776 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SUAL 2 @350MW; ILIJAN A / B @851MW [WEBSMS] | CLUZ
4/27/2022 6:04:10 AM | VRCC-04/27/2022 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2640MW, PK=2147MW, RR=0MW, NetOpMargin: AM=493, PM=445, EVE=364 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 335MW, TPC at 82MW [WEBSMS] | CVIS
4/27/2022 4:40:25 AM | LEYTE ACC-04/27/22 04:45: STA. RITA SS, Sta. Rita - Quinapondan 69kV Line tripped/restored at 0426H/0429H. Load=4.0MW. Weather: Fair | CVIS
4/27/2022 4:26:49 AM | LRCC-04/27/2022 04:17: GNPD Unit 1 online 0416H (Unplanned Outage) [WEBSMS] | CLUZ
4/27/2022 4:02:43 AM | PANAY ACC-04/27/22 03:15: STA. BARBARA SS, Sta. Barbara-Ingore 69 kV Line (5LI1SBA-INR), TIME OUT: 03:13:00, WEATHER: FAIR. Emergency repair of Str. 4HT. | CVIS
4/27/2022 4:02:42 AM | PANAY ACC-04/27/22 03:12: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW), TIME OUT: 03:10:00, RELAY: NONE, WEATHER: FAIR. Emergency repair of str. 4HT along 69kV sta. Barbara - Ingore 69kV Line. | CVIS
4/27/2022 4:02:41 AM | PANAY ACC-04/27/22 03:12: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW), TIME OUT: 03:10:00, RELAY: NONE, WEATHER: FAIR. Emergency repair of str. 4HT along 69kV sta. Barbara - Ingore 69kV Line. | CVIS
4/27/2022 4:02:38 AM | LRCC-04/27/2022 04:01: GNPD Unit 1 (86MW) tripped at 0356H (Unplanned Outage) [WEBSMS] | CLUZ
4/27/2022 3:52:38 AM | PANAY ACC-04/27/22 03:08: BUENAVISTA SS, Buenavista-GUIMELCO 69kV Line (CO (5LI1BVI-GUI), TIME OUT: 03:05:00, RELAY: NONE, WEATHER: FAIR; Emergency repair of str. 4HT along 69kV Sta. Barbara - Ingore Line. | CVIS
4/27/2022 3:05:27 AM | LEYTE ACC-04/27/22 03:09: TGPP, GCGI-TGPP unit #3 cut-in to the system at 0251H. Weather: Fair. | CVIS
4/27/2022 3:05:25 AM | LRCC-04/27/2022 02:59: GNPD Unit 1 online 0252H (Unplanned Outage) [WEBSMS] | CLUZ
4/27/2022 12:44:55 AM | LEYTE ACC-04/27/22 00:45: TGPP, GCGI-TGPP unit #3 tripped at 0026H, under assessment. Gen. Load=37.8MW. Weather: Fair. | CVIS
4/26/2022 11:58:01 PM | LRCC-04/26/2022 23:51: Binan - San Pedro 115kV Line de-energized at 2349H (Planned Outage) [WEBSMS] | CLUZ
4/26/2022 7:39:03 PM | NEGROS ACC: 04/26/2022, 69kV Mabinay-Kabankalan Sub T/L restored at 1933H. URC isolated. | CVIS
4/26/2022 7:15:28 PM | NEGROS ACC: 04/26/2022, 69kV Mabinay-Kabankalan Sub T/L(-12.16MW) auto tripped at 1905H with ind.; Z3 DEF START CN 35.46KM. due to customers(URC) caused outage. | CVIS
4/26/2022 7:15:25 PM | LRCC-04/26/2022 19:05: Mexico-Hermosa 230kV L2 and L1 restored at 1853H and 1854H, respectively (Unplanned Outage). [WEBSMS] | CLUZ
4/26/2022 7:02:05 PM | LRCC-04/26/2022 18:58: Mexico-Hermosa 230kV L1 tripped at 1840H (Unplanned Outage). [WEBSMS] | CLUZ
4/26/2022 6:38:14 PM | LRCC-04/26/2022 18:37: Affected ALD feeders from Meralco and NGCP were restored at 1830H and 1831H, respectively. [WEBSMS] | CLUZ
4/26/2022 6:05:19 PM | VRCC-04/26/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2331MW, PK=1905MW, RR=40MW, NetOpMargin: EVE=386 Highest Unit O/L: TVI units at 169MW each Derated Plant: EDC at 328MW, TPC at 82MW [WEBSMS] | CVIS
4/26/2022 5:51:03 PM | LRCC-04/26/2022 17:42: Balsik 1000MVA T02 restored at 1740H. (Planned Outage) [WEBSMS] | CLUZ
4/26/2022 5:41:03 PM | LRCC-04/26/2022 17:37: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12855MW, PK=10380MW, RR=400MW, NetOpMargin: EVE=2075 Highest Unit O/L: GNPD Unit 1 at 668MW Derated Plant: GMEC 2 at 300MW, Ilijan at 851MW and Sual 2 at 330MW [WEBSMS] | CLUZ
4/26/2022 4:53:56 PM | LEYTE ACC-04/26/22 16:55:ORMOC SS,Ormoc-Tongonan 138 kV L,Energized ,1618H,per Customers WEATHER: RAINY | CVIS
4/26/2022 4:20:13 PM | LRCC-04/26/2022 16:19: Naga-Labo 230kV line 2 was restored at 1616H. (Planned Outage) [WEBSMS] | CLUZ
4/26/2022 3:50:58 PM | LEYTE ACC-04/26/22 15:48:ORMOC SS,138kV Ormoc-Maasin Line 1,energized at 1530H,affected by TROPICAL STORM (``Agaton``) | CVIS
4/26/2022 2:53:50 PM | NEGROS ACC: 04/26/2022, 69kV Cadiz-San Carlos Sub T/L restored at 1437H. Customer owned and maintained line. | CVIS
4/26/2022 2:43:47 PM | NEGROS ACC: 04/26/2022, 69kV Cadiz-San Carlos Sub T/L (-2.62MW) auto-tripped at 1423H with indication: Z2 Delay AB , 32.11km.SACASOL & SCBP isolated. Customer owned and maintained line. | CVIS
4/26/2022 2:25:58 PM | LRCC-04/26/2022 14:22: GNPD Unit 2 online 1409H. (Commissioning test) [WEBSMS] | CLUZ
4/26/2022 1:16:38 PM | LRCC-04/26/2022 13:06: Balsik 1000MVA T02 was de-energized at 1304H. (Planned Outage) [WEBSMS] | CLUZ
4/26/2022 1:03:14 PM | LEYTE ACC-04/26/22 12:52: ORMOC SS, 138kV Ormoc-Tongonan line energized at 1250H. WEATHER: FAIR | CVIS
4/26/2022 1:03:13 PM | VRCC-04/26/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2506MW, PK=2169MW, RR=40MW, NetOpMargin: PM=297, EVE=386 Highest Unit O/L: TVI Units @ 169MW each Derated Plant: EDC at 328MW, TPC at 82MW [WEBSMS] | CVIS
4/26/2022 1:03:12 PM | LEYTE ACC-04/26/22 12:38: CALBAYOG SS, 69kV Palanas Cara-Allen-Lao-ang line re-energized at 1234H. WEATHER: FAIR | CVIS
4/26/2022 1:03:09 PM | LRCC-04/26/2022 12:41: Balsik 1000MVA T01 restored at 1237H. (Planned Outage) [WEBSMS] | CLUZ
4/26/2022 1:03:08 PM | LRCC-04/26/2022 12:12: GNPD Unit 2 online at 1210H. (Commissioning Test) [WEBSMS] | CLUZ
4/26/2022 10:52:45 AM | LEYTE ACC-04/26/22 10:40: CALBAYOG SS, 69kV Palanas Cara-Allen-Lao-ang line tripped at 1036H, phase CN, Z1, 24.36kms., load=17.63MW. Reclose attempt failed with same indications. WEATHER: FAIR | CVIS
4/26/2022 9:43:41 AM | LEYTE ACC-04/26/22 09:33: 350kV HVDC manually blocked/deblocked at 0916H/0926H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
4/26/2022 9:20:25 AM | LRCC-04/26/2022 09:10: For info: Balsik 1000MVA T01 was de-energized at 0804H. (Planned Outage) [WEBSMS] | CLUZ
4/26/2022 7:33:00 AM | LRCC-04/26/2022 07:32: System Advisory: ALD affected feeders of Meralco and NGCP were restored at 0727H. [WEBSMS] | CLUZ
4/26/2022 6:12:45 AM | LRCC-04/26/2022 06:12: Naga-Labo 230kV line 2 was de-energized at 0609H. (Planned Outage) [WEBSMS] | CLUZ
4/26/2022 5:59:54 AM | VRCC-04/26/2022 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2657MW, PK=2189MW, RR=40MW, NetOpMargin: AM=428, PM=297, EVE=386 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 328 MW, TPC = 82 MW [WEBSMS] | CVIS
4/26/2022 5:49:15 AM | LRCC-04/26/2022 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13079MW, PK=10556MW, RR=426MW, NetOpMargin: AM=2097, PM=1771, EVE=2259 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 360MW [WEBSMS] | CLUZ
4/26/2022 5:39:14 AM | LRCC-04/26/2022 05:38: Bayombong-Santiago 230kV Line 1 restored at 0537H. (Planned Outage) [WEBSMS] | CLUZ
4/26/2022 5:12:25 AM | LRCC-04/26/2022 05:04: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
4/26/2022 2:51:48 AM | LEYTE ACC-04/26/22 02:40: STA. RITA SS, 69kV Sta Rita-Quinapondan line tripped at 0229H, phase BN, 46.54kms., load=4.3MW. Restored at 0231H. WEATHER: FAIR | CVIS
4/26/2022 12:21:13 AM | LRCC-04/26/2022 00:13: Las Pinas (Zapote) 300MVA T02 restored at 0010H. (Unplanned Outage) [WEBSMS] | CLUZ
4/26/2022 12:11:07 AM | LRCC-04/26/2022 00:10: Dinginin (GNPD) Unit 1 online at 0007H. (Unplanned Outage) [WEBSMS] | CLUZ
4/26/2022 12:07:39 AM | LRCC-04/25/2022 23:59: Las Pinas (Zapote) 300MVA T03 restored at 2353H. (Unplanned Outage) [WEBSMS] | CLUZ
4/25/2022 10:10:28 PM | LRCC-04/25/2022 22:07: Bayombong-Santiago 230kV Line 1 de-energized at 2207H. (Planned Outage) [WEBSMS] | CLUZ
4/25/2022 9:27:01 PM | LEYTE ACC-04/25/22 21:38: 350kV HVDC manually blocked/deblocked at 2109H/2119H on normal power flow per RTD. Weather: Cloudy. | CVIS
4/25/2022 6:05:54 PM | VRCC-04/25/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2331MW, PK=1950MW, RR=23MW, NetOpMargin: EVE=358 Highest Unit O/L: TVI units at 169MW each Derated Plant: EDC at 328MW, TPC at 82MW [WEBSMS] | CVIS
4/25/2022 5:52:30 PM | LRCC-04/25/2022 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11904MW, PK=10292MW, RR=301MW, NetOpMargin: EVE=1388 Highest Unit O/L: Sual 1 at 600MW Derated Plant: Sual 2 at 330MW, GMEC 2 at 300MW and Ilijan at 851MW [WEBSMS] | CLUZ
4/25/2022 5:42:28 PM | LRCC-04/25/2022 17:40: Concepcion-Mexico 230kV line 2 was restored at 1740H. (Planned Outage) [WEBSMS] | CLUZ
4/25/2022 5:19:02 PM | LRCC-04/25/2022 17:16: Santiago-NIA Baligatan 69kV line energized at 1712H. (Planned Outage) [WEBSMS] | CLUZ
4/25/2022 5:05:37 PM | LRCC-04/25/2022 16:58: Naga-Labo 230kV line 1 was restored at 1658H. (Planned Outage) [WEBSMS] | CLUZ
4/25/2022 1:34:20 PM | LRCC-04/25/2022 13:31: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12418MW, PK=11119MW, RR=353MW, NetOpMargin: PM=946, EVE=1582 Highest Unit O/L: Sual 1 at 600MW Derated Plant: Sual 2 at 330MW, GMEC 2 at 300MW and Ilijan at 851MW [WEBSMS] | CLUZ
4/25/2022 1:07:29 PM | VRCC-04/25/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2506MW, PK=2163MW, RR=22MW, NetOpMargin: PM=321, EVE=358 Highest Unit O/L: TVI units at 169MW each Derated Plant: EDC at 328MW, TPC at 82MW [WEBSMS] | CVIS
4/25/2022 10:45:31 AM | LEYTE ACC-04/25/22 10:29: ORMOC OCS, 350kV HVDC manually blocked/deblocked at 1015H/1025H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
4/25/2022 8:13:15 AM | LRCC-04/25/2022 08:12: Santiago-NIA Baligatan 69kV line de-energized at 0804H. (Planned Outage) [WEBSMS] | CLUZ
4/25/2022 7:14:18 AM | LRCC-04/25/2022 07:08: Concepcion-Mexico 230kV line 2 was de-energized at 0706H. (Planned Outage) [WEBSMS] | CLUZ
4/25/2022 6:26:10 AM | LRCC-04/25/2022 06:18: Naga-Labo 230kV line 1 was de-energized at 0614H. (Planned Outage) [WEBSMS] | CLUZ
4/25/2022 6:05:54 AM | VRCC-04/25/2022 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2657MW, PK=2136MW, RR=9MW, NetOpMargin: AM=512, PM=334, EVE=381 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 328 MW, TPC = 82 MW [WEBSMS] | CVIS
4/25/2022 5:51:36 AM | LRCC-04/25/2022 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12596MW, PK=10848MW, RR=329MW, NetOpMargin: AM=1419, PM=871, EVE=1452 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GMEC 2 @300MW; SUAL 2 @400MW; ILJJAN A / B @851MW [WEBSMS] | CLUZ
4/25/2022 4:17:46 AM | LRCC-04/25/2022 04:12: Quezon (Balintawak) 300MVA T02 restored at 0408H (Planned Outage) [WEBSMS] | CLUZ
4/25/2022 1:20:26 AM | NEGROS ACC: 04/25/2022, 69kV Guihulngan -San Carlos Line section energized at 0109H back to Amlan SS | CVIS
4/25/2022 12:23:12 AM | NEGROS ACC: 04/25/2022, 69KV Guihulngan - San Carlos Line section (4.5 MW) de-energized at 0008H to conduct hotspot correction at Guihulngan 3-way switch | CVIS
4/24/2022 11:46:19 PM | LRCC-04/24/2022 23:39: Quezon (Balintawak) 300MVA T02 de-energized at 2337H (Planned Outage) [WEBSMS] | CLUZ
4/24/2022 10:36:00 PM | VRCC-04/24/2022 22:33: Cebu-Quiot 138kV line energized at 2145H, Cebu TR#4 energized also at 2227H. [WEBSMS] | CVIS
4/24/2022 8:54:34 PM | VRCC-04/24/2022 20:51: 34.5KV Sangi-CarCon line 3 manually open at 1946H to correct Hot spot detected. [WEBSMS] | CVIS
4/24/2022 6:41:32 PM | NEGROS ACC: 04/24/2022, 69KV Guihulngan - San Carlos Line section load shifted to 69kV Cadiz-San Carlos Sub T/L at 1825H. | CVIS
4/24/2022 6:08:06 PM | VRCC-04/24/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2331MW, PK=1822MW, RR=0MW, NetOpMargin: EVE=509 Highest Unit O/L: TVI units at 169MW each Derated Plant: Derated Plant: EDC at 328MW, TPC at 82MW [WEBSMS] | CVIS
4/24/2022 5:54:41 PM | LRCC-04/24/2022 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12073MW, PK=9510MW, RR=379MW, NetOpMargin: EVE=2204 Highest Unit O/L: Sual 1 at 600MW Derated Plant: GMEC 2 at 300MW; SUAL 2 at 350MW; ILIJAN A / B at 851MW [WEBSMS] | CLUZ
4/24/2022 5:31:28 PM | PANAY ACC-04/24/22 17:20: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST), TIME IN: 05:17:00, WEATHER: FAIR. Pre-Arranged Maintenance Activities. | CVIS
4/24/2022 5:31:26 PM | PANAY ACC-04/24/22 17:18: PANIT-AN SS, Panit-an-Sara 69 kV Line (5LI1PNT-SAR), TIME IN: 17:15:00, RELAY: NONE, WEATHER: FAIR. Pre-Arranged Maintenance Activities. | CVIS
4/24/2022 5:31:24 PM | LRCC-04/24/2022 17:24: Naga-Tayabas 230kV line 2 was restored at 1724H. (Planned Outage) [WEBSMS] | CLUZ
4/24/2022 5:21:15 PM | PANAY ACC-04/24/22 17:04: PANIT-AN SS, Panit-an-Sara 69 kV Line (5LI1PNT-SAR), TIME OUT: 17:00:00, RELAY: NONE, WEATHER: FAIR. Pre-Arranged Maintenance Activities. | CVIS
4/24/2022 5:11:08 PM | NEGROS ACC: 04/24/2022, 69kV Bindoy-San Carlos line section (0.7 MW) auto-tripped at 1646H with indication Z3 DEF START BN,100.3 km. SACASUN(4.19MW) isolated. | CVIS
4/24/2022 5:11:07 PM | PANAY ACC-04/24/22 17:04: PANIT-AN SS, Panit-an-Sara 69 kV Line (5LI1PNT-SAR), TIME OUT: 17:00:00, RELAY: NONE, WEATHER: FAIR. Pre-Arranged Maintenance Activities. | CVIS
4/24/2022 5:06:31 PM | PANAY ACC-04/24/22 16:52: CONCEPCION S/S SS, Concepcion 138/69/13.8 kV T1 (50MVA) (7XF01CNE), TIME OUT: 06:51:00, TIME IN: 16:49:00, RELAY: NONE, WEATHER: FAIR.Pre-arranged Maintenance Activities. | CVIS
4/24/2022 4:43:05 PM | NEGROS ACC: 04/24/2022, 69kV Amlan-Bindoy-San Carlos Sub TL energized at 1627H after completion of maintenance activity. | CVIS
4/24/2022 4:19:38 PM | NEGROS ACC: 04/24/2022, 69KV Guihulngan -San Carlos Line section(4.4MW) de-energize at 1609H to facilitate load shift back to 69kV Amlan-Bindoy-San Carlos Sub TL. | CVIS
4/24/2022 3:59:33 PM | LRCC-04/24/2022 15:56: Binga-Nagsaag 230kV line 2 was restored at 1554H. (Planned Outage) [WEBSMS] | CLUZ
4/24/2022 3:56:08 PM | LRCC-04/24/2022 15:50: Hermosa-Mexico 230kV line 2 was restored at 1548H. (Planned Outage) [WEBSMS] | CLUZ
4/24/2022 1:25:28 PM | LRCC-04/24/2022 13:16: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12668MW, PK=8534MW, RR=351MW, NetOpMargin: PM=3783, EVE=2738 Highest Unit O/L: Sual 1 at 600MW Derated Plant: GMEC 2 @300MW; SUAL 2 @350MW; ILIJAN A / B @851MW [WEBSMS] [WEBSMS] | CLUZ
4/24/2022 1:14:12 PM | LRCC-04/24/2022 13:10: Nagsaag-Binga 230kV line 2 was de-energized at 1308H. (Planned Outage) [WEBSMS] | CLUZ
4/24/2022 1:02:01 PM | VRCC-04/24/2022 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2506MW, PK=1614MW, RR=0MW, NetOpMargin: PM=852, EVE=509 Highest Unit O/L: TVI units at 169MW each Derated Plant: EDC at 328MW, TPC at 82MW [WEBSMS] | CVIS
4/24/2022 12:48:35 PM | LRCC-04/24/2022 12:46: Bayombong-Santiago 230kV line 2 new M1 and M2 protection commissioning was completed at 1241H. [WEBSMS] | CLUZ
4/24/2022 12:24:16 PM | LRCC-04/24/2022 12:18: Hermosa-Mexico 230kV line 2 was de-energized at 1218H. (Planned Outage) [WEBSMS] | CLUZ
4/24/2022 12:14:12 PM | PANAY ACC-04/24/22 11:35: DINGLE SS, Dingle-Panit-an 138 kV L1 (7LI1DIN-PNT), TIME IN: 11:34:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/24/2022 12:14:10 PM | PANAY ACC-04/24/22 06:09: DINGLE SS, Dingle-Panit-an 138 kV L1 (7LI1DIN-PNT), TIME OUT: 06:08:00, WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
4/24/2022 12:14:08 PM | LRCC-04/24/2022 12:07: Bayombong-Santiago 230kV line 2 was looped at 1203H. (On-going commissioning of M1 and M2 protection) [WEBSMS] | CLUZ
4/24/2022 12:14:06 PM | LRCC-04/24/2022 12:01: Binga-Nagsaag 230kV line 1 was restored at 1158H. (Planned Outage) [WEBSMS] | CLUZ
4/24/2022 11:34:32 AM | LRCC-04/24/2022 11:25: Mexico-Hermosa 230kV line 1 restored at 1122H. (Planned Outage) [WEBSMS] | CLUZ
4/24/2022 11:11:03 AM | NEGROS ACC: 04/24/2022, 69kV Sipalay-Mambaroto Sub T/L energized at 1107H after completion of activity. | CVIS
4/24/2022 8:50:33 AM | NEGROS ACC: 04/24/2022, 69KV Guihulngan - San Carlos Line section load shifted to 69kV Cadiz-San Carlos Sub T/L at 0833H. | CVIS
4/24/2022 8:40:23 AM | NEGROS ACC: 04/24/2022, 69kV Sipalay-Mambaroto Sub T/L(4.06MW) de-energized at 0804H to conduct hotspot correction at T-conductor support joint betwwen 5Z-02DS05SIP and 5Z-02DS23SIP. | CVIS
4/24/2022 8:18:43 AM | LRCC-04/24/2022 08:12: Binga-Nagsaag 230kV line 1 was de-energized at 0810H. (Planned Outage) [WEBSMS] | CLUZ
4/24/2022 7:16:37 AM | NEGROS ACC: 04/24/2022, 69kV Amlan-Bindoy-San Carlos Sub TL (8.23MW) de-energized at 0700H to conduct woodpole replacement and and correction of defects at the affected HVEs including protection and secondary devices.Sacasun (4.0MW) and Montesol(1.22MW) isolated. | CVIS
4/24/2022 7:06:34 AM | NEGROS ACC: 04/24/2022, 69kV Amlan-Bindoy-San Carlos Sub TL (8.23MW) de-energized at 0700H to conduct woodpole replacement and and correction of defects at the affected HVEs including protection and secondary devices.Sacasun (4.0MW) and Montesol(1.22MW) isolated. | CVIS
4/24/2022 6:54:16 AM | PANAY ACC-04/24/22 06:44: PANIT-AN SS, Panit-an-Sara 69 kV Line (5LI1PNT-SAR), TIME IN: 06:43:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/24/2022 6:43:08 AM | LRCC-04/24/2022 06:34: Mexico-Hermosa 230kV line 1 de-energized at 0629H. (Planned Outage) [WEBSMS] | CLUZ
4/24/2022 6:29:45 AM | PANAY ACC-04/24/22 06:24: PANIT-AN SS, Panit-an-Sara 69 kV Line (5LI1PNT-SAR), TIME OUT: 06:23:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/24/2022 6:29:44 AM | PANAY ACC-04/24/22 06:22: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME IN: 06:21:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/24/2022 6:19:42 AM | PANAY ACC-04/24/22 06:11: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST), TIME OUT: 06:10:00, WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
4/24/2022 6:19:39 AM | LRCC-04/24/2022 06:17: Naga-Tayabas 230kV line 2 was de-energized at 0617H. (Planned Outage) [WEBSMS] | CLUZ
4/24/2022 6:09:35 AM | LRCC-04/24/2022 06:05: Las Pinas - Dasmarinas 230kV Line 2 & Las Pinas 300MVA T04 restored at 0600H & 0605H, respectively (Unplanned Outage) [WEBSMS] | CLUZ
4/24/2022 6:04:30 AM | VRCC-04/24/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2657MW, PK=1610MW, RR=40MW, NetOpMargin: AM=1007, PM=892, EVE=509 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 328, TPC at 82 MW [WEBSMS] | CVIS
4/24/2022 5:54:21 AM | LRCC-04/24/2022 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12766MW, PK=8585MW, RR=350MW, NetOpMargin: AM=3831, PM=3366, EVE=2524 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GMEC 2 @300MW; SUAL 2 @400MW; ILIJAN A / B @851MW [WEBSMS] | CLUZ
4/24/2022 5:44:15 AM | PANAY ACC-04/24/22 05:43: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME IN: 05:42:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/24/2022 5:30:49 AM | PANAY ACC-04/24/22 05:30: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 05:29:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/24/2022 5:30:48 AM | PANAY ACC-04/24/22 05:10: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME OUT: 05:09:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/24/2022 5:07:20 AM | VRCC-04/24/2022 05:06: 100 MVA TR4 at Cebu SS de-energized at 0503H, VPD request under CNP3P3, ETC: 2355H [WEBSMS] | CVIS
4/24/2022 3:20:11 AM | PANAY ACC-04/24/22 02:48: BUENAVISTA SS, Buenavista-GUIMELCO 69kV Line (CO (5LI1BVI-GUI), TIME OUT: 02:43:00, TIME IN: 02:47:00, WEATHER: FAIR; To facilitate request of SB SS to conduct Tap change of 50MA TR#1 and 50MVA TR#2 form tap 14 to Tap 17. | CVIS
4/24/2022 3:20:10 AM | PANAY ACC-04/24/22 02:48: STA. BARBARA SS, Sta. Barbara-Ingore 69 kV Line (5LI1SBA-INR), TIME OUT: 02:43:00, TIME IN: 02:47:00, WEATHER: FAIR; To facilitate request of SB SS to conduct Tap change of 50MA TR#1 and 50MVA TR#2 form tap 14 to Tap 17. | CVIS
4/24/2022 2:33:14 AM | PANAY ACC-04/24/22 02:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME OUT: 02:13:00, TIME IN: 02:18:00, WEATHER: FAIR; To facilitate request of SB SS to conduct Tap change of 50MA TR#1 and 50MVA TR#2 form tap 14 to Tap 17. | CVIS
4/24/2022 12:34:07 AM | LRCC-04/24/2022 00:31: Las Pinas 300MVA T04 & Las Pinas - Dasmarinas 230kV Line 2 de-energized at 0025H & 0031H, respectively (Unplanned Outage) [WEBSMS] | CLUZ
4/23/2022 8:07:18 PM | LRCC-04/23/2022 20:03: San Jose 750MVA T04 restored at 2002H (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 8:07:15 PM | LRCC-04/23/2022 20:01: GNPD Unit 2 online at 1959H (Commissioning Test). [WEBSMS] | CLUZ
4/23/2022 7:29:55 PM | LEYTE ACC-04/23/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1915H/1925H, on normal flow per RTD | CVIS
4/23/2022 7:29:54 PM | LEYTE ACC-04/23/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1915H/1925H, on normal flow per RTD | CVIS
4/23/2022 7:19:49 PM | LRCC-04/23/2022 19:14: Lumban - Malaya 230kV line 2 was restored at 1913H (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 6:32:17 PM | LEYTE ACC-04/23/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1811H/1821H, on reverse flow per RTD | CVIS
4/23/2022 6:32:15 PM | LEYTE ACC-04/23/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1811H/1821H, on reverse flow per RTD | CVIS
4/23/2022 6:19:16 PM | VRCC-04/23/2022 18:11: 69KV Colon- Sibonga line energized @1757H. [WEBSMS] | CVIS
4/23/2022 6:09:12 PM | LRCC-04/23/2022 18:05: Naga-Tayabas 230kV line 2 was restored at 1804H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 5:58:44 PM | VRCC-04/23/2022 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2435MW, PK=1929MW, RR=0MW, NetOpMargin: EVE=506 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 390 MW, TPC = 82 MW [WEBSMS] | CVIS
4/23/2022 5:33:07 PM | LRCC-04/23/2022 17:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12024MW, PK=9920MW, RR=379MW, NetOpMargin: EVE=1725 Highest Unit O/L: Sual 1 at 600MW Derated Plant: Calaca 1 @220MW, Sual 2 @380MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
4/23/2022 5:02:58 PM | LRCC-04/23/2022 17:02: San Jose 115kV Bus 2 was energized at 1701H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 4:19:28 PM | PANAY ACC-04/23/22 16:18: NABAS SS, Nabas-Ibajay 69 kV Line, TIME IN: 04:08:00, Facilitate load transfer of AKELCO Andagao SS & Altavas SS from Panit-an SS to Nabas SS. | CVIS
4/23/2022 4:19:25 PM | LRCC-04/23/2022 16:16: Balsik-Hermosa 230kV tie line 1 was restored at 1614H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 4:16:01 PM | LRCC-04/23/2022 16:09: Balsik 230kV Bus 1 was energized at 1609H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 3:55:58 PM | PANAY ACC-04/23/22 15:25: NABAS SS, Nabas-Ibajay 69 kV Line, TIME OUT: 03:14:00, Load: 4.5mw, Pre arranged maintenance, WEATHER: FAIR | CVIS
4/23/2022 3:42:36 PM | PANAY ACC-04/23/22 15:28: PANIT-AN SS, Panit-an-Andagao 69 kV Line, TIME OUT: 03:13:00, TIME IN: 03:26:00, Load: 28.7mw, Load transfer of AKELCO Altavas & Andagao SS from Panit-an SS to Nabas SS. | CVIS
4/23/2022 2:32:18 PM | NEGROS ACC: 04/23/2022, 34.5kV Amlan-AHEP Line energized at 1405H after completion of maintenance activities | CVIS
4/23/2022 1:29:10 PM | PANAY ACC-04/23/22 13:27: DINGLE SS, Dingle-Calinog 69KV (5LI1DIN-CLI), TIME IN: 13:24:00, RELAY: Z1, A - N, 13.2Km., WEATHER: FAIR. Cause under investigation. | CVIS
4/23/2022 1:29:08 PM | PANAY ACC-04/23/22 13:27: DINGLE SS, Dingle-Calinog 69KV (5LI1DIN-CLI), TIME IN: 13:24:00, RELAY: Z1, A - N, WEATHER: FAIR. Cause under investigation. | CVIS
4/23/2022 1:29:07 PM | PANAY ACC-04/23/22 13:16: DINGLE SS, Dingle-Calinog 69KV (5LI1DIN-CLI)(5.7MW), TIME OUT: 13:13:00, RELAY: Z1, A - N, WEATHER: FAIR. Cause under investigation. | CVIS
4/23/2022 1:19:04 PM | PANAY ACC-04/23/22 13:16: DINGLE SS, Dingle-Calinog 69KV (5LI1DIN-CLI)(5.7MW), TIME OUT: 13:13:00, RELAY: Z1, A - N, WEATHER: FAIR. Cause under investigation. | CVIS
4/23/2022 1:19:03 PM | VRCC-04/23/2022 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2706MW, PK=1769MW, RR=40MW, NetOpMargin: PM=937, EVE=506 Highest Unit O/L: TVI U @ 169 MW Derated Plant: EDC = 390 MW, TPC = 82 MW [WEBSMS] | CVIS
4/23/2022 1:05:41 PM | LRCC-04/23/2022 13:03: GNPD Unit 2 online at 1302H. (Commissioning Test) [WEBSMS] | CLUZ
4/23/2022 1:05:39 PM | LRCC-04/23/2022 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12506MW, PK=9941MW, RR=391MW, NetOpMargin: PM=2174, EVE=1652 Highest Unit O/L: Sual 1 at 600MW Derated Plant: Calaca 1 @220MW, Sual 2 @380MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
4/23/2022 12:42:42 PM | LRCC-04/23/2022 12:36: GNPD Unit 2 offline at 1228H. (Under Commissioning Test) [WEBSMS] | CLUZ
4/23/2022 12:32:10 PM | LRCC-04/23/2022 12:24: Correction: GNPD Unit 2 synchronized at 1221H. (Under Commissioning Test) [WEBSMS] | CLUZ
4/23/2022 12:32:08 PM | LRCC-04/23/2022 12:23: GNPD Unit 1 synchronized at 1221H. (Under Commissioning Test) [WEBSMS] | CLUZ
4/23/2022 11:56:33 AM | LEYTE ACC-04/23/22: GCGI-TGPP, Unit #3 cut-in at 0909H | CVIS
4/23/2022 11:56:32 AM | LEYTE ACC-04/23/22: GCGI-TGPP, Unit #3 cut-in at 0909H | CVIS
4/23/2022 11:56:30 AM | LEYTE ACC-04/23/22: PARANAS SS, 69kV Paranas-Borongan-Quinapondan Line back to normal configuration at 1049H | CVIS
4/23/2022 11:56:29 AM | LEYTE ACC-04/23/22: PARANAS SS, 69kV Paranas-Borongan-Quinapondan Line back to normal configuration at 1049H | CVIS
4/23/2022 11:56:28 AM | LEYTE ACC-04/23/22: ORMOC CS, 350kV HVDC manually deblocked at 1141H (pre-arranged activity completed), on normal flow per RTD | CVIS
4/23/2022 10:44:54 AM | PANAY ACC-04/23/22 10:42: PANIT-AN SS, Sigma-Dao 69 kV L (CO) (5LI1SGM-DAX), TIME IN: 10:40:00, WEATHER: FAIR. CAPELCO PMS of their 69kV Sigma - Dao Line. | CVIS
4/23/2022 9:58:22 AM | LEYTE ACC-04/23/22: GCGI-TGPP, Unit #3 cut-in to system at 0909H | CVIS
4/23/2022 9:58:21 AM | LEYTE ACC-04/23/22: PARANAS SS, 69kV Taft Feeder re-energized up to ABS Nato at 0943H | CVIS
4/23/2022 9:47:56 AM | LRCC-04/23/2022 09:38: Santiago-Magat 230kV line 2 was restored at 0937H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 9:14:26 AM | LEYTE ACC-04/23/22: PARANAS SS, 69kV Paranas-Borongan-Quinapondan Line, sustained, TIME OUT: 09:02:00, RELAY: phase CN, 116.99kms, load=7.93MW, WEATHER: FAIR | CVIS
4/23/2022 9:11:03 AM | LEYTE ACC-04/23/22: PARANAS SS, 69kV Paranas-Borongan-Quinapondan Line, sustained, TIME OUT: 09:02:00, RELAY: phase CN, 116.99kms, load=7.93MW, WEATHER: FAIR | CVIS
4/23/2022 8:37:38 AM | LEYTE ACC-04/23/22: ORMOC CS, 350kV HVDC manually blocked at 0829H for scheduled corrective maintenance activity | CVIS
4/23/2022 8:37:35 AM | LRCC-04/23/2022 08:29: Balsik-Hermosa 230kV tie line 1 was de-energized at 0827H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 8:14:06 AM | LRCC-04/23/2022 08:10: Balsik 230kV Bus 1 was de-energized at 0806H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 7:40:36 AM | LEYTE ACC-04/23/22: GCGI-TGPP, Unit #1 cut-in at 0722H | CVIS
4/23/2022 7:40:34 AM | LEYTE ACC-04/23/22: GCGI-TGPP, Unit #1 cut-in at 0722H | CVIS
4/23/2022 7:35:36 AM | LRCC-04/23/2022 07:34: San Jose 115kV Bus 2 was de-energized at 0733H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 7:11:31 AM | LRCC-04/23/2022 07:08: Lumban-Malaya 230kV line 2 was de-energized at 0706H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 7:01:32 AM | LEYTE ACC-04/23/22: GCGI-TGPP, Unit #2 cut-in at 0656H | CVIS
4/23/2022 7:01:30 AM | LEYTE ACC-04/23/22: GCGI-TGPP, Unit #2 cut-in at 0656H | CVIS
4/23/2022 7:01:27 AM | LRCC-04/23/2022 06:56: Santiago-Bayombong 230kV line 2 was de-energized at 0655H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 6:50:59 AM | LRCC-04/23/2022 06:50: San Jose 750MVA T04 was de-energized at 0646H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 6:47:29 AM | LRCC-04/23/2022 06:39: Santiago-Magat 230kV line 2 was de-energized at 0636H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 6:37:33 AM | VRCC-04/23/2022 06:34: 5MVA Transformer Medellin Ss de-energized at 0618H, pre-arranged activity. [WEBSMS] | CVIS
4/23/2022 6:27:30 AM | NEGROS ACC: 04/23/2022, 34.5KV Amlan-AHEP Line(0.68MW) de-energized at 0610H due to PMS. | CVIS
4/23/2022 6:27:29 AM | PANAY ACC-04/23/22 06:13: NABAS SS, Nabas -Ibajay 69 kV Line (5LI1NBS-SPN), TIME IN:0611H , Pre-arranged maintenance | CVIS
4/23/2022 6:27:27 AM | PANAY ACC-04/23/22 06:13: NABAS SS, Nabas -Ibajay 69 kV Line (5LI1NBS-SPN), TIME IN:0611H , Pre-arranged maintenance | CVIS
4/23/2022 6:27:26 AM | PANAY ACC-04/23/22 05:51: PANIT-AN SS, Panit-an-Sapian- Andagao 69 kV Line (5LI1PNT-SPN), TIME IN: 05:49:00,Pre-arranged maintenance | CVIS
4/23/2022 6:20:23 AM | LRCC-04/23/2022 06:18: Naga-Tayabas 230kV line 2 was de-energized at 0617H. (Planned Outage) [WEBSMS] | CLUZ
4/23/2022 6:10:23 AM | VRCC-04/23/2022 06:07: 69kV Naga-Sibonga line de-energized at 0603H, pre-arranged activity. [WEBSMS] | CVIS
4/23/2022 6:10:22 AM | VRCC-04/23/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2618MW, PK=1782MW, RR=40MW, NetOpMargin: AM=796, PM=777, EVE=346 Highest Unit O/L: TVI at 169MW each Derated Plant: EDC at 390MW, TPC at 82MW [WEBSMS] | CVIS
4/23/2022 5:57:56 AM | LRCC-04/23/2022 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12437MW, PK=9676MW, RR=388MW, NetOpMargin: AM=2373, PM=2034, EVE=1869 Highest Unit O/L: Sual 1 @600MW Derated Plant: Calaca 1 @220MW, Sual 2 @380MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
4/23/2022 5:43:14 AM | PANAY ACC-04/23/22 05:37: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN), Load:3.0MW TIME OUT: 05:35:00, Pre-arranged maintenance | CVIS
4/23/2022 5:32:54 AM | PANAY ACC-04/23/22 05:15: PANIT-AN SS, Sigma-Dao 69 kV L (CO) (5LI1SGM-DAX), TIME OUT: 05:10:00,Facilitated request of CAPELCO to conduct PMS at their 69kV line; ETR:1200H | CVIS
4/23/2022 5:32:52 AM | PANAY ACC-04/23/22 05:13: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN),Load:21.9MW, TIME OUT: 05:10:00, Pre-arranged maintenance | CVIS
4/23/2022 5:32:51 AM | PANAY ACC-04/23/22 05:13: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN),Load:21.9MW, TIME OUT: 05:10:00, Pre-arranged maintenance | CVIS
4/23/2022 5:32:49 AM | PANAY ACC-04/23/22 05:13: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN),Load:21.9MW, TIME OUT: 05:10:00, Pre-arranged maintenance | CVIS
4/23/2022 5:32:48 AM | LRCC-04/23/2022 05:26: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
4/23/2022 5:04:11 AM | LEYTE ACC-04/23/22 05:00: MAASIN SS, 69kV Maasin-Baybay line de-energized at 0403H, pre arranged activity. Re-energized at 0455H. WEATHER: FAIR | CVIS
4/23/2022 1:46:35 AM | LEYTE ACC-04/23/22 01:40: TGPP, GCGI-TGPP unit no.1 & 2 simultaneous tripped at 0130H, total load=74.75. WEATHER: FAIR | CVIS
4/23/2022 12:02:47 AM | LEYTE ACC-04/23/22 00:00: TGPP, GCGI-TGPP unit 2 cut-in to the system at 2350H. WEATHER: FAIR | CVIS
4/22/2022 11:36:15 PM | LEYTE ACC-04/22/22 23:35: TGPP, GCGI-TGPP unit no. 1 cut-in to the system at 2331H. WEATHER: FAIR | CVIS
4/22/2022 10:48:46 PM | LEYTE ACC-04/22/22 22:09: ORMOC SS, 69kV Ormoc-Lemon-Tolosa-San Isidro line back to normal configuration at 2202H. WEATHER: FAIR | CVIS
4/22/2022 8:28:02 PM | LRCC-04/22/2022 20:26: For Info: Commissioning of Mariveles - GNPD 500kV L2 completed at 1810H. [WEBSMS] | CLUZ
4/22/2022 7:54:20 PM | LEYTE ACC-04/22/22 20:03: CALBAYOG SS, Palanas-Catarman/Allen-Lao-ang 69kV Line re-energized at 1945H. 69kV Catarman Feeder back to its normal line configuration. Weather: Fair. | CVIS
4/22/2022 7:07:27 PM | LEYTE ACC-04/22/22 19:17: ISABEL SS, Isabel 138kV BUS 2 re-energized at 1830H, pre-arranged activity completed. Weather: Fair. | CVIS
4/22/2022 6:02:44 PM | VRCC-04/22/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2283MW, PK=1992MW, RR=0MW, NetOpMargin: EVE=291 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 390, TPC at 82 MW [WEBSMS] | CVIS
4/22/2022 6:02:41 PM | LRCC-04/22/2022 17:59: Mariveles - GNPD 500kV L2 closed at GNPD side at 1757H(On-going commissioning test). [WEBSMS] | CLUZ
4/22/2022 6:02:40 PM | LRCC-04/22/2022 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12063MW, PK=10135MW, RR=387MW, NetOpMargin: EVE=1541 Highest Unit O/L: SUAL 1 @647MW Derated Plant: CALACA 1 @220MW; GMEC 2 @300MW; SUAL 2 @415MW; ILIJAN A / B @851MW [WEBSMS] | CLUZ
4/22/2022 5:42:11 PM | LRCC-04/22/2022 17:34: Mariveles - GNPD 500kV L2 energized at Mariveles side at 1730H(On-going commissioning test). [WEBSMS] | CLUZ
4/22/2022 5:42:09 PM | LRCC-04/22/2022 17:33: Commissioning of Mariveles - GNPD 500kV L1 completed at 1727H. [WEBSMS] | CLUZ
4/22/2022 5:27:19 PM | LRCC-04/22/2022 17:20: Mariveles - GNPD 500kV L1 closed at GNPD side at 1720H(On-going commissioning test). [WEBSMS] | CLUZ
4/22/2022 5:03:46 PM | LRCC-04/22/2022 16:58: Mariveles - GNPD 500kV L1 energized at Mariveles side at 1654H(On-going commissioning test). [WEBSMS] | CLUZ
4/22/2022 3:16:25 PM | VRCC-04/22/2022 15:07: 37.5MVA TR1 at Toledo SS energized at 1502H (Energization of Newly Installed 37.5MVA(7Z-XF01TOL) Transformer), On-going testing [WEBSMS] | CVIS
4/22/2022 1:09:12 PM | VRCC-04/22/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2507MW, PK=2143MW, RR=0MW, NetOpMargin: PM=364, EVE=291 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 390, TPC at 82 MW [WEBSMS] | CVIS
4/22/2022 1:09:09 PM | LRCC-04/22/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12578MW, PK=11212MW, RR=422MW, NetOpMargin: PM=944, EVE=1541 Highest Unit O/L: SUAL 1 @647MW Derated Plant: CALACA 1 @220MW; GMEC 2 @300MW; SUAL 2 @415MW; ILJJAN A / B @851MW [WEBSMS] | CLUZ
4/22/2022 10:00:45 AM | LEYTE ACC-04/22/22: ORMOC SS, 69kV Ormoc-Simangan-Baybay, TIME OUT: 09:19:00, TIME IN: 09:24:00, RELAY: phase BN, 9.8kms, WEATHER: FAIR | CVIS
4/22/2022 9:46:38 AM | LEYTE ACC-04/22/22: CALBAYOG SS, 69kV Palanas-Allen-Lao-ang Line tripped again at 0941H, RELAY: z1, phase CN, 24.48kms, load=11.4MW, WEATHER: FAIR | CVIS
4/22/2022 9:46:36 AM | LEYTE ACC-04/22/22: CALBAYOG SS, 69kV Palanas-Allen-Lao-ang Line tripped/restored again at 0933H/0937H, RELAY: z1, phase CN, 24.39kms, load=13.5MW, WEATHER: FAIR | CVIS
4/22/2022 9:46:34 AM | LEYTE ACC-04/22/22: CALBAYOG SS, 69kV Palanas-Allen-Lao-ang Line tripped/restored again at 0933H/0937H, RELAY: z1, phase CN, 24.39kms, load=13.5MW, WEATHER: FAIR | CVIS
4/22/2022 9:36:27 AM | LEYTE ACC-04/22/22: CALBAYOG SS, 69kV Palanas-Allen-Lao-ang Line tripped/restored at 0927H/0930H, RELAY: z1, phase CN, 24.42kms, load=14.9MW, WEATHER: FAIR | CVIS
4/22/2022 9:36:26 AM | LEYTE ACC-04/22/22: CALBAYOG SS, 69kV Palanas-Allen-Lao-ang Line tripped/restored at 0927H/0930H, RELAY: z1, phase CN, 24.42kms, load=14.9MW, WEATHER: FAIR | CVIS
4/22/2022 9:36:24 AM | LEYTE ACC-04/22/22: ORMOC SS, 69kV Ormoc-Simangan-Baybay tripped/restored at 0919H/0924H, RELAY: phase BN, 9.8kms, load=32.32MW, WEATHER: FAIR | CVIS
4/22/2022 9:36:22 AM | LEYTE ACC-04/22/22: ORMOC SS, 69kV Ormoc-Simangan-Baybay tripped/restored at 0919H/0924H, RELAY: phase BN, 9.8kms, load=32.32MW, WEATHER: FAIR | CVIS
4/22/2022 6:52:12 AM | LRCC-04/22/2022 06:47: Bay-Makban Plant A 230kV Line 2 de-energized at 0645H (Planned Outage). [WEBSMS] | CLUZ
4/22/2022 6:28:54 AM | LEYTE ACC-04/22/22: ISABEL SS, 138kV Isabel SS Bus 2 pre-arranged activity, TIME OUT: 06:17:00, WEATHER: FAIR | CVIS
4/22/2022 6:28:52 AM | LEYTE ACC-04/22/22: ISABEL SS, 138kV Isabel SS Bus 2 pre-arranged activity, TIME OUT: 06:17:00, WEATHER: FAIR | CVIS
4/22/2022 6:15:23 AM | LRCC-04/22/2022 06:14: Naga-Tayabas 230kV line 2 was de-energized at 0614H (Planned Outage) . [WEBSMS] | CLUZ
4/22/2022 6:05:22 AM | VRCC-04/22/2022 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2594MW, PK=2022MW, RR=0MW, NetOpMargin: AM=572, PM=489, EVE=321 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 390 MW, TPC = 82 MW [WEBSMS] | CVIS
4/22/2022 6:05:19 AM | LRCC-04/22/2022 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12552MW, PK=10589MW, RR=447MW, NetOpMargin: AM=1572, PM=1148, EVE=1523 Highest Unit O/L: Sual 1 at 647MW Derated Plant: GMEC 2 at 300MW, Calaca 1 at 220MW, Ilijan at 851MW and Sual 2 at 415MW [WEBSMS] | CLUZ
4/22/2022 5:51:51 AM | LRCC-04/22/2022 05:43: Weather Update as of 0500H of April 22, 2022: Easterlies affecting the country. Davao Region and Surigao del Sur will experience cloudy skies with scattered rainshowers and thunderstorms. Metro Manila and the rest of the country will have partly cloudy to cloudy skies with isolated rainshowers or thunderstorms. [WEBSMS] | CLUZ
4/21/2022 9:52:49 PM | LEYTE ACC-04/21/22 21:42: ORMOC SS, 138kV Isabel-Tongonan line re-energized at 2138H. WEATHER: FAIR | CVIS
4/21/2022 9:19:18 PM | PANAY ACC-04/21/22 20:48: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME IN: 20:45, Facilitated emergency request of AKELCO to isolate due to hotspot correction. Customer Owned and maintained line | CVIS
4/21/2022 9:14:57 PM | LRCC-04/21/2022 21:07: Pagbilao Unit 1 online at 2104H. (From an unplanned outage) [WEBSMS] | CLUZ
4/21/2022 8:20:38 PM | LEYTE ACC-04/21/22 20:14: ORMOC SS, 69kV Tolosa-San Isidro line tripped at 2002H, phase CN, Z2, 32.8kms., load=5.6MW. Reclosed attempt failed with same indications. Sustained. WEATHER: FAIR | CVIS
4/21/2022 8:20:36 PM | PANAY ACC-04/21/22 20:23: NABAS SS, PPC3 Nabas-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 20:00, Load: 16.5MW Facilitated emergency request of AKELCO to isolate due to burning pole at their Caticlan SS. Customer Owned and maintained line | CVIS
4/21/2022 8:20:35 PM | PANAY ACC-04/21/22 20:23: NABAS SS, PPC3 Nabas-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 20:00, Load: 16.5MW Facilitated emergency request of AKELCO to isolate due to burning pole at their Caticlan SS. Customer Owned and maintained line | CVIS
4/21/2022 8:20:33 PM | LRCC-04/21/2022 20:08: System Advisory: ALD affected feeders of NGCP and Meralco were restored at 1958H and 2003H respectively. [WEBSMS] | CLUZ
4/21/2022 8:06:35 PM | LEYTE ACC-04/21/22 20:00: ORMOC SS, 69kV Tolosa-San Isidro line tripped at 1948H, phase CN, Z2, 34.8kms., load=6.0MW. Restored at 1955H. WEATHER: FAIR | CVIS
4/21/2022 8:06:33 PM | LRCC-04/21/2022 19:58: System Advisory: ALD occurred at Meralco and NGCP feeders due to the tripping of GNPD Unit 1 at 1951H from 618MW load. The lowest system frequency dip is 58.909Hz. [WEBSMS] | CLUZ
4/21/2022 6:54:17 PM | VRCC-04/21/2022 18:47: 40MVA Transformer 3 Toledo SS energized at 1846H [WEBSMS] | CVIS
4/21/2022 6:54:16 PM | VRCC-04/21/2022 18:46: TPC1-A (on islanding operation) synchronized to the grid in Toledo SS at 1844H [WEBSMS] | CVIS
4/21/2022 6:44:12 PM | LRCC-04/21/2022 18:37: Naga-Tayabas 230kV line 2 was restored at 1835H. (Planned Outage) [WEBSMS] | CLUZ
4/21/2022 6:31:50 PM | VRCC-04/21/2022 18:23: 40MVA Transformer 2 Toledo SS auto-tripped at 1815H during synchronization of TPC1-A (on islanding operation), re-energized at 1822H [WEBSMS] | CVIS
4/21/2022 6:10:19 PM | VRCC-04/21/2022 18:02: 40MVA Transformer 2 Toledo SS energized at 1749H [WEBSMS] | CVIS
4/21/2022 6:10:18 PM | VRCC-04/21/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2313MW, PK=2048MW, RR=40MW, NetOpMargin: EVE=225 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 390, TPC at 82 MW [WEBSMS] | CVIS
4/21/2022 6:10:16 PM | LRCC-04/21/2022 17:58: Bay - Makban Plant A 230kV Line 1 restored at 1732H (Planned Outage) [WEBSMS] | CLUZ
4/21/2022 6:10:13 PM | LRCC-04/21/2022 17:57: Bay - Makban Plant A 230kV Line 1 de-energized at 0858H (Planned Outage) [WEBSMS] | CLUZ
4/21/2022 5:54:19 PM | LRCC-04/21/2022 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12041MW, PK=10440MW, RR=391MW, NetOpMargin: EVE=1210 Highest Unit O/L: SUAL 1 @647MW Derated Plant: CALACA 1 @150MW; GMEC 2 @300MW; GNPD 1 @501MW; SLTEC 1 @62MW; SUAL 2 @415MW; ILJJAN A / B @851MW [WEBSMS] | CLUZ
4/21/2022 3:29:55 PM | LRCC-04/21/2022 15:23: GNPD 1 online at 1520H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2022 1:32:36 PM | LRCC-04/21/2022 13:31: San Jose - Angat 115kV Line 4 restored at 1329H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2022 1:09:10 PM | VRCC-04/21/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2484MW, PK=2167MW, RR=40MW, NetOpMargin: PM=277, EVE=225 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 390, TPC at 82 MW [WEBSMS] | CVIS
4/21/2022 1:09:08 PM | LRCC-04/21/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12050MW, PK=10889MW, RR=431MW, NetOpMargin: PM=730, EVE=982 Highest Unit O/L: SUAL 1 @647MW Derated Plant: CALACA 1 @150MW; GMEC 2 @300MW; SLTEC 1 @61MW; SUAL 2 @430MW; ILJJAN A / B @851MW [WEBSMS] | CLUZ
4/21/2022 12:56:23 PM | NEGROS ACC: 04/21/2022, 69kV Mabinay-Kabankalan Sub T/L(1.98MW) auto tripped at 1244H with ind.; Z3 DEF START BN 34.7KM. due to exploded CT at URC S/S.URC isolated. Restored at 1247H. | CVIS
4/21/2022 12:56:21 PM | LEYTE ACC-04/21/22 12:59: MAASIN SS, Maasin 138/69kV 30MVA TR No. 1 re-energized at 1243H, pre-arranged activity completed. Weather: Fair. | CVIS
4/21/2022 12:45:41 PM | LRCC-04/21/2022 12:44: San Jose - Angat 115kV Line 4 de-energized at 1243H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2022 11:01:17 AM | LRCC-04/21/2022 11:00: SCPC 3 online at 1057H (Unplanned Outage). [WEBSMS] | CLUZ
4/21/2022 8:26:59 AM | LEYTE ACC-04/21/22 08:34: MAASIN SS, Maasin 138/69kV 30MVA TR No. 1 isolated at 0814H, pre-arranged activity (0801-1700H). Weather: Fair. | CVIS
4/21/2022 8:03:29 AM | LRCC-04/21/2022 07:58: Sta. Rita 40 (161MW) tripped at 0750H. Lowest frequency = 59.45Hz. [WEBSMS] | CLUZ
4/21/2022 7:29:58 AM | VRCC-04/21/2022 07:27: 40MVA Transformer 3 Toledo SS de-energized at 0724H, Pre-arranged activity, TPC1-A on islanding operation starting 0723H, ETC: 1800H [WEBSMS] | CVIS
4/21/2022 7:03:01 AM | VRCC-04/21/2022 06:55: 40MVA Transformer 2 Toledo SS de-energized at 0654H. Pre-arranged activity. [WEBSMS] | CVIS
4/21/2022 6:32:37 AM | LRCC-04/21/2022 06:21: Tayabas - Naga 230kV Line 2 de-energized at 0626H (Planned Outage) . [WEBSMS] | CLUZ
4/21/2022 6:12:15 AM | LRCC-04/21/2022 06:10: Las Pinas-Dasmarinas 230kV Line 2 restored at 0606H (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2022 6:02:15 AM | VRCC-04/21/2022 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2594MW, PK=2121MW, RR=40MW, NetOpMargin: AM=433, PM=388, EVE=225 Highest Unit O/L: TVI at 169 MW per unit Derated Plant: EDC at 390 MW, TPC at 82 MW [WEBSMS] | CVIS
4/21/2022 6:02:12 AM | LRCC-04/21/2022 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12052MW, PK=10159MW, RR=426MW, NetOpMargin: AM=1467, PM=668, EVE=948 Highest Unit O/L: Sual 1 @647MW Derated Plant: Calaca 1 @150MW, SLTEC 1 @24MW, Sta Rita 40 @161MW, Sual 2 @430MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
4/21/2022 4:15:00 AM | LRCC-04/21/2022 04:07: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/21/2022 3:18:12 AM | LEYTE ACC-04/21/22: CALBAYOG SS, Palanas-Catarman-Allen-Lao-ang 69kV Line tripped/restored, TIME OUT: 03:10:00, TIME IN: 03:13:00, RELAY: z1, CN, 24.43kms, WEATHER: FAIR | CVIS
4/21/2022 3:18:10 AM | LEYTE ACC-04/21/22: CALBAYOG SS, Palanas-Catarman-Allen-Lao-ang 69kV Line tripped/restored, TIME OUT: 03:10:00, TIME IN: 03:13:00, RELAY: z1, CN, 24.43kms, WEATHER: FAIR | CVIS
4/21/2022 2:07:48 AM | LRCC-04/21/2022 02:04: Las Pinas 300MVA T04 & Las Pinas-Dasmarinas 230kV Line 2 de-energized at 0156H & 0159H, respectively (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2022 1:21:06 AM | PANAY ACC-04/21/22 01:11: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME IN: 01:11:00, WEATHER: FAIR; Restored after isolation of Andagao 7.5MVAR Capacitor. | CVIS
4/21/2022 1:09:12 AM | PANAY ACC-04/21/22 01:06: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 01:06:00, WEATHER: FAIR; Ld: 23.6MW; Facilitate request of Nabas Ss to de-energized the said TL to isolate Anadagao 7.5MVAR Capacitor due to defective PCB mechanism. | CVIS
4/21/2022 1:09:09 AM | LRCC-04/21/2022 00:57: Las Pinas (Zapote) 300MVA T01, T02 & T03 tripped at high side at 0012H during opening of breaker CB04(8LI1LPI-DAS)LPI for the emergency shutdown of Las Pinas-Dasmarinas 230kV Line 1 (Unplanned Outage) [WEBSMS] | CLUZ
4/21/2022 12:17:33 AM | LRCC-04/21/2022 00:14: Calaca 1 online at 2358H (Unplanned Outage). [WEBSMS] | CLUZ
4/20/2022 9:08:34 PM | LRCC-04/20/2022 20:59: SLTEC 1 online at 2054H (Unplanned Outage). [WEBSMS] | CLUZ
4/20/2022 7:57:55 PM | LRCC-04/20/2022 19:55: Calaca 1 @111MW tripped at 1947H. Lowest Frequency is 59.66Hz (Unplanned Outage) [WEBSMS] | CLUZ
4/20/2022 6:50:55 PM | LRCC-04/20/2022 18:50: Tayabas - Naga 230kV Line 2 restored at 1841H (Planned Outage) [WEBSMS] | CLUZ
4/20/2022 6:24:04 PM | LRCC-04/20/2022 18:17: Calaca 1 online at 1813H (Unplanned Outage) . [WEBSMS] | CLUZ
4/20/2022 6:14:00 PM | LRCC-04/20/2022 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11319MW, PK=9963MW, RR=391MW, NetOpMargin: EVE=965 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GMEC 2 @300MW; SUAL 2 @445MW; ILJJAN A / B @851MW; STA RITA 40 @161MW [WEBSMS] | CLUZ
4/20/2022 6:03:59 PM | VRCC-04/20/2022 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2302MW, PK=2032MW, RR=36MW, NetOpMargin: EVE=234 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 380 MW, TPC = 82 MW [WEBSMS] | CVIS
4/20/2022 5:37:06 PM | LRCC-04/20/2022 17:27: GNPD 1 (179MW) tripped at 1722H. Lowest frequency = 59.46Hz [WEBSMS] | CLUZ
4/20/2022 5:14:57 PM | VRCC-04/20/2022 17:03: Market Operator / WESM declared at 1655H of April 20,2022 on the MO initiated Market Intervention. Said intervention was due to I.T. problem. [WEBSMS] | CVIS
4/20/2022 5:14:55 PM | LRCC-04/20/2022 17:11: Market Intervention initiated by Market Operator was lifted at 1709H. [WEBSMS] | CLUZ
4/20/2022 5:03:36 PM | LRCC-04/20/2022 17:02: Market Intervention starting 1657H was initiated by Market Operator. [WEBSMS] | CLUZ
4/20/2022 4:40:06 PM | LRCC-04/20/2022 16:31: GNPD 1 online at 1619H (Unplanned Outage) [WEBSMS] | CLUZ
4/20/2022 1:55:44 PM | PANAY ACC-04/20/22 13:37: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME IN: 01:35:00, Energized up to structure # 06. | CVIS
4/20/2022 1:18:55 PM | VRCC-04/20/2022 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2599MW, PK=2148MW, RR=36MW, NetOpMargin: PM=415, EVE=234 Highest Unit O/L: TVI U @ 169 MW Derated Plant: EDC = 380 MW, TPC = 82 MW [WEBSMS] | CVIS
4/20/2022 1:08:49 PM | LRCC-04/20/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12051MW, PK=10896MW, RR=431MW, NetOpMargin: PM=724, EVE=854 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GMEC 2 @300MW; SUAL 2 @445MW; ILJJAN A / B @851MW; STA RITA 40 @161MW [WEBSMS] | CLUZ
4/20/2022 11:54:37 AM | LEYTE ACC-04/20/22 12:01: ORMOC SS, 69kV PCB Tolosa (Tolosa-Mabuhay-Javier) de-energized/re-energized at 1134H/1145H. 69kV Tunga Feeder back to its normal line configuration. Load=5.2MW. Weather: Fair. | CVIS
4/20/2022 10:08:36 AM | NEGROS ACC: 04/20/2022, 69KV Kabankalan-La Castellana Sub T/L(12.25MW) auto tripped at 1000H with ind.; Z1 AN 4.8KM. Restored at 1004H. Customer owned and maintained line. | CVIS
4/20/2022 10:08:32 AM | LRCC-04/20/2022 10:07: Affected ALD feeders from NGCP and MERALCO restored at 0957H and 0958H, respectively. [WEBSMS] | CLUZ
4/20/2022 9:55:05 AM | LRCC-04/20/2022 09:52: GNPD 1 (521MW) tripped at 0942H resulting in ALD on Meralco and NGCP feeders. Lowest frequency = 58.956Hz [WEBSMS] | CLUZ
4/20/2022 9:31:42 AM | LEYTE ACC-04/20/22 09:32: BABATNGON SS, Babatngon 7.5MVAr Cap. Bank #1 emergency isolated at 0817H as per request from O & M. Ready for operation at 0918H, repair completed. Weather: Fair. | CVIS
4/20/2022 6:57:24 AM | LEYTE ACC-04/20/22 06:58: ORMOC SS, Tolosa-Mabuhay 69kV Line re-energized at 0644H up to Javier ABS 2 only, serving power to Dorelco (Mayorga & Javier). Still isolated Javier-San Isidro 69kV Line. Weather: Fair. | CVIS
4/20/2022 6:34:01 AM | LRCC-04/20/2022 06:27: Tayabas - Naga 230kV Line 2 de-energized at 0626H (Planned Outage) [WEBSMS] | CLUZ
4/20/2022 6:10:32 AM | VRCC-04/20/2022 06:09: Magdugo SS 230kV Bus 2 de-energized at 0607H, for APMS and correction of defects, ETC: 1800H [WEBSMS] | CVIS
4/20/2022 6:10:29 AM | LRCC-04/20/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12411MW, PK=10507MW, RR=426MW, NetOpMargin: AM=1478, PM=1025, EVE=1384 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Sta Rita 40 @161MW, Sual 2 @400MW, GMEC 2 @ 300MW, & Ilijan @851MW, [WEBSMS] | CLUZ
4/20/2022 6:00:28 AM | VRCC-04/20/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2628MW, PK=2149MW, RR=40MW, NetOpMargin: AM=439, PM=411, EVE=230 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 380, TPC at 82 MW [WEBSMS] | CVIS
4/20/2022 5:37:00 AM | PANAY ACC-04/20/22 05:28: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME IN: 05:25:00, WEATHER: FAIR. Load Transfer of ANTECO Culasi SS to San Jose SS. | CVIS
4/20/2022 5:26:55 AM | PANAY ACC-04/20/22 05:17: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 05:14:00, WEATHER: FAIR. Transfer of ANTECO Culasi SS to San JOse SS> | CVIS
4/20/2022 5:18:32 AM | PANAY ACC-04/20/22 05:17: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 05:14:00, WEATHER: FAIR. Transfer of ANTECO Culasi SS to San JOse SS> | CVIS
4/20/2022 5:18:31 AM | PANAY ACC-04/20/22 05:07: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME OUT: 05:04:00, WEATHER: FAIR. Pre-arranged maintenance activities. | CVIS
4/20/2022 5:18:27 AM | LRCC-04/20/2022 05:06: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
4/20/2022 4:49:38 AM | LRCC-04/20/2022 04:49: Quezon-Dona Imelda 230 kV Line restored at 0448H (Planned Outage). [WEBSMS] | CLUZ
4/20/2022 4:33:53 AM | LRCC-04/20/2022 04:33: Binan-Balibago 115 kV Line restored at 0431H (Planned Outage). [WEBSMS] | CLUZ
4/20/2022 3:46:57 AM | PANAY ACC-04/20/22 03:17: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW), TIME IN: 03:14:00, WEATHER: FAIR | CVIS
4/20/2022 3:46:56 AM | PANAY ACC-04/20/22 03:00: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW), TIME OUT: 02:56:00, WEATHER: FAIR | CVIS
4/20/2022 3:46:54 AM | PANAY ACC-04/20/22 03:07: BUENAVISTA SS, Buenavista-GUIMELCO 69kV Line (CO (5LI1BVI-GUI), TIME IN: 03:04:00, WEATHER: FAIR; Pre-Arranged Outage Re-Tap Changed of Tr #1 & 2 @ SB SS. | CVIS
4/20/2022 3:46:53 AM | PANAY ACC-04/20/22 02:57: BUENAVISTA SS, Buenavista-GUIMELCO 69kV Line (CO (5LI1BVI-GUI), TIME OUT: 02:54:00, WEATHER: FAIR. Pre-arranged Outage Re-Tap Changed of TR # 1 & 2. | CVIS
4/20/2022 3:23:10 AM | PANAY ACC-04/20/22 03:10: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:07:00, WEATHER: FAIR. Pre-arranged Outaage Re-Tap Changed Of TR #1. | CVIS
4/20/2022 3:23:09 AM | PANAY ACC-04/20/22 03:06: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME OUT: 03:04:00, WEATHER: FAIR. Pre-arranged Outage Re-Tap Change of TR #1. | CVIS
4/20/2022 3:13:07 AM | PANAY ACC-04/20/22 02:43: STA. BARBARA SS, Sta. Barbara-Baldoza 69 kV L (5LI1SBA-BAL), TIME IN: 02:39:00, RELAY: NONE, WEATHER: FAIR; Pre-arranged Outage re-tap changed of TR #2. | CVIS
4/20/2022 2:59:43 AM | PANAY ACC-04/20/22 02:43: STA. BARBARA SS, Sta. Barbara-Baldoza 69 kV L (5LI1SBA-BAL), TIME IN: 02:39:00, RELAY: NONE, WEATHER: FAIR; Pre-arranged Outage re-tap changed of TR #2. | CVIS
4/20/2022 2:59:41 AM | PANAY ACC-04/20/22 02:36: STA. BARBARA SS, Sta. Barbara-Baldoza 69 kV L (5LI1SBA-BAL)(17.MW), TIME OUT: 02:33:00, RELAY: NONE, WEATHER: FAIR; Pre-arranged Outage Re-tap changed of Tr #2. | CVIS
4/20/2022 2:36:22 AM | LEYTE ACC-04/20/22 02:42:ORMOC SS, Tolosa-San Isidro 69kV L,Reclosed at 0213H but failed, Z2,Phase CN, fd=34.38kms, WEATHER: FAIR | CVIS
4/20/2022 2:36:20 AM | NEGROS ACC: 04/20/2022, 69kV Mabinay-Kabankalan Sub T/L restored at 0223H, URC 69kV lateral line isolated. | CVIS
4/20/2022 2:36:18 AM | NEGROS ACC: 04/20/2022, 69kV Mabinay-Kabankalan Sub T/L restored at 0223H, URC 69kV lateral line isolated. | CVIS
4/20/2022 2:26:16 AM | NEGROS ACC: 04/20/2022, 69kV Mabinay-Kabankalan Sub T/L auto-tripped 0213H with indication Z3 DEF start BN, 34.61km. URC plant (26.6MW) isolated. | CVIS
4/20/2022 2:26:14 AM | NEGROS ACC: 04/20/2022, 69kV Mabinay-Kabankalan Sub T/L auto-tripped 0213H with indication Z3 DEF start BN, 34.61km. URC plant (26.6MW) isolated. | CVIS
4/20/2022 2:26:13 AM | NEGROS ACC: 04/20/2022, 69kV Mabinay-Kabankalan Sub T/L auto-tripped 0213H with indication Z3 DEF start BN, 34.61km. URC plant (26.6MW) isolated. | CVIS
4/20/2022 1:49:27 AM | LEYTE ACC-04/20/22 01:51:ORMOC SS, Tolosa-San Isidro 69kV L, TIME OUT: 01:30:00,Under assessment,load=4.0mw, WEATHER: FAIR | CVIS
4/20/2022 12:05:18 AM | LRCC-04/19/2022 23:57: Binan-Balibago 115kV Line de-energized at 2354H (Planned Outage) [WEBSMS] | CLUZ
4/19/2022 11:08:15 PM | LRCC-04/19/2022 23:07: Quezon-Dona Imelda 230kV Line de-energized at 2302H (Planned Outage) [WEBSMS] | CLUZ
4/19/2022 9:21:01 PM | LEYTE ACC-04/19/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 2108H/2118H, on normal flow per RTD | CVIS
4/19/2022 7:57:15 PM | NEGROS ACC: 04/19/2022, 69kV Silay-VMC line section energized at 1940H after completion of customer (Silay Solar) activity. | CVIS
4/19/2022 6:36:58 PM | NEGROS ACC: 04/19/2022, 69kV Silay-VMC line section de-energized at 1822H as per customer request(Silay Solar) to conduct hot spot correction at DS03(5XFO1SSF). HPCo aand VMC- cogen isolated. | CVIS
4/19/2022 6:36:56 PM | LEYTE ACC-04/19/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1818H/1828H, on reverse flow per RTD | CVIS
4/19/2022 6:36:55 PM | LEYTE ACC-04/19/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1818H/1828H, on reverse flow per RTD | CVIS
4/19/2022 6:36:52 PM | LRCC-04/19/2022 18:35: Tayabas - Naga 230kV Line 2 restored at 1829H (Planned Outage) [WEBSMS] | CLUZ
4/19/2022 6:01:59 PM | VRCC-04/19/2022 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2289MW, PK=2032MW, RR=36MW, NetOpMargin: EVE=221 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 355 MW, TPC = 82 MW [WEBSMS] | CVIS
4/19/2022 6:01:58 PM | LRCC-04/19/2022 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11968MW, PK=10055MW, RR=387MW, NetOpMargin: EVE=1526 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SUAL 2 @445MW; ILJJAN A / B @851MW; STA RITA 40 @161MW [WEBSMS] | CLUZ
4/19/2022 4:04:49 PM | LRCC-04/19/2022 16:01: Concepcion - Clark 230kV Line 1 auto-tripped/auto-reclosed at 1525h (Unplanned Outage) [WEBSMS] | CLUZ
4/19/2022 2:28:51 PM | LEYTE ACC-04/19/22: TABANGO SS, 230kV Kananga - Tabango Line 2 pre-arranged activity done, TIME IN: 14:20:00, RELAY: N/A, WEATHER: FAIR | CVIS
4/19/2022 2:28:49 PM | LEYTE ACC-04/19/22: TABANGO SS, 230kV Kananga - Tabango Line 2 pre-arranged activity done, TIME IN: 14:20:00, RELAY: N/A, WEATHER: FAIR | CVIS
4/19/2022 12:58:09 PM | VRCC-04/19/2022 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2592MW, PK=2142MW, RR=36MW, NetOpMargin: PM=414, EVE=221 Highest Unit O/L: TVI U @ 169 MW Derated Plant: EDC = 355 MW, TPC = 82 MW [WEBSMS] | CVIS
4/19/2022 12:57:04 PM | LRCC-04/19/2022 12:51: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12096MW, PK=10874MW, RR=423MW, NetOpMargin: PM=799, EVE=1050 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GMEC 2 @300MW; SUAL 2 @445MW; ILJJAN A / B @851MW; STA RITA 40 @161MW [WEBSMS] | CLUZ
4/19/2022 12:27:58 PM | LRCC-04/19/2022 12:19: GNPD 1 online at 1210H (Planned Outage) [WEBSMS] | CLUZ
4/19/2022 10:50:44 AM | LRCC-04/19/2022 10:45: San Jose 750MVA T02 restored at 1045H (Unplanned Outage). [WEBSMS] | CLUZ
4/19/2022 8:11:32 AM | LRCC-04/19/2022 08:04: San Jose 750MVA T02 tripped at 0759H (Unplanned Outage). [WEBSMS] | CLUZ
4/19/2022 6:37:42 AM | LEYTE ACC-04/19/22 06:44: TABANGO SS, Kananga - Tabango 230kV Line 2 de-energized at 0620H, pre-arranged activity (0601H-1800H). Weather: Fair. | CVIS
4/19/2022 6:23:19 AM | LRCC-04/19/2022 06:20: Tayabas - Naga 230kV Line 2 de-energized at 0617H (Planned Outage) [WEBSMS] | CLUZ
4/19/2022 6:13:23 AM | VRCC-04/19/2022 06:09: Magdugo SS 230kV Bus 1 de-energized at 0605H, for APMS and correction of defects, ETC: 1800H [WEBSMS] | CVIS
4/19/2022 6:03:18 AM | VRCC-04/19/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2628MW, PK=2156MW, RR=36MW, NetOpMargin: AM=436, PM=414, EVE=221 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 355, TPC at 82 MW [WEBSMS] | CVIS
4/19/2022 5:58:49 AM | LRCC-04/19/2022 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11712MW, PK=10396MW, RR=391MW, NetOpMargin: AM=925, PM=637, EVE=847 Highest Unit O/L: Sual 1 @600MW Derated Plant: Sta Rita 40 @161MW, Sual 2 @460MW, GMEC 2 @ 300MW, & Ilijan @851MW, Sta. Rita 40 @161MW. [WEBSMS] | CLUZ
4/19/2022 5:25:19 AM | LRCC-04/19/2022 05:17: Weather Update: Issued at 0400H, Easterlies affecting the country. [WEBSMS] | CLUZ
4/19/2022 4:24:38 AM | LRCC-04/19/2022 04:22: Calaca 1(70MW) emergency shutdown at 0259H (Unplanned Outage) [WEBSMS] [WEBSMS] | CLUZ
4/19/2022 1:43:41 AM | LRCC-04/19/2022 01:34: Sta. Rita 10 changeover from oil to gas at 0131H [WEBSMS] | CLUZ
4/19/2022 1:14:09 AM | LRCC-04/19/2022 01:11: Calaca 1 online at 0107H (Unplanned Outage) [WEBSMS] | CLUZ
4/18/2022 11:39:48 PM | LEYTE ACC-04/18/22 23:39: MARSHALLING SS,EDC-Mahanagdong B cut-in at 2306H, capability at 355 Mw, WEATHER: FAIR | CVIS
4/18/2022 9:56:11 PM | LEYTE ACC-04/18/22: EDC-Leyte A, Mahanagdong Unit #1 cut-in at 2141H | CVIS
4/18/2022 8:45:38 PM | LRCC-04/18/2022 20:43: Calaca 1 (152MW) tripped at 2039H, lowest frequency at 59.552hz (Unplanned Outage) [WEBSMS] | CLUZ
4/18/2022 6:57:15 PM | LEYTE ACC-04/18/22: EDC-Leyte A, Mahanagdong Unit #1 tripped at 1851H. Under assessment | CVIS
4/18/2022 6:10:22 PM | VRCC-04/18/2022 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2239MW, PK=1911MW, RR=40MW, NetOpMargin: EVE=288 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 330 MW, TPC = 82 MW [WEBSMS] | CVIS
4/18/2022 5:47:01 PM | LRCC-04/18/2022 17:45: Tayabas-Naga 230kV Line 2 restored at 1743H (Planned Outage) [WEBSMS] | CLUZ
4/18/2022 5:46:58 PM | LRCC-04/18/2022 17:39: Mexico-Concepcion 230kV Line 1 restored at 1738H (Planned Outage) [WEBSMS] | CLUZ
4/18/2022 5:36:53 PM | LRCC-04/18/2022 17:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11448MW, PK=9825MW, RR=404MW, NetOpMargin: EVE=1219 Highest Unit O/L: Sual 1 @600MW Derated Plant: Sta Rita 40 @161MW, Masinloc 1/3 @260MW/300MW, Sual 2 @500MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
4/18/2022 3:39:32 PM | LEYTE ACC-04/18/22: ORMOC SS, 69kV Tolosa-San Isidro (PCB Tolosa), TIME OUT: 15:25:00, TIME IN: 15:31:00 , RELAY: z1, BN, 6.4kms, load=5.6MW, WEATHER: FAIR | CVIS
4/18/2022 3:39:30 PM | LEYTE ACC-04/18/22: ORMOC SS, 69kV Tolosa-San Isidro (PCB Tolosa), TIME OUT: 15:25:00, TIME IN: 15:31:00 , RELAY: z1, BN, 6.4kms, load=5.6MW, WEATHER: FAIR | CVIS
4/18/2022 1:04:31 PM | VRCC-04/18/2022 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2428MW, PK=2090MW, RR=40MW, NetOpMargin: PM=298, EVE=288 Highest Unit O/L: TVI U @ 169 MW Derated Plant: EDC = 330 MW, TPC = 82 MW [WEBSMS] | CVIS
4/18/2022 1:04:27 PM | LRCC-04/18/2022 13:04: Calaca 1 online at 1302H (Unplanned Outage) [WEBSMS] | CLUZ
4/18/2022 1:04:26 PM | LRCC-04/18/2022 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12069MW, PK=10720MW, RR=426MW, NetOpMargin: PM=923, EVE=1578 Highest Unit O/L: Sual 1 @600MW Derated Plant: Sta Rita 40 @161MW, Masinloc 1/3 @260MW/300MW, Sual 2 @500MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
4/18/2022 10:23:37 AM | VRCC-04/18/2022 10:19: 138KV Maasin-Ubay Submarine Cable synchronized at Ubay SS at 1014H. [WEBSMS] | CVIS
4/18/2022 10:17:41 AM | LEYTE ACC-04/18/22: MAASIN SS, 138kV Maasin-Ubay Line, TIME IN: 10:05:00, WEATHER: FAIR | CVIS
4/18/2022 10:17:39 AM | LEYTE ACC-04/18/22: MAASIN SS, 138kV Maasin-Ubay Line, TIME IN: 10:05:00, WEATHER: FAIR | CVIS
4/18/2022 8:36:41 AM | LRCC-04/18/2022 08:32: For info: Sta Rita Module 10 completed fuel changeover from gas to oil at 0829H. [WEBSMS] | CLUZ
4/18/2022 8:21:07 AM | VRCC-04/18/2022 06:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2494MW, PK=2018MW, RR=18MW, NetOpMargin: AM=458, PM=298, EVE=288 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 330, TPC at 82 MW [WEBSMS] | CVIS
4/18/2022 8:20:59 AM | LRCC-04/18/2022 07:08: Mexico-Concepcion 230kV Line 1 de-energized at 0707H (Planned Outage) [WEBSMS] | CLUZ
4/18/2022 8:20:58 AM | LRCC-04/18/2022 06:16: Tayabas-Naga 230kV Line 2 de-energized at 0615H (Planned Outage) [WEBSMS] | CLUZ
4/18/2022 8:20:57 AM | LRCC-04/18/2022 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12213MW, PK=9846MW, RR=416MW, NetOpMargin: AM=1951, PM=1502, EVE=1835 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GMEC 2 @300MW; SUAL 2 @550MW; ILJJAN A / B @851MW; STA RITA 30 @240MW [WEBSMS] | CLUZ
4/17/2022 1:04:25 PM | VRCC-04/17/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2552MW, PK=1688MW, RR=40MW, NetOpMargin: PM=824, EVE=390 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 330, TPC at 82 MW [WEBSMS] | CVIS
4/17/2022 12:54:22 PM | LRCC-04/17/2022 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12069MW, PK=7834MW, RR=356MW, NetOpMargin: PM=3879, EVE=2666 Highest Unit O/L: Sual 1 @600MW Derated Plant: Sta Rita 30/40 @240MW/161MW, San Gabriel @211MW, Sual 2 @500MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
4/17/2022 11:35:59 AM | LRCC-04/17/2022 11:31: Ambuklao-Bayombong 230kV Line 1 restored at 1131H (Planned Outage) [WEBSMS] | CLUZ
4/17/2022 11:26:00 AM | LEYTE ACC-04/17/22 11:30: MARSHALLING SS, Mahanagdong B tripped/cut-in at 1031H/1114H,load=load=46.0mw, Under assesment, WEATHER: FAIR | CVIS
4/17/2022 10:52:22 AM | NEGROS ACC: 04/17/2022, 69kV Escalante-San Carlos Line section (3.9 MW) de-energized at 1023H to facilitate transfer of load back to Cadiz S/S. 69kV Escalante-San Carlos Line section energized thru Cadiz S/S at 1033H. | CVIS
4/17/2022 10:02:07 AM | NEGROS ACC: 04/17/2022: Cadiz 50MVA TR No.1 energized and in parallel operation with 50 MVA TR2 at 0910H and 0912H respectively | CVIS
4/17/2022 10:02:05 AM | LEYTE ACC-04/17/22 09:39: ORMOC SS, Tolosa-San Isidro 69 kV L,Energized at 0949H with clearnce from O&M, WEATHER: FAIR | CVIS
4/17/2022 9:38:35 AM | LEYTE ACC-04/17/22 09:39: ORMOC SS, Tolosa-San Isidro 69 kV L tripped at 0920H,load=17.7mw, Under assesment, WEATHER: FAIR | CVIS
4/17/2022 8:31:37 AM | LRCC-04/17/2022 08:28: Angat HEPP 115kV Bus 2 de-energized at 0826H (Planned Outage) [WEBSMS] | CLUZ
4/17/2022 8:18:09 AM | LRCC-04/17/2022 08:08: Ambuklao-Bayombong 230kV Line 1 de-energized at 0806H (Planned Outage) [WEBSMS] | CLUZ
4/17/2022 7:07:51 AM | LRCC-04/17/2022 06:58: San Jose-Angat 115kV Line 1 de-energized at 0656H (Planned Outage) [WEBSMS] | CLUZ
4/17/2022 6:54:24 AM | NEGROS ACC: 04/17/2022, 69kV Escalante-San Carlos Line section (5 MW) de-energized at 0559H to facilitate transfer of load to 69kV Amlan-San Carlos Sub T/L | CVIS
4/17/2022 6:44:21 AM | NEGROS ACC: 04/17/2022, 69kV Escalante-San Carlos Line section energized through 69kV Amlan-San Carlos Sub T/L at 0611H | CVIS
4/17/2022 6:34:19 AM | NEGROS ACC: 04/17/2022, 69kV Escalante-San Carlos Line section (5 MW) de-energized at 0559H to facilitate transfer of load to 69kV Amlan-San Carlos Sub T/L | CVIS
4/17/2022 6:30:54 AM | LRCC-04/17/2022 06:21: San Jose-Nagsaag 500kV Line 2 de-energized at 0621H (Planned Outage) [WEBSMS] | CLUZ
4/17/2022 6:07:31 AM | VRCC-04/17/2022 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2574MW, PK=1640MW, RR=40MW, NetOpMargin: AM=894, PM=804, EVE=381 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 330 MW, TPC = 82 MW [WEBSMS] | CVIS
4/17/2022 5:34:01 AM | LRCC-04/17/2022 05:25: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11947MW, PK=7809MW, RR=337MW, NetOpMargin: AM=3801, PM=3745, EVE=2563 Highest Unit O/L: Sual 1 @600MW Derated Plant: Sta Rita 30 @240MW, STA. RITA 40 @ 161MW, Sual 2 @500MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
4/17/2022 5:20:36 AM | PANAY ACC-04/17/22 03:47: SAN JOSE SS, San Jose-Sibalom 69 kV L (5LI1SJB-SIB), TIME OUT: 03:41:00, TIME IN: 03:45:00, RELAY: OC 2 PHASE C/ROC, Load: 7.8mw, Momentary line fault, WEATHER: FAIR | CVIS
4/17/2022 4:57:07 AM | LRCC-04/17/2022 04:54: Weather Update: Issued at 0400H, Northeasterly Surface Windflow affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
4/16/2022 10:08:25 PM | LRCC-04/16/2022 22:03: San Gabriel online at 2201H (Unplanned Outage) [WEBSMS] | CLUZ
4/16/2022 8:44:37 PM | NEGROS ACC: 04/16/2022: Cadiz 50MVA TR No.1(20.21MW) auto-tripped at 2030H with indication: activation of lock-out relay, no indication on M1 and M2 relay . Load of TR1 transferred to 50- MVA TR2. | CVIS
4/16/2022 8:44:36 PM | NEGROS ACC: 04/16/2022: Cadiz 50MVA TR No.1(20.21MW) auto-tripped at 2030H with indication: activation of lock-out relay, no indication on M1 and M2 relay . Load of TR1 transferred to 50- MVA TR2. | CVIS
4/16/2022 7:10:45 PM | VRCC-04/16/2022 19:06: Visayas Spot Peak as of April 16, 2022, 1686 MW at 1842H, previous spot peak 2224 MW at 1400H on May 16, 2019 [WEBSMS] | CVIS
4/16/2022 6:13:50 PM | VRCC-04/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2345MW, PK=1936MW, RR=40MW, NetOpMargin: EVE=379 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 330, TPC at 82 MW [WEBSMS] | CVIS
4/16/2022 5:37:04 PM | LRCC-04/16/2022 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10773MW, PK=8402MW, RR=373MW, NetOpMargin: EVE=1998 Highest Unit O/L: Sual 1 @600MW Derated Plant: Sta Rita 10,30 & 40 @161MW, Sual 2 @500MW, GMEC 2 @ 300MW, & Ilijan @695MW [WEBSMS] | CLUZ
4/16/2022 5:16:54 PM | LRCC-04/16/2022 17:13: San Jose-Nagsaag 500kV Line 1 restored at 1713H (Planned Outage) [WEBSMS] | CLUZ
4/16/2022 4:26:43 PM | LRCC-04/16/2022 16:23: Tayabas-Pagbilao 230kV Line 1 restored at 1622H (Planned Outage) [WEBSMS] | CLUZ
4/16/2022 1:08:51 PM | VRCC-04/16/2022 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2532MW, PK=1792MW, RR=40MW, NetOpMargin: PM=701, EVE=379 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 330, TPC at 82 MW [WEBSMS] | CVIS
4/16/2022 1:08:48 PM | LRCC-04/16/2022 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11260MW, PK=7939MW, RR=368MW, NetOpMargin: PM=2953, EVE=2174 Highest Unit O/L: Sual 1 @600MW Derated Plant: Sta Rita 10,30 & 40 @161MW, Sual 2 @500MW, GMEC 2 @ 300MW, & Ilijan @695MW [WEBSMS] | CLUZ
4/16/2022 9:41:16 AM | LRCC-04/16/2022 09:33: For info: Sta Rita Module 10 completed fuel changeover from oil to natural gas at 0926H. [WEBSMS] | CLUZ
4/16/2022 8:20:49 AM | LRCC-04/16/2022 08:18: Tayabas-Pagbilao 230kV Line 1 de-energized at 0817H (Planned Outage) [WEBSMS] | CLUZ
4/16/2022 7:57:23 AM | LRCC-04/16/2022 07:49: San Jose-Nagsaag 500kV Line 1 de-energized at 0747H (Planned Outage) [WEBSMS] | CLUZ
4/16/2022 6:11:57 AM | VRCC-04/16/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2574MW, PK=1763MW, RR=40MW, NetOpMargin: AM=771, PM=701, EVE=379 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 330, TPC at 82 MW [WEBSMS] | CVIS
4/16/2022 6:11:55 AM | LRCC-04/16/2022 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11515MW, PK=7237MW, RR=341MW, NetOpMargin: AM=3937, PM=3263, EVE=2406 Highest Unit O/L: Sual 1 @600MW Derated Plant: Sta Rita 30 @240MW, Sual 2 @500MW, GMEC 2 @ 300MW, & Ilijan @540MW [WEBSMS] | CLUZ
4/16/2022 5:36:07 AM | LRCC-04/16/2022 05:29: Weather Update: Issued at 0400H, Northeasterly Surface Windflow affecting Extreme Northern Luzon. [WEBSMS] | CLUZ
4/16/2022 5:22:43 AM | LRCC-04/16/2022 05:13: Dasmarinas 600MVA T02 restored at 0446H (Planned Outage). [WEBSMS] | CLUZ
4/16/2022 1:31:18 AM | PANAY ACC-04/16/22 01:20: DINGLE SS, Dingle-Passi 69 kV L (5LI1DIN-PSS), TIME IN: 01:18:00, RELAY: Z1 CN at 4.54kms, Snake intrusion at Str#28, Brgy Rumagayray San Enrique, Iloilo | CVIS
4/16/2022 12:18:43 AM | PANAY ACC-04/16/22 00:03: DINGLE SS, Dingle-Passi 69 kV L (5LI1DIN-PSS), TIME OUT: 00:00, RELAY: Z1 CN at 4.54kms, Load:4.35MW, WEATHER: FAIR; Cause: under investigation | CVIS
4/16/2022 12:18:42 AM | PANAY ACC-04/16/22 00:03: DINGLE SS, Dingle-Passi 69 kV L (5LI1DIN-PSS), TIME OUT: 00:00, RELAY: Z1 CN at 4.54kms, Load:4.35MW, WEATHER: FAIR; Cause: under investigation | CVIS
4/16/2022 12:18:40 AM | PANAY ACC-04/15/22 23:50: DINGLE SS, Dingle-Passi 69 kV L (5LI1DIN-PSS), TIME IN: 23:48:00, RELAY: Z1 CN at 4.54kms, WEATHER: FAIR; Cause: under investigation | CVIS
4/15/2022 10:43:51 PM | LRCC-04/15/2022 22:36: San Gabriel shutdown at 2232H (Unplanned Outage). [WEBSMS] | CLUZ
4/15/2022 10:43:49 PM | LRCC-04/15/2022 22:34: San Gabriel shutdown at 2232H (Planned Outage). [WEBSMS] | CLUZ
4/15/2022 10:20:13 PM | LRCC-04/15/2022 22:10: Dasmarinas 600MVA T02 de-energized at 2210H (Planned Outage). [WEBSMS] | CLUZ
4/15/2022 9:33:06 PM | LRCC-04/15/2022 21:33: Las Pinas(Zapote) 300MVA T01 restored 2132H (Planned Outage). [WEBSMS] | CLUZ
4/15/2022 9:23:04 PM | LRCC-04/15/2022 21:17: Las Pinas (Zapote) 300MVA T04 restored at 2112H (Planned Outage). [WEBSMS] | CLUZ
4/15/2022 9:09:37 PM | LRCC-04/15/2022 21:04: Las Pinas(Zapote)-Dasmarinas 230kV Line 2 restored 2102H (Planned Outage) [WEBSMS] | CLUZ
4/15/2022 9:09:35 PM | LRCC-04/15/2022 21:01: Las Pinas(Zapote)-Dasmarinas 230kV Line 1, Zapote T03 and T02 restored 2056 (Planned Outage). [WEBSMS] | CLUZ
4/15/2022 8:00:10 PM | NEGROS ACC: 04/15/2022, 69kV Bacolod-Islasol II Line section restored at 1951H. NOCECO San Enrique S/S isolated. | CVIS
4/15/2022 7:02:23 PM | NEGROS ACC: 04/15/2022, 69KV Bacolod-San Enrique Sub T/L(22.29MW) emergency opened at 1841H customers(NOCECO) request due to fire at NOCECO San Enrique S/S 10MVA Transformer. CENPRI, SNBP and ISLASOL II. | CVIS
4/15/2022 6:15:27 PM | VRCC-04/15/2022 18:09: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2299MW, PK=1924MW, RR=69MW, NetOpMargin: EVE=335 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 288 MW, TPC = 82 MW [WEBSMS] | CVIS
4/15/2022 5:41:54 PM | LRCC-04/15/2022 17:39: Dasmarinas-Amadeo 230kV Line 2 restored at 1739H (Planned Outage) [WEBSMS] | CLUZ
4/15/2022 5:38:15 PM | LRCC-04/15/2022 17:33: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11535MW, PK=7930MW, RR=305MW, NetOpMargin: EVE=3300 Highest Unit O/L: Sual 1 @600MW Derated Plant: Sta Rita 30 @240MW, San Gabriel @211MW, Sual 2 @500MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
4/15/2022 5:14:48 PM | NEGROS ACC: 04/15/2022, 69kV Bacolod-Reclamation Sub T/L(14.64MW) auto tripped at 1658H with ind.; Z1 L3E 0.6KM. Restored at 1703H. Customer owned and maintained line. | CVIS
4/15/2022 3:42:17 PM | PANAY ACC-04/15/22 15:37: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME OUT: 03:30:00, TIME IN: 03:33:00, Load: 2.3mw, RELAY: STARTED AN TRIP N 47.24kms, Momentary line fault, WEATHER: FAIR | CVIS
4/15/2022 2:45:49 PM | LRCC-04/15/2022 14:42: Tayabas 600MVA TO3 restored at 1441H (Planned Outage) [WEBSMS] | CLUZ
4/15/2022 1:23:35 PM | VRCC-04/15/2022 13:21: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2445MW, PK=1798MW, RR=70MW, NetOpMargin: PM=607, EVE=335 Highest Unit O/L: TVI U @169 MW. Derated Plant: EDC = 288 MW, TPC = 82 MW [WEBSMS] | CVIS
4/15/2022 1:00:07 PM | LRCC-04/15/2022 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12040MW, PK=6986MW, RR=275MW, NetOpMargin: PM=4779, EVE=3300 Highest Unit O/L: Sual 1 @600MW Derated Plant: Sta Rita 30 @240MW, San Gabriel @211MW, Sual 2 @500MW, GMEC 2 @ 300MW, & Ilijan @851MW [WEBSMS] | CLUZ
4/15/2022 11:19:27 AM | LRCC-04/15/2022 11:17: Lumban -Malaya 230kV Line 1 auto-tripped & auto-reclosed at 1107H with SLGF Phase C indication (Unplanned Outage) [WEBSMS] | CLUZ
4/15/2022 9:35:22 AM | LRCC-04/15/2022 09:35: Taytay(Dolores)-New Teresa 115kV Line restored at 0934H. (Planned Outage) [WEBSMS] | CLUZ
4/15/2022 8:35:31 AM | MRCC-04/15/2022 04:44: GRID UPDATE AS OF 6:00 AM System Condition: CAP=3065MW, PK=1440MW, RR=58MW, NetOpMargin: AM=1567, PM=1492, EVE=1343 Highest Unit O/L: GNPK U3 and U4 @ 138 MW each. Derated Plant: Ag1@40MW, Ag2@82MW, Ag4@97MW, Ag5@15MW, Ag6@89MW, Ag7@21MW, Pul4@104MW, MGPP@75MW, STEAG@200MW, TSI@270MW, FDC@ 245, GNPK@276MW, SMCPC@270MW, MCC@150MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
4/15/2022 8:14:58 AM | LRCC-04/15/2022 08:11: Dasmarinas-Amadeo 230kV Line 2 de-energized at 0704H (Planned Outage) [WEBSMS] | CLUZ
4/15/2022 6:39:20 AM | LRCC-04/15/2022 06:39: Tayabas 600MVA TO3 de-energized at 0636H (Planned Outage) [WEBSMS] | CLUZ
4/15/2022 6:02:26 AM | VRCC-04/15/2022 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2491MW, PK=1759MW, RR=40MW, NetOpMargin: AM=692, PM=607, EVE=335 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 288 MW, TPC = 82 MW [WEBSMS] | CVIS
4/15/2022 5:52:22 AM | LRCC-04/15/2022 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12327MW, PK=7473MW, RR=258MW, NetOpMargin: AM=4596, PM=4197, EVE=2975 Highest Unit O/L: Sual 1 at 600MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, Sta. Rita 30 at 240MW [WEBSMS] | CLUZ
4/15/2022 5:02:02 AM | LEYTE ACC-04/15/22 05:06: CALBAYOG SS, 69kV PCB Palanas Cara tripped/restored at 0444H/0450H as per clearance from Line Engineer, ind.: Phase-A, NO fault distance. Weather: Fair. | CVIS
4/15/2022 4:51:58 AM | LRCC-04/15/2022 04:45: Dasmarinas 600MVA T01 restored at 0445H. (Planned Outage) [WEBSMS] | CLUZ
4/15/2022 1:20:45 AM | LRCC-04/15/2022 01:17: Dasmarinas 600MVA T01 de-energized at 0116H. (Planned Outage) [WEBSMS] | CLUZ
4/15/2022 12:57:19 AM | LRCC-04/15/2022 00:56: Taytay(Dolores)-New Teresa 115kV Line de-energized at 0050H. (Planned Outage) [WEBSMS] | CLUZ
4/15/2022 12:00:25 AM | LEYTE ACC-04/14/22 23:59: TGPP, GCGI-TGPP unit #3 cut-in to the system at 2342H. Weather: Fair. | CVIS
4/14/2022 10:23:14 PM | LEYTE ACC-04/14/22 22:29: TGPP, GCGI-TGPP unit #2 cut-in to the system at 2207H. Weather: Fair. | CVIS
4/14/2022 9:59:45 PM | LEYTE ACC-04/14/22 22:09: TGPP, GCGI-TGPP unit #1 cut-in to the system at 2155H. Weather: Fair. | CVIS
4/14/2022 9:39:37 PM | LRCC-04/14/2022 21:39: San Gabriel online at 2136H. (Unplanned Outage) [WEBSMS] | CLUZ
4/14/2022 7:28:58 PM | LRCC-04/14/2022 19:23: San Lorenzo-Sta. Rita 230kV Bus 1 and 2 tie breakers were opened at 1917H. Batangas 300MVA T04 and T05 on parallel configuration at 1922H. [WEBSMS] | CLUZ
4/14/2022 6:55:27 PM | NEGROS ACC: 04/14/2022 ALD in Negros area restored at 1658H, with total load drop of 15.67MW energized 69 kV Kabankalan- Sipalay Sub TL. | CVIS
4/14/2022 6:18:34 PM | LRCC-04/14/2022 18:09: Limay-BPC 230kV Line 1 & 2 restored at 1759H and 1757H. (Planned Outage) [WEBSMS] | CLUZ
4/14/2022 6:05:12 PM | VRCC-04/14/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2181MW, PK=1724MW, RR=76MW, NetOpMargin: EVE=381 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 275, TPC at 82 MW [WEBSMS] | CVIS
4/14/2022 5:41:48 PM | LEYTE ACC-04/14/22 17:45: MARSHALLING CS, EDC-Mahanagdong A units #2 & #1 cut-in to the system at 1713H & 1725H respectively. Weather: Cloudy. | CVIS
4/14/2022 5:31:50 PM | LRCC-04/14/2022 17:28: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10833MW, PK=8020MW, RR=359MW, NetOpMargin: EVE=2454 Highest Unit O/L: Sual 1 @ 600MW Derated Plant: Sual 2 @500MW, Sta Rita 10, 30 & 40 @161MW each, Ilijan @695MW, GMEC 2 @300MW [WEBSMS] | CLUZ
4/14/2022 5:31:43 PM | VRCC-04/14/2022 17:22: Tripping of four VECO Feeders (13 MW total load) by first level ALD after the Auto-blocking of HVDC at 1633H restored at 1648H [WEBSMS] | CVIS
4/14/2022 5:18:16 PM | LEYTE ACC-04/14/22 17:26: ORMOC CONVERTER STATION SS, 350kV HVDC deblocked at 1710H on normal power flow per RTD. Weather: Cloudy. | CVIS
4/14/2022 5:08:14 PM | NEGROS ACC: 04/14/2022 MLD in Negros area restored at 1658H, with total load drop of 15.67MW energized 69 kV Kabankalan- Sipalay Sub TL. | CVIS
4/14/2022 4:52:51 PM | PANAY ACC-04/14/22 16:51: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME IN: 04:48:00, WEATHER: FAIR | CVIS
4/14/2022 4:52:49 PM | NEGROS ACC: 04/14/2022 1st level ALD activation in Negros area at 1634H isolating 69KV Kabankalan-Sipalay Sub TL (15.67MW) due to tripping of HVDC. | CVIS
4/14/2022 4:52:48 PM | LEYTE ACC-04/14/22 16:53: HVDC OCS, 350kV HVDC auto-tripped at 1633H, details to follow. Weather: Cloudy. | CVIS
4/14/2022 4:52:46 PM | PANAY ACC-04/14/22 16:40: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME OUT: 04:34:00, Load: 2.2mw, UFR 1ST level activation due to tripping of 230kV HVDC, WEATHER: FAIR | CVIS
4/14/2022 4:52:44 PM | LRCC-04/14/2022 16:45: HVDC (322MW) tripped at 1633H, lowest frequency at 59.018hz with ALD at MECO. and NGCP (Unplanned Outage). [WEBSMS] | CLUZ
4/14/2022 3:32:31 PM | PANAY ACC-04/14/22 14:30: PANIT-AN SS, Panit-an-Sara 69 kV Line (5LI1PNT-SAR), TIME IN: 02:24:00, Energized up to CAPELCO Timpas TR1 & TR2, Pres Roxas SS transfered to Concepcion SS. | CVIS
4/14/2022 2:30:17 PM | LRCC-04/14/2022 14:25: Naga-Tayabas 230kV L2 restored at 1425H (Planned Outage). [WEBSMS] | CLUZ
4/14/2022 2:20:13 PM | PANAY ACC-04/14/22 14:10: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST), TIME IN: 14:07:00, RELAY: NONE, WEATHER: FAIR. Load Transfer of CAPELCO Pres. Roxas SS to Concepcion SS. | CVIS
4/14/2022 2:20:11 PM | PANAY ACC-04/14/22 14:10: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST), TIME IN: 14:07:00, RELAY: NONE, WEATHER: FAIR. Load Transfer of CAPELCO Pres. Roxas SS to Concepcion SS. | CVIS
4/14/2022 2:06:45 PM | PANAY ACC-04/14/22 13:59: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST)(12.6MW), TIME OUT: 13:55:00, RELAY: NONE, WEATHER: FAIR. To facilitate Load transfer of CAPELCO Pres. Roxas SS to Concepcion SS. | CVIS
4/14/2022 2:06:44 PM | PANAY ACC-04/14/22 13:59: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST)(12.6MW), TIME OUT: 01:55:00, RELAY: NONE, WEATHER: FAIR. To facilitate Load transfer of CAPELCO Pres. Roxas SS to Concepcion SS. | CVIS
4/14/2022 1:09:17 PM | VRCC-04/14/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2488MW, PK=2082MW, RR=40MW, NetOpMargin: PM=366, EVE=343 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 325, TPC at 82 MW [WEBSMS] | CVIS
4/14/2022 12:22:15 PM | LRCC-04/14/2022 12:21: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11300MW, PK=7739MW, RR=345MW, NetOpMargin: PM=3216, EVE=1700 Highest Unit O/L: Sual 1 @ 600MW Derated Plant: Sual 2 @500MW, Sta Rita 10, 30 & 40 @161MW each, Ilijan @695MW, GMEC 2 @300MW [WEBSMS] | CLUZ
4/14/2022 10:45:14 AM | LRCC-04/14/2022 10:39: Ambuklao-Bayombong 230kV Line 2 restored at 1039H (Planned Outage). [WEBSMS] | CLUZ
4/14/2022 10:31:14 AM | LRCC-04/14/2022 10:26: Sta. Rita 10 changeover from oil to gas at 1022H. [WEBSMS] | CLUZ
4/14/2022 10:31:13 AM | LRCC-04/14/2022 10:22: Payocpoc (1590EC) Unit 3 Main Transformer (OAT3) de-energized at 0811H (Planned Outage). [WEBSMS] | CLUZ
4/14/2022 10:21:09 AM | LRCC-04/14/2022 10:12: Tayabas 600MVA T01 restored at 1011H (Planned Outage). [WEBSMS] | CLUZ
4/14/2022 9:47:36 AM | NEGROS ACC: 04/14/2022, 69kV Mabinay-Kabankalan Sub T/L (4.9 MW) auto-tripped 0906H with indication Z1 BN, 10.02km. URC plant isolated. Restored at 0908H. | CVIS
4/14/2022 9:47:35 AM | VRCC-04/14/2022 08:21: CEDC Unit 1 cut-in at 0811H with an initial load of 8 MW [WEBSMS] | CVIS
4/14/2022 9:47:33 AM | VRCC-04/14/2022 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2491MW, PK=2058MW, RR=36MW, NetOpMargin: AM=397, PM=287, EVE=299 Highest Unit O/L: TVI at 169 MW per unit Derated Plant: EDC at 288 MW, TPC at 82 MW, CEDC at 164MW [WEBSMS] | CVIS
4/14/2022 9:47:31 AM | LRCC-04/14/2022 08:06: Ambuklao-Bayombong 230kV Line 2 de-energized at 0804H (Planned Outage). [WEBSMS] | CLUZ
4/14/2022 9:47:30 AM | LRCC-04/14/2022 07:35: Las Pinas(Zapote) 300MVA T03 and T02 de-energized 0724H and 0730H (Planned Outage). [WEBSMS] | CLUZ
4/14/2022 9:47:29 AM | LRCC-04/14/2022 07:33: Las Pinas(Zapote)-Dasmarinas 230kV Line 1 de-energized 0721 (Planned Outage). [WEBSMS] | CLUZ
4/14/2022 9:47:28 AM | LRCC-04/14/2022 07:28: Tayabas 600MVA T01 de-energized at 0724H (Planned Outage). [WEBSMS] | CLUZ
4/14/2022 9:47:27 AM | LRCC-04/14/2022 07:25: Limay-BPC 230kV Line 1 & 2 de-energized at 0714H and 0713H (Planned Outage). [WEBSMS] | CLUZ
4/14/2022 9:47:25 AM | LRCC-04/14/2022 07:17: Las Pinas (Zapote) 300MVA T04 de-energized at 0704H (Planned Outage). [WEBSMS] | CLUZ
4/14/2022 9:47:23 AM | LRCC-04/14/2022 07:08: Las Pinas(Zapote)-Dasmarinas 230kV Line 2 de-energized 0701H (Planned Outage) [WEBSMS] | CLUZ
4/14/2022 9:47:21 AM | LRCC-04/14/2022 06:11: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11448MW, PK=8410MW, RR=321MW, NetOpMargin: AM=2717, PM=2481, EVE=1535 Highest Unit O/L: Sual 1 @ 647MW Derated Plant: Sual 2 @500MW, Sta Rita 30 &40 @180MW each, Ilijan @540MW, GMEC 2 @300MW [WEBSMS] | CLUZ
4/14/2022 9:47:19 AM | LRCC-04/14/2022 05:06: Muntinlupa (Sucat) 230 kV Bus B restored at 0500H (Planned Outage). [WEBSMS] | CLUZ
4/13/2022 4:14:18 PM | LEYTE ACC-04/13/22: PARANAS SS, 69kV Taft Feeder opened/closed at 1559H/1602H to facilitate normalization of Sta Rita SS Quinapondan Feeder. Tripper cleared. | CVIS
4/13/2022 2:17:00 PM | LRCC-04/13/2022 14:08: Balsik 230kV Bus 2 restored at 1402H (Unplanned Outage). [WEBSMS] | CLUZ
4/13/2022 1:06:41 PM | VRCC-04/13/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2450MW, PK=2047MW, RR=40MW, NetOpMargin: PM=363, EVE=309 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 275, TPC at 82 MW [WEBSMS] | CVIS
4/13/2022 12:43:15 PM | LRCC-04/13/2022 12:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12747MW, PK=10018MW, RR=391MW, NetOpMargin: PM=2338, EVE=2247 Highest Unit O/L: Sual 1 at 600MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, QPPL at 450MW, Sta. Rita 30 at 240MW [WEBSMS] | CLUZ
4/13/2022 9:52:53 AM | LRCC-04/13/2022 09:46: Balsik 500kV Bus A de-energized at 0943H (unplanned Outage). [WEBSMS] | CLUZ
4/13/2022 9:42:49 AM | LRCC-04/13/2022 09:39: Binan-Calaca 230kV Line 1 restored at 0938H (Unplanned Outage).. [WEBSMS] | CLUZ
4/13/2022 8:28:54 AM | LRCC-04/13/2022 08:20: Balsik 230kV Bus 2 de-energized at 0820H (Unplanned Outage). [WEBSMS] | CLUZ
4/13/2022 8:18:50 AM | LRCC-04/13/2022 08:10: Binan - San Pedro 115kV Line restored at 0733H. (Planned Outage) [WEBSMS] | CLUZ
4/13/2022 7:18:32 AM | LRCC-04/13/2022 07:11: Naga-Tayabas 230kV L2 de-energized at 0618H (Planned Outage). [WEBSMS] | CLUZ
4/13/2022 7:08:28 AM | LRCC-04/13/2022 07:02: San Jose-Angat 115kV Line 3 de-energized at 0619H (Planned Outage). [WEBSMS] | CLUZ
4/13/2022 6:44:57 AM | PANAY ACC-04/13/22 06:22: DINGLE SS, Dingle-Dumangas 69KV (5LI1DIN-DUM), TIME OUT: 06:11:00, TIME IN: 06:19:00, Load: 12.2mw, RELAY: OVERCURRENT AC, Customers fault, WEATHER: FAIR | CVIS
4/13/2022 6:25:19 AM | LRCC-04/13/2022 06:20: San Jose-Tayabas 230kV L2 de-energized at 0618H (Planned Outage). [WEBSMS] | CLUZ
4/13/2022 6:25:17 AM | LRCC-04/13/2022 06:16: San Juan(Kalayaan)-Calauan 230kV Line 2 restored at 0606H. (Planned Outage) [WEBSMS] | CLUZ
4/13/2022 6:07:53 AM | VRCC-04/13/2022 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2527MW, PK=2012MW, RR=36MW, NetOpMargin: AM=479, PM=384, EVE=348 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 332, TPC at 82 MW, Weather Condition: Blue Alert [WEBSMS] | CVIS
4/13/2022 5:47:46 AM | LRCC-04/13/2022 05:44: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12798MW, PK=9947MW, RR=399MW, NetOpMargin: AM=2452, PM=2461, EVE=2216 Highest Unit O/L: Sual 1 at 600MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, QPPL at 450MW, Sta. Rita 30 at 240MW [WEBSMS] | CLUZ
4/13/2022 5:39:55 AM | LRCC-04/13/2022 05:35: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) (formerly ``AGATON``) was estimated based on all available data at 65 km Southeast of Guiuan, Eastern Samar (10.7?N, 126.2?E). [WEBSMS] | CLUZ
4/13/2022 5:39:54 AM | LRCC-04/13/2022 05:30: San Jose-Taytay(Dolores) 230kV Line 1 restored at 0529H. (Planned Outage) [WEBSMS] | CLUZ
4/13/2022 5:16:27 AM | LEYTE ACC-04/13/22 05:08: STA. RITA SS, 69kV Sta. Rita-Quinapondan line tripped at 0458H, phase BN, 46.56kms., load=2.8MW. Reclose attempt failed with same indications. Sustained. WEATHER: Tropical Depression Agaton. | CVIS
4/13/2022 4:56:21 AM | LRCC-04/13/2022 04:52: Malolos-Hermosa 230kV Line and Malolos 230kV Bus 2 restored at 0447H and 0446H, respectively. (Planned Outage) [WEBSMS] | CLUZ
4/13/2022 4:50:34 AM | LEYTE ACC-04/13/22 04:49: STA. RITA SS, 69kV Sta. Rita-Quinapondan line tripped at 0439H, phase BN, 46.56kms., load=3.4MW. Restored at 0445H.WEATHER: FAIR | CVIS
4/13/2022 4:17:03 AM | LEYTE ACC-04/13/22 04:03: CALBAYOG SS, 69kV Palanas Cara-Allen-Lao-ang line tripped at 0350H, phase AN, Z1, 45.4kms, load=11.5MW. Restored at 0353H. WEATHER: FAIR | CVIS
4/13/2022 4:07:00 AM | LEYTE ACC-04/13/22 02:13: ORMOC SS, 69kV Tunga-Tolosa-San Isidro line restored at 0152H, while 69kV Ormoc-Tolosa-San Isidro line is extended up to Maasin Ss at 0200H. Energized whole SOLECO franchise. WEATHER: TROPICAL DEPRESSION | CVIS
4/13/2022 4:03:37 AM | PANAY ACC-04/13/22 03:52: PANIT-AN SS, Panit-an-Sara 69 kV Line (5LI1PNT-SAR), TIME OUT: 03:30:00, TIME IN: , RELAY: Z1, BN, 4.954kms., WEATHER: TROPICAL DEPRESSION; Test energized at 0351H but failed with same indication. Sustained fault. | CVIS
4/13/2022 3:43:32 AM | LRCC-04/13/2022 03:40: Binan-Calaca 230kV Line 1 tripped at 0335H. [WEBSMS] | CLUZ
4/13/2022 2:32:48 AM | LRCC-04/13/2022 02:30: Dasmarinas-Rosario 115kV Line restored at 0228H. (Unplanned Outage) [WEBSMS] | CLUZ
4/13/2022 1:19:40 AM | LRCC-04/13/2022 01:09: SLPGC Unit 2 offline at 0106H. (Planned Outage) [WEBSMS] | CLUZ
4/13/2022 12:34:05 AM | LRCC-04/13/2022 00:33: Dasmarinas-Rosario 115kV Line de-energized at 0032H. (Unplanned Outage) [WEBSMS] | CLUZ
4/13/2022 12:30:43 AM | LRCC-04/13/2022 00:23: San Jose-Taytay(Dolores) 230kV Line 1 de-energized at 0021H. (Planned Outage) [WEBSMS] | CLUZ
4/13/2022 12:20:36 AM | LRCC-04/13/2022 00:20: Malolos-Hermosa 230kV Line and Malolos 230kV Bus 2 de-energized at 0015H and 0013H, respectively. (Planned Outage) [WEBSMS] | CLUZ
4/12/2022 11:57:07 PM | LRCC-04/12/2022 23:53: Dinginin 1 offline at 2350H. (Planned Outage) [WEBSMS] | CLUZ
4/12/2022 11:40:12 PM | LRCC-04/12/2022 23:39: Binan - San Pedro 115kV Line de-energized at 2334H. (Planned Outage) [WEBSMS] | CLUZ
4/12/2022 10:53:21 PM | LEYTE ACC-04/12/22 22:55:ORMOC SS,69kV Ormoc-Lemon-Tunga line energized back at 2233H with clearance from O&M up to Tunga ABS#1,WEATHER: TROPICAL DEPRESSION(Agaton) | CVIS
4/12/2022 10:33:14 PM | LRCC-04/12/2022 22:30: San Jose 115kV Bus 2 restored at 2229H. (Unplanned Outage) [WEBSMS] | CLUZ
4/12/2022 10:19:52 PM | LRCC-04/12/2022 22:12: San Juan(Kalayaan)-Calauan 230kV Line 2 de-energized at 2211H. (Planned Outage) [WEBSMS] | CLUZ
4/12/2022 9:56:20 PM | LEYTE ACC-04/12/22: ORMOC SS, 69kV Ormoc-Lemon-Tolosa-San Isidro-Sogod-Nasaug tripped at 2148H, load=23.7MW. Indications to follow. WEATHER: Tropical Depression Agaton | CVIS
4/12/2022 7:49:04 PM | NEGROS ACC: 04/12/2022, PGPP1 U3 re-online at 1939H. | CVIS
4/12/2022 6:58:53 PM | NEGROS ACC: 04/12/2022, PGPP1 U3 (37.2 MW) auto-tripped at 1840H. Cause off tripping under investigation | CVIS
4/12/2022 6:35:15 PM | LRCC-04/12/2022 18:27: San Jose 115kV Bus 2 de-energized at 1826H. (Unplanned Outage) [WEBSMS] | CLUZ
4/12/2022 6:01:48 PM | VRCC-04/12/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2356MW, PK=1872MW, RR=49MW, NetOpMargin: EVE=435 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 332, TPC at 82 MW, Weather Condition: Blue Alert [WEBSMS] | CVIS
4/12/2022 6:01:46 PM | LRCC-04/12/2022 17:55: Balsik 1000MVA T01 restored at 1752H (Unplanned Outage). [WEBSMS] | CLUZ
4/12/2022 5:38:22 PM | LRCC-04/12/2022 17:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13236MW, PK=9736MW, RR=361MW, NetOpMargin: EVE=3139 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, Sta. Rita 30 at 240MW [WEBSMS] | CLUZ
4/12/2022 3:51:03 PM | LRCC-04/12/2022 15:48: Mariveles 500kV Bus 1 restored at 1546H (Unplanned Outage). [WEBSMS] | CLUZ
4/12/2022 1:30:11 PM | VRCC-04/12/2022 13:26: Daan Bantayan SS 69 KV Lanao Feeder re-energized at 1325H [WEBSMS] | CVIS
4/12/2022 1:06:55 PM | VRCC-04/12/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2454MW, PK=2007MW, RR=49MW, NetOpMargin: PM=398, EVE=435 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 332, TPC at 82 MW, Weather Condition: Blue Alert [WEBSMS] | CVIS
4/12/2022 12:56:40 PM | LRCC-04/12/2022 12:55: Mariveles 500kV Bus 1 de-energized at 1253H (Unplanned Outage). [WEBSMS] | CLUZ
4/12/2022 12:33:20 PM | LRCC-04/12/2022 12:27: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13507MW, PK=10244MW, RR=391MW, NetOpMargin: PM=2872, EVE=2498 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, Sta. Rita 30 at 240MW [WEBSMS] | CLUZ
4/12/2022 12:33:09 PM | VRCC-04/12/2022 12:32: Daan Bantayan SS 69 KV Lanao Feeder auto-tripped at 1222H with 14.3 MW load, Phase CN fault, Weather: Rainy [WEBSMS] | CVIS
4/12/2022 9:29:31 AM | LRCC-04/12/2022 09:22: San Rafael 230kV Bus B restored after the isolation of Capacitor breaker on lockout at 0920H (Unplanned Outage). [WEBSMS] | CLUZ
4/12/2022 9:19:24 AM | LRCC-04/12/2022 09:10: San Rafael 230kV Bus B de-energized for isolation of Capacitor breaker on lockout at 0908H (Unplanned Outage). [WEBSMS] | CLUZ
4/12/2022 6:50:03 AM | LRCC-04/12/2022 06:47: Balsik-Mariveles 500kV L1 and Balsik 1000MVA T01 de-energized at 0631H and 0635H, respectively (Unplanned Outage). [WEBSMS] | CLUZ
4/12/2022 6:03:10 AM | VRCC-04/12/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2533MW, PK=2017MW, RR=72MW, NetOpMargin: AM=444, PM=416, EVE=445 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 332MW, TPC at 82MW. Visayas grid on blue alert status. [WEBSMS] | CVIS
4/12/2022 5:49:45 AM | LRCC-04/12/2022 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13427MW, PK=9770MW, RR=381MW, NetOpMargin: AM=3276, PM=3045, EVE=3442 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, Masinloc 3 at 170MW, Sta. Rita 30 at 240MW [WEBSMS] | CLUZ
4/12/2022 5:26:18 AM | PANAY ACC-04/12/22 05:22: DINGLE SS, Dingle-PDPP1 138 kV L1 (CO) (7LI1DIN-PD1), TIME IN: 05:17:00, RELAY: NONE, WEATHER: RAINY. Cause under investigation. | CVIS
4/12/2022 5:26:17 AM | PANAY ACC-04/12/22 05:22: DINGLE SS, Dingle-PDPP1 138 kV L1 (CO) (7LI1DIN-PD1), TIME IN: 05:17:00, RELAY: NONE, WEATHER: RAINY. Cause under investigation. | CVIS
4/12/2022 5:06:13 AM | PANAY ACC-04/12/22 04:58: DINGLE SS, Dingle-PDPP1 138 kV L1 (CO) (7LI1DIN-PD1), TIME OUT: 04:54:00, WEATHER: RAINY. Cause under investigation. | CVIS
4/12/2022 5:02:48 AM | LRCC-04/12/2022 04:56: Weather Update: At 3:00 AM today, the center of Tropical Depression ``AGATON`` was estimated based on all available data over the coastal waters of Tacloban City, Leyte (11.2?N, 125.1?E) with maximum sustained winds of 45 km/h near the center and gustiness of up to 70 km/h. It is almost stationary. [WEBSMS] | CLUZ
4/12/2022 1:21:50 AM | LEYTE ACC-04/12/22: ORMOC SS, 69kV Ormoc-Simangan-Baybay (extended up to Ley IV Hilongos),emergency hotspot correction done, TIME IN: 01:17:00, WEATHER: TROPICAL STORM AGATON | CVIS
4/12/2022 12:11:24 AM | LEYTE ACC-04/11/22: ORMOC SS, 69kV Ormoc-Simangan-Baybay-Hilongos emergency hot-spot correction on ABS 1 Baybay, TIME OUT: 23:59:00, load=14.3MW, WEATHER: Tropical Storm Agathon | CVIS
4/12/2022 12:11:22 AM | LEYTE ACC-04/11/22: ORMOC SS, 69kV Ormoc-Simangan-Baybay-Hilongos emergency hot-spot correction on ABS 1 Baybay, TIME OUT: 23:59:00, load=14.3MW, WEATHER: Tropical Storm Agathon | CVIS
4/11/2022 10:14:08 PM | LEYTE ACC-04/11/22 22:05: CALBAYOG SS, 69kV Palanas Cara-Allen-Lao-ang line tripped at 2157H, phase AN, Z1, 40.69kms., load=14.9MW. Restored at 2200H. WEATHER: Tropical Depression | CVIS
4/11/2022 10:00:39 PM | LEYTE ACC-04/11/22 21:50: ORMOC SS, 69kV Ormoc-Simangan-Baybay line tripped at 2136H, phae ABC, O/C inverse trip, load=14MW. WEATHER: Tropical Depression | CVIS
4/11/2022 9:50:36 PM | LEYTE ACC-04/11/22 21:37: ORMOC SS, 69kV Ormoc-Simangan-Baybay line tripped at 2118H, phase AC, O/C Inverse trip, load=20.2MW. Restored per clearance from Line Engineer at 2128H. WEATHER: TROPICAL DEPRESSION | CVIS
4/11/2022 8:50:13 PM | PANAY ACC-04/11/22 20:46: STA. BARBARA SS, MORE LaPaz Ss, TIME IN: 20:45:00, RELAY: SIPS activation, WEATHER: FAIR, Last feeder restored. | CVIS
4/11/2022 8:03:18 PM | PANAY ACC-04/11/22 19:55: STA. BARBARA SS, Sta. Barbara 138/69/13.8 kV T2 (50MVA) (7XF02SBA), TIME IN: 19:54:00, RELAY: Non electrical trip, WEATHER: Rainy; Cause due to moisture at local panel board. | CVIS
4/11/2022 7:06:21 PM | LEYTE ACC-04/11/22 19:03: TGPP, GCGI-TGPP unit no. 3 cut in to the system at 1859H. WEATHER: TROPICAL STORM | CVIS
4/11/2022 6:05:59 PM | VRCC-04/11/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2367MW, PK=1821MW, RR=69MW, NetOpMargin: EVE=477 Highest Unit O/L: TVI at 169 MW per unit Derated Plant: EDC at 328, TPC at 82, LGPP at 80 MW, Weather Condition: Blue Alert [WEBSMS] | CVIS
4/11/2022 5:45:54 PM | LRCC-04/11/2022 17:42: Naga-Tayabas 230kV line 2 restored at 1741H. (Planned Outage) [WEBSMS] | CLUZ
4/11/2022 5:31:17 PM | LRCC-04/11/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12795MW, PK=9427MW, RR=361MW, NetOpMargin: EVE=3007 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, Sual 2 at 550MW, Ilijan at 851MW and Sta Rita 30 at 240MW [WEBSMS] | CLUZ
4/11/2022 4:53:33 PM | PANAY ACC-04/11/22 16:33: STA. BARBARA SS, MORE LaPaz Ss, TIME OUT: 04:32:00, RELAY: SIPS activation, Ld: 12.1MW; WEATHER: Rainy; SIPS activated due to tripping of SB Ss 50MVATR2. | CVIS
4/11/2022 4:53:32 PM | PANAY ACC-04/11/22 16:33: STA. BARBARA SS, Sta. Barbara 138/69/13.8 kV T2 (50MVA) (7XF02SBA), TIME OUT: 04:32:00, RELAY: Non electrical trip, WEATHER: FAIR; Still under investigation. load transfered to 50MVA TR1. | CVIS
4/11/2022 4:06:43 PM | PANAY ACC-04/11/22 15:59: STA. BARBARA SS, MORE- Lapaz SS, TIME IN: 15:58:00, Last feeder in. | CVIS
4/11/2022 4:06:42 PM | PANAY ACC-04/11/22 15:52: STA. BARBARA SS, Sta. Barbara 138/69/13.8 kV T2 (50MVA) (7XF02SBA), TIME IN: 15:51:00, RELAY: M2: Non elec trip, WEATHER: FAIR; Cause of tripping was to moisture at local panel board. | CVIS
4/11/2022 3:45:35 PM | LRCC-04/11/2022 15:45: Masinloc 3 on line at 1538H (Unplanned Outage). [WEBSMS] | CLUZ
4/11/2022 3:18:41 PM | LEYTE ACC-04/11/22 15:00: ORMOC SS, 69kV Ormoc-Simangan-Baybay line energized up to Maasin Ss at 1451H. Energized Leyeco IV ( San Agustin, Baybay & Hilongos) WEATHER: TROPICAL STORM | CVIS
4/11/2022 1:21:12 PM | VRCC-04/11/2022 13:14: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2553MW, PK=1818MW, RR=72MW, NetOpMargin: PM=663, EVE=477 Highest Unit O/L: TVI at 169 MW per unit Derated Plant: EDC at 328, TPC at 82, LGPP at 80 MW, Weather Condition: Blue Alert [WEBSMS] | CVIS
4/11/2022 12:47:59 PM | PANAY ACC-04/11/22 12:05: STA. BARBARA SS, MORE- Lapaz SS, TIME OUT: 12:01, Load:19.4MW; RELAY: SIPS, Isolated due to tripping of Sta. Barbara 50MVA TR#2 | CVIS
4/11/2022 12:37:37 PM | PANAY ACC-04/11/22 12:05: STA. BARBARA SS, MORE- Lapaz SS, TIME OUT: 12:01, Load:19.4MW; RELAY: SIPS, Isolated due to tripping of Sta. Barbara 50MVA TR#2 | CVIS
4/11/2022 12:37:36 PM | PANAY ACC-04/11/22 12:05: STA. BARBARA SS, MORE- Lapaz SS, TIME OUT: 12:01, Load:19.4MW; RELAY: SIPS, Isolated due to tripping of Sta. Barbara 50MVA TR#2 | CVIS
4/11/2022 12:37:34 PM | PANAY ACC-04/11/22 12:05: STA. BARBARA SS, MORE- Lapaz SS, TIME OUT: 12:01, RELAY: SIPS, Isolated due to tripping of Sta. Barbara 50MVA TR#2 | CVIS
4/11/2022 12:34:13 PM | PANAY ACC-04/11/22 12:04: STA. BARBARA SS, Sta. Barbara 138/69/13.8 kV T2 (50MVA) (7XF02SBA), TIME OUT: 12:01, RELAY: M1: none, M2: Non elec trip, WEATHER: Rainy; Cause: Under investigation | CVIS
4/11/2022 12:24:09 PM | LRCC-04/11/2022 12:21: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13094MW, PK=10377MW, RR=391MW, NetOpMargin: PM=2326, EVE=2687 Highest Unit O/L: Sual 1 at 647MW Derated Plant: GMEC 2 at 300MW, Sual 2 at 550MW, GNPD 1 at 501MW, Ilijan at 851MW and Sta Rita 30 at 240MW [WEBSMS] | CLUZ
4/11/2022 9:23:08 AM | LEYTE ACC-04/11/22 09:22: MAASIN SS,(7XF02MAA)50MVA 138/69kV TR#2 energized via 69kV at 0908H for S/S use only,WEATHER: TROPICAL STORM(Agaton) | CVIS
4/11/2022 9:02:57 AM | LEYTE ACC-04/11/22 09:09: MAASIN SS,Maasin Nasaug 69kVL restored via Tunga feeder at 0808H, WEATHER: TROPICAL STORM (Agaton) | CVIS
4/11/2022 6:38:49 AM | LEYTE ACC-04/11/22 06:38:PARANAS SS, Paranas-Calbayog 138 kV L2 ,Energized 0616H from voltage regulation, WEATHER: TROPICAL DEPRESSION(Agaton) | CVIS
4/11/2022 6:28:44 AM | LRCC-04/11/2022 06:21: Naga-Tayabas 230kV line 2 de-energized at 0621H. (Planned Outage) [WEBSMS] | CLUZ
4/11/2022 6:05:22 AM | VRCC-04/11/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2535MW, PK=2163MW, RR=40MW, NetOpMargin: AM=332, PM=201, EVE=233 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 328, TPC at 82, LGPP at 80 MW, Weather Condition: Blue Alert [WEBSMS] | CVIS
4/11/2022 6:05:19 AM | LRCC-04/11/2022 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13042MW, PK=10086MW, RR=321MW, NetOpMargin: AM=2635, PM=2022, EVE=2522 Highest Unit O/L: Sual 1 at 647MW Derated Plant: GMEC 2 at 300MW, Sual 2 at 550MW, GNPD 1 at 501MW, Ilijan at 851MW and Sta Rita 30 at 240MW [WEBSMS] | CLUZ
4/11/2022 6:05:17 AM | LRCC-04/11/2022 05:57: Weather Update: TROPICAL STORM ``AGATON`` CONTINUES TO MOVE VERY SLOWLY AND IS NOW OVER SAN PABLO BAY. The center of Tropical Storm ``AGATON`` was estimated over the coastal waters of Tanauan, Leyte (11.1N, 125.1E). I has a maximum sustained winds of 65 km/h near the center, gustiness of up to 90 km/h. It is moving West northwestward slowly. [WEBSMS] | CLUZ
4/11/2022 1:31:06 AM | LEYTE ACC-04/11/22: GCGI-TGPP Unit #3 tripped at 0112H, under assessment | CVIS
4/11/2022 1:31:03 AM | LRCC-04/11/2022 01:11: Dona Imelda(Araneta) 300MVA T01 was restored at 0110H. (Planned Outage) [WEBSMS] | CLUZ
4/11/2022 12:09:34 AM | LEYTE ACC-04/11/22: ORMOC SS, 138kV Ormoc-Maasin Line 1&2 tripped at 0003H indications to follow. WEATHER: Tropical Storm Agaton. | CVIS
4/11/2022 12:09:33 AM | LEYTE ACC-04/11/22: ORMOC SS, 138kV Ormoc-Maasin Line 1&2 tripped at 0003H indications to follow. WEATHER: Tropical Storm Agaton. | CVIS
4/10/2022 11:46:06 PM | LEYTE ACC-04/10/22: ORMOC SS, 69kV Ormoc-Simangan re-energized at 2332H up to ABS Simangan and LEYECO IV Baybay transferred to Maasin SS. Line patrol continues. Weather: Tropical Storm Agaton | CVIS
4/10/2022 11:46:05 PM | LEYTE ACC-04/10/22: ORMOC SS, 69kV Ormoc-Simangan re-energized at 2332H up to ABS Simangan and LEYECO IV Baybay transferred to Maasin SS. Line patrol continues. Weather: Tropical Storm Agaton | CVIS
4/10/2022 10:45:42 PM | LEYTE ACC-04/10/22: ORMOC SS, 69kV Ormoc-Simangan-Baybay tripped, indications to follow, TIME OUT: 22:33:00,, load=13.3MW, WEATHER: Tropical Storm ``Agaton`` | CVIS
4/10/2022 8:48:28 PM | LRCC-04/10/2022 20:41: Botolan-Labrador 230kV line restored at 2040H. (Planned Outage) [WEBSMS] | CLUZ
4/10/2022 8:38:24 PM | LRCC-04/10/2022 20:38: Labrador 230kV Bus 1 energized at 2035H. (Planned Outage) [WEBSMS] | CLUZ
4/10/2022 8:01:37 PM | LEYTE ACC-04/10/22 19:55: MAASIN SS, Nasaug-Sogod-St. Bernard 69 kV line tripped at 1952H, Phase BN, load=3.1MW. Restored at 1954H. Weather:Tropical Depression (Agaton), WEATHER: TROPICAL DEPRESSION | CVIS
4/10/2022 7:17:56 PM | LRCC-04/10/2022 19:17: Balsik-Mariveles 500kV line 1 looped(Mariveles side) at 1913H. On-going energization and commissioning. [WEBSMS] | CLUZ
4/10/2022 6:06:19 PM | VRCC-04/10/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2342MW, PK=1821MW, RR=40MW, NetOpMargin: EVE=481 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 328MW, TPC at 82MW. Visayas grid on blue alert status. [WEBSMS] | CVIS
4/10/2022 5:56:16 PM | LEYTE ACC-04/10/22 17:47: MAAIN SS, 69kV Tolosa-San Isidro line manually open/closed at 1724H/1733H, 69kV Maasin-Nasaug-San Isidro line back to normal configuration at 1741H. WEATHER: TROPICAL DEPRESSION | CVIS
4/10/2022 5:56:13 PM | LRCC-04/10/2022 17:47: Balsik-Mariveles 500kV Line 2 commissioned at 1744H. [WEBSMS] | CLUZ
4/10/2022 5:43:03 PM | LRCC-04/10/2022 17:40: Balsik-Mariveles 500kV Line 1 restored at 1725H. (Planned Outage) [WEBSMS] | CLUZ
4/10/2022 5:43:01 PM | LRCC-04/10/2022 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12682MW, PK=9148MW, RR=325MW, NetOpMargin: EVE=3209 Highest Unit O/L: Sual 1 at 600MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, SLPGC 2 at 110MW, Sta. Rita 20 at 240MW, Dinginin 1 at 501MW [WEBSMS] | CLUZ
4/10/2022 5:30:40 PM | LRCC-04/10/2022 17:22: Balsik-Mariveles 500kV Line 2 looped at 1719H. (Ongoing Commissioning) [WEBSMS] | CLUZ
4/10/2022 5:17:06 PM | LRCC-04/10/2022 17:08: Binan-Calamba 230kV Line 2 restored at 1708H. (Planned Outage) [WEBSMS] | CLUZ
4/10/2022 5:09:47 PM | LEYTE ACC-04/10/22 15:40: MAASIN SS, Nasaug-Bontoc 69 kV line portion energized at 1526H. WEATHER: TROPICAL DEPRESSION | CVIS
4/10/2022 5:09:45 PM | LEYTE ACC-04/10/22 16:50: MAASIN SS, Himayangan-St. Bernard 69 kV line portion energized at 1637H. WEATHER: TROPICAL DEPRESSION | CVIS
4/10/2022 5:05:02 PM | LRCC-04/10/2022 17:01: San Jose 115kV Bus 2 restored at 1659H. (Planned Outage) [WEBSMS] | CLUZ
4/10/2022 4:57:08 PM | NEGROS ACC: 04/10/2022, 69kV Mabinay-Bayawan Sub T/L energized at 1655H after completion of maintenance activities. | CVIS
4/10/2022 4:57:07 PM | NEGROS ACC: 04/10/2022, 69kV Mabinay-Bayawan Sub T/L energized at 1655H after completion of maintenance activities. | CVIS
4/10/2022 4:57:05 PM | VRCC-04/10/2022 16:54: Correction: 138 KV Colon-Cebu L2 indication on both sides, phase C fault only. [WEBSMS] | CVIS
4/10/2022 4:57:04 PM | VRCC-04/10/2022 16:51: 138 KV Colon-Cebu L2 energized at 1651H. [WEBSMS] | CVIS
4/10/2022 4:40:12 PM | VRCC-04/10/2022 16:32: 138 KV Colon-Cebu L2 tripped at 1625H w/a load of 125 MW, Cebu SS: BC, differential tripped. Colon: differential, ABC. [WEBSMS] | CVIS
4/10/2022 2:29:44 PM | VRCC-04/10/2022 14:29: 138 KV Colon Cebu L3 energized at 1427H. [WEBSMS] | CVIS
4/10/2022 1:32:37 PM | PANAY ACC-04/10/22 13:09: STA. BARBARA SS, Sta. Barbara-Miagao/COSMO 69 kV Line (5LI1SBA-SJD), TIME IN: 13:05, Pre-arranged maintenance | CVIS
4/10/2022 1:22:34 PM | PANAY ACC-04/10/22 13:09: STA. BARBARA SS, Sta. Barbara-Miagao/COSMO 69 kV Line (5LI1SBA-SJD), TIME IN: 13:05, Pre-arranged maintenance | CVIS
4/10/2022 1:22:33 PM | PANAY ACC-04/10/22 13:09: STA. BARBARA SS, Sta. Barbara-Miagao/COSMO 69 kV Line (5LI1SBA-SJD), TIME IN: 13:05, Pre-arranged maintenance | CVIS
4/10/2022 1:08:19 PM | VRCC-04/10/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2578MW, PK=1818MW, RR=40MW, NetOpMargin: PM=695, EVE=506 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 320MW, TPC at 82MW [WEBSMS] | CVIS
4/10/2022 12:54:53 PM | LRCC-04/10/2022 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12965MW, PK=8913MW, RR=327MW, NetOpMargin: PM=3725, EVE=3090 Highest Unit O/L: Dinginin at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, SLPGC 2 at 110MW, Sta. Rita 20 at 240MW [WEBSMS] | CLUZ
4/10/2022 12:08:30 PM | LRCC-04/10/2022 12:02: San Lorenzo-Batangas 230kV Line 2 restored at 12:01H. (Planned Outage) [WEBSMS] | CLUZ
4/10/2022 10:38:51 AM | LEYTE ACC-04/10/22 10:41: ORMOC SS, Tolosa-San Isidro re-energized at 1023H, extended up to Bontoc/San Miguel-Himay-angan 69kV Line portion only. Still isolated Himay-angan-St. Bernard and Nasaug-Bontoc 69kV Lines, affected customer: Soleco (St. Bernard). Weather: Tropical Depression ``Agaton. | CVIS
4/10/2022 9:40:52 AM | VRCC-04/10/2022 09:37: Visayas Grid is on ``BLUE ALERT`` status starting 0935H due to TS ``Agaton`` probable landfall in Eastern Samar this afternoon. [WEBSMS] | CVIS
4/10/2022 9:27:20 AM | LEYTE ACC-04/10/22 09:29: ORMOC SS, Tolosa-San Isidro extended up to Bontoc/San Miguel-St. Bernard 69kV Line tripped at 0907H, indication to follow due to NO Operator on duty at Tolosa PCB station. Load=8.49MW. Weather: Tropical Depression ``Agaton``. | CVIS
4/10/2022 9:17:18 AM | LEYTE ACC-04/10/22 09:20: ORMOC SS, Himay-angan - St. Bernard 69kV Line re-energized at 0906H via 69kV Tunga Feeder. Still isolated Nasaug - Bontoc 69kV Line portion. Weather: Tropical Depression ``Agaton`` | CVIS
4/10/2022 8:42:33 AM | LEYTE ACC-04/10/22 08:45: ISABEL SS, Isabel - LEYECO 5 69kV Line (customers owned) tripped/restored at 0826H/0833H, ind.: Phase-B. Load=3.1MW. Weather: Tropical Depression ``Agaton``. | CVIS
4/10/2022 8:42:32 AM | PANAY ACC-04/10/22 08:21: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME OUT: 08:19,Load:28.6MW; Pre-arranged maintenance; ETR:1800H | CVIS
4/10/2022 8:42:30 AM | PANAY ACC-04/10/22 08:21: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME OUT: 08:19,Load:28.6MW; Pre-arranged maintenance; ETR:1800H | CVIS
4/10/2022 8:16:05 AM | LEYTE ACC-04/10/22 08:26: ORMOC SS, San Miguel - Himay-angan 69kV Line portion re-energized at 0805H, serving power to Soleco (Himay-angan). Still isolated Himay-angan - St. Bernard 69kV Line. Weather: Tropical Depression ``Agaton``. | CVIS
4/10/2022 8:16:04 AM | LEYTE ACC-04/10/22 08:15: ORMOC SS, San Isidro - Bontoc/San Miguel 69kV Line re-energized at 0757H via 69kV Tunga Feeder. Still isolated San Miguel - St. Bernard 69kV Line. Weather: Tropical Depression ``Agaton``. | CVIS
4/10/2022 7:39:09 AM | LRCC-04/10/2022 07:38: Botolan-Labrador 230kV Line de-energized at 0735H. (Planned Outage) [WEBSMS] | CLUZ
4/10/2022 7:29:02 AM | LRCC-04/10/2022 07:27: San Jose 115kV Bus 2 de-energized at 0725H. (Planned Outage) [WEBSMS] | CLUZ
4/10/2022 7:29:00 AM | LRCC-04/10/2022 07:21: Balsik-Mariveles 500kV Line 1 de-energized at 0629H. (Planned Outage) [WEBSMS] | CLUZ
4/10/2022 7:18:15 AM | VRCC-04/10/2022 07:15: 138 KV Colon Cebu L3 de energized at 0715H, corrective maint. [WEBSMS] | CVIS
4/10/2022 6:28:26 AM | LRCC-04/10/2022 06:22: San Lorenzo-Batangas 230kV Line 2 de-energized at 0622H. (Planned Outage) [WEBSMS] | CLUZ
4/10/2022 6:18:20 AM | NEGROS ACC: 04/10/2022, 69kV Mabinay-Bayawan Sub T/L(5.36MW) de-energized at 0605H due to PMS. | CVIS
4/10/2022 6:18:17 AM | LRCC-04/10/2022 06:15: Binan-Calamba 230kV Line 2 de-energized at 0614H. (Planned Outage) [WEBSMS] | CLUZ
4/10/2022 6:08:15 AM | VRCC-04/10/2022 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2558MW, PK=1796MW, RR=60MW, NetOpMargin: AM=702, PM=668, EVE=398 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 378MW, TPC at 82MW, TGPP at 80MW [WEBSMS] | CVIS
4/10/2022 6:08:13 AM | LRCC-04/10/2022 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13107MW, PK=8010MW, RR=315MW, NetOpMargin: AM=4782, PM=4524, EVE=3808 Highest Unit O/L: Sual 1 at 600MW Derated Plant: GNPD 1 @ 550MW, Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, [WEBSMS] | CLUZ
4/10/2022 5:16:03 AM | LRCC-04/10/2022 05:11: Weather Update: Issued at 0400h, At 3:00 AM today, the center of Tropical Storm ``AGATON`` was estimated based on all available data over the coastal waters of Guiuan, Eastern Samar (11.0?N, 126.2?E) with maximum sustained winds of 65 km/h near the center and gustiness of up to 80 km/h. It is moving West Northwest at 10 km/h. Meanwhile, a Low Pressure Area (LPA) was estimated based on all available data at 415 km West Southwest of Puerto Princesa City, Palawan (8.2?N, 115.3?E). [WEBSMS] | CLUZ
4/10/2022 4:05:55 AM | LRCC-04/10/2022 04:05: Dona Imelda(Araneta) 300MVA T02 de-energized at 0401H. (Planned Outage) [WEBSMS] | CLUZ
4/10/2022 3:05:34 AM | LEYTE ACC-04/10/22 03:10: ORMOC SS,Tolosa-San Isidro 69 kV L ,tripped/restored,0048H/0248H, Z1, Phase CN, fd=0.91kms,load=5.0mw, with clearance from O&M,WEATHER: TROPICAL DEPRESSION(``Agaton``) | CVIS
4/10/2022 2:18:38 AM | LRCC-04/10/2022 02:12: Dona Imelda(Araneta) 300MVA T01 restored at 0210H. (Planned Outage) [WEBSMS] | CLUZ
4/10/2022 2:05:17 AM | LEYTE ACC-04/10/22 02:10: MAASIN SS, Nasaug-Sogod-St. Bernard 69 kV L,tripped at 0150H,load=1.5mw,Phase CN,Sustained line fault. WEATHER: TROPICAL DEPRESSION (Agaton) | CVIS
4/10/2022 1:41:41 AM | LEYTE ACC-04/10/22 01:46: MAASIN SS, Nasaug-Sogod-St. Bernard 69 kV L,tripped/restored,0049H/0118H,Phase CN,up to ABS San Miguel,load=4.0mw,Weather: Tropical Depression (Agaton) | CVIS
4/10/2022 1:08:11 AM | LEYTE ACC-04/10/22 01:06:ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69 kV L,tripped at 0048H/0058H,load=19.0mw,under assessment, with clearance from O&M,WEATHER: Tropical Depression ``Agaton`` | CVIS
4/9/2022 11:20:49 PM | LEYTE ACC-04/09/22 23:28: MAASIN SS, Nasaug-Sogod-St. Bernard 69 kV L restored at 2311H up to ABS San Miguel,Soleco Himayangan & St. Bernard still isolated, WEATHER: TROPICAL DEPRESSION | CVIS
4/9/2022 10:47:19 PM | LEYTE ACC-04/09/22 22:55: MAASIN SS,Nasaug-Sogod-St. Bernard 69 kV L tripped at 2237H,Phase CN,load=4.0mw,Sustained line fault.WEATHER: TROPICAL DEPRESSION. | CVIS
4/9/2022 10:33:48 PM | LEYTE ACC-04/09/22 22:43: MAASIN SS,Nasaug-Sogod-St. Bernard 69 kV L,tripped/restored,2205H/2213H,Phase-C/N,load=2.3mw, WEATHER: TROPICAL DEPRESSION | CVIS
4/9/2022 10:23:46 PM | LEYTE ACC-04/09/22 22:23: MAASIN SS,Nasaug-Sogod-St. Bernard 69 kV L ,tripped/restored at 2205H/2213H,Phase-C/N, load=2.3mw,WEATHER: TROPICAL DEPRESSION | CVIS
4/9/2022 10:23:44 PM | LEYTE ACC-04/09/22 22:23: MAASIN SS,Nasaug-Sogod-St. Bernard 69 kV L ,tripped/restored at 2201H/2204H,Phase-C/N, load=4.1mw,WEATHER: TROPICAL DEPRESSION | CVIS
4/9/2022 9:46:52 PM | LEYTE ACC-04/09/22: Greencore-TGPP Unit #3 cut-in at 2138H | CVIS
4/9/2022 8:59:57 PM | LRCC-04/09/2022 20:53: Balsik 500kV Bus 1 energized at 2050H (on going commissioning). [WEBSMS] | CLUZ
4/9/2022 8:02:59 PM | LRCC-04/09/2022 19:55: Balsik-Mariveles 500kV L2 energized in Balsik side at 1952H (on going commissioning). [WEBSMS] | CLUZ
4/9/2022 7:29:27 PM | LRCC-04/09/2022 19:20: Balsik 500kV Bus 2 commissioned at 1917H.. [WEBSMS] | CLUZ
4/9/2022 7:19:32 PM | VRCC-04/09/2022 19:10: Visayas Spot Peak as of April 09, 2022, 1694 MW at 1852H, previous spot peak 2224 MW at 1400H on May 16, 2019. [WEBSMS] | CVIS
4/9/2022 7:19:29 PM | LRCC-04/09/2022 19:09: Balsik 500kV Bus 2 energized at 1842H (on commissioning). [WEBSMS] | CLUZ
4/9/2022 7:05:56 PM | LRCC-04/09/2022 19:03: San Jose 750MVA T01 restored at 1903H. (Planned Outage) [WEBSMS] | CLUZ
4/9/2022 6:52:23 PM | NEGROS ACC: 04/09/2022, 69kV Bacolod-Silay Sub T/L energized at 1836H.Customer-owned and maintained line. | CVIS
4/9/2022 6:08:32 PM | VRCC-04/09/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2379MW, PK=1940MW, RR=40MW, NetOpMargin: EVE=399 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 378MW, TPC at 82MW, TGPP at 80MW [WEBSMS] | CVIS
4/9/2022 6:08:29 PM | LRCC-04/09/2022 18:02: Balsik 1000MVA T02 energized from 230kV side at 1754H. (Planned Outage) [WEBSMS] | CLUZ
4/9/2022 5:55:25 PM | NEGROS ACC: 04/09/2022, 69kV Cadiz-VMC Sub T/L restored at 1750H. Customer owned and maintained line. | CVIS
4/9/2022 5:51:08 PM | LRCC-04/09/2022 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12792MW, PK=8816MW, RR=301MW, NetOpMargin: EVE=3675 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, Sta. Rita 40 at 240MW [WEBSMS] | CLUZ
4/9/2022 5:41:04 PM | LRCC-04/09/2022 17:40: Weather Update: At 3:00 PM today, the center of Tropical Depression ``AGATON`` was estimated based on all available data at 130 km East of Guiuan, Eastern Samar (10.8N, 126.9E) with maximum sustained winds of 55 km/h near the center and gustiness of up to 70 km/h. It is moving Northeast slowly. [WEBSMS] | CLUZ
4/9/2022 5:41:02 PM | LRCC-04/09/2022 17:30: Nagsaag-Pantabangan 230kV line restored at 1729H. (Planned Outage) [WEBSMS] | CLUZ
4/9/2022 5:28:12 PM | LRCC-04/09/2022 17:25: Tayabas-Naga 230kV line 2 restored at 1722H. (Planned Outage) [WEBSMS] | CLUZ
4/9/2022 5:02:31 PM | LEYTE ACC-04/09/22: MAASIN SS, 69kV Himay-angan-St.Bernard portion restored at 16:50:00, RELAY: phase CN, WEATHER: TROPICAL DEPRESSION ``AGATON`` | CVIS
4/9/2022 4:37:56 PM | VRCC-04/09/2022 16:28: Compostela SS. 5 MVA TR at Lugo LESS energized at 1619H. [WEBSMS] | CVIS
4/9/2022 4:14:30 PM | NEGROS ACC: 04/09/2022, BACOLOD SS 69KV Bus 2 energized at 1604H after completion of P& E activity. | CVIS
4/9/2022 3:03:58 PM | NEGROS ACC: 04/09/2022, 69kV Cadiz-VMC -Silay-Mt.View Sub T/L de-energized at 1455H as per customers request due to unbalanced voltage.NONECO will conduct line patrol.Customer owned and maintained line. | CVIS
4/9/2022 2:53:46 PM | NEGROS ACC: 04/09/2022, 69kV Cadiz-VMC -Silay-Mt.View Sub T/L restored at 1415H.Customer owned and maintained line. | CVIS
4/9/2022 2:30:20 PM | NEGROS ACC: 04/09/2022, 69kV Cadiz-VMC -Silay-Mt.View Sub T/L (47.0MW) auto-tripped at 1405H with indication: Z2 CN DELAY, 24.27km.Customer owned and maintained line. | CVIS
4/9/2022 1:54:45 PM | PANAY ACC-04/09/22 13:36: PANIT-AN SS, Panit-an-Sara 69 kV Line (5LI1PNT-SAR), TIME IN: 13:35:00, WEATHER: FAIR, Pre-arranged maintenance activity. | CVIS
4/9/2022 1:54:44 PM | VRCC-04/09/2022 13:50: 138 KV Colon-Cebu L2 energized at 1347H. [WEBSMS] | CVIS
4/9/2022 1:43:28 PM | LEYTE ACC-04/09/22 13:45: MAASIN SS, San Miguel - Himay-angan 69kV Line re-energized at 1332H. Still isolated Himay-angan - St. Bernard 69kV Line, affected customer: Soleco (St. Bernard). Weather: Tropical Depression ``Agaton``. | CVIS
4/9/2022 1:09:52 PM | VRCC-04/09/2022 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2525MW, PK=1910MW, RR=76MW, NetOpMargin: PM=539, EVE=399 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 378MW, TPC at 82MW, TGPP at 80MW [WEBSMS] | CVIS
4/9/2022 1:03:36 PM | PANAY ACC-04/09/22 12:53: PANIT-AN SS, Panit-an-Sara 69 kV Line (5LI1PNT-SAR), TIME OUT: 12:53:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 1:03:24 PM | LRCC-04/09/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13133MW, PK=9007MW, RR=341MW, NetOpMargin: PM=3785, EVE=3551 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, Sta. Rita 40 at 240MW [WEBSMS] | CLUZ
4/9/2022 12:53:32 PM | PANAY ACC-04/09/22 12:48: CONCEPCION S/S SS, Concepcion-Sara 69 kV Line (5LI1CNE-SAR), TIME IN: 12:47:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 12:53:30 PM | LEYTE ACC-04/09/22 12:55: MAASIN SS, Nasaug - San Miguel 69kV Line tripped/restored at 1231H/1241H as per clearance from Line Engineer, ind.: Phae-C/N. Load=2.1MW. Still isolated San Miguel - St. Bernard 69kV Line. Weather: Tropical Depression ``Agaton``. | CVIS
4/9/2022 12:43:22 PM | PANAY ACC-04/09/22 12:37: CONCEPCION S/S SS, Concepcion-Sara 69 kV Line (5LI1CNE-SAR), TIME OUT: 12:36:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 12:07:58 PM | NEGROS ACC: 04/09/2022, 138kV Kabankalan-Bacolod Line 1 energized at 1149H after completion of maintenance activity. | CVIS
4/9/2022 12:07:56 PM | LEYTE ACC-04/09/22 12:05: MAASIN SS, Nasaug - San Miguel re-energized at 1151H. Still isolated San Miguel - St. Bernard 69kV Line. Affected customer: Soleco (Himay-angan & St. Bernard). Weather: Tropical Depression ``Agaton``. | CVIS
4/9/2022 11:53:00 AM | PANAY ACC-04/09/22 09:32: BUENAVISTA SS, Buenavista-GUIMELCO 69kV Line (CO (5LI1BVI-GUI), TIME IN: 09:32:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 11:52:59 AM | PANAY ACC-04/09/22 09:27: BUENAVISTA SS, Buenavista-Ingore 69kV Line (5LI1BVI-INR), TIME IN: 09:27:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 11:52:58 AM | PANAY ACC-04/09/22 09:38: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW), TIME IN: 09:37:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 11:42:55 AM | PANAY ACC-04/09/22 10:42: DINGLE SS, Dingle-Passi 69 kV L (5LI1DIN-PSS), TIME IN: 10:41:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 11:32:52 AM | LEYTE ACC-04/09/22 11:42: MAASIN SS, 69kV PCB Nasaug (Nasaug - St. Bernard Line) tripped at 1126H, ind.: Phase-C/N. Load=2.4MW. Weather: Tropical Depression ``Agaton``. | CVIS
4/9/2022 11:31:05 AM | LEYTE ACC-04/09/22 11:35: MAASIN SS, 69kV PCB Nasaug (Nasaug - St. Bernard Line) re-energized at 1116H as per clearance from Line Engineer. Weather: Tropical Depression ``Agaton``. | CVIS
4/9/2022 11:21:03 AM | LEYTE ACC-04/09/22 11:25: MAASIN SS, 69kV PCB Nasaug (Nasaug - St. Bernard Line) tripped at 1105H, ind.: Phase-C/N. Load=3.4MW. Weather: Tropical Depression ``Agaton``. | CVIS
4/9/2022 11:05:57 AM | LEYTE ACC-04/09/22 11:08: MAASIN SS, 69kV PCB Nasaug (Nasaug - St. Bernard Line) tripped/restored at 1053H/1055H, ind.: Phase-C/N. Load=5MW. Weather: Tropical Depression ``Agaton``. | CVIS
4/9/2022 10:55:54 AM | LEYTE ACC-04/09/22 11:00: MAASIN SS, 69kV PCB Nasaug (Nasaug - St. Bernard Line) tripped/restored at 1043H/1046H, ind.: Phase-C/N. Load=6.11MW. Weather: Tropical Depresion ``Agaton``. | CVIS
4/9/2022 10:55:51 AM | LRCC-04/09/2022 10:48: Santiago-Magat 230kV line 1 energized at 1047H from Santiago side. (Planned Outage) [WEBSMS] | CLUZ
4/9/2022 10:45:52 AM | LEYTE ACC-04/09/22 10:54: MAASIN SS, Maasin - Ubay sub-marine cable 138kV Line re-energized at 1033H, pre-arranged activity completed. Weather: Tropical Depression ``Agaton``. | CVIS
4/9/2022 10:42:26 AM | LEYTE ACC-04/09/22 10:47: ORMOC SS, Ormoc - Maasin 138kV Line 2 re-energized at 1004H, pre-arranged activity completed. Weather: Tropical Depression ``Agaton``. | CVIS
4/9/2022 9:45:33 AM | LEYTE ACC-04/09/22 09:47: ORMOC SS, Ormoc - Maasin 138kV Line 2 de-energized at 0917H, pre-arranged activity (0801H-1200H). Weather: Tropical Depression ``Agaton``. | CVIS
4/9/2022 8:48:26 AM | NEGROS ACC: 04/09/2022, 138kV Kabankalan-Bacolod Line 1 de-energized at 0843H to conduct reconnection of Tubular connection between DS5 to PCB.Load of L1 transferred to L2. | CVIS
4/9/2022 8:24:57 AM | PANAY ACC-04/09/22 08:23: DINGLE SS, Dingle-Passi 69 kV L (5LI1DIN-PSS), TIME OUT: 08:22:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 8:21:32 AM | PANAY ACC-04/09/22 08:10: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST), TIME IN: 08:09:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 8:11:28 AM | LRCC-04/09/2022 08:10: Santiago-Magat 230kV line 1 de-energized at 0807H. (Planned Outage) [WEBSMS] | CLUZ
4/9/2022 8:01:27 AM | PANAY ACC-04/09/22 07:58: CONCEPCION S/S SS, Concepcion-Sara-Estancia 69 kV Line (5LI1CNE-EST), TIME OUT: 07:57:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 7:58:58 AM | PANAY ACC-04/09/22 07:53: STA. BARBARA SS, Sta. Barbara-Ingore 69 kV Line (5LI1SBA-INR), TIME IN: 07:52:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 7:58:56 AM | PANAY ACC-04/09/22 07:53: STA. BARBARA SS, Sta. Barbara-Baldoza 69 kV L (5LI1SBA-BAL), TIME IN: 07:52:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 7:58:55 AM | PANAY ACC-04/09/22 07:22: PANIT-AN SS, Panit-an-Sara 69 kV Line (5LI1PNT-SAR), TIME IN: 07:21:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 7:24:31 AM | LRCC-04/09/2022 07:16: Labrador 230kV Bus 1 de-energized at 0714H. (Planned Outage) [WEBSMS] | CLUZ
4/9/2022 7:14:29 AM | NEGROS ACC: 04/09/2022: 69kV Talisay-Silay Line section temporarily energized through Cadiz SS at 0704H. Customer owned and maintained line. | CVIS
4/9/2022 7:14:27 AM | LRCC-04/09/2022 07:09: Naga-Tayabas 230kV line 2 de-energized at 0707H. (Planned Outage) [WEBSMS] | CLUZ
4/9/2022 7:09:25 AM | PANAY ACC-04/09/22 06:35: STA. BARBARA SS, Sta. Barbara-Baldoza 69 kV L (5LI1SBA-BAL), TIME OUT: 06:33:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 7:09:24 AM | PANAY ACC-04/09/22 06:35: STA. BARBARA SS, Sta. Barbara-Ingore 69 kV Line (5LI1SBA-INR), TIME OUT: 06:33:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 6:59:21 AM | PANAY ACC-04/09/22 06:20: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW), TIME OUT: 06:18:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 6:59:20 AM | PANAY ACC-04/09/22 06:20: BUENAVISTA SS, Buenavista-Ingore 69kV Line (5LI1BVI-INR), TIME OUT: 06:18:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 6:59:19 AM | PANAY ACC-04/09/22 06:16: PANIT-AN SS, Panit-an-Sara 69 kV Line (5LI1PNT-SAR), TIME OUT: 06:14:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 6:59:17 AM | PANAY ACC-04/09/22 06:08: BUENAVISTA SS, Buenavista-GUIMELCO 69kV Line (CO (5LI1BVI-GUI), TIME OUT: 06:06:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
4/9/2022 6:49:15 AM | NEGROS ACC: 04/09/2022, 69kV Bacolod-Silay Sub T/L (33.4MW) de-energized at 0644H per P&E request under VSRP1 for swinging of its take-off from Bay 53 to newly installed 69KV Bay 54.FFHC,HPC,SILAY SOLAR and VMC-Cogen isolated. | CVIS
4/9/2022 6:22:28 AM | NEGROS ACC: 04/09/2022, BACOLOD SS 69KV Bus 2 de-energized at 0613H per P&E request under VSRP1 for tapping of 69KV Bay 54 inside Bacolod SS. | CVIS
4/9/2022 6:22:26 AM | LRCC-04/09/2022 06:21: San Jose 750MVA T01 de-energized at 0618H. (Planned Outage) [WEBSMS] | CLUZ
4/9/2022 6:22:24 AM | LRCC-04/09/2022 06:19: System Advisory: Weather Disturbance Alert Notice (WDAN) is issued at 0600H, April 9, 2022, A TROPICAL DEPRESSION DEVELOPED INSIDE THE PHILIPPINE AREA OF RESPONSIBILITY AND WAS NAMED ``AGATON``. At 3:00 AM today, the center of Tropical Depression ``AGATON`` was estimated at 120 km East of Guiuan, Eastern Samar (10.9N, 126.8E) with maximum sustained winds of 45 km/h near the center and gustiness of up to 55 km/h. It is moving West Northwestward slowly. [WEBSMS] | CLUZ
4/9/2022 6:12:22 AM | VRCC-04/09/2022 06:12: Cebu-Colon 138kV Line 2 de-energized at 0610H, for Corrective Maintenance [WEBSMS] | CVIS
4/9/2022 6:12:21 AM | VRCC-04/09/2022 06:11: 5 MVA TR at Lugo LESS de-energized at 0606H, for APMS [WEBSMS] | CVIS
4/9/2022 6:12:18 AM | LRCC-04/09/2022 06:10: Nagsaag-Pantabangan 230kV line de-energized at 0610H. (Planned Outage) [WEBSMS] | CLUZ
4/9/2022 6:02:16 AM | VRCC-04/09/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2567MW, PK=1860MW, RR=76MW, NetOpMargin: AM=631, PM=552, EVE=412 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 378, TPC at 82, LGPP at 80 MW [WEBSMS] | CVIS
4/9/2022 5:47:29 AM | LRCC-04/09/2022 05:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13069MW, PK=8999MW, RR=325MW, NetOpMargin: AM=3745, PM=3379, EVE=3067 Highest Unit O/L: Dinginin at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, Sta. Rita 40 at 240MW [WEBSMS] | CLUZ
4/9/2022 5:34:14 AM | LEYTE ACC-04/09/22 05:41: MAASIN SS, Maasin-Ubay 138 kV L,Deenergized at 0426H,Pre arranged per PANR VRCC-2022-04-0016,(4am-6Pm) WEATHER: RAINY | CVIS
4/9/2022 2:49:39 AM | LEYTE ACC-04/09/22 02:52: PARANAS SS, Paranas-Borongan-Quinapondan 69 kV L,tripped/restored at 0235H/0242H, Z2,Phase BC, fd=107.71kms,load=6.7mw,with clearance from O&M, WEATHER: RAINY | CVIS
4/9/2022 2:29:32 AM | LRCC-04/09/2022 02:25: Masinloc 3 (96MW) tripped at 0220H. Lowest frequency is 59.729Hz. [WEBSMS] | CLUZ
4/9/2022 1:27:16 AM | LRCC-04/09/2022 01:20: Calaca Unit 1 emergency shutdown at 0118H. (Unplanned Outage) [WEBSMS] | CLUZ
4/9/2022 12:40:22 AM | LRCC-04/09/2022 00:31: Dona Imelda(Araneta) 300MVA T01 de-energized at 0023H. (Planned Outage) [WEBSMS] | CLUZ
4/8/2022 9:09:15 PM | NEGROS ACC: 04/08/2022, 69kV Amlan-Siaton Sub T/L restored at 2101H. | CVIS
4/8/2022 9:09:14 PM | NEGROS ACC: 04/08/2022, 69kV Amlan-Siaton Sub T/L restored at 2101H. | CVIS
4/8/2022 6:58:32 PM | NEGROS ACC: 04/08/2022, 69kV Amlan-Siaton Sub T/L (42.23 MW) auto-triped at 1848H with ind. Z1 BN, 14.27km. | CVIS
4/8/2022 6:58:31 PM | NEGROS ACC: 04/08/2022, 69kV Amlan-Siaton Sub T/L (42.23 MW) auto-triped at 1848H with ind. Z1 BN, 14.27km. | CVIS
4/8/2022 6:11:36 PM | VRCC-04/08/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2310MW, PK=1987MW, RR=40MW, NetOpMargin: EVE=283 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, TGPP at 80MW [WEBSMS] | CVIS
4/8/2022 5:48:08 PM | LRCC-04/08/2022 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13170MW, PK=9397MW, RR=386MW, NetOpMargin: EVE=3387 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, Calaca 1 at 230MW, Sta. Rita 40 at 240MW [WEBSMS] | CLUZ
4/8/2022 5:14:38 PM | LRCC-04/08/2022 17:06: Naga-Tayabas 230kV line 2 restored ay 1703H. (Planned Outage) [WEBSMS] | CLUZ
4/8/2022 1:10:44 PM | VRCC-04/08/2022 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2450MW, PK=2072MW, RR=40MW, NetOpMargin: PM=338, EVE=283 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, TGPP at 80MW [WEBSMS] | CVIS
4/8/2022 1:10:43 PM | VRCC-04/08/2022 13:06: GRID UPDATE AS OF 1:00 PM System Condition: YELLOW ALERT CAP=2450MW, PK=2072MW, RR=40MW, NetOpMargin: PM=338, EVE=283 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, TGPP at 80MW [WEBSMS] | CVIS
4/8/2022 1:10:40 PM | LRCC-04/08/2022 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13541MW, PK=10619MW, RR=411MW, NetOpMargin: PM=2511, EVE=3116 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, Calaca 1 at 230MW, Sta. Rita 40 at 240MW [WEBSMS] | CLUZ
4/8/2022 6:17:44 AM | LRCC-04/08/2022 06:17: Naga-Tayabas 230kV line 2 de-energized at 0612H. (Planned Outage) [WEBSMS] | CLUZ
4/8/2022 6:14:21 AM | VRCC-04/08/2022 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2504MW, PK=2169MW, RR=40MW, NetOpMargin: AM=295, PM=207, EVE=212 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, TGPP at 80MW [WEBSMS] | CVIS
4/8/2022 5:30:47 AM | LRCC-04/08/2022 05:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13560MW, PK=10274MW, RR=381MW, NetOpMargin: AM=2906, PM=2710, EVE=3016 Highest Unit O/L: Dinginin at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, Calaca 1 at 230MW, Sta. Rita 40 at 240MW [WEBSMS] | CLUZ
4/8/2022 4:20:20 AM | LRCC-04/08/2022 04:18: Dona Imelda(Araneta)-Valencia-Kamuning 115kV Line restored at 0415H. (Planned Outage) [WEBSMS] | CLUZ
4/7/2022 10:51:58 PM | PANAY ACC-04/07/22 22:42: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME IN: 22:39, RELAY: Z1 CN at 75.17kms, Sustained Fault | CVIS
4/7/2022 10:38:31 PM | PANAY ACC-04/07/22 22:27: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), Load:23.7MW; TIME OUT: 22:22, RELAY: Z1 CN at 75.17kms, Sustained Fault | CVIS
4/7/2022 10:16:01 PM | LRCC-04/07/2022 22:10: Dona Imelda(Araneta)-Valencia-Kamuning 115kV Line de-energized at 2208H. (Planned Outage) [WEBSMS] | CLUZ
4/7/2022 6:10:29 PM | VRCC-04/07/2022 18:10: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2347MW, PK=1950MW, RR=40MW, NetOpMargin: EVE=357 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, TGPP at 80MW [WEBSMS] | CVIS
4/7/2022 5:57:04 PM | LEYTE ACC-04/07/22 18:01:ORMOC SS, Ormoc-Baybay 69 kV L,Deenergized/Energized at 1727H/1732H,load=33.3mw,while Maasin Baybay restored at 1742H,Pre arranged per PANR No.TLOS V_LEY-2022-03-0017. WEATHER: RAINY | CVIS
4/7/2022 5:44:35 PM | LRCC-04/07/2022 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12998MW, PK=9610MW, RR=379MW, NetOpMargin: EVE=3009 Highest Unit O/L: Sual 1 at 647MW Derated Plant: GMEC 2 at 300MW, Sual 2 at 550MW, Ilijan at 851MW, Sta Rita 40 at 240MW, Calaca 1 at 230MW, and GNPD 1 at 500MW [WEBSMS] | CLUZ
4/7/2022 5:34:26 PM | LRCC-04/07/2022 17:30: Naga-Tayabas 230kV line 2 restored at 1729H. (Planned Outage) [WEBSMS] | CLUZ
4/7/2022 5:34:24 PM | LRCC-04/07/2022 17:25: Labo 230kV Bus 1 energized at 1722H. (Planned Outage) [WEBSMS] | CLUZ
4/7/2022 5:10:02 PM | NEGROS ACC: 04/07/2022, PGPP2 SOG1 re-online at 1601H. | CVIS
4/7/2022 5:10:01 PM | NEGROS ACC: 04/07/2022, PGPP2 SOG1 re-online at 1601H. | CVIS
4/7/2022 5:09:59 PM | VRCC-04/07/2022 17:02: Compostela SS 138KV Bus 2 energized at 1700H, APMS activity completed. [WEBSMS] | CVIS
4/7/2022 3:20:07 PM | LEYTE ACC-04/07/22 15:26:PARANAS SS,Paranas-Bliss 69 kV L,Deenergized/Energized at 1445H/1448H,load=11.8mw,to effect the opening of DS Bliss and load Transfer back to Gandara feeder at 1509H,Pre arranged per PANR No.TLOS V_LEY-2022-03-0016.RAINY | CVIS
4/7/2022 3:20:06 PM | NEGROS ACC: 04/07/2022, PGPP2 SOG1 (18.61MW) auto-tripped at 1504H. Ongoing investigation on cause of tripping. | CVIS
4/7/2022 3:20:04 PM | NEGROS ACC: 04/07/2022, PGPP2 SOG1 (18.61MW) auto-tripped at 1504H. Ongoing investigation on cause of tripping. | CVIS
4/7/2022 1:59:30 PM | LEYTE ACC-04/07/22 14:04:CALBAYOG SS,Palanas Catarman 69kVL(Bobolosan),Energized at 1345H,cut-off OHGW in between Str. # 85-C & 86-B,loc at Brgy Makiwalo,Mondragon,Northern Samar. | CVIS
4/7/2022 1:25:54 PM | VRCC-04/07/2022 13:23: Sangi-Carcon 34.5KV Line 2 tripped/energized at 1254H/1320H, indication phase AB to Ground. Customer owned line. [WEBSMS] | CVIS
4/7/2022 1:11:46 PM | VRCC-04/07/2022 13:11: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2518MW, PK=2233MW, RR=40MW, NetOpMargin: PM=245, EVE=185 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, TGPP at 80MW [WEBSMS] | CVIS
4/7/2022 1:11:43 PM | LRCC-04/07/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13342MW, PK=10276MW, RR=411MW, NetOpMargin: PM=2655, EVE=2924 Highest Unit O/L: Sual 1 at 647MW Derated Plant: GMEC 2 at 300MW, Sual 2 at 550MW, Ilijan at 851MW, Sta Rita 40 at 240MW, Calaca 1 at 230MW, and GNPD 1 at 500MW [WEBSMS] | CLUZ
4/7/2022 11:47:54 AM | LRCC-04/07/2022 11:38: Calauan 230kV Bus 1 energized at 1133H which simultaneously looped Calauan-San Juan(Kalayaan) 230kV line 2 at Calauan side. (Unplanned Outage) [WEBSMS] | CLUZ
4/7/2022 10:40:53 AM | VRCC-04/07/2022 10:38: Compostela SS 138KV Bus 2 de-energized at 1014H, APMS activity. ECD: 1700H [WEBSMS] | CVIS
4/7/2022 9:26:54 AM | LRCC-04/07/2022 09:21: Nagsaag 500kV PCB 9-02CB04NGS closed at 0917H. (Planned Outage) [WEBSMS] | CLUZ
4/7/2022 7:52:55 AM | LEYTE ACC-04/07/22 07:51:CALBAYOG SS,Palanas Cara-Catarman,Energized at 0738H while Bobolosan SS still isolated, WEATHER: RAINY | CVIS
4/7/2022 7:19:29 AM | LEYTE ACC-04/07/22 07:25:CALBAYOG SS, Palanas Cara-Catarman,Tripped at 0706H,load=11.5mw,Z1, Phase AB N, fd=60.6kms, WEATHER: RAINY | CVIS
4/7/2022 7:19:27 AM | LRCC-04/07/2022 07:14: Labo 230kV Bus 1 de-energized at 0707H. (Planned Outage) [WEBSMS] | CLUZ
4/7/2022 7:05:59 AM | LEYTE ACC-04/07/22 07:15:MAASIN SS,Maasin-Baybay 69 kVL,Deenergized/Load transferred,0642H/0656H,Pre arranged per PANR no.TLOS V_LEY-2022-03-0017,6am-6pm. WEATHER: RAINY | CVIS
4/7/2022 6:55:56 AM | LEYTE ACC-04/07/22 06:55: CALBAYOG SS,Calbayog Bliss 69kVL,Deenergized/Load transferred,0602H/0625H,load=2.01mw,Pre arranged per PANR no.TLOS V_LEY-2022-03-0016,6am-6pm. WEATHER:Rainy | CVIS
4/7/2022 6:22:24 AM | LRCC-04/07/2022 06:21: Nagsaag 500kV PCB 9-02CB04NGS open at 0621H. (Planned Outage) [WEBSMS] | CLUZ
4/7/2022 6:19:51 AM | LRCC-04/07/2022 06:11: Naga-Tayabas 230kV line 2 de-energized at 0607H. (Planned Outage) [WEBSMS] | CLUZ
4/7/2022 6:09:03 AM | VRCC-04/07/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2559MW, PK=2179MW, RR=40MW, NetOpMargin: AM=340, PM=245, EVE=185 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, TGPP at 80MW [WEBSMS] | CVIS
4/7/2022 6:09:00 AM | LRCC-04/07/2022 06:06: Calauan 230kV Bus 1 tripped at 0505H (Unplanned Outage) [WEBSMS] | CLUZ
4/7/2022 6:08:58 AM | LRCC-04/07/2022 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13456MW, PK=10310MW, RR=391MW, NetOpMargin: AM=2755, PM=2279, EVE=2950 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SUAL 2 @550MW; ILJJAN A / B @851MW; STA RITA 40 @240MW, Calaca 1 @ 220MW. [WEBSMS] | CLUZ
4/7/2022 5:45:48 AM | LRCC-04/07/2022 05:39: San Jose 115kV Bus 1 restored at 0538H (Planned Outage). [WEBSMS] | CLUZ
4/7/2022 5:23:33 AM | LRCC-04/07/2022 05:19: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 130 km East of Hinatuan, Surigao del Sur (8.4?N, 127.5?E). It is embedded along the Intertropical Convergence Zone (ITCZ) affecting Visayas and Mindanao. [WEBSMS] | CLUZ
4/7/2022 4:58:33 AM | LRCC-04/07/2022 04:49: Dasmarinas PCB 9-01CB24DAS manually closed at 0441H, facilitated the transfer of the bourdon tube to PCB 9-03CB24DAS.(Unplanned Outage) [WEBSMS] | CLUZ
4/7/2022 1:27:23 AM | LEYTE ACC-04/07/22 01:33: PARANAS SS, 69kV Taft Feeder tripped/restored at 0117H/0119H, ind.: Phase-B/N & 146.2kms. Load=8.5MW. Weather: rainy. | CVIS
4/6/2022 9:09:09 PM | LRCC-04/06/2022 21:04: San Jose 115kV Bus 1 de-energized at 2104H (Planned Outage). [WEBSMS] | CLUZ
4/6/2022 8:12:10 PM | LEYTE ACC-04/06/22 20:22: ORMOC CONVERTER STATION SS,350kV HVDC Leyte-Luzon,Blocked/Deblocked at 1919H/2003H, on normal power flow per RTD,Delayed due to open line test conducted by LRCC., WEATHER: FAIR | CVIS
4/6/2022 6:34:47 PM | LRCC-04/06/2022 18:30: Tayabas-Naga 230kV Line 2 restored at 1824H (Planned Outage). [WEBSMS] | CLUZ
4/6/2022 6:14:44 PM | LEYTE ACC-04/06/22 18:20: ORMOC SS,Tolosa-San Isidro 69kV line,Deenergized/Energized at 1743H/1753H,load=11.2mw,while PCB Nasaug closed at 1756H,back to normal configuration.WEATHER: FAIR | CVIS
4/6/2022 6:11:22 PM | VRCC-04/06/2022 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2332MW, PK=1976MW, RR=40MW, NetOpMargin: EVE=316 Highest Unit O/L: TVI at 169MW per unit. Derated Plant: EDC at 388MW, LGPP at 80MW, TPC at 82MW [WEBSMS] | CVIS
4/6/2022 5:47:54 PM | LRCC-04/06/2022 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13100MW, PK=9489MW, RR=387MW, NetOpMargin: EVE=3224 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SUAL 2 @550MW; ILJJAN A / B @851MW; STA RITA 40 @240MW [WEBSMS] | CLUZ
4/6/2022 5:14:27 PM | VRCC-04/06/2022 17:07: 34.5KV Sangi-Carcon L2 energized at 1529H, metering activity completed. [WEBSMS] | CVIS
4/6/2022 4:51:00 PM | LEYTE ACC-04/06/22 16:53:PARANAS SS,Paranas-Bliss 69 kV L,Deenergized/Energized at 1615H/1617H to load transferred back Samelco 1 (San Agustin) to Calbayog SS at 1635H,load=12.3mw,as per PANR No. TLOS V_LEY-2022-03-0015. WEATHER: FAIR | CVIS
4/6/2022 1:56:37 PM | VRCC-04/06/2022 13:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2549MW, PK=2151MW, RR=72MW, NetOpMargin: PM=326, EVE=316 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 388MW, LGPP at 80MW, TPC at 82MW [WEBSMS] | CVIS
4/6/2022 1:02:10 PM | LRCC-04/06/2022 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13427MW, PK=10544MW, RR=411MW, NetOpMargin: PM=2472, EVE=2809 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SUAL 2 @550MW; ILJJAN A / B @851MW; STA RITA 40 @200MW [WEBSMS] | CLUZ
4/6/2022 11:03:38 AM | VRCC-04/06/2022 10:57: THVI unit no.2 cut-in to the system at 1053H, initial load 9MW. [WEBSMS] | CVIS
4/6/2022 10:06:42 AM | VRCC-04/06/2022 10:02: 34.5KV Sangi-Carcon L2 de-energized at 0957H, Metering activity. ECD: 1700H. [WEBSMS] | CVIS
4/6/2022 9:21:00 AM | NEGROS ACC: 04/06/2022, 69kV Amlan-San Carlos Sub T/L (14.2 MW) auto-trippeed at 0854H with ind. Z2 PhB-N, DELAY, 64.7km. Sacasun and Montesol isolated. Restored at 0906H. | CVIS
4/6/2022 8:21:36 AM | PANAY ACC-04/06/22 08:17: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME IN: 08:12:00 | CVIS
4/6/2022 8:10:00 AM | LRCC-04/06/2022 08:03: Balsik 1000MVA T02 de-energized at 0803H (Planned Outage) [WEBSMS] | CLUZ
4/6/2022 7:10:17 AM | PANAY ACC-04/06/22 07:06: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME OUT: 07:03:00, Customers request to conduct repair of damage 13.2kV DSW | CVIS
4/6/2022 7:06:32 AM | LEYTE ACC-04/06/22 06:34: 69kV Maasin-Nasaug line de-energized at 0604H, pre arranged maintenance activity. SOLECO (Sogod, Himayangan & St. Bernard) loads were transferred to Ormoc Ss at 0626H. While SOLECO (Maasin) will be transferred to Ormoc Ss after correction of hotspot. Duration: 0601H-1800H. WEATHER: FAIR | CVIS
4/6/2022 6:56:29 AM | LEYTE ACC-04/06/22 06:44: CALBAYOG SS, 69kV Calbayog-Bliss line de-energized at 0603H, pre arranged maintenance activity. SAMELCO I (San Agustin) loads (2.0MW) were transferred to Paranas Ss at 0634H. Duration: 0601H-1800H. WEATHER: FAIR | CVIS
4/6/2022 6:33:59 AM | LRCC-04/06/2022 06:29: Tayabas-Naga 230kV Line 2 de-energized at 0628 (Planned Outage). [WEBSMS] | CLUZ
4/6/2022 6:08:41 AM | VRCC-04/06/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2443MW, PK=2106MW, RR=40MW, NetOpMargin: AM=297, PM=163, EVE=8 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 388MW, TVI at 169MW, LGPP at 80MW, TPC at 82MW [WEBSMS] | CVIS
4/6/2022 5:33:45 AM | LRCC-04/06/2022 05:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13467MW, PK=10259MW, RR=411MW, NetOpMargin: AM=2797, PM=2383, EVE=2633 Highest Unit O/L: Dinginin at 668MW Derated Plant: Ilijan A/B at 851MW, GMEC 2 at 300MW, Sual 2 at 550MW, Sta. Rita 40 at 200MW [WEBSMS] | CLUZ
4/6/2022 4:21:26 AM | LRCC-04/06/2022 04:16: Dona Imelda(Araneta)-Sta. Mesa 115kV Line 2 energized at 0411H. (Planned Outage) [WEBSMS] | CLUZ
4/6/2022 1:05:04 AM | PANAY ACC-04/06/22 00:54: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME OUT: 00:49:00, TIME IN: 00:53:00, Ld: 2.2MW, RELAY: Started AN, Trip N, WEATHER: FAIR; Momentary line fault. | CVIS
4/6/2022 12:02:53 AM | LEYTE ACC-04/06/22 00:01: MAASIN SS, 69kV Nasaug-San Isidro line tripped at 2355H, phase CN, load=5.4MW. Restored at 2357H. WEATHER: FAIR | CVIS
4/5/2022 11:52:49 PM | LEYTE ACC-04/05/22 23:45: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2329H/2339H, on normal power flow per RTD. WEATHER: FAIR | CVIS
4/5/2022 11:05:52 PM | LRCC-04/05/2022 22:56: Dona Imelda(Araneta)-Sta. Mesa 115kV Line 2 de-energized at 2252H. (Planned Outage) [WEBSMS] | CLUZ
4/5/2022 6:26:16 PM | VRCC-04/05/2022 18:24: TVI U2 indication IDF motor high vibration. [WEBSMS] | CVIS
4/5/2022 6:26:14 PM | VRCC-04/05/2022 18:22: TVI U2 tripped at 1817H w/a load of 169MW, acquiring indication. [WEBSMS] | CVIS
4/5/2022 6:10:54 PM | VRCC-04/05/2022 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2313MW, PK=1895MW, RR=40MW, NetOpMargin: EVE=378 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, TGPP at 80MW [WEBSMS] | CVIS
4/5/2022 5:37:26 PM | LRCC-04/05/2022 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=13005MW, PK=9168MW, RR=400MW, NetOpMargin: EVE=3437 Highest Unit O/L: Sual 1 at 600MW Derated Plant: Dinginin at 450MW, GMEC 2 at 300MW, Sual 2 at 550MW, Ilijan A/B at 817MW, Sta. Rita 40 at 200MW, SLTEC 1 at 91MW [WEBSMS] | CLUZ
4/5/2022 5:00:29 PM | LRCC-04/05/2022 16:53: Naga-Tayabas 230kV line 2 restored at 1653H. (Planned Outage) [WEBSMS] | CLUZ
4/5/2022 3:03:13 PM | LRCC-04/05/2022 14:53: Dasmarinas PCB 9-01CB24DAS manually open at 1447H to facilitate the transfer of the bourdon tube to PCB 9-03CB24DAS. (Unplanned Outage) [WEBSMS] | CLUZ
4/5/2022 1:32:35 PM | VRCC-04/05/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2523MW, PK=2059MW, RR=36MW, NetOpMargin: PM=428, EVE=382 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, TGPP at 80MW [WEBSMS] | CVIS
4/5/2022 1:11:02 PM | LRCC-04/05/2022 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13512MW, PK=10220MW, RR=448MW, NetOpMargin: PM=2844, EVE=3325 Highest Unit O/L: Sual 1 at 647MW Derated Plant: GMEC 2 at 300MW, SLTEC 1 at 91MW, GNPD 1 at 500MW, Sual 2 at 580MW, Ilijan at 817MW and Sta Rita 40 at 200MW [WEBSMS] | CLUZ
4/5/2022 11:16:51 AM | LEYTE ACC-04/05/22 11:23: 350kV HVDC manually blocked/deblocked at 1016H/1039H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
4/5/2022 10:40:06 AM | LRCC-04/05/2022 10:32: Sta Rita Module 10 completed fuel changeover from oil to gas at 1028H. [WEBSMS] | CLUZ
4/5/2022 6:55:15 AM | LRCC-04/05/2022 06:52: Naga-Tayabas 230kV line 2 de-energized at 0649H. (Planned Outage) [WEBSMS] | CLUZ
4/5/2022 6:09:26 AM | VRCC-04/05/2022 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2478MW, PK=2049MW, RR=61MW, NetOpMargin: AM=368, PM=298, EVE=288 Highest Unit O/L: TVI at 169MW per unit. Derated Plant: EDC at 388MW, LGPP at 80MW, TPC at 82MW, PCPC 135MW [WEBSMS] | CVIS
4/5/2022 6:09:23 AM | LRCC-04/05/2022 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13382MW, PK=10373MW, RR=438MW, NetOpMargin: AM=2571, PM=1933, EVE=2573 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GMEC 2 @300MW; GNPD 1 @500MW; SLTEC 1 @91MW; SUAL 2 @580MW; ILJJAN A / B @817MW; STA RITA 40 @200MW [WEBSMS] | CLUZ
4/4/2022 9:23:51 PM | LRCC-04/04/2022 21:15: Ilijan B-3 online at 2102H (Unplanned Outage) [WEBSMS] | CLUZ
4/4/2022 8:04:43 PM | LRCC-04/04/2022 19:59: Ilijan B1 online at 1945H (Planned Outage). [WEBSMS] | CLUZ
4/4/2022 6:07:29 PM | VRCC-04/04/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2301MW, PK=1961MW, RR=40MW, NetOpMargin: EVE=300 Highest Unit O/L: TVI at 169MW each Derated Plant: EDC at 375MW, LGPP at 80MW, TPC at 82MW [WEBSMS] | CVIS
4/4/2022 6:07:27 PM | LRCC-04/04/2022 18:02: Tayabas-Naga 230kV line 2 restored at 1800H. (Planned Outage) [WEBSMS] | CLUZ
4/4/2022 5:57:22 PM | LRCC-04/04/2022 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12500MW, PK=9860MW, RR=412MW, NetOpMargin: EVE=2428 Highest Unit O/L: Sual 1 at 647MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW; SUAL 2 @580MW; SAN LORENZO 50 @250MW; SAN LORENZO 60 @250MW; STA RITA 30 @161MW; STA RITA 40 @161MW; GNPD 1 @334MW [WEBSMS] | CLUZ
4/4/2022 5:34:49 PM | LRCC-04/04/2022 17:32: Tayabas PCB 9-02CB08TAY closed at 1737H. (Unplanned outage) [WEBSMS] | CLUZ
4/4/2022 2:48:51 PM | VRCC-04/04/2022 14:45: 40MVA TR 3 Toledo SS energized at 1432H, pre-arranged activity completed. [WEBSMS] | CVIS
4/4/2022 2:48:48 PM | LRCC-04/04/2022 14:40: Ilijan B-2 shutdown at 1439H. (Unplanned Outage) [WEBSMS] | CLUZ
4/4/2022 2:34:55 PM | LRCC-04/04/2022 14:34: Ilijan B-3 shutdown at 1429H. (Unplanned Outage) [WEBSMS] | CLUZ
4/4/2022 1:16:16 PM | VRCC-04/04/2022 13:06: 40MVA TR 2 Toledo SS energized at 1150H, pre-arranged activity completed. [WEBSMS] | CVIS
4/4/2022 1:16:15 PM | VRCC-04/04/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2505MW, PK=2129MW, RR=40MW, NetOpMargin: PM=336, EVE=300 Highest Unit O/L: TVI at 169MW each Derated Plant: EDC at 375MW, LGPP at 80MW, TPC at 82MW [WEBSMS] | CVIS
4/4/2022 1:16:12 PM | LRCC-04/04/2022 13:08: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13110MW, PK=10605MW, RR=457MW, NetOpMargin: PM=2048, EVE=2447 Highest Unit O/L: Sual 1 at 647MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW; SUAL 2 @580MW; ILJJAN A / B @817MW; SAN LORENZO 50 @250MW; SAN LORENZO 60 @250MW; STA RITA 30 @161MW; STA RITA 40 @161MW and GNPD 1 at 334MW [WEBSMS] | CLUZ
4/4/2022 12:57:09 PM | VRCC-04/04/2022 12:53: 40MVA TR 3 Toledo SS de-energized at 1249H, pre-arranged activity [WEBSMS] | CVIS
4/4/2022 12:57:07 PM | VRCC-04/04/2022 12:52: 40MVA TR 3 Toledo SS de-energized at 1249H, pre-arranged activity [WEBSMS] | CVIS
4/4/2022 12:57:06 PM | VRCC-04/04/2022 12:51: 40MVA TR 2 Toledo SS energized at 1150H, pre-arranged activity completed. [WEBSMS] | CVIS
4/4/2022 11:34:14 AM | LEYTE ACC-04/04/22: PARANAS SS, 69kV Paranas-Borongan-Quinapondan Line tripped/restored, TIME OUT: 11:14:00, TIME IN: 11:16:00, RELAY: phase AN, 191.08kms, load=11.2MW, WEATHER: FAIR | CVIS
4/4/2022 11:34:12 AM | LEYTE ACC-04/04/22: PARANAS SS, 69kV Paranas-Borongan-Quinapondan Line tripped/restored, TIME OUT: 11:14:00, TIME IN: 11:16:00, RELAY: phase AN, 191.08kms, load=11.2MW, WEATHER: FAIR | CVIS
4/4/2022 10:27:38 AM | LEYTE ACC-04/04/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 1015H/1025H, on reverse flow per RTD | CVIS
4/4/2022 8:11:51 AM | VRCC-04/04/2022 08:10: 40MVA TR 2 Toledo SS de-energized at 0809H, pre-arranged activity [WEBSMS] | CVIS
4/4/2022 6:52:09 AM | LRCC-04/04/2022 06:49: Tayabas-Naga 230kV line 2 de-energized at 0649H. (Planned Outage) [WEBSMS] | CLUZ
4/4/2022 6:06:05 AM | VRCC-04/04/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2623MW, PK=2080MW, RR=40MW, NetOpMargin: AM=503, PM=336, EVE=300 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, LGPP at 80MW [WEBSMS] | CVIS
4/4/2022 5:54:22 AM | LRCC-04/04/2022 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13442MW, PK=10767MW, RR=442MW, NetOpMargin: AM=2233, PM=1846, EVE=2451 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW; SUAL 2 @580MW; ILJJAN A / B @817MW; SAN LORENZO 50 @250MW; SAN LORENZO 60 @250MW; STA RITA 30 @161MW; STA RITA 40 @161MW [WEBSMS] | CLUZ
4/4/2022 3:20:16 AM | LRCC-04/04/2022 03:17: San Jose - Malolos 230kV Line restored at 0316H (Planned Outage) [WEBSMS] | CLUZ
4/4/2022 12:22:07 AM | LRCC-04/04/2022 00:13: San Jose - Malolos 230kV Line de-energized at 0009H (Planned Outage) [WEBSMS] | CLUZ
4/3/2022 9:14:20 PM | LRCC-04/03/2022 21:11: GNPD 1 online at 2109H (Unplanned Outage) [WEBSMS] | CLUZ
4/3/2022 7:43:53 PM | VRCC-04/03/2022 19:40: 138 KV Cebu-Quiot line energized at 1938H. [WEBSMS] | CVIS
4/3/2022 7:28:48 PM | VRCC-04/03/2022 19:22: Cebu SS. 100 MVA TR4 energized at 1918H. [WEBSMS] | CVIS
4/3/2022 7:08:15 PM | LRCC-04/03/2022 19:03: Limay 230kV Bus 2 energized at 1902H (Planned Outage) [WEBSMS] | CLUZ
4/3/2022 6:28:28 PM | NEGROS ACC: 04/03/2022, 69kV Cadiz-Tinampa-an Sub TL, 69kV Cadiz-ISLASOL III Sub TL, 69kV Cadiz-VMC Sub TL and 69kV Cadiz-San Carlos Sub TL, energized at 1706H, 1707H, 1739H and 1757H respectively after completion of activities | CVIS
4/3/2022 6:28:26 PM | NEGROS ACC: 04/03/2021, 138kV Bacolod-Cadiz T/L and 138kV Cadiz-Helios T/L energized at 1649H and 1734H respectively after completion of activities | CVIS
4/3/2022 6:06:45 PM | VRCC-04/03/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2286MW, PK=1800MW, RR=40MW, NetOpMargin: EVE=446 Highest Unit O/L: TVI at 169MW each Derated Plant: EDC at 375MW, TPC at 82MW, LGPP at 80MW [WEBSMS] | CVIS
4/3/2022 5:44:53 PM | LRCC-04/03/2022 17:38: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12239MW, PK=9631MW, RR=364MW, NetOpMargin: EVE=2244 Highest Unit O/L: Sual 1 at 600MW Derated Plant: GMEC 2 at 300MW, SLTEC 1 at 91MW, Sual 2 at 530MW, Ilijan at 800MW, Sta Rita 30 and 40 at 161MW each and San Lorenzo 50 and 60 at 250MW each [WEBSMS] | CLUZ
4/3/2022 5:38:06 PM | LEYTE ACC-04/03/22: ORMOC SS, 138kV Ormoc-Isabel Line annual PMS done, TIME IN: 17:23:00, WEATHER: FAIR | CVIS
4/3/2022 5:28:03 PM | LEYTE ACC-04/03/22: MAASIN SS, 138kV Maasin-Ubay Line pre-arranged activity done, TIME IN: 17:08:00, WEATHER: FAIR | CVIS
4/3/2022 5:17:59 PM | LRCC-04/03/2022 17:16: Calaca-Malamig(Sta Rosa) 230kV line restored at 1714H. (Planned Outage) [WEBSMS] | CLUZ
4/3/2022 4:41:05 PM | LRCC-04/03/2022 16:32: Mexico-Quezon(Balintawak) 230kV line restored at 1631H. (Planned Outage) [WEBSMS] | CLUZ
4/3/2022 4:04:14 PM | LEYTE ACC-04/03/22: PARANAS SS, Paranas-Bliss 69 kV Line back to normal configuration from activity at 1552H, WEATHER: FAIR | CVIS
4/3/2022 1:12:08 PM | VRCC-04/03/2022 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2372MW, PK=1696MW, RR=40MW, NetOpMargin: PM=636, EVE=446 Highest Unit O/L: TVI at 169MW each Derated Plant: EDC at 375MW, TPC at 82MW, LGPP at 80MW [WEBSMS] | CVIS
4/3/2022 1:12:05 PM | LRCC-04/03/2022 13:07: Bayombong-Santiago 230kV line 1 M1 and M2 protection commissioning were completed at 1305H. [WEBSMS] | CLUZ
4/3/2022 1:12:03 PM | LRCC-04/03/2022 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12704MW, PK=8620MW, RR=359MW, NetOpMargin: PM=3725, EVE=2304 Highest Unit O/L: Sual 1 at 600MW Derated Plant: GMEC 2 at 300MW, SLTEC 1 at 91MW, Sual 2 at 530MW, Ilijan at 800MW, Sta Rita 30 and 40 at 161MW each and San Lorenzo 50 and 60 at 250MW each [WEBSMS] | CLUZ
4/3/2022 12:33:15 PM | LRCC-04/03/2022 12:33: Bayombong-Santiago 230kV line 1 was looped at 1231H at Bayombong side. On-going commissioning of new M1 and M2 protection. [WEBSMS] | CLUZ
4/3/2022 12:23:11 PM | LRCC-04/03/2022 12:16: Bayombong-Santiago 230kV line 1 was energized at 1213H from Santiago side. On-going commissioning of new M1 and M2 protection. [WEBSMS] | CLUZ
4/3/2022 11:36:35 AM | NEGROS ACC: 04/03/2022, Bacolod SS 69kV Bus No. 2 energized at 1131H after completion of P&E activities under VSRP1. | CVIS
4/3/2022 11:36:34 AM | NEGROS ACC: 04/03/2022, Bacolod SS 69kV Bus No. 2 energized at 1131H after completion of P&E activities under VSRP1. | CVIS
4/3/2022 11:26:06 AM | PANAY ACC-04/03/22 11:07: PANIT-AN SS, Panit-an-Circuit 124 69kV Tie Line (CO) (5LI1PNT-CKT), TIME IN: 11:05, Pre-arranged maintenance | CVIS
4/3/2022 11:22:45 AM | PANAY ACC-04/03/22 10:46: PANIT-AN SS, Panit-an-Roxas 69KV (5LI1PNT-ROX), TIME IN: 10:43; Pre-arranged Maintenance | CVIS
4/3/2022 11:22:43 AM | PANAY ACC-04/03/22 10:45: PANIT-AN SS, 69kV Bus 2 Panitan SS, TIME IN: 10:42:00, Pre-arranged maintenance | CVIS
4/3/2022 8:38:34 AM | NEGROS ACC: 04/03/2022, 69kV Cadiz-VMC Sub TL energized at 0822H via 69kV Bacolod-Silay Sub T/L. Customer owned and maintained line. | CVIS
4/3/2022 8:38:32 AM | NEGROS ACC: 04/03/2022, 69kV Cadiz-VMC Sub TL energized at 0822H via 69kV Bacolod-Silay Sub T/L. Customer owned and maintained line. | CVIS
4/3/2022 8:05:04 AM | NEGROS ACC: 04/03/2022, 69kV NONECO San Carlos SS temporarily energized through 69kV Amlan-San Carlos Sub TL at 0754H. | CVIS
4/3/2022 8:05:03 AM | NEGROS ACC: 04/03/2022, 69kV NONECO San Carlos SS temporarily energized through 69kV Amlan-San Carlos Sub TL at 0754H. | CVIS
4/3/2022 7:18:10 AM | LEYTE ACC-04/03/22: ORMOC SS, 138kV Ormoc-Isabel annual PMS, TIME OUT: 07:05:00, WEATHER: FAIR | CVIS
4/3/2022 7:18:07 AM | LRCC-04/03/2022 07:16: Tayabas PCB 9-02CB08TAY open at 0713H. Unplanned outage due to continuous drop of SF6 pressure. [WEBSMS] | CLUZ
4/3/2022 6:54:41 AM | NEGROS ACC: 04/03/2022, 138kV Cadiz-Helios TL, 50MVA Cadiz TR2, 50MVA Cadiz TR1, 138kV Bacolod-Cadiz TL de-energized at 0641H, 0641H, 0641H and 0644H respectively to conduct installation of Lightning Arresters along 138kV Bacolod-Cadiz TL. Helios Solar Plant isolated. | CVIS
4/3/2022 6:54:40 AM | NEGROS ACC: 04/03/2022, 138kV Cadiz-Helios TL, 50MVA Cadiz TR2, 50MVA Cadiz TR1, 138kV Bacolod-Cadiz TL de-energized at 0641H, 0641H, 0641H and 0644H respectively to conduct installation of Lightning Arresters along 138kV Bacolod-Cadiz TL. Helios Solar Plant isolated. | CVIS
4/3/2022 6:42:10 AM | NEGROS ACC: 04/03/2022, 69kV Cadiz-San Carlos Sub TL(16.38MW), 69kV Cadiz-Tinampaan Sub TL(4.8MW), 69kV Cadiz-VMC Sub TL (9.06MW) and 69kV Cadiz-ISLASOL III Sub TL de-energized at 0637H, 0637H, 0637H and 0638H respectively to conduct installation of Lightning Arresters along 138kV Bacolod-Cadiz TL. SACASOL AB, SACASOL | CVIS
4/3/2022 6:42:08 AM | NEGROS ACC: 04/03/2022, 69kV Cadiz-San Carlos Sub TL(16.38MW), 69kV Cadiz-Tinampaan Sub TL(4.8MW), 69kV Cadiz-VMC Sub TL (9.06MW) and 69kV Cadiz-ISLASOL III Sub TL de-energized at 0637H, 0637H, 0637H and 0638H respectively to conduct installation of Lightning Arresters along 138kV Bacolod-Cadiz TL. SACASOL AB, SACASOL | CVIS
4/3/2022 6:42:07 AM | LEYTE ACC-04/03/22: MAASIN SS, 138kV Maasin-Ubay Line PMS, TIME OUT: 06:29:00, WEATHER: FAIR | CVIS
4/3/2022 6:42:04 AM | PANAY ACC-04/03/22 06:19: PANIT-AN SS, 69kV Bus 2 Panitan SS, TIME OUT: 06:14,Pre-arranged maintenance; ETR:1200H | CVIS
4/3/2022 6:42:02 AM | LRCC-04/03/2022 06:35: Tayabas 230kV Bus 1 energized at 0634H. (Planned Outage) [WEBSMS] | CLUZ
4/3/2022 6:31:19 AM | PANAY ACC-04/03/22 06:17 PANIT-AN SS, Panit-an-Roxas 69KV (5LI1PNT-ROX), TIME OUT: 06:12:00, Load:12MW, Pre-arranged maintenance; ETR:1200H | CVIS
4/3/2022 6:31:18 AM | PANAY ACC-04/03/22 06:17: PANIT-AN SS, Panit-an-Circuit 124 69kV Tie Line (CO) (5LI1PNT-CKT), TIME OUT: 06:12,Load:3.1MW Pre-arranged maintenance; ETR:1200H | CVIS
4/3/2022 6:31:17 AM | PANAY ACC-04/03/22 06:17: PANIT-AN SS, Panit-an-Circuit 124 69kV Tie Line (CO) (5LI1PNT-CKT), TIME OUT: 06:12, Pre-arranged maintenance; ETR:1200H | CVIS
4/3/2022 6:31:15 AM | LEYTE ACC-04/03/22: PARANAS SS, 69kV Paranas-Bliss Line PMS, load transferred, TIME OUT:06:01, TIME IN:06:14, WEATHER: FAIR | CVIS
4/3/2022 6:31:14 AM | LEYTE ACC-04/03/22: PARANAS SS, 69kV Paranas-Bliss Line PMS, load transferred, TIME OUT:06:01, TIME IN:06:14, WEATHER: FAIR | CVIS
4/3/2022 6:31:11 AM | LRCC-04/03/2022 06:25: Calaca-Malamig(Sta Rosa) 230kV line de-energized at 0624H. (Planned Outage) [WEBSMS] | CLUZ
4/3/2022 6:19:34 AM | VRCC-04/03/2022 06:12: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2493MW, PK=1711MW, RR=59MW, NetOpMargin: AM=723, PM=744, EVE=442 Highest Unit O/L: THVI at 169MW per unit. Derated Plant: EDC at 375MW, TPC at 82MW, PGPP1 at 87MW, LGPP at 80MW [WEBSMS] | CVIS
4/3/2022 6:19:31 AM | LRCC-04/03/2022 06:16: Mexico-Quezon(Balintawak) 230kV line de-energized at 0615H. (Planned Outage) [WEBSMS] | CLUZ
4/3/2022 6:07:49 AM | LRCC-04/03/2022 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13103MW, PK=8910MW, RR=353MW, NetOpMargin: AM=3840, PM=3387, EVE=2534 Highest Unit O/L: Sual 1 @600MW Derated Plant: SLTEC 1 @91MW, Sual 2 @530MW, GMEC 2 @ 300MW, & Ilijan @800MW [WEBSMS] | CLUZ
4/3/2022 5:44:23 AM | VRCC-04/03/2022 05:40: CEBU-QUIOT 138KV T/L de-energized at 0529H, per P&E request. ECD:2355H [WEBSMS] | CVIS
4/3/2022 5:44:22 AM | VRCC-04/03/2022 05:37: CEBU SS 100MVA TR4 de-energized at 0510H per P&E request. ECD:2355H. [WEBSMS] | CVIS
4/3/2022 5:34:14 AM | NEGROS ACC: 04/03/2022, Bacolod SS 69kV Bus No. 2 de-energized at 0530H per P&E request to conduct commissioning of 5-04CB08BCL, 5-04CB24BCL and bay 5-04 BCU under VSRP1. | CVIS
4/3/2022 5:34:13 AM | NEGROS ACC: 04/03/2022, Bacolod SS 69kV Bus No. 2 de-energized at 0530H per P&E request to conduct commissioning of 5-04CB08BCL, 5-04CB24BCL and bay 5-04 BCU under VSRP1. | CVIS
4/3/2022 1:00:44 AM | PANAY ACC-04/03/22 00:38: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 00:33:00, RELAY: NONE, WEATHER: FAIR. Cause under investigation. | CVIS
4/3/2022 12:50:36 AM | PANAY ACC-04/03/22 00:45: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME IN: 12:41:00, RELAY: NONE, WEATHER: FAIR. Cause under investigation. | CVIS
4/3/2022 12:45:58 AM | PANAY ACC-04/03/22 00:8: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 00:33:00, RELAY: NONE, WEATHER: FAIR. Cause under investigation. | CVIS
4/3/2022 12:25:54 AM | PANAY ACC-04/03/22 00:23: DINGLE SS, Dingle-Passi 69 kV L (5LI1DIN-PSS), TIME IN: 00:19:00, WEATHER: FAIR. Cause under investigation. | CVIS
4/3/2022 12:11:19 AM | PANAY ACC-04/03/22 00:05: DINGLE SS, Dingle-Passi 69 kV L (5LI1DIN-PSS), TIME OUT: 12:02:00, WEATHER: FAIR. Cause under investigation. | CVIS
4/2/2022 10:50:40 PM | LRCC-04/02/2022 22:48: Tayabas 230kV Bus 1 de-energized at 2247H (Planned Outage) [WEBSMS] | CLUZ
4/2/2022 9:59:55 PM | LRCC-04/02/2022 21:56: Mexico - Concepcion 230kV Line 1 restored at 2154H (Planned outage). [WEBSMS] | CLUZ
4/2/2022 9:49:53 PM | LRCC-04/02/2022 21:48: GNPD 1 emergency shutdown at 2143H for removal of turbine balancing weight (Unplanned Outage) [WEBSMS] | CLUZ
4/2/2022 9:35:36 PM | LEYTE ACC-04/02/22 21:38:ORMOC CONVERTER STATION SS,350kV HVDC Leyte-Luzon,Blocked/Deblocked at 2112H/2122H,on normal power flow per RTD.WEATHER: FAIR | CVIS
4/2/2022 7:28:26 PM | LEYTE ACC-04/02/22 19:35: BABATNGON SS,69KV Bus 1 Energized at 1920H completed emergency removal of Birds Nest,Weather:Cloudy | CVIS
4/2/2022 7:04:18 PM | LRCC-04/02/2022 18:57: Tayabas - Naga 230kV Line 2 restored at 1856H (Planned Outage). [WEBSMS] | CLUZ
4/2/2022 6:30:31 PM | LRCC-04/02/2022 18:27: For info: New Balsik 1000MVA T02 completed commissioning at secondary side (230kV) at 1820H. [WEBSMS] | CLUZ
4/2/2022 6:26:51 PM | LRCC-04/02/2022 18:16: Binan 230kV Bus 2 restored at 1815H (Planned outage). [WEBSMS] | CLUZ
4/2/2022 6:16:49 PM | LEYTE ACC-04/02/22 18:18: BABATNGON SS,69KV Bus 1 de-energized at 1757H to effect the emergency removal of Birds nest,Weather:Cloudy | CVIS
4/2/2022 6:01:42 PM | VRCC-04/02/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2288MW, PK=1990MW, RR=40MW, NetOpMargin: EVE=258 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, PGPP1 at 87MW, LGPP at 80MW [WEBSMS] | CVIS
4/2/2022 5:51:38 PM | LRCC-04/02/2022 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12538MW, PK=9791MW, RR=380MW, NetOpMargin: EVE=2367 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW; SLTEC 2 @117MW; SUAL 2 @580MW; ILJJAN A / B @800MW; SAN LORENZO 50 @250MW; SAN LORENZO 60 @250MW; STA RITA 30 @161MW; STA RITA 40 @161MW [WEBSMS] | CLUZ
4/2/2022 5:28:04 PM | LEYTE ACC-04/02/22 17:31:PARANAS SS,Paranas-Borongan-Quinapondan 69 kV L,Deenergized/Energized, at 1651H/1659H,load=12.7mw, while Sta Rita Quinapondan line restored at 1709H back to normal as per PANR No. TLOS V_LEY-2022-03-0010, WEATHER:Cloudy | CVIS
4/2/2022 5:18:00 PM | VRCC-04/02/2022 17:14: Compostela SS. 150 MVA TR 2 energized at 1706H, pre arranged. [WEBSMS] | CVIS
4/2/2022 4:49:52 PM | LRCC-04/02/2022 16:39: Quezon - San Jose 230kV L2 restored at 1638H (Planned Outage). [WEBSMS] | CLUZ
4/2/2022 4:26:28 PM | NEGROS ACC: 04/02/2022, PGPP1 U3 re-online at 1556H | CVIS
4/2/2022 3:52:53 PM | LEYTE ACC-04/02/22 15:57: ORMOC SS,Ormoc 138/69 kV T1 (100MVA),Pre arranged activity completed Energized at 1539H per PANR No. VRCC-2022-03-0054, Weather:Cloudy | CVIS
4/2/2022 2:53:38 PM | VRCC-04/02/2022 14:51: 34.5 KV Sangi-CEB 3 restored at 1446H. note: correction tripped line was not pinamungajan fdr. [WEBSMS] | CVIS
4/2/2022 2:53:37 PM | VRCC-04/02/2022 14:43: 34.5 KV Pinamungan feeder tripped at1435H w/ lockout indication, L=11.34MW. [WEBSMS] | CVIS
4/2/2022 1:08:38 PM | VRCC-04/02/2022 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2534MW, PK=2011MW, RR=40MW, NetOpMargin: PM=483, EVE=241 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, PGPP1 at 70MW, LGPP at 80MW [WEBSMS] | CVIS
4/2/2022 1:08:36 PM | LRCC-04/02/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12934MW, PK=9812MW, RR=414MW, NetOpMargin: PM=2708, EVE=2086 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW; SLTEC 2 @98MW; SUAL 2 @580MW; ILJJAN A / B @817MW; SAN LORENZO 50 @250MW; SAN LORENZO 60 @250MW; STA RITA 30 @161MW; STA RITA 40 @161MW [WEBSMS] | CLUZ
4/2/2022 11:43:13 AM | PANAY ACC-04/02/22 10:54: BAROTAC VIEJO SS, Barotac Viejo-Dingle 138 kV Line 1 (7LI1BAR-DIN), TIME IN: 10:49:00, Pre-arranged maintenance | CVIS
4/2/2022 11:43:12 AM | PANAY ACC-04/02/22 10:54: BAROTAC VIEJO SS, Barotac Viejo-Dingle 138 kV Line 1 (7LI1BAR-DIN), TIME IN: 10:49:00, Pre-arranged maintenance | CVIS
4/2/2022 11:10:56 AM | VRCC-04/02/2022 11:06: 34.5 KV Pinamungajan feeder restored at 1059H. [WEBSMS] | CVIS
4/2/2022 11:10:54 AM | VRCC-04/02/2022 11:04: 34.5 KV Carcon-Toledo L1 re energized at 1056H with clearance from Global. [WEBSMS] | CVIS
4/2/2022 10:56:22 AM | VRCC-04/02/2022 10:49: 34.5 KV Toledo TR 2 synchronized with the system at 1044H. [WEBSMS] | CVIS
4/2/2022 9:12:29 AM | VRCC-04/02/2022 09:05: 34.5 KV Toledo-Carcon L1L2 tripped at 0842H, Pinamungajan feeder isolated by UFR L=2.48MW, under assessment. [WEBSMS] | CVIS
4/2/2022 7:52:08 AM | LRCC-04/02/2022 07:50: Binan 230kV Bus 2 de-energized at 0750H (Planned outage). [WEBSMS] | CLUZ
4/2/2022 7:25:14 AM | LRCC-04/02/2022 07:24: Tayabas - Naga 230kV Line 2 de-energized at 0723H (Planned Outage). [WEBSMS] | CLUZ
4/2/2022 7:15:13 AM | LRCC-04/02/2022 07:10: Mexico - Concepcion 230kV L1 de-energized at 0708H (Planned outage). [WEBSMS] | CLUZ
4/2/2022 6:58:32 AM | PANAY ACC-04/02/22 06:46: ILOILO 1 S/S SS, Iloilo - Baldoza 69 kV Line (CO) (5LI1ILO-BDO), TIME IN: 06:45:00,Facilitated emergency shutdown request of MORE Power to conduct repair of damaged 69kV transmission line conductor at Megaworld area. | CVIS
4/2/2022 6:58:31 AM | PANAY ACC-04/02/22 06:46: ILOILO 1 S/S SS, Iloilo - Baldoza 69 kV Line (CO) (5LI1ILO-BDO), TIME IN: 06:45:00,Facilitated emergency shutdown request of MORE Power to conduct repair of damaged 69kV transmission line conductor at Megaworld area. | CVIS
4/2/2022 6:58:29 AM | PANAY ACC-04/02/22 06:45: BAROTAC VIEJO SS, Barotac Viejo-Dingle 138 kV Line 1 (7LI1BAR-DIN), TIME OUT: 06:42, Pre-arranged maintenance; ETR:1800H | CVIS
4/2/2022 6:58:28 AM | PANAY ACC-04/02/22 06:45: BAROTAC VIEJO SS, Barotac Viejo-Dingle 138 kV Line 1 (7LI1BAR-DIN), TIME OUT: 06:42, Pre-arranged maintenance; ETR:1800H | CVIS
4/2/2022 6:58:27 AM | LEYTE ACC-04/02/22 07:00:STA. RITA SS,STA. RITA SS, Sta. Rita Quinapondan 69kV line Deenergized at 0623H,load=3.6mw,Load transferred Buenavista SS via Paranas SS at 0629H,Pre arranged per PANR No.TLOS V_LEY-2022-03-0010,6am-6pm,WEATHER: Cloudy | CVIS
4/2/2022 6:58:25 AM | PANAY ACC-04/02/22 06:12: ILOILO 1 S/S SS, Iloilo - Baldoza 69 kV Line (CO) (5LI1ILO-BDO), TIME OUT: 06:11, Load:21.8MW; Facilitated emergency shutdown request of MORE Power to conduct repair of damaged 69kV transmission line conductor at Megaworld area. | CVIS
4/2/2022 6:58:24 AM | PANAY ACC-04/02/22 06:12: ILOILO 1 S/S SS, Iloilo - Baldoza 69 kV Line (CO) (5LI1ILO-BDO), TIME OUT: 06:11, Load:21.8MW; Facilitated emergency shutdown request of MORE Power to conduct repair of damaged 69kV transmission line conductor at Megaworld area. | CVIS
4/2/2022 6:58:21 AM | LRCC-04/02/2022 06:50: Quezon - San Jose 230kV L2 de-energized at 0648H (Planned Outage). [WEBSMS] | CLUZ
4/2/2022 6:48:20 AM | LRCC-04/02/2022 06:38: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12859MW, PK=10052MW, RR=400MW, NetOpMargin: AM=2407, PM=1995, EVE=1908 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, SLTEC 1 at 91MW, SLTEC 2 at 98MW, Sta Rita 30 at 161MW, Sta Rita 40 at 161MW, San Lorenzo 50 at 250MW, San Lorenzo 60 at 250MW, Ilijan A at 537MW, Ilijan B at 200MW and Sual 2 at 580MW [WEBSMS] | CLUZ
4/2/2022 6:38:19 AM | LEYTE ACC-04/02/22 06:40: ORMOC SS, Ormoc 138/69 kV T1 (100MVA) ,Deenergized at 0618H,Pre arranged per PANR No. VRCC-2022-03-0054,6am-6pm, WEATHER: Cloudy | CVIS
4/2/2022 6:14:49 AM | LRCC-04/02/2022 06:13: Bayombong - Santiago 230kV line 1 de-energized at 0606H (Planned Outage) [WEBSMS] | CLUZ
4/2/2022 6:13:25 AM | VRCC-04/02/2022 06:10: Compostela Ss 150MVA TR 5 de-energized at 0609H, pre-arranged. [WEBSMS] | CVIS
4/2/2022 6:13:23 AM | LRCC-04/02/2022 06:04: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12859MW, PK=10052MW, RR=400MW, NetOpMargin: AM=2407, PM=1995, EVE=1908 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, SLTEC 1 at 91MW, SLTEC 2 at 98MW, Sta Rita 30 at 161MW, Sta Rita 40 at 161MW, San Lorenzo 50 at 250MW, San Lorenzo 60 at 250MW, Ilijan at 573MW and Sual 2 at 580MW [WEBSMS] | CLUZ
4/2/2022 6:01:23 AM | VRCC-04/02/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2558MW, PK=1974MW, RR=40MW, NetOpMargin: AM=544, PM=473, EVE=241 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 375MW, TPC at 82MW, PGPP1 at 70MW, LGPP at 80MW [WEBSMS] | CVIS
4/2/2022 5:24:34 AM | LRCC-04/02/2022 05:18: Weather Update: April 2, 2022, Shear Line affecting the eastern section of Northern Luzon. Easterlies affecting the eastern sections of Southern Luzon, Visayas, and Mindanao. Metro Manila and the rest of the country will have partly cloudy to cloudy skies with isolated rainshowers or thunderstorms [WEBSMS] | CLUZ
4/2/2022 1:53:17 AM | LRCC-04/02/2022 01:47: Taytay(Dolores) 230kV Bus 2 energized at 0146H. (Unplanned Outage) [WEBSMS] | CLUZ
4/1/2022 9:15:00 PM | LRCC-04/01/2022 21:13: Taytay(Dolores) 230kV Bus 2 de-energized at 2111H. (Unplanned Outage) [WEBSMS] | CLUZ
4/1/2022 8:48:09 PM | LEYTE ACC-04/01/22 20:50:ORMOC CONVERTER STATION SS,350kV Leyte Luzon,Blocked/Deblocked at 2022H/2032H,on normal power flow per RTD. WEATHER: FAIR | CVIS
4/1/2022 6:07:15 PM | VRCC-04/01/2022 18:04: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2252MW, PK=2122MW, RR=42MW, NetOpMargin: EVE=88 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, PGPP1 at 70MW, LGPP at 80MW [WEBSMS] | CVIS
4/1/2022 5:53:48 PM | LRCC-04/01/2022 17:47: Naga-Tayabas 230kV line 2 restored at 1746H. (Planned Outage) [WEBSMS] | CLUZ
4/1/2022 5:20:14 PM | LRCC-04/01/2022 17:18: Balsik 1000MVA T02 energized at 230kV side at 1706H. (On-going energization and commissioning.) [WEBSMS] | CLUZ
4/1/2022 5:16:50 PM | LRCC-04/01/2022 17:12: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12279MW, PK=10209MW, RR=421MW, NetOpMargin: EVE=12279 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; MASINLOC 1 @240MW; SLTEC 1 @91MW; SUAL 2 @590MW; SCPC 3 @120MW; ILJJAN A / B @800MW; STA RITA 30 @161MW; STA RITA 40 @161MW [WEBSMS] | CLUZ
4/1/2022 4:29:58 PM | PANAY ACC-04/01/22 16:27: CONCEPCION S/S SS, Concepcion-PCPC 138 kV Line (CO) (7LI1CNE-CCF), TIME IN: 16:20:00, WEATHER: FAIR. Pre-arranged Activities. | CVIS
4/1/2022 4:29:56 PM | PANAY ACC-04/01/22 16:27: CONCEPCION S/S SS, Concepcion-PCPC 138 kV Line (CO) (7LI1CNE-CCF), TIME IN: 16:20:00, WEATHER: FAIR. Pre-arranged Activities. | CVIS
4/1/2022 1:01:52 PM | VRCC-04/01/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2517MW, PK=2177MW, RR=37MW, NetOpMargin: PM=303, EVE=88 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 375MW, TPC at 82MW, PGPP1 at 75MW, LGPP at 80MW [WEBSMS] | CVIS
4/1/2022 12:35:01 PM | NEGROS ACC: 04/01/2022, 69kV Bacolod-Reclamation Sub T/L restored at 1228H. Customer owned and maintained line. | CVIS
4/1/2022 12:24:58 PM | NEGROS ACC: 69kV Bacolod-Reclamation Sub T/L(37.75MW) auto tripped at 1215H with ind.;Z1 L3E 0.5KM.Customer owned and maintained line. | CVIS
4/1/2022 12:14:56 PM | LEYTE ACC-04/01/22 12:18:BABATNGON SS,69KV Bus 2 energized at 1202H, WEATHER: Cloudy | CVIS
4/1/2022 12:07:55 PM | LEYTE ACC-04/01/22 12:15: ORMOC SS,Ormoc-Babatngon 138 kV L1,energized at 1158H, WEATHER: Cloudy | CVIS
4/1/2022 12:07:53 PM | LRCC-04/01/2022 11:58: Bantay - Currimao/Laoag 115kV Line tripped/reclosed at 1133H [WEBSMS] | CLUZ
4/1/2022 11:53:09 AM | LEYTE ACC-04/01/22 11:44:Babatngon SS,138kV Ormoc Babatngon Line 1 tripped at 1141, under assessment, WEATHER: Cloudy | CVIS
4/1/2022 11:39:50 AM | LEYTE ACC-04/01/22 11:44:Babatngon SS, Deenergized 69kV Bus 2 at 1054H, per O&M request to effect the removal of Birds nest, WEATHER: FAIR | CVIS
4/1/2022 8:31:50 AM | LEYTE ACC-04/01/22 08:34:ORMOC CONVERTER STATION SS,350kV HVDC Leyte-Luzon,Blocked/Deblocked at 0810H/0820H,on reverse power flow per RTD.,WEATHER: FAIR | CVIS
4/1/2022 8:21:47 AM | NEGROS ACC: 04/01/2022, Mabinay S/S 138kV Bus 2 de-energized at 0816H due to APMS. | CVIS
4/1/2022 7:58:18 AM | LRCC-04/01/2022 07:51: Limay 230kV Bus 2 de-energized at 0735H (Planned Outage) [WEBSMS] | CLUZ
4/1/2022 7:48:12 AM | LRCC-04/01/2022 07:45: Limay - Batangas II (BPC) 230kV Line 1 de-energized at 0741H (Planned Outage) [WEBSMS] | CLUZ
4/1/2022 6:24:25 AM | LRCC-04/01/2022 06:22: Tayabas - Naga 230kV Line 2 de-energized at 0615H (Planned Outage) [WEBSMS] | CLUZ
4/1/2022 6:00:57 AM | VRCC-04/01/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2508MW, PK=2126MW, RR=36.6MW, NetOpMargin: AM=345, PM=272, EVE=48 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 375MW, PGPP1 at 71MW, LGPP at 80MW [WEBSMS] | CVIS
4/1/2022 6:00:54 AM | LRCC-04/01/2022 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12702MW, PK=10931MW, RR=400MW, NetOpMargin: AM=1371, PM=767, EVE=1375 Highest Unit O/L: GNPD1 @668MW Derated Plant: SLTEC 1 @91MW, SLPGC 3 @120MW, Sual 2 @590MW, GMEC 2 @ 300MW, Sta Rita 30/40MW @161MW/161MW & Ilijan @737MW [WEBSMS] | CLUZ
4/1/2022 5:23:56 AM | VRCC-04/01/2022 05:16: TVI U2 synchronized at 0510H. [WEBSMS] | CVIS
4/1/2022 5:23:54 AM | LRCC-04/01/2022 05:23: Weather Update: Easterlies affecting the eastern section of the country. [WEBSMS] | CLUZ
4/1/2022 4:13:32 AM | LRCC-04/01/2022 04:09: SLTEC 2 online at 0405H (Unplanned Outage). [WEBSMS] | CLUZ
3/31/2022 11:31:38 PM | VRCC-03/31/2022 23:24: TVI U2 tripped at 2318H with 53.5MW load involved. Cause under investigation [WEBSMS] | CVIS
3/31/2022 11:08:51 PM | LEYTE ACC-03/31/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 2244H/2254H, on normal flow per RTD | CVIS
3/31/2022 10:58:48 PM | LEYTE ACC-03/31/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 2244H/2254H, on normal flow per RTD | CVIS
3/31/2022 9:49:40 PM | VRCC-03/31/2022 21:43: TVI U2 synchronized at 2138H. [WEBSMS] | CVIS
3/31/2022 7:40:07 PM | VRCC-03/31/2022 19:32: Viisayas grid red alert lifted at 1925H. MLD in Negros and Panay area due to 138kV Cebu-Negros Line 2 overloading already restored. [WEBSMS] | CVIS
3/31/2022 7:30:17 PM | PANAY ACC; 03/31/2022 1921H: MLD IMPLEMENTED AT PANAY AREA IS LIFTED WITH LAST FEEDER IN 1920H(ILECO 1 OTON FDR.). | CVIS
3/31/2022 7:30:15 PM | PANAY ACC; 03/31/2022 1921H: MLD IMPLEMENTED AT PANAY AREA IS LIFTED WITH LAST FEEDER IN 1920H(ILECO 1 OTON FDR.). | CVIS
3/31/2022 7:30:14 PM | NEGROS ACC: 03/31/2022: MLD in Negros area restored at 1920H, with total load drop of 17.44MW last feeder in NONECOs San Carlos Fdr 3. | CVIS
3/31/2022 7:30:13 PM | NEGROS ACC: 03/31/2022: MLD in Negros area restored at 1920H, with total load drop of 17.44MW last feeder in NONECOs San Carlos Fdr 3. | CVIS
3/31/2022 7:30:11 PM | VRCC-03/31/2022 19:26: SO initiated market intervention lifted at interval 1925H. [WEBSMS] | CVIS
3/31/2022 7:20:09 PM | VRCC-03/31/2022 19:12: Visayas grid is on RED ALERT starting at 1815H due to overloading of Cebu-Negros cable 2. [WEBSMS] | CVIS
3/31/2022 7:06:42 PM | VRCC-03/31/2022 19:03: VRCC declared SO initiated Market Intervention starting interval 1825H due to MLD implementation in Negros and Panay due to prevent overloading of Cebu-Negros cable. [WEBSMS] | CVIS
3/31/2022 6:56:39 PM | PANAY ACC; 3/31/2022 1836H: Implemented MLD w/1st Fdr. Out at 1820H and Total Load Drop of 12.6MW to avoid overloading of Negros - Cebu Sub. Cable with PCPC On emergency shutdown. | CVIS
3/31/2022 6:56:38 PM | PANAY ACC; 3/31/2022 1836H: Implemented MLD w/1st Fdr. Out at 1820H and Total Load Drop of 12.6MW to avoid overloading of Negros - Cebu Sub. Cable with PCPC On emergency shutdown. | CVIS
3/31/2022 6:41:51 PM | NEGROS ACC: 03/31/2022, Implemented MLD in Negros area at 1817H to avoid overloading of 138kV Amlan-Samboan Line 2. 1st feeder out- VMC F1(1.34MW). | CVIS
3/31/2022 6:41:50 PM | NEGROS ACC: 03/31/2022, Implemented MLD in Negros area at 1817H to avoid overloading of 138kV Amlan-Samboan Line 2. 1st feeder out- VMC F1(1.34MW). | CVIS
3/31/2022 6:08:28 PM | VRCC-03/31/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2078MW, PK=2072MW, RR=40MW, NetOpMargin: EVE=6 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 375MW, PGPP1 at 73MW, PEDC at 239MW, LGPP at 80MW [WEBSMS] | CVIS
3/31/2022 6:08:25 PM | LRCC-03/31/2022 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12380MW, PK=10737MW, RR=394MW, NetOpMargin: EVE=12380 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW; SUAL 2 @600MW; SCPC 3 @120MW; ILJJAN A / B @800MW [WEBSMS] | CLUZ
3/31/2022 6:08:23 PM | LRCC-03/31/2022 18:02: Tayabas - Naga 230kV Line 2 restored at 1757H (Planned Outage) [WEBSMS] | CLUZ
3/31/2022 4:23:58 PM | NEGROS ACC: 03/31/2022: 69kV Bacolod-Silay Sub TL restored at 1606H. Customer owned and maintained line. | CVIS
3/31/2022 4:15:52 PM | NEGROS ACC: 03/31/2022: 69kV Bacolod-Silay Sub TL restored at 1606H. Customer owned and maintained line. | CVIS
3/31/2022 4:15:50 PM | NEGROS ACC: 03/31/2022: 69kV Bacolod-Silay Sub TL restored at 1606H. Customer owned and maintained line. | CVIS
3/31/2022 4:15:49 PM | NEGROS ACC: 03/31/2022: SIPS activation in Negros area at 1551H, isolating 69kV Bacolod-Silay Sub TL(46.32MW) to prevent overloading of 138kV Cebu-Negros Submarine Cable L2 due to sudden load reduction of Solar Plants by 53.4MW. | CVIS
3/31/2022 4:15:47 PM | NEGROS ACC: 03/31/2022: SIPS activation in Negros area at 1551H, isolating 69kV Bacolod-Silay Sub TL(46.32MW) to prevent overloading of 138kV Cebu-Negros Submarine Cable L2 due to sudden load reduction of Solar Plants by 53.4MW. | CVIS
3/31/2022 4:15:46 PM | NEGROS ACC: 03/31/2022: SIPS activation in Negros area at 1551H, isolating 69kV Bacolod-Silay Sub TL(46.32MW) to prevent overloading of 138kV Cebu-Negros Submarine Cable L2 due to sudden load reduction of Solar Plants by 53.4MW. | CVIS
3/31/2022 3:43:19 PM | PANAY ACC; 03/31/2022 15:35H: PEDC UNIT #3 RE-ONLINE?SYNCHRONIZED WITH THE SYSTEM AT 1530H. | CVIS
3/31/2022 3:43:18 PM | PANAY ACC; 03/31/2022 15:35H: PEDC UNIT #3 RE-ONLINE?SYNCHRONIZED WITH THE SYSTEM AT 1530H. | CVIS
3/31/2022 2:04:04 PM | NEGROS ACC: 03/31/2022, Mabinay S/S 138kV Bus 1 energized at 1351H after APMS. | CVIS
3/31/2022 1:40:18 PM | LEYTE ACC-03/31/22 13:41: IASCO PP, IASCO Diesel Power Plant cut-in to the system at 1325H per RTD (commercial operation). Weather: Cloudy. | CVIS
3/31/2022 1:06:44 PM | VRCC-03/31/2022 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2221MW, PK=2182MW, RR=40MW, NetOpMargin: PM=39, EVE=6 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 375MW, TVI at 169MW, PGPP1 at 73MW, PEDC at 164MW, LGPP at 80MW [WEBSMS] | CVIS
3/31/2022 1:06:43 PM | VRCC-03/31/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2221MW, PK=2182MW, RR=40MW, NetOpMargin: PM=39, EVE=6 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 375MW, TPC at 82MW, TVI at 169MW, PGPP1 at 73MW, PEDC at 164MW, LGPP at 80MW [WEBSMS] | CVIS
3/31/2022 1:06:41 PM | VRCC-03/31/2022 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2221MW, PK=2182MW, RR=40MW, NetOpMargin: PM=39, EVE=6 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 375MW, TPC at 82MW, TVI at 169MW, PGPP1 at 73MW, PEDC at 164MW, LGPP at 80MW [WEBSMS] | CVIS
3/31/2022 1:01:53 PM | LRCC-03/31/2022 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12753MW, PK=11525MW, RR=400MW, NetOpMargin: PM=828, EVE=1600 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW; SUAL 2 @600MW; SCPC 3 @120MW; ILJJAN A / B @800MW [WEBSMS] | CLUZ
3/31/2022 12:41:58 PM | MRCC-03/31/2022 12:29: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2965MW, PK=2030MW, RR=81MW, NetOpMargin: PM=854, EVE=949 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@25MW, Ag2@80MW, Ag4@104MW, Ag5@40MW, Ag6@98MW, Ag7@26MW, Pul4@194MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@129MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/31/2022 12:38:29 PM | LRCC-03/31/2022 12:29: Sta. Rita 30 on-line at 1227H (Unplanned Outage) [WEBSMS] | CLUZ
3/31/2022 10:53:51 AM | LRCC-03/31/2022 10:53: Sta. Rita 30 @ 73MW tripped at 1031H (Unplanned Outage) [WEBSMS] | CLUZ
3/31/2022 10:06:51 AM | LRCC-03/31/2022 10:02: Sta. Rita 30 on-line at 0959H (Unplanned Outage) [WEBSMS] | CLUZ
3/31/2022 9:09:51 AM | PANAY ACC-03/31/22 06:13: CONCEPCION S/S SS, Concepcion-PCPC 138 kV Line (CO) (7LI1CNE-CCF), TIME OUT: 06:12:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
3/31/2022 8:33:57 AM | NEGROS ACC: 03/31/2022, Mabinay S/S 138kV Bus 1 de-energized at 0810H due to APMS. | CVIS
3/31/2022 8:19:22 AM | LEYTE ACC-03/31/22 08:29: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 0806H/0816H on reverse power flow per RTD. Weather: Fair. | CVIS
3/31/2022 6:21:50 AM | LRCC-03/31/2022 06:14: Tayabas-Naga 230kV Line 2 de-energized at 0611H (Planned Outage). [WEBSMS] | CLUZ
3/31/2022 6:11:43 AM | VRCC-03/31/2022 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2317MW, PK=2161MW, RR=40MW, NetOpMargin: AM=116, PM=-17, EVE=-135 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 375 MW, PEDC = 164 MW, LGPP 1 = 80 MW, TPC = 82 MW, PGPP 1 = 54 MW, TVI = 169 MW [WEBSMS] | CVIS
3/31/2022 6:01:38 AM | LRCC-03/31/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12565MW, PK=10843MW, RR=400MW, NetOpMargin: AM=1322, PM=925, EVE=1793 Highest Unit O/L: GNPD1 @668MW Derated Plant: SLTEC 1 @91MW, SLPGC 3 @120MW, Sual 2 @550MW, GMEC 2 @ 300MW, & Ilijan @827MW [WEBSMS] | CLUZ
3/31/2022 5:56:14 AM | LRCC-03/31/2022 05:56: Sta. Rita 30 @83MW tripped at 0552H (Unplanned Outage) [WEBSMS] | CLUZ
3/31/2022 5:22:44 AM | LRCC-03/31/2022 05:20: Sta. Rita 30 online at 0516H (Planned Outage). [WEBSMS] | CLUZ
3/31/2022 5:09:20 AM | PANAY ACC-03/31/22 04:15: PEDC U3 (125MW), OUT:0409H; To conduct emergency repair of sea water derby filter. | CVIS
3/31/2022 5:09:19 AM | PANAY ACC-03/31/22 04:15: PEDC U3 (125MW), OUT:0409H; To conduct emergency repair of sea water derby filter. | CVIS
3/31/2022 4:59:27 AM | MRCC-03/31/2022 04:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2961MW, PK=1920MW, RR=58MW, NetOpMargin: AM=964, PM=854, EVE=949 Highest Unit O/L: GNPK U3 & U4 @138MW each. Derated Plant: Ag1@25MW, Ag2@80MW, Ag4@104MW, Ag5@40MW, Ag6@98MW, Ag7@26MW, Pul4@194MW, MGPP@77MW, STEAG@200MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@100MW. [WEBSMS] | CMIN
3/31/2022 4:49:12 AM | LRCC-03/31/2022 04:47: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
3/31/2022 4:08:08 AM | LRCC-03/31/2022 04:04: Sta. Rita 20 online at 0401H (Unplanned Outage). [WEBSMS] | CLUZ
3/31/2022 1:33:54 AM | LEYTE ACC-03/31/22 01:36:ORMOC CONVERTER STATION SS,350kV Leyte Luzon,Blocked/Deblocked at 0103H/0113H,on normal power flow per RTD,WEATHER: FAIR | CVIS
3/30/2022 7:54:28 PM | LRCC-03/30/2022 19:53: For info: New Balsik-Mariveles 500kV Line 1 successfully energized at Balsik side at 1912H and completed commissioning at Balsik side only at 1946H (Energized up to PT at Mariveles side) [WEBSMS] | CLUZ
3/30/2022 6:23:36 PM | LRCC-03/30/2022 18:21: Sta Rita 20 runback from 165MW to 108MW due to tripping of ST at 1802H but eventually tripped while @106MW at 1803H. Lowest System Frequency dip is 59.64Hz. (Unplanned Outage) [WEBSMS] | CLUZ
3/30/2022 6:10:12 PM | VRCC-03/30/2022 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2122MW, PK=2031MW, RR=40MW, NetOpMargin: EVE=51 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 375MW, TPC at 82MW, TVI at 169MW, PGPP1 at 87.5MW, PEDC at 292MW, LGPP at 80MW, Luzon to augment Visayas [WEBSMS] | CVIS
3/30/2022 5:54:54 PM | LRCC-03/30/2022 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12702MW, PK=10667MW, RR=397MW, NetOpMargin: EVE=1638 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW; SUAL 2 @600MW; ILJJAN A / B @888MW [WEBSMS] | CLUZ
3/30/2022 5:54:51 PM | LRCC-03/30/2022 17:46: Tayabas-Naga 230kV Line 2 restored at 1743H (Planned Outage). [WEBSMS] | CLUZ
3/30/2022 5:11:22 PM | MRCC-03/30/2022 17:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2910MW, PK=1890MW, RR=56MW, NetOpMargin: EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 4:18:00 PM | VRCC-03/30/2022 16:17: THIS IS A DRILL: Dispatchers from VBURCC arrived in RCC at 1635H to assume duty/take-over back to normal operations after completion of SCADA works by SED group. ``THIS IS A DRILL`` [WEBSMS] | CVIS
3/30/2022 4:06:40 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 4:06:29 PM | VRCC-03/30/2022 16:02: THIS IS A DRILL: SO-Visayas initiated Market Intervention lifted 1600H. Operations is normalize back to VRCC from BVURCC. ``THIS IS A DRILL`` [WEBSMS] | CVIS
3/30/2022 3:51:30 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 3:41:21 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 3:31:05 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 3:28:42 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 3:18:32 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 3:07:31 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 3:04:15 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 2:54:06 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 2:43:57 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 2:43:47 PM | VRCC-03/30/2022 14:42: THIS IS A DRILL: SO-Visayas initiated Market Intervention starting interval 1430H to 1600H, after turned-over of generation dispatching to Negros ACC prior to Evacuation to Back-up RCC. ``THIS IS A DRILL`` [WEBSMS] | CVIS
3/30/2022 2:40:39 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 2:30:30 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 2:19:07 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 2:18:57 PM | VRCC-03/30/2022 14:13: THIS IS A DRILL: Please be informed that VRCC is conducting an Evacuation Drill starting at 1410H. ``THIS IS A DRILL`` [WEBSMS] | CVIS
3/30/2022 2:06:58 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 2:06:44 PM | NEGROS ACC: 03/30/2022, ``THIS IS ONLY A DRILL`` Negros Sub Grid Power Highway (Backbone line) restored at 1401H. | CVIS
3/30/2022 2:06:43 PM | NEGROS ACC: 03/30/2022, ``THIS IS ONLY A DRILL`` Negros Sub Grid Power Highway (Backbone line) restored at 1401H. | CVIS
3/30/2022 1:56:49 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 1:53:36 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 1:43:26 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 1:43:10 PM | LEYTE ACC-03/30/22 13:43: Leyte/Samar backbone line restored at 1331H. Note: This is only a drill. | CVIS
3/30/2022 1:33:16 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 1:29:42 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 1:19:33 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 1:09:23 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 1:09:12 PM | LRCC-03/30/2022 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13114MW, PK=11441MW, RR=420MW, NetOpMargin: PM=1253, EVE=1716 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW; SUAL 2 @600MW; ILJJAN A / B @888MW [WEBSMS] | CLUZ
3/30/2022 1:01:15 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 1:00:55 PM | VRCC-03/30/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2350MW, PK=2237MW, RR=40MW, NetOpMargin: PM=73, EVE=51 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 375MW, TPC at 82MW, TVI at 169MW, PGPP1 at 87.5MW, PEDC at 292MW, LGPP at 80MW, Luzon to augment Visayas [WEBSMS] | CVIS
3/30/2022 12:51:05 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 12:50:50 PM | LRCC-03/30/2022 12:50: SCPC 4 online at 1248H (Unplanned Outage). [WEBSMS] | CLUZ
3/30/2022 12:40:56 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 12:37:41 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 12:27:31 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 12:27:14 PM | VRCC-03/30/2022 12:21: THIS IS A DRILL, Visayas table top drill has been completed, if sequence be followed starting Cebu feedback power, Visayas simulation drill will be completed at 1516H, Panay sub grid restoration. [WEBSMS] | CVIS
3/30/2022 12:16:37 PM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 12:16:22 PM | VRCC-03/30/2022 11:54: THIS IS A DRILL, Cebu sub grid backbone lines restored at 1148H, this is a drill. [WEBSMS] | CVIS
3/30/2022 12:16:21 PM | VRCC-03/30/2022 11:50: THIS IS A DRILL, Cebu sub grid ready to provide feedback power to Negros sub grid at 1151H, this is a drill. [WEBSMS] | CVIS
3/30/2022 12:16:20 PM | VRCC-03/30/2022 11:47: THIS IS A DRILL, Cebu sub grid ready to provide feedback power to Leyte sub grid at 1147H, this is a drill. [WEBSMS] | CVIS
3/30/2022 11:47:13 AM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 11:37:17 AM | MRCC-03/30/2022 11:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2890MW, PK=2010MW, RR=59MW, NetOpMargin: PM=799, EVE=945 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@105MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/30/2022 11:37:05 AM | VRCC-03/30/2022 11:27: THIS IS A DRILL, CEDC 1st unit cut in at 1104H, KSPC 1st unit at 1117H, This is a drill. [WEBSMS] | CVIS
3/30/2022 11:37:04 AM | VRCC-03/30/2022 11:25: THIS IS A DRILL, TPVI 1st unit cut in at 0953H, CPPC 1st unit at 1010H, EAUC synchronized at 1038H, This is a drill. [WEBSMS] | CVIS
3/30/2022 11:23:34 AM | VRCC-03/30/2022 11:19: THIS IS A DRILL, Carmen diesel 1st unit & 2nd unit cut in at 0859H & 0914H. This is a drill. [WEBSMS] | CVIS
3/30/2022 10:34:06 AM | LRCC-03/30/2022 10:27: SCPC 4 (12MW) tripped at 1021H (Unlanned Outage). [WEBSMS] | CLUZ
3/30/2022 10:06:33 AM | VRCC-03/30/2022 10:01: DaanBantayan SS 69 KV Lanao Feeder (CEBECO 2) de-energized/energized at 0947H/0955H to facilitate closing of disconnect switch at customer side. [WEBSMS] | CVIS
3/30/2022 9:21:30 AM | VRCC-03/30/2022 09:18: DaanBantayan SS. 69 KV Lanao Feeder (CEBECO 2) energized at 0847H with customer clearance. [WEBSMS] | CVIS
3/30/2022 9:18:32 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 9:08:22 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 8:57:40 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 8:57:30 AM | VRCC-03/30/2022 08:54: THIS IS A DRILL, VRCC declared SO initiated MARKET INTERVENTION starting interval 0835H. [WEBSMS] | CVIS
3/30/2022 8:57:29 AM | VRCC-03/30/2022 08:50: THIS IS A DRILL, VRCC implement power restoration thru the NGCP black start services at 0831H. [WEBSMS] | CVIS
3/30/2022 8:57:26 AM | LRCC-03/30/2022 08:48: SCPC 4 online at 0839H (Planned Outage). [WEBSMS] | CLUZ
3/30/2022 8:43:47 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 8:43:36 AM | VRCC-03/30/2022 08:36: THIS IS A DRILL, Visayas power grid is on system blackout at 0827H, possibly due to lightning strike. [WEBSMS] | CVIS
3/30/2022 8:32:27 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 8:32:13 AM | LEYTE ACC-03/30/22 08:39: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 0815H/0825H on reverse power flow per RTD. Weather: Fair. | CVIS
3/30/2022 8:29:04 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 8:18:54 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 8:08:45 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 8:05:34 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 8:05:08 AM | VRCC-03/30/2022 07:55: 37.5MVA TR 1 under T/C at Toledo SS de-energized at 0748H. Pre-arranged activity. [WEBSMS] | CVIS
3/30/2022 7:55:23 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 7:45:11 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 7:41:57 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 7:31:47 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 7:21:38 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 7:18:29 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 7:08:19 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 6:58:05 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 6:55:52 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 6:45:34 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 6:34:33 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 6:31:21 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 6:21:11 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 6:20:55 AM | LRCC-03/30/2022 06:11: Tayabas-Naga 230kV Line 2 de-energized at 0610H (Planned Outage). [WEBSMS] | CLUZ
3/30/2022 6:11:01 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 6:08:41 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 6:08:30 AM | VRCC-03/30/2022 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2461MW, PK=2122MW, RR=40MW, NetOpMargin: AM=299, PM=73, EVE=51 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 375MW, TPC at 82MW, TVI at 169MW, PGPP1 at 87.5MW, PEDC at 292MW, LGPP at 80MW [WEBSMS] | CVIS
3/30/2022 6:08:29 AM | VRCC-03/30/2022 05:57: DaanBantayan SS. 69 KV Lanao Feeder (CEBECO 2) tripped at 0549H, L=18MW, ind=OCR. [WEBSMS] | CVIS
3/30/2022 5:57:38 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 5:57:19 AM | LRCC-03/30/2022 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13303MW, PK=10907MW, RR=438MW, NetOpMargin: AM=1958, PM=1387, EVE=1957 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, SLTEC 1 at 91MW, Ilijan at 800MW, and Sual 2 at 600MW [WEBSMS] | CLUZ
3/30/2022 5:47:28 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 5:45:59 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 5:34:04 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 5:23:46 AM | LRCC-03/30/2022 05:22: Weather Update: Easterlies affecting the country. [WEBSMS] | CLUZ
3/30/2022 5:21:27 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 5:21:12 AM | LRCC-03/30/2022 05:19: Binan-San Pedro 115kV line restored at 0518H. (Planned Outage) [WEBSMS] | CLUZ
3/30/2022 5:10:38 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 4:57:15 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 4:47:06 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 4:36:55 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 4:32:19 AM | MRCC-03/30/2022 04:18: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2877MW, PK=1930MW, RR=77MW, NetOpMargin: AM=870, PM=800, EVE=945 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@174MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/30/2022 1:15:37 AM | NEGROS ACC: 03/30/2022, PGPP1 U1 re-online at 0111H. | CVIS
3/30/2022 12:04:45 AM | LEYTE ACC-03/29/22 23:22: ORMOC CONVERTER STATION SS,350kV HVDC Leyte-Luzon,Blocked/Deblocked at 2242H/2252H,on normal power flow per Visayas requirement WEATHER: FAIR | CVIS
3/29/2022 11:41:21 PM | LRCC-03/29/2022 23:34: Binan-San Pedro 115kV line de-energized at 2333H. (Planned Outage) [WEBSMS] | CLUZ
3/29/2022 11:17:49 PM | LEYTE ACC-03/29/22 23:22: ORMOC CONVERTER STATION SS,350kV HVDC Leyte-Luzon,Blocked/Deblocked at 2242H/2252H,on normal power flow per Visayas requirement WEATHER: FAIR | CVIS
3/29/2022 9:10:30 PM | MRCC-03/29/2022 16:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2772MW, PK=1895MW, RR=76MW, NetOpMargin: EVE=801 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@138MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/29/2022 9:07:21 PM | MRCC-03/29/2022 16:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2772MW, PK=1895MW, RR=76MW, NetOpMargin: EVE=801 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@138MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/29/2022 8:57:07 PM | MRCC-03/29/2022 16:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2772MW, PK=1895MW, RR=76MW, NetOpMargin: EVE=801 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@138MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/29/2022 8:46:58 PM | MRCC-03/29/2022 16:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2772MW, PK=1895MW, RR=76MW, NetOpMargin: EVE=801 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@138MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/29/2022 8:43:48 PM | MRCC-03/29/2022 16:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2772MW, PK=1895MW, RR=76MW, NetOpMargin: EVE=801 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@138MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/29/2022 8:33:39 PM | MRCC-03/29/2022 16:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2772MW, PK=1895MW, RR=76MW, NetOpMargin: EVE=801 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@138MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/29/2022 8:23:26 PM | MRCC-03/29/2022 16:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2772MW, PK=1895MW, RR=76MW, NetOpMargin: EVE=801 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@138MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/29/2022 8:20:15 PM | MRCC-03/29/2022 16:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2772MW, PK=1895MW, RR=76MW, NetOpMargin: EVE=801 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@138MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/29/2022 8:10:03 PM | MRCC-03/29/2022 16:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2772MW, PK=1895MW, RR=76MW, NetOpMargin: EVE=801 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@138MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/29/2022 7:59:53 PM | MRCC-03/29/2022 16:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2772MW, PK=1895MW, RR=76MW, NetOpMargin: EVE=801 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@138MW, MGPP@77MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@68MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/29/2022 7:59:43 PM | VRCC-03/29/2022 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2089MW, PK=1980MW, RR=40MW, NetOpMargin: EVE=69 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 372 MW, LGPP 1 = 80 MW, TPC = 82 MW, PGPP 1 = 54 MW, TVI = 169 MW [WEBSMS] | CVIS
3/29/2022 7:59:42 PM | LEYTE ACC-03/29/22 15:29: CALBAYOG SS, 69kV Catarman-Bobolosan line re-energized at 1527H, tripper found: corroded phase B strain insulator at STR. 259-E, located at San Roque, Northern, Samar. WEATHER: FAIR | CVIS
3/29/2022 7:59:40 PM | LRCC-03/29/2022 17:41: Concepcion-Concepcion Solar Power Plant 69kV Line restored at 1741H (Planned Outage) [WEBSMS] | CLUZ
3/29/2022 7:59:38 PM | LRCC-03/29/2022 17:23: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12534MW, PK=10375MW, RR=411MW, NetOpMargin: EVE=1748 Highest Unit O/L: GNPD1 @668MW Derated Plant: SLTEC 1 @91MW, Sual 2 @550MW, GMEC 2 @ 300MW, & Ilijan @827MW [WEBSMS] | CLUZ
3/29/2022 7:59:36 PM | LRCC-03/29/2022 16:52: Tayabas-Naga 230kV Line 2 restored at 1650H (Planned Outage) [WEBSMS] | CLUZ
3/29/2022 9:03:58 AM | MRCC-03/29/2022 04:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2849MW, PK=1910MW, RR=55MW, NetOpMargin: AM=862, PM=779, EVE=810 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@138MW, MGPP@77MW, STEAG@100MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/29/2022 9:03:48 AM | PANAY ACC-03/29/22 08:43: ILOILO 1 S/S SS, Iloilo 1-San Rafael 69kV L (CO), TIME OUT: 08:22:00, TIME IN: 08:33:00, RELAY: 50 / 51 N, Customer fault, WEATHER: FAIR | CVIS
3/29/2022 9:03:47 AM | LEYTE ACC-03/29/22 08:34: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 0811H/0821H on reverse power flow per RTD. Weather: Fair. | CVIS
3/29/2022 9:03:45 AM | PANAY ACC-03/29/22 06:50: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW), TIME IN: 06:48:00, Pre arranged maintenance | CVIS
3/29/2022 9:03:44 AM | PANAY ACC-03/29/22 07:46: BUENAVISTA SS, Buenavista-GUIMELCO 69kV Line (CO (5LI1BVI-GUI), TIME IN: 06:43:00, Pre arranged maintenance | CVIS
3/29/2022 9:03:42 AM | PANAY ACC-03/29/22 06:45: BUENAVISTA SS, Buenavista-Ingore 69kV Line (5LI1BVI-INR), TIME IN: 06:40:00, Pre arranged maintenance | CVIS
3/29/2022 9:03:41 AM | PANAY ACC-03/29/22 06:44: STA. BARBARA SS, Sta. Barbara-Baldoza 69 kV L (5LI1SBA-BAL), TIME IN: 06:38:00, Pre arranged maintenance | CVIS
3/29/2022 9:03:39 AM | PANAY ACC-03/29/22 06:43: STA. BARBARA SS, Sta. Barbara-Ingore 69 kV Line (5LI1SBA-INR), TIME IN: 06:38:00, Pre arranged maintenance | CVIS
3/29/2022 9:03:38 AM | VRCC-03/29/2022 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2427MW, PK=2002MW, RR=40MW, NetOpMargin: AM=385, PM=279, EVE=69 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 375MW, TPC at 82MW, PGPP1 U1 at 54MW, LGPP at 80MW [WEBSMS] | CVIS
3/29/2022 9:03:36 AM | PANAY ACC-03/29/22 05:18: STA. BARBARA SS, Sta. Barbara-Ingore 69 kV Line (5LI1SBA-INR), TIME OUT: 05:05:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
3/29/2022 9:03:35 AM | PANAY ACC-03/29/22 05:18: BUENAVISTA SS, Buenavista-GUIMELCO 69kV Line (CO (5LI1BVI-GUI), TIME OUT: 05:13:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
3/29/2022 9:03:33 AM | PANAY ACC-03/29/22 05:18: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW), TIME OUT: 05:14:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
3/29/2022 9:03:32 AM | PANAY ACC-03/29/22 05:18: BUENAVISTA SS, Buenavista-Ingore 69kV Line (5LI1BVI-INR), TIME OUT: 05:15:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
3/29/2022 9:03:30 AM | PANAY ACC-03/29/22 05:17: STA. BARBARA SS, Sta. Barbara-Baldoza 69 kV L (5LI1SBA-BAL), TIME OUT: 05:17:00, WEATHER: FAIR; Pre-arranged maintenance activity. | CVIS
3/29/2022 9:03:26 AM | LRCC-03/29/2022 07:16: Concepcion-Concepcion Solar Power Plant 69kV Line de-energized at 0713H (Planned Outage) [WEBSMS] | CLUZ
3/29/2022 9:03:25 AM | LRCC-03/29/2022 06:19: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12977MW, PK=10961MW, RR=435MW, NetOpMargin: AM=1581, PM=955, EVE=1418 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW; SUAL 2 @600MW; ILJJAN A / B @817MW [WEBSMS] | CLUZ
3/29/2022 9:03:24 AM | LRCC-03/29/2022 06:18: Tayabas-Naga 230kV Line 2 de-energized at 0615H (Planned Outage) [WEBSMS] | CLUZ
3/29/2022 9:03:23 AM | LRCC-03/29/2022 04:41: Quezon 300MVA T08 restored at 0436H (Planned Outage). [WEBSMS] | CLUZ
3/29/2022 5:04:59 AM | LRCC-03/29/2022 04:41: Quezon 300MVA T08 restored at 0436H (Planned Outage). [WEBSMS] | CLUZ
3/29/2022 4:12:11 AM | MRCC-03/29/2022 04:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2849MW, PK=1910MW, RR=55MW, NetOpMargin: AM=862, PM=779, EVE=810 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@88MW, Ag7@26MW, Pul4@138MW, MGPP@77MW, STEAG@100MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/29/2022 12:15:36 AM | LRCC-03/29/2022 00:07: Quezon 300MVA T08 de-energized at 0005H (Planned Outage). [WEBSMS] | CLUZ
3/28/2022 11:42:08 PM | LEYTE ACC-03/28/22 23:49: STA. RITA SS, Sta. Rita-Quinapondan 69kV Line tripped/restored at 2331H/2333H, ind.: Phase-A/N & 95.77kms. Load=4.7MW. Weather: Cloudy. | CVIS
3/28/2022 8:47:56 PM | LEYTE ACC-03/28/22 20:55:ORMOC CONVERTER STATION SS,350kV HVDC Leyte-Luzon,Blocked/Deblocked at 2029H/2039H on normal power flow per RTD.WEATHER: FAIR | CVIS
3/28/2022 6:02:32 PM | VRCC-03/28/2022 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2009MW, PK=2044MW, RR=40MW, NetOpMargin: EVE=-75 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 372 MW, LGPP 1 = 80 MW, TPC = 82 MW, PGPP 1 = 54 MW, TVI = 169 MW, Luzon grid max. of 250MW to augment Visayas generation. [WEBSMS] | CVIS
3/28/2022 6:02:31 PM | VRCC-03/28/2022 17:54: Projected 60mw MLD in Negros & Panay area this evening peak due to overloading of Negros-Samboan L2 caused by non-availability of PCPC & PGPP u#1. [WEBSMS] | CVIS
3/28/2022 6:02:28 PM | LRCC-03/28/2022 17:59: Tayabas-Naga 230kV Line 2 restored at 1754H (Planned Outage). [WEBSMS] | CLUZ
3/28/2022 5:29:34 PM | LRCC-03/28/2022 17:16: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12678MW, PK=10327MW, RR=419MW, NetOpMargin: EVE=1932 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW, Sual 2 @570MW, SLTEC 1 @91MW & Ilijan @817MW [WEBSMS] | CLUZ
3/28/2022 4:05:02 PM | VRCC-03/28/2022 15:55: Toledo SS new 37.5MVA TR#1 energized for soaking @1545H. [WEBSMS] | CVIS
3/28/2022 3:41:32 PM | VRCC-03/28/2022 15:32: CEDC unit# 3 cut-in to the system @1527H. [WEBSMS] | CVIS
3/28/2022 3:28:23 PM | MRCC-03/28/2022 15:19: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2823MW, PK=1890MW, RR=56MW, NetOpMargin: EVE=857 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@98MW, Ag7@26MW, Pul4@165MW, MGPP@75MW, STEAG@100MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/28/2022 2:54:37 PM | LEYTE ACC-03/28/22 14:35:CALBAYOG SS,69Kv PCB Palanas Cara closed at 1421H and DS Bobon closed at 1445H while Catarman to Bobolosan still isolated ,Weather: Cloudy | CVIS
3/28/2022 1:58:51 PM | LRCC-03/28/2022 13:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13160MW, PK=11235MW, RR=458MW, NetOpMargin: PM=1467, EVE=1937 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW, Sual 2 @570MW, SLTEC 1 @91MW & Ilijan @817MW [WEBSMS] | CLUZ
3/28/2022 1:01:53 PM | VRCC-03/28/2022 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2142MW, PK=2128MW, RR=40MW, NetOpMargin: PM=-26, EVE=-157 Highest Unit O/L: TVI U @ 169 MW Derated Plant: EDC = 372 MW, LGPP 1 = 80 MW, TPC = 82 MW, PGPP 1 = 54 MW, TVI = 169 MW [WEBSMS] | CVIS
3/28/2022 12:48:31 PM | PANAY ACC-03/28/22 12:40: ILOILO 1 S/S SS, PEDC Unit #1, TIME IN: 12:35:00 | CVIS
3/28/2022 12:48:30 PM | PANAY ACC-03/28/22 10:50: ILOILO 1 S/S SS, 138kV Iloilo-PEDC L1, TIME IN: 10:40:00 | CVIS
3/28/2022 11:32:53 AM | MRCC-03/28/2022 11:22: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2898MW, PK=2010MW, RR=59MW, NetOpMargin: PM=808, EVE=857 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@98MW, Ag7@26MW, Pul4@165MW, MGPP@75MW, STEAG@100MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/28/2022 11:22:43 AM | MRCC-03/28/2022 11:15: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2898MW, PK=2010MW, RR=59MW, NetOpMargin: PM=808, EVE=857 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@40MW, Ag6@98MW, Ag7@26MW, Pul4@165MW, MGPP@75MW, STEAG@100MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@68MW. [WEBSMS] | CMIN
3/28/2022 7:29:56 AM | NEGROS ACC: 03/28/2022, 69kV Silay-VMC line section de-energized at 0632H to conduct pole and insulator replacement. HPCo isolated | CVIS
3/28/2022 6:14:48 AM | VRCC-03/28/2022 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2132MW, PK=2095MW, RR=40MW, NetOpMargin: AM=37, PM=-66, EVE=-198 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 355MW, TPC at 82MW, TVI at 169MW, PGPP1 at 54MW, PEDC at 234MW, LGPP at 80MW [WEBSMS] | CVIS
3/28/2022 6:14:45 AM | LRCC-03/28/2022 06:11: Tayabas-Naga 230kV Line 2 de-energized at 0609H (Planned Outage) [WEBSMS] | CLUZ
3/28/2022 5:52:38 AM | LRCC-03/28/2022 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13146MW, PK=10887MW, RR=442MW, NetOpMargin: AM=1817, PM=1490, EVE=2020 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, SLTEC 1 at 91MW, Ilijan at 817MW and Sual 2 at 625MW [WEBSMS] | CLUZ
3/28/2022 5:11:15 AM | LRCC-03/28/2022 05:09: Weather Update: March 28, 2022, at 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 20 km Northeast of Zamboanga City, Zamboanga del Sur (7.0N, 122.2E). It is embedded along the Intertropical Convergence Zone (ITCZ) affecting Southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/28/2022 4:11:17 AM | MRCC-03/28/2022 04:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2835MW, PK=1915MW, RR=77MW, NetOpMargin: AM=843, PM=753, EVE=802 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@78MW, Ag6@54MW, Ag7@26MW, Pul4@115MW, MGPP@75MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@100MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/27/2022 11:29:16 PM | LEYTE ACC-03/27/22 23:34: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2309H/2319H on normal power flow per RTD. Weather: Cloudy. | CVIS
3/27/2022 9:45:36 PM | VRCC-03/27/2022 21:38: 138 KV Colon-Quiot line energized at 2115H, Quiot 100 MVA TR 2 energized at 2118H (transformer soaking). [WEBSMS] | CVIS
3/27/2022 8:47:57 PM | LRCC-03/27/2022 20:26: Nagsaag 230kV Bus 1 energized at 2025H. (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 7:00:32 PM | LRCC-03/27/2022 18:44: Nagsaag 230kV Bus 1 de-energized at 1843H. (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 6:41:50 PM | LRCC-03/27/2022 18:37: Hermosa-Mexico 230kV line 1 restored at 1836H. (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 6:41:48 PM | LRCC-03/27/2022 18:15: Sta. Rita 230kV Busbar 1 restored at 1807H (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 6:02:17 PM | VRCC-03/27/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1836MW, PK=1831MW, RR=40MW, NetOpMargin: EVE=-35 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC = 368 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, TVI = 169 MW, PGPP 1 = 54 MW Luzon to augment Visayas reserve [WEBSMS] | CVIS
3/27/2022 6:02:14 PM | LRCC-03/27/2022 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12170MW, PK=9591MW, RR=380MW, NetOpMargin: EVE=2199 Highest Unit O/L: GNPD1 @668MW Derated Plant: SLTEC 1 @91MW, SLPGC 2 @75MW, GMEC 2 @ 300MW, & Ilijan @817MW [WEBSMS] | CLUZ
3/27/2022 5:28:06 PM | NEGROS ACC: 03/27/2022, 69KV Mabinay-Bayawan Sub T/L energized at 1719H after PMS. | CVIS
3/27/2022 4:53:43 PM | LRCC-03/27/2022 16:30: Naga-Daraga 230kV Line restored at 1629H (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 3:52:00 PM | LRCC-03/27/2022 15:49: La Trinidad-Bauang 230kV Line 2 restored at 1549H (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 3:28:08 PM | LRCC-03/27/2022 15:10: For info: Commissioning of Balsik New 1000MVA Transformer No. 1 completed at 1508H. [WEBSMS] | CLUZ
3/27/2022 3:07:10 PM | LRCC-03/27/2022 15:01: San Jose-Taytay 230kV Line 2 restored at 1501H (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 1:02:08 PM | VRCC-03/27/2022 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2126MW, PK=1641MW, RR=40MW, NetOpMargin: PM=445, EVE=-35 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 368 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, TVI = 169 MW, PGPP 1 = 54 MW [WEBSMS] | CVIS
3/27/2022 1:01:58 PM | LRCC-03/27/2022 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12537MW, PK=9199MW, RR=373MW, NetOpMargin: PM=2965, EVE=1888 Highest Unit O/L: GNPD1 @668MW Derated Plant: SLTEC 1 @91MW,, SLPGC 2 @65MW, GMEC 2 @ 300MW, & Ilijan @817MW [WEBSMS] | CLUZ
3/27/2022 12:28:29 PM | NEGROS ACC: 03/27/2022, 138kV Kabankalan-Bacolod Line 1 energized at 1214H | CVIS
3/27/2022 11:27:41 AM | MRCC-03/27/2022 11:19: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2825MW, PK=1590MW, RR=64MW, NetOpMargin: PM=1171, EVE=1042 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@158MW, Ag5@219MW, Ag6@54MW, Ag7@26MW, Pul4@114MW, MGPP@75MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@100MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/27/2022 9:59:52 AM | LRCC-03/27/2022 09:57: Tayabas-Mauban 230kV Line 2 restored at 0956H (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 8:44:08 AM | NEGROS ACC: 03/27/2022, 138kV Kabankalan-Bacolod Line 1 de-energized at 0808H to conduct HVE replacement and correction of defects along the line | CVIS
3/27/2022 7:45:48 AM | LRCC-03/27/2022 07:44: Tayabas-Mauban 230kV Line 2 de-energized at 0744H (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 7:44:48 AM | LRCC-03/27/2022 07:09: La Trinidad-Bauang 230kV Line 2 de-energized at 0708H (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 7:44:46 AM | LRCC-03/27/2022 07:06: San Jose-Taytay 230kV Line 2 de-energized at 0705H (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 6:54:45 AM | NEGROS ACC: 03/27/2022, 69kV Mabinay-Bayawan Sub T/L (5.6MW) de-energized at 0606H to conduct woodpole replacement and correction of defects along the line | CVIS
3/27/2022 6:54:44 AM | NEGROS ACC: 03/27/2022, 69kV Mabinay-Bayawan Sub T/L (5.6MW) de-energized at 0606H to conduct woodpole replacement and correction of defects along the line | CVIS
3/27/2022 6:54:41 AM | LRCC-03/27/2022 06:39: Naga-Daraga 230kV Line de-energized at 0638H (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 6:54:39 AM | LRCC-03/27/2022 06:38: Sta. Rita 230kV Busbar 1 de-energized at 0635H (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 6:11:48 AM | VRCC-03/27/2022 06:02: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2187MW, PK=1636MW, RR=61.4MW, NetOpMargin: AM=490, PM=487, EVE=33 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 372 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, TVI = 169 MW [WEBSMS] | CVIS
3/27/2022 6:11:46 AM | LRCC-03/27/2022 06:11: Hermosa-Mexico 230kV Line 1 de-energized at 0609H (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 6:11:43 AM | LRCC-03/27/2022 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12202MW, PK=9146MW, RR=359MW, NetOpMargin: AM=2697, PM=2354, EVE=1309 Highest Unit O/L: Sual 1 and 2 at 647MW Derated Plant: GMEC 2 at 300MW, SLTEC 1 at 91MW and SLPGC 2 at 45MW [WEBSMS] | CLUZ
3/27/2022 6:11:41 AM | LRCC-03/27/2022 05:46: GNPD Unit 1 online at 0545H. (Unplanned Outage) [WEBSMS] | CLUZ
3/27/2022 5:44:04 AM | VRCC-03/27/2022 05:26: 138KV QUIOT 100MVA TR#2 manually open @0520H, Pre-arranged maintenance activity. [WEBSMS] | CVIS
3/27/2022 5:15:21 AM | PANAY ACC-03/27/22 04:58: ILOILO 1 S/S SS, Iloilo - Baldoza 69 kV Line (CO) (5LI1ILO-BDO)(24.9MW), TIME IN: 04:55:00, RELAY: 50/51, 86Lock Out, WEATHER: FAIR. Line Fault along MORE City Proper 69kV Feeder. | CVIS
3/27/2022 5:15:20 AM | PANAY ACC-03/27/22 04:46: ILOILO 1 S/S SS, Iloilo - Baldoza 69 kV Line (CO) (5LI1ILO-BDO)(24.9MW), TIME OUT: 04:42:00, RELAY: 50/51, 86Lock Out, WEATHER: FAIR. Auto-tripped when MORE energized their 69kV City Proper Feeder. | CVIS
3/27/2022 5:15:18 AM | LRCC-03/27/2022 05:01: Weather Update: March 27, 2022, at 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 200 km East of Davao City (7.0N, 127.6E). It is embedded along the Intertropical Convergence Zone (ITCZ) affecting Southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/27/2022 5:15:15 AM | LRCC-03/27/2022 04:54: San Jose PCB 9-01CB04SJO energized at 0451H. (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 4:28:48 AM | MRCC-03/27/2022 04:10: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2823MW, PK=1520MW, RR=50MW, NetOpMargin: AM=1242, PM=1171, EVE=1041 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@150MW, Ag5@40MW, Ag6@78MW, Ag7@26MW, Pul4@114MW, MGPP@75MW, STEAG@100MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@100MW. [WEBSMS] | CMIN
3/27/2022 4:18:31 AM | VRCC-03/27/2022 03:57: KSPC u#2 cut-in to the system @0353H. [WEBSMS] | CVIS
3/27/2022 4:18:29 AM | LRCC-03/27/2022 03:56: Batangas 230 kV Bus 2 was restored at 0351H. (Planned Outage) [WEBSMS] | CLUZ
3/27/2022 1:58:43 AM | LRCC-03/27/2022 01:49: SLPGC Unit 2 online at 0145H. (Unplanned Outage) [WEBSMS] | CLUZ
3/27/2022 12:28:16 AM | PANACC: 03/27/2022: PCPC Unit OUT:0012H; FORCED OUTAGE; | CVIS
3/26/2022 11:41:17 PM | LRCC-03/26/2022 23:12: San Jose PCB 9-01CB04SJO open at 2308H. (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 11:41:16 PM | LRCC-03/26/2022 23:12: San Jose PCB 9-01CB04SJO open at 2308H. (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 11:02:23 PM | LRCC-03/26/2022 23:00: System Advisory: Luzon Grid ``YELLOW ALERT`` notice issued today, March 26, 2022 is lifted effective 2300H due to sufficient operating reserve. [WEBSMS] | CLUZ
3/26/2022 10:19:54 PM | LRCC-03/26/2022 22:10: Batangas 230kV Bus 2 was de-energized at 2208H. (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 10:19:52 PM | LRCC-03/26/2022 21:58: System Advisory: March 26, 2022: Luzon Grid issued ``YELLOW ALERT`` is extended until 2300H. Generators on forced outage are: GNPD 1 (668MW), SLTEC 2 (123MW), SLPGC 2,3&4 (200MW), Kalayaan (720MW -unavailable to low water elevation) and Calaca 2 (300MW) (Total = 2011MW). While de-rated Plants: Sual 1 @220MW (600MW), Sual 2 @570MW (600MW), SLTEC 1 @91MW(121MW), & Ilijan A/B @817MW each block (1200MW) (Total deration= 823MW). [WEBSMS] | CLUZ
3/26/2022 10:19:51 PM | LRCC-03/26/2022 21:36: Malaya-Lumban 230kV line 2 was restored at 2134H. (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 10:19:49 PM | LRCC-03/26/2022 21:33: For information, observance of the Earth Hour 2022 ended at 2130H. [WEBSMS] | CLUZ
3/26/2022 8:53:37 PM | LRCC-03/26/2022 20:31: For information, observance of the Earth Hour 2022 started at 2030H. [WEBSMS] | CLUZ
3/26/2022 8:12:05 PM | VRCC-03/26/2022 20:05: Visayas Grid on Yellow Alert lifted 2000H with reserve meets system reserve requirement. [WEBSMS] | CVIS
3/26/2022 8:00:46 PM | LEYTE ACC-03/26/22 19:10: PARANAS SS, Sta. Rita - Quinapondan 69kV Line and 69kV Taft Feeder re-energized at 1844H & 1856H respectively, affected by pre-arranged activity. Weather: Cloudy. | CVIS
3/26/2022 8:00:44 PM | LEYTE ACC-03/26/22 19:03: PARANASC SS, Paranas 30MVA 138/69kV TR No. 1 re-energized at 1831H, pre-arranged activity completed. Weather: Cloudy. | CVIS
3/26/2022 8:00:42 PM | LRCC-03/26/2022 19:19: Dasmarinas-Rosario 115kV line restored at 1917H. (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 8:00:40 PM | LRCC-03/26/2022 18:51: San Manuel-San Manuel BESS 69kV line restored at 1846H. (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 6:49:11 PM | VRCC-03/26/2022 18:20: Visayas Grid on Yellow Alert starting 1818H with reserve below system reserve requirement. [WEBSMS] | CVIS
3/26/2022 6:49:08 PM | LRCC-03/26/2022 18:42: Lumban-Malaya 230kV Line 2 de-energized at 1740H. (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 6:49:06 PM | LRCC-03/26/2022 18:33: Labrador 230kV Bus 1 energized at 1832H. (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 6:49:05 PM | LRCC-03/26/2022 18:31: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=10487MW, PK=9998MW, RR=389MW, NetOpMargin: EVE=100 Highest Unit O/L: Sual 2@570MW Derated Plant: SLTEC 1 @91MW, Sual 1/2 @220MW/570MW & Ilijan @817MW [WEBSMS] | CLUZ
3/26/2022 6:19:28 PM | VRCC-03/26/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: YELLOW ALERT CAP=1886MW, PK=1897MW, RR=40MW, NetOpMargin: EVE=-51 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 402 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, TVI = 169 MW, PGPP 1 =75MW, Luzon to augment Visayas [WEBSMS] | CVIS
3/26/2022 6:19:25 PM | LRCC-03/26/2022 18:17: System Advisory: March 26, 2022: Luzon Grid is on ``YELLOW ALERT`` for intervals 1900H to 2200H. Generators on force outage are: GNPD 1 (668MW), SLTEC 2 (123MW), SLPGC 2,3&4 (200MW), Kalayaan (720MW -unavailable to low water elevation) and Calaca 2 (300MW) (Total = 2011MW). While de-rated Plants: Sual 1 @220MW (600MW), Sual 2 @570MW (600MW), SLTEC 1 @91MW(121MW), & Ilijan A/B @817MW each block (1200MW) (Total deration= 823MW). [WEBSMS] | CLUZ
3/26/2022 5:27:28 PM | LRCC-03/26/2022 17:02: Hermosa-Mexico 230kV Line 2 restored at 1701H (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 5:27:27 PM | LRCC-03/26/2022 16:39: Cabanatuan-Pantabangan 230kV Line restored at 1637H (Unplanned Outage) [WEBSMS] | CLUZ
3/26/2022 5:27:26 PM | LRCC-03/26/2022 16:34: Cabanatuan-Pantabangan 230kV Line tripped at 1629H (Unplanned Outage) [WEBSMS] | CLUZ
3/26/2022 5:27:25 PM | LRCC-03/26/2022 16:23: San Juan 230kV Bus 1 restored at 1615H (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 4:20:59 PM | NEGROS ACC: 03/26/2022, 34.5KV Amlan-AHEP Line energized at 1556H after PMS. | CVIS
3/26/2022 3:46:17 PM | LRCC-03/26/2022 15:36: GNPD 1 @53MW tripped at 1519H. Lowest Frequency is 59.64Hz (Unplanned Outage) [WEBSMS] | CLUZ
3/26/2022 3:18:25 PM | LRCC-03/26/2022 15:09: GNPD 1 online at 1501H (Unplanned Outage) [WEBSMS] | CLUZ
3/26/2022 3:07:44 PM | LEYTE ACC-03/26/22 15:05: KANANGA CSS, EDC-Mahanagdong unit #3 cut-in to the system at 1440H, back to normal operation. Weather: Fair. | CVIS
3/26/2022 2:11:12 PM | LRCC-03/26/2022 13:46: Binga-Ambuklao 230kV Line 2 restored at 1345H (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 1:17:25 PM | LRCC-03/26/2022 13:16: Balsik New 1000MVA Transformer No. 1 energized at secondary side (230kV) at 1309H. On-going commissioning test. [WEBSMS] | CLUZ
3/26/2022 1:07:24 PM | VRCC-03/26/2022 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2207MW, PK=1854MW, RR=40MW, NetOpMargin: PM=313, EVE=-20 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 369 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, TVI = 169 MW, PGPP 1 =75MW, CEDC = 164MW [WEBSMS] | CVIS
3/26/2022 12:51:17 PM | MRCC-03/26/2022 12:13: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2888MW, PK=1800MW, RR=59MW, NetOpMargin: PM=1016, EVE=985 Highest Unit O/L: GNPK U2 & U4 @138MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@35MW, Ag6@78MW, Ag7@26MW, Pul4@154MW, MGPP@75MW, STEAG@100MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@100MW. [WEBSMS] | CMIN
3/26/2022 12:51:07 PM | LRCC-03/26/2022 12:25: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11589MW, PK=10269MW, RR=407MW, NetOpMargin: PM=913, EVE=862 Highest Unit O/L: Sual 2@600MW Derated Plant: SLTEC 1 @91MW, Sual 1 @225MW & Ilijan @817MW [WEBSMS] | CLUZ
3/26/2022 9:45:54 AM | VRCC-03/26/2022 09:36: 69kV Veco Pardo North Feeder load transferred to other Veco feeders starting 0900H. [WEBSMS] | CVIS
3/26/2022 9:11:06 AM | VRCC-03/26/2022 08:55: 69kV Veco Pardo North Feeder Quiot Ss tripped at 0847H with 52MW load. Customer owned. [WEBSMS] | CVIS
3/26/2022 9:11:04 AM | LRCC-03/26/2022 08:43: San Juan 230kV Bus 1 de-energized at 0840H (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 7:56:00 AM | LRCC-03/26/2022 07:53: Labrador 230kV Bus 1 de-energized at 0752H (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 7:55:58 AM | LRCC-03/26/2022 07:37: Binga-Ambuklao 230kV Line 2 de-energized at 0735H (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 7:55:56 AM | LRCC-03/26/2022 07:26: Dasmarinas-Rosario 115kV Line de-energized at 0722H (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 7:19:25 AM | LRCC-03/26/2022 07:10: SLPGC 2 @141MW tripped at 0706H. Lowest Frequency is 59.54Hz (Unplanned Outage) [WEBSMS] | CLUZ
3/26/2022 7:09:24 AM | VRCC-03/26/2022 06:37: 138KV Compostela 100MVA TR#3 manually open @0637H, APMS. [WEBSMS] | CVIS
3/26/2022 7:09:21 AM | LRCC-03/26/2022 06:50: Daraga-Tiwi A 230kV Line de-energized at 0649H (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 6:35:03 AM | MRCC-03/26/2022 05:28: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2881MW, PK=1730MW, RR=69MW, NetOpMargin: AM=1082, PM=1016, EVE=984 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@80MW, Ag4@156MW, Ag5@35MW, Ag6@78MW, Ag7@26MW, Pul4@154MW, MGPP@75MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@100MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/26/2022 6:34:53 AM | NEGROS ACC: 03/26/2022, 34.5kV Amlan-AHEP Line(0.67MW) de-energized at 0615H due to PMS. AHEP plant isolated. | CVIS
3/26/2022 6:34:52 AM | VRCC-03/26/2022 05:55: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2204MW, PK=1825MW, RR=40MW, NetOpMargin: AM=339, PM=313, EVE=20 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 369 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, TVI = 169 MW, PGPP 1 =75MW [WEBSMS] | CVIS
3/26/2022 6:34:51 AM | VRCC-03/26/2022 05:50: 138KV Cebu Bus 2 manually open @0537H, corrective maintenance. [WEBSMS] | CVIS
3/26/2022 6:34:48 AM | LRCC-03/26/2022 06:23: Hermosa-Mexico 230kV Line 2 de-energized at 0622H (Planned Outage) [WEBSMS] | CLUZ
3/26/2022 6:34:46 AM | LRCC-03/26/2022 06:09: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12012MW, PK=9742MW, RR=390MW, NetOpMargin: AM=1880, PM=1389, EVE=1200 Highest Unit O/L: Sual 2 at 600MW Derated Plant: GMEC 2 at 300MW, SLTEC 1 at 91MW, Sual 1 at 250MW [WEBSMS] | CLUZ
3/26/2022 5:41:05 AM | LRCC-03/26/2022 05:22: Weather Update: Issued at 0400H, Intertropical Convergence Zone (ITCZ) affecting Southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/26/2022 5:20:28 AM | LRCC-03/26/2022 05:17: Batangas 230kV Bus A restored at 0516H (Planned Outage). [WEBSMS] | CLUZ
3/26/2022 5:17:04 AM | VRCC-03/26/2022 05:15: 138KV Colon-Quiot manually open @0506H, P&A activity. [WEBSMS] | CVIS
3/25/2022 11:59:26 PM | LRCC-03/25/2022 23:55: Sta. Rita 30 shutdown at 2342H (Planned Outage). [WEBSMS] | CLUZ
3/25/2022 11:12:30 PM | VRCC-03/25/2022 23:04: 230KV New Magdugo 300MVA energized @2258H for soaking. [WEBSMS] | CVIS
3/25/2022 10:24:45 PM | LRCC-03/25/2022 22:18: Batangas 230kV Bus A de-energized at 2218H (Planned Outage). [WEBSMS] | CLUZ
3/25/2022 10:14:37 PM | LEYTE ACC-03/25/22 22:21: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2158H/2208H on normal power flow per RTD. Weather: Fair. | CVIS
3/25/2022 9:40:34 PM | LRCC-03/25/2022 21:38: GNPD 1 (100MW) tripped at 2133H (Unplanned Outage). [WEBSMS] | CLUZ
3/25/2022 7:43:10 PM | VRCC-03/25/2022 19:42: Magdugo SS 230 KV Bus 1 energized at 1937H, [WEBSMS] | CVIS
3/25/2022 7:32:37 PM | LRCC-03/25/2022 19:09: Nagsaag-Casecnan 230kV line 1 restored at 1907H. (Planned Outage) [WEBSMS] | CLUZ
3/25/2022 6:29:39 PM | LRCC-03/25/2022 18:03: Naga-Tayabas 230kV line 2 restored at 1756H. (Planned Outage) [WEBSMS] | CLUZ
3/25/2022 6:01:55 PM | VRCC-03/25/2022 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1955MW, PK=1880MW, RR=40MW, NetOpMargin: EVE=35 Highest Unit O/L: TVI U1 at 169 MW Derated Plant: EDC at 407, PEDC at 234, TVI at 169, CEDC at 164, KSPC at 103, TPC at 82, LGPP at 80, PGPP1 at 75 MW Luzon to augment Visayas reserve [WEBSMS] | CVIS
3/25/2022 5:38:25 PM | LRCC-03/25/2022 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12619MW, PK=10261MW, RR=428MW, NetOpMargin: EVE=1930 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, SLTEC 1 at 91MW and Sual 1 at 250MW [WEBSMS] | CLUZ
3/25/2022 4:38:19 PM | MRCC-03/25/2022 16:25: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2909MW, PK=1890MW, RR=76MW, NetOpMargin: EVE=943 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@156MW, Ag5@40MW, Ag6@78MW, Ag7@21MW, Pul4@130MW, MGPP@75MW, STEAG@100.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@100MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/25/2022 12:51:31 PM | LRCC-03/25/2022 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13022MW, PK=11499MW, RR=463MW, NetOpMargin: PM=1060, EVE=1230 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, SLTEC 1 at 91MW, Sual 1 at 250MW [WEBSMS] | CLUZ
3/25/2022 12:31:16 PM | MRCC-03/25/2022 11:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2809MW, PK=1890MW, RR=76MW, NetOpMargin: PM=696, EVE=843 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@30MW, Ag2@110MW, Ag4@156MW, Ag5@40MW, Ag6@78MW, Ag7@21MW, Pul4@130MW, MGPP@75MW, STEAG@0.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@100MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/25/2022 10:54:18 AM | LRCC-03/25/2022 10:46: For info: San Lorenzo Module 60 completed fuel changeover from gas to oil at 1031H. [WEBSMS] | CLUZ
3/25/2022 10:02:14 AM | LRCC-03/25/2022 09:56: For info: Sta Rita Module 40 completed fuel changeover from gas to oil at 0943H. (Planned Outage) [WEBSMS] | CLUZ
3/25/2022 7:54:52 AM | MRCC-03/25/2022 04:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2809MW, PK=1915MW, RR=58MW, NetOpMargin: AM=817, PM=725, EVE=779 Highest Unit O/L: GNPK U2 & U4 @ 138MW each. Derated Plant: Ag1@55MW, Ag2@110MW, Ag4@156MW, Ag5@35MW, Ag6@78MW, Ag7@26MW, Pul4@154MW, MGPP@75MW, STEAG@0.0MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@100MW. [WEBSMS] | CMIN
3/25/2022 6:53:29 AM | LRCC-03/25/2022 06:16: Nagsaag-Casecnan 230kV line 1 de-energized at 0616H. (Planned Outage) [WEBSMS] | CLUZ
3/25/2022 6:11:37 AM | LRCC-03/25/2022 06:11: Naga-Tayabas 230kV line 2 de-energized at 0610H. (Planned Outage) [WEBSMS] | CLUZ
3/25/2022 6:10:38 AM | VRCC-03/25/2022 06:06: Magdugo SS 230 KV Bus 1 de-energized at 0604H, P&E activity [WEBSMS] | CVIS
3/25/2022 6:10:37 AM | VRCC-03/25/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2242MW, PK=1928MW, RR=40MW, NetOpMargin: AM=274, PM=245, EVE=35 Highest Unit O/L: TVI U1 at 169 MW, Derated Plant: EDC at 407, PEDC at 234, TVI at 169, CEDC at 164, KSPC at 103, TPC at 82, LGPP at 80, PGPP1 at 75 MW [WEBSMS] | CVIS
3/25/2022 6:10:35 AM | LRCC-03/25/2022 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13167MW, PK=11064MW, RR=443MW, NetOpMargin: AM=1660, PM=1149, EVE=1713 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @91MW, GMEC 2 @300MW, & Ilijan @851MW [WEBSMS] | CLUZ
3/25/2022 6:10:33 AM | LRCC-03/25/2022 05:38: Weather Update: Intertropical Convergence Zone (ITCZ) affecting Southern Mindanao. Easterlies affecting the rest of the country. [WEBSMS] | CLUZ
3/25/2022 4:23:00 AM | LRCC-03/25/2022 04:20: Binan-Balibago 115kV line restored at 0418H. (Planned Outage) [WEBSMS] | CLUZ
3/25/2022 12:38:13 AM | LRCC-03/25/2022 00:35: For info: Sta Rita Module 10 completed fuel changeover from oil to natural gas at 0022H. [WEBSMS] | CLUZ
3/24/2022 11:43:46 PM | LRCC-03/24/2022 23:35: Binan-Balibago 115kV line de-energized at 2334H (Planned Outage) [WEBSMS] | CLUZ
3/24/2022 11:23:19 PM | VRCC-03/24/2022 22:48: CEDC U3 emergency cut-out at 2245H, possible tube leak [WEBSMS] | CVIS
3/24/2022 10:42:01 PM | LRCC-03/24/2022 22:33: San Juan-Lumban 230kV line 1 restored at 2226H. (Unplanned Outage) [WEBSMS] | CLUZ
3/24/2022 10:42:00 PM | LRCC-03/24/2022 22:32: San Juan-Lumban 230kV line 1 restored at 2026H. (Unplanned Outage) [WEBSMS] | CLUZ
3/24/2022 9:11:33 PM | LEYTE ACC-03/24/22: EDC-Leyte A, Mahanagdong Unit #3 cut-in at 2048H | CVIS
3/24/2022 9:11:32 PM | LEYTE ACC-03/24/22: EDC-Leyte A, Mahanagdong Unit #3 cut-in at 2048H | CVIS
3/24/2022 6:52:46 PM | LEYTE ACC-03/24/22: EDC-Leyte A, Mahanagdong Unit #1 cut-in at 1837H | CVIS
3/24/2022 6:52:45 PM | LEYTE ACC-03/24/22: EDC-Leyte A, Mahanagdong Unit #1 cut-in at 1837H | CVIS
3/24/2022 6:52:43 PM | LEYTE ACC-03/24/22: MAASIN SS, 69kV Maasin-Baybay Line back to normal configuration at 1803H per PANR LEY-2022-03-0007, WEATHER: FAIR | CVIS
3/24/2022 6:52:42 PM | LEYTE ACC-03/24/22: MAASIN SS, 69kV Maasin-Baybay Line back to normal configuration at 1803H per PANR LEY-2022-03-0007, WEATHER: FAIR | CVIS
3/24/2022 6:52:41 PM | VRCC-03/24/2022 18:05: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2091MW, PK=1870MW, RR=40MW, NetOpMargin: EVE=181 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, TVI = 169 MW, PGPP 1 =72MW [WEBSMS] | CVIS
3/24/2022 6:52:38 PM | LRCC-03/24/2022 18:16: Tayabas-Naga 230kV line 2 restored at 1815H. (Planned Outage) [WEBSMS] | CLUZ
3/24/2022 6:02:31 PM | LEYTE ACC-03/24/22: MAASIN SS, 69kV Maasin-Nasaug-Sogod-St.Bernard opened/closed per per PANR VRCC-2022-03-0034 at 1742H/1747H, WEATHER: FAIR | CVIS
3/24/2022 6:02:29 PM | LEYTE ACC-03/24/22: MAASIN SS, 69kV Maasin-Nasaug-Sogod-St.Bernard opened/closed per per PANR VRCC-2022-03-0034 at 1742H/1747H, WEATHER: FAIR | CVIS
3/24/2022 6:02:28 PM | LEYTE ACC-03/24/22: MAASIN SS, 138/69kV 50MVA TR2 Maasin SS re-energized per PANR VRCC-2022-03-0034, TIME IN: 17:38:00, WEATHER: FAIR | CVIS
3/24/2022 6:02:26 PM | LEYTE ACC-03/24/22: MAASIN SS, 138/69kV 50MVA TR2 Maasin SS re-energized per PANR VRCC-2022-03-0034, TIME IN: 17:38:00, WEATHER: FAIR | CVIS
3/24/2022 6:01:59 PM | LRCC-03/24/2022 17:59: San Juan-Lumban 230kV line 1 de-energized at 1757H. (Unplanned Outage) [WEBSMS] | CLUZ
3/24/2022 6:01:57 PM | LRCC-03/24/2022 17:48: Concepcion 230kV Bus 2 energized at 1747H. (Planned Outage) [WEBSMS] | CLUZ
3/24/2022 6:01:55 PM | LRCC-03/24/2022 17:35: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12918MW, PK=10662MW, RR=421MW, NetOpMargin: EVE=1835 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW and SLTEC 1 at 91MW [WEBSMS] | CLUZ
3/24/2022 4:04:53 PM | LEYTE ACC-03/24/22: EDC-Leyte A, Mahanagdong Unit #3 tripped at 1536H, scrubber high level indication. | CVIS
3/24/2022 4:04:52 PM | LEYTE ACC-03/24/22: EDC-Leyte A, Mahanagdong Unit #3 tripped at 1536H, scrubber high level indication. | CVIS
3/24/2022 4:04:50 PM | LEYTE ACC-03/24/22: EDC-Leyte A, Mahanagdong Unit #3 tripped at 1536H, scrubber high level indication. | CVIS
3/24/2022 3:40:46 PM | LRCC-03/24/2022 15:18: Dasmarinas-Ternate 115kV line energized at 1518H. (Planned Outage) [WEBSMS] | CLUZ
3/24/2022 2:49:28 PM | VRCC-03/24/2022 14:43: 138KV Colon-Kepco line 2 energized @1430H. [WEBSMS] | CVIS
3/24/2022 2:02:24 PM | LRCC-03/24/2022 13:57: Sual 1 online at 1354H. (Unplanned Outage) [WEBSMS] | CLUZ
3/24/2022 1:15:26 PM | LRCC-03/24/2022 13:12: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12741MW, PK=11563MW, RR=458MW, NetOpMargin: PM=720, EVE=1189 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW and SLTEC 1 at 91MW [WEBSMS] | CLUZ
3/24/2022 1:02:11 PM | VRCC-03/24/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2328MW, PK=1930MW, RR=40MW, NetOpMargin: PM=358, EVE=181 Highest Unit O/L: TVI U @ 169 MW Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, TVI = 169 MW, PGPP 1=72MW [WEBSMS] | CVIS
3/24/2022 11:47:55 AM | MRCC-03/24/2022 11:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2793MW, PK=2020MW, RR=59MW, NetOpMargin: PM=692, EVE=770 Highest Unit O/L: GNPK U2 & U4 @ 138MW each. Derated Plant: Ag1@55MW, Ag2@110MW, Ag4@156MW, Ag5@42MW, Ag6@63MW, Ag7@26MW, Pul4@147MW, MGPP@75MW, STEAG@0.0MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@100MW. [WEBSMS] | CMIN
3/24/2022 11:30:39 AM | LRCC-03/24/2022 11:28: Sual Unit 1 tripped at 1123H from 321MW load. The lowest frequency dip is 59.151Hz. No ALD actuated. [WEBSMS] | CLUZ
3/24/2022 9:51:34 AM | LRCC-03/24/2022 09:42: For info: Sta Rita Module 10 completed fuel changeover from gas to oil at 0929H. [WEBSMS] | CLUZ
3/24/2022 9:51:32 AM | LRCC-03/24/2022 09:26: Dasmarinas-Ternate 115kV line de-energized at 0925H. (Planned Outage) (CO) [WEBSMS] | CLUZ
3/24/2022 9:19:46 AM | LRCC-03/24/2022 09:11: Ilijan GT1-1 online at 0858H. (Unplanned Outage) [WEBSMS] | CLUZ
3/24/2022 9:06:09 AM | LEYTE ACC-03/23/22: EDC-Leyte A, Maha A Unit #1 cut-out at 0843H for emergency shutdown to repair damaged turbine communicator rack (8hrs sched) | CVIS
3/24/2022 9:06:07 AM | LEYTE ACC-03/23/22: EDC-Leyte A, Maha A Unit #1 cut-out at 0843H for emergency shutdown to repair damaged turbine communicator rack (8hrs sched) | CVIS
3/24/2022 8:45:16 AM | LEYTE ACC-03/24/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 0814H/0824H, on reverse flow per RTD | CVIS
3/24/2022 8:45:14 AM | LEYTE ACC-03/24/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 0814H/0824H, on reverse flow per RTD | CVIS
3/24/2022 8:45:13 AM | LEYTE ACC-03/24/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 0814H/0824H, on reverse flow per RTD | CVIS
3/24/2022 8:45:07 AM | LRCC-03/24/2022 08:21: Binga-Binga HEPP 230kV overhead line 2 was de-energized at 0815H. (Planned Outage) [WEBSMS] | CLUZ
3/24/2022 7:08:15 AM | LRCC-03/24/2022 07:06: Concepcion 230kV Bus 2 de-energized at 0704H. (Planned Outage) [WEBSMS] | CLUZ
3/24/2022 6:54:49 AM | VRCC-03/24/2022 06:52: EAUC isolated from the grid at 0624H for switchyard PMS. Pre-arranged activity [WEBSMS] | CVIS
3/24/2022 6:07:49 AM | VRCC-03/24/2022 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2367MW, PK=1910MW, RR=36.4MW, NetOpMargin: AM=421, PM=362, EVE=185 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 402, PEDC at 234, KSPC at 103, TPC at 82, LGPP at 80, PGPP1 at 75 MW [WEBSMS] | CVIS
3/24/2022 5:44:39 AM | LRCC-03/24/2022 05:36: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13114MW, PK=11207MW, RR=436MW, NetOpMargin: AM=1471, PM=874, EVE=1462 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW and SLTEC 1 at 91MW [WEBSMS] | CLUZ
3/24/2022 5:02:57 AM | LRCC-03/24/2022 04:46: Weather Update; Issued at 0400H, Northeasterly surface windflow affecting Northern Luzon. [WEBSMS] | CLUZ
3/24/2022 5:02:55 AM | LRCC-03/24/2022 04:37: QPPL on line at 0411H (Unplanned Outage). [WEBSMS] | CLUZ
3/24/2022 4:30:57 AM | MRCC-03/24/2022 04:21: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2821MW, PK=1930MW, RR=77MW, NetOpMargin: AM=814, PM=726, EVE=810 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@100MW, Ag4@148MW, Ag5@35MW, Ag6@48MW, Ag7@21MW, Pul4@130MW, MGPP@75MW, STEAG@0.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@100MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/24/2022 12:49:07 AM | LRCC-03/24/2022 00:46: Sta. Rita 10 changeover from oil to gas at 0034H. [WEBSMS] | CLUZ
3/23/2022 10:01:36 PM | LRCC-03/23/2022 21:55: Malaya 2 shutdown at 2152H (Planned Outage). [WEBSMS] | CLUZ
3/23/2022 9:39:35 PM | LRCC-03/23/2022 21:38: San Jose-Angat 115kV L2 restored at 2137H (Unplanned Outage). [WEBSMS] | CLUZ
3/23/2022 8:05:05 PM | LRCC-03/23/2022 19:49: San Jose-Angat 115kV L2 and Angat Auxiliary Unit 5 & 6 tripped at 1936H (Unplanned Outage). [WEBSMS] | CLUZ
3/23/2022 7:06:17 PM | LEYTE ACC-03/23/22 18:40:ORMOC SS,Ormoc-Simangan-Baybay 69 kV L ,Deenergized/Energized at 1802H/1807H,while Maasin Baybay 69kV L back to normal at 1824H,load=38.9mw,per PANR no. TLOS V_2022-03-0006,WEATHER: FAIR | CVIS
3/23/2022 7:06:15 PM | LRCC-03/23/2022 18:33: Naga-Tayabas 230kV Line 2 restored at 1831H. (Planned Outage) [WEBSMS] | CLUZ
3/23/2022 7:06:13 PM | LRCC-03/23/2022 18:31: Ilijan A-1 shutdown at 1828H (Planned Outage). [WEBSMS] | CLUZ
3/23/2022 6:02:27 PM | VRCC-03/23/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2041MW, PK=1882MW, RR=40MW, NetOpMargin: EVE=119 Highest Unit O/L: PEDC U3 at 150 MW, Derated Plant: EDC at 402, PEDC at 234, TVI at 140, KSPC at 103, TPC at 82, LGPP at 80, PGPP1 at 75 MW, Luzon supplying Visayas Grid [WEBSMS] | CVIS
3/23/2022 5:49:00 PM | LRCC-03/23/2022 17:41: Concepcion 230kV Bus 1 energized at 1739H. (Planned Outage) [WEBSMS] | CLUZ
3/23/2022 5:35:19 PM | LRCC-03/23/2022 17:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12522MW, PK=10901MW, RR=405MW, NetOpMargin: EVE=1216 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW and SLTEC 1 at 91MW [WEBSMS] | CLUZ
3/23/2022 5:15:14 PM | LRCC-03/23/2022 17:00: Binga-Binga HEPP 230kV tie line 1 was energized at 1656H. (Planned Outage) [WEBSMS] | CLUZ
3/23/2022 4:59:55 PM | LRCC-03/23/2022 16:58: QPPL offline at 1653H. (Re-commissioning test) [WEBSMS] | CLUZ
3/23/2022 4:49:49 PM | LRCC-03/23/2022 16:47: Limay 230kV Bus 1 and Limay-BCCPP 230kV tie line 1 was restored at 1643h and 1645h respectively. (Planned Outage) [WEBSMS] | CLUZ
3/23/2022 4:49:47 PM | LRCC-03/23/2022 16:40: Ilijan GT1-2 online at 1635H. (Unplanned Outage) [WEBSMS] | CLUZ
3/23/2022 2:43:04 PM | PANAY ACC-03/23/22 14:31: ILOILO 1 S/S SS, MORE Feeder 1 Jaro Ss, TIME IN: 02:27:00 | CVIS
3/23/2022 2:43:03 PM | NEGROS ACC: 03/23/2022, PGPP2 SOG1 re-online at 1410H. | CVIS
3/23/2022 2:43:01 PM | PANAY ACC-03/23/22 13:28: ILOILO 1 S/S SS, MORE Feeder 1 Jaro Ss, TIME OUT: 13:27:00, Ld: 2MW; Conducted MLD to avoid overloading of Iloilo Ss 50MVA Xformer. | CVIS
3/23/2022 2:41:51 PM | LRCC-03/23/2022 14:36: System Advisory: ``THIS IS ONLY A DRILL``. Extension of power to BACC sub-grid started at 1434H ``THIS IS ONLY A DRILL``. [WEBSMS] | CLUZ
3/23/2022 2:41:49 PM | LRCC-03/23/2022 14:30: System Advisory: ``THIS IS ONLY A DRILL``. The Metro Manila-STACC-Avion Sub-grid were synchronized & looped with CLACC Sub-grid at 1422H & 1427H, respectively. ?THIS IS ONLY A DRILL? [WEBSMS] | CLUZ
3/23/2022 1:51:33 PM | PANAY ACC-03/23/22 12:51: PANIT-AN SS, Panit-an-Roxas 69KV (5LI1PNT-ROX), TIME IN: 12:50:00, RELAY: FD L3EC trip IETC, WEATHER: FAIR; Tripping was caused by a Cut jumper loop phase C str. 69 at Brgy. Arcabalo, Roxas City. | CVIS
3/23/2022 1:51:31 PM | VRCC-03/23/2022 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2318MW, PK=1955MW, RR=40MW, NetOpMargin: PM=323, EVE=148 Highest Unit O/L: TVI U1 at 169 MW, Derated Plant: EDC at 402 MW, PEDC at 234 MW, TVI at 169 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 75 MW [WEBSMS] | CVIS
3/23/2022 1:51:29 PM | LRCC-03/23/2022 13:48: System Advisory: ``THIS IS ONLY A DRILL``. The Metro Manila-STACC Sub-grid were synchronized & looped with Avion Sub-grid at 1342H & 1346H, respectively. ``THIS IS ONLY A DRILL``. [WEBSMS] | CLUZ
3/23/2022 1:51:27 PM | LRCC-03/23/2022 13:35: System Advisory: ``THIS IS ONLY A DRILL``. The Metro Manila Sub-grid and the STACC Sub-grid were synchronized/looped at 1330H/1333H.`` THIS IS ONLY A DRILL``. [WEBSMS] | CLUZ
3/23/2022 1:51:25 PM | LRCC-03/23/2022 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=13235MW, PK=11602MW, RR=413MW, NetOpMargin: PM=1184, EVE=1646 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, SLTEC 1 at 91MW and QPPL at 300MW [WEBSMS] | CLUZ
3/23/2022 1:51:22 PM | LRCC-03/23/2022 12:21: System Advisory: ``THIS IS ONLY A DRILL``. At around 1211H of March 23, 2022 ?SYSTEM BLACKOUT? occurred in the Luzon Grid. Please implement the Black Start recovery procedure in your area of responsibility effective immediately. No actual opening and closing of breakers. ?THIS IS ONLY A DRILL?. [WEBSMS] | CLUZ
3/23/2022 1:51:20 PM | LRCC-03/23/2022 12:20: For info: Ilijan ST1 online at 1202H. (Unplanned Outage) [WEBSMS] | CLUZ
3/23/2022 1:51:18 PM | LRCC-03/23/2022 12:19: System Advisory: ``THIS IS ONLY A DRILL``. Multiple transmission line tripping occurred at Luzon grid: Consecutive tripping of Hermosa-BCCPP 230kV Lines 1, 2 & 3 resulting in the isolation of Bataan Power Plants (GNPD, GMEC1 & 2, SCPC 1,2,3 & 4, Limay CCPP) ``THIS IS ONLY A DRILL``. [WEBSMS] | CLUZ
3/23/2022 12:15:23 PM | NEGROS ACC: 03/23/2022, PGPP2 SOG1 (17.58MW) auto-tripped at 1121H with indication condenser level high high affected by hot well pump tripping. | CVIS
3/23/2022 12:15:22 PM | NEGROS ACC: 03/23/2022, PGPP2 SOG1 (17.58MW) auto-tripped at 1121H with indication condenser level high high affected by hot well pump tripping. | CVIS
3/23/2022 11:55:14 AM | LRCC-03/23/2022 11:53: System Advisory: Please be informed that Network Operations Division (NOD-LSO) will conduct a Blackout Simulation Drill anytime today, March 23, 2022. No actual opening and closing of breakers. [WEBSMS] | CLUZ
3/23/2022 11:31:45 AM | NEGROS ACC: 03/23/2022, PGPP2 SOG1 (17.58MW) auto-tripped at 1121H. Ongoing investigation on cause of tripping. | CVIS
3/23/2022 11:31:43 AM | NEGROS ACC: 03/23/2022, PGPP2 SOG1 (17.58MW) auto-tripped at 1121H. Ongoing investigation on cause of tripping. | CVIS
3/23/2022 11:08:03 AM | MRCC-03/23/2022 11:02: GRID UPDATE AS OF 1:00 PM System Condition: CAP=2850MW, PK=2000MW, RR=67MW, NetOpMargin: PM=770, EVE=865 Highest Unit O/L: GNPK U2 and U4 @ 150 MW each. Derated Plant: Ag1@0.0MW, Ag2@100MW, Ag4@156MW, Ag5@42MW, Ag6@53MW, Ag7@26MW, Pul4@148MW, MGPP@75.3MW, STEAG@0.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@100MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/23/2022 11:07:54 AM | PANAY ACC-03/23/22 10:41: PANIT-AN SS, Panit-an-Roxas 69KV (5LI1PNT-ROX), TIME OUT: 10:36:00, RELAY: FD L3EC trip IETC, load:P 23.3MW, WEATHER: FAIR; Still under investigation. | CVIS
3/23/2022 10:45:36 AM | LRCC-03/23/2022 10:43: Daraga-Bacman 230kV line 1 de-energized at 1042H. (Unplanned Outage) [WEBSMS] | CLUZ
3/23/2022 10:17:01 AM | LRCC-03/23/2022 10:14: Ilijan GT1-1 online at 1011H. (Unplanned Outage) [WEBSMS] | CLUZ
3/23/2022 8:23:35 AM | LRCC-03/23/2022 08:02: Malaya Unit 2 online at 0801H. (Recommissioning test) [WEBSMS] | CLUZ
3/23/2022 8:23:30 AM | LRCC-03/23/2022 07:48: Sta Rita Module 10 completed fuel changeover from gas to oil at 0735H. [WEBSMS] | CLUZ
3/23/2022 7:17:28 AM | LRCC-03/23/2022 07:17: BCCPP-Limay 230kV Tie line 1 de-energized at 0714H. (Planned Outage) [WEBSMS] | CLUZ
3/23/2022 7:17:26 AM | LRCC-03/23/2022 07:13: Limay 230kV Bus 1 de-energized at 0712H. (Planned Outage) [WEBSMS] | CLUZ
3/23/2022 7:17:24 AM | LRCC-03/23/2022 07:08: Concepcion 230kV Bus 1 de-energized at 0702H. (Planned Outage) [WEBSMS] | CLUZ
3/23/2022 6:48:12 AM | LRCC-03/23/2022 06:08: Naga-Tayabas 230kV Line 2 de-energized at 0605H. (Planned Outage) [WEBSMS] | CLUZ
3/23/2022 6:48:10 AM | LRCC-03/23/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13094MW, PK=11004MW, RR=437MW, NetOpMargin: AM=1653, PM=963, EVE=1460 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: GMEC2 at 300MW, SLTEC1 at 91MW, QPPL at 275MW [WEBSMS] | CLUZ
3/23/2022 5:48:20 AM | LRCC-03/23/2022 05:30: Weather Update: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
3/23/2022 5:48:18 AM | LRCC-03/23/2022 05:24: Binan-Balibago 115kV line restored at 0524H. (Planned Outage) [WEBSMS] | CLUZ
3/23/2022 4:36:27 AM | MRCC-03/23/2022 04:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2795MW, PK=1930MW, RR=69MW, NetOpMargin: AM=787, PM=726, EVE=819 Highest Unit O/L: GNPK U2&U4 @ 138MW each. Derated Plant: Ag1@55MW, Ag2@140MW, Ag4@156MW, Ag5@42MW, Ag6@53MW, Ag7@26MW, Pul4@148MW, MGPP@75MW, STEAG@0.0MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW & MCC@100MW. [WEBSMS] | CMIN
3/23/2022 2:44:21 AM | LRCC-03/23/2022 02:34: Binan-Balibago 115kV line de-energized at 2353H. (Planned Outage) [WEBSMS] | CLUZ
3/22/2022 11:17:51 PM | LRCC-03/22/2022 22:56: Malaya Unit 2 offline at 2254H. (Commissioning test) [WEBSMS] | CLUZ
3/22/2022 10:50:01 PM | LRCC-03/22/2022 22:30: QPPL online at 2228H. (Unplanned Outage) [WEBSMS] | CLUZ
3/22/2022 6:01:26 PM | VRCC-03/22/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2076MW, PK=1877MW, RR=40MW, NetOpMargin: EVE=159 Highest Unit O/L: TVI U1 at 169MW, Derated Plant: EDC at 402, PEDC at 234, TVI at 169, KSPC at 103, TPC at 82, LGPP at 80, PGPP1 at 75 MW, Luzon supplying Visayas Grid [WEBSMS] | CVIS
3/22/2022 6:01:23 PM | LRCC-03/22/2022 17:58: Naga-Tayabas 230kV line 2 restored at 1758H. (Planned Outage) [WEBSMS] | CLUZ
3/22/2022 6:01:21 PM | LRCC-03/22/2022 17:35: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12196MW, PK=10697MW, RR=395MW, NetOpMargin: EVE=1104 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW and SLTEC 1 at 91MW [WEBSMS] | CLUZ
3/22/2022 6:01:19 PM | LRCC-03/22/2022 17:28: Nagsaag-San Roque 230kV line 1 was restored at 1728H. (Planned Outage) [WEBSMS] | CLUZ
3/22/2022 4:55:42 PM | MRCC-03/22/2022 16:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2755MW, PK=1850MW, RR=56MW, NetOpMargin: EVE=831 Highest Unit O/L: GNPK U2&U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@140MW, Ag4@156MW, Ag5@42MW, Ag6@53MW, Ag7@26MW, Pul4@148MW, MGPP@75MW, STEAG@0.0MW, TSI@270MW, FDC@ 244.5MW, SMCPC@270MW, GNPK@276MW, SEC1@105MW, SEC2@105MW, MCC@98MW. [WEBSMS] | CMIN
3/22/2022 4:33:16 PM | LRCC-03/22/2022 16:10: For info: Mexico 100MVAR Capacitor Bank 5 was declared available at 1600H after the correction of a cut conductor. (Unplanned Outage) [WEBSMS] | CLUZ
3/22/2022 4:33:14 PM | LRCC-03/22/2022 15:39: Dasmarinas-Ternate 115kV line energized at 1538H. (Planned Outage) [WEBSMS] | CLUZ
3/22/2022 4:33:13 PM | LRCC-03/22/2022 15:37: System Advisory: The Luzon Grid Highest Peak Load for the year 2022 is 11,513MW occurring at 1414H today, Tuesday, March 22, 2022. The Previous highest peak is 11,392MW which occurred last March 17, 2022, Thursday at 1429H. [WEBSMS] | CLUZ
3/22/2022 1:04:18 PM | VRCC-03/22/2022 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2324MW, PK=2064MW, RR=40MW, NetOpMargin: PM=220, EVE=159 Highest Unit O/L: TVI U1 at 169 MW, Derated Plant: EDC at 402 MW, PEDC at 234 MW, TVI at 169 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 75 MW [WEBSMS] | CVIS
3/22/2022 1:04:15 PM | LRCC-03/22/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12616MW, PK=11370MW, RR=440MW, NetOpMargin: PM=806, EVE=1392 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW and SLTEC 1 at 91MW [WEBSMS] | CLUZ
3/22/2022 10:53:23 AM | MRCC-03/22/2022 10:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2828MW, PK=1980MW, RR=59MW, NetOpMargin: PM=769, EVE=831 Highest Unit O/L: GNPK U2 and U4 @ 138 MW each. Derated Plant: Ag1@55MW, Ag2@140MW, Ag4@156MW, Ag5@42MW, Ag6@53MW, Ag7@26MW, Pul4@148MW, MGPP@75MW, STEAG@0.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@98MW, SEC1@105MW, SEC2@105MW. [WEBSMS] [WEBSMS] | CMIN
3/22/2022 9:41:56 AM | LRCC-03/22/2022 09:20: Dasmarinas-Ternate 115kV line de-energized at 0919H. (Planned Outage) [WEBSMS] | CLUZ
3/22/2022 8:48:05 AM | PANAY ACC-03/22/22 08:36: NABAS SS, Nabas-Culasi 69KV(2.5MW) (5LI1NBS-CSI), TIME IN: 08:33:00, RELAY: Started A-N, Trip N, 87.08km., WEATHER: FAIR. Momentary Line Fault. | CVIS
3/22/2022 8:48:04 AM | PANAY ACC-03/22/22 08:32: NABAS SS, Nabas-Culasi 69KV(2.5MW) (5LI1NBS-CSI), TIME OUT: 08:29:00, RELAY: Started A-N, Trip N, WEATHER: FAIR. Cause under investigation. | CVIS
3/22/2022 7:34:13 AM | LRCC-03/22/2022 07:09: Nagsaag-San Roque 230kV line 1 de-energized at 0708H. (Planned Outage) [WEBSMS] | CLUZ
3/22/2022 6:23:59 AM | LRCC-03/22/2022 06:15: Naga-Tayabas 230kV line 2 de-energized at 0613H. (Planned Outage) [WEBSMS] | CLUZ
3/22/2022 6:23:51 AM | LEYTE ACC-03/22/22 06:29:ORMOC CONVERTER STATION SS,350kV Leyte Luzon,Blocked/Deblocked at 0603H/0614H,on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/22/2022 6:02:57 AM | VRCC-03/22/2022 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2381MW, PK=2040MW, RR=40MW, NetOpMargin: AM=301, PM=214, EVE=153 Highest Unit O/L: TVI U1 at 169MW Derated Plant: EDC at 396MW, PEDC at 233MW, KSPC at 103MW, TPC at 82MW, PGPP1 at 75MW [WEBSMS] | CVIS
3/22/2022 6:02:54 AM | LRCC-03/22/2022 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12646MW, PK=10754MW, RR=421MW, NetOpMargin: AM=1471, PM=886, EVE=1443 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: GMEC2 at 300MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/22/2022 5:35:45 AM | LRCC-03/22/2022 05:29: Weather Update: Issued at 0400H, Intertropical Convergence Zone (ITCZ) affecting Palawan and Southern Mindanao. [WEBSMS] | CLUZ
3/22/2022 12:09:30 AM | NEGROS ACC: 03/22/2022, PGPP1 U1 (3.52MW) offline at 0001H to conduct replacement of high pressure middle casing. | CVIS
3/22/2022 12:09:29 AM | NEGROS ACC: 03/22/2022, PGPP1 U1 (3.52MW) offline at 0001H to conduct replacement of high pressure middle casing. | CVIS
3/22/2022 12:09:27 AM | NEGROS ACC: 03/21/2022, PGPP2 SOG1 (18.92MW) auto-tripped at 2336H. Ongoing investigation on cause of tripping. | CVIS
3/22/2022 12:09:26 AM | NEGROS ACC: 03/21/2022, PGPP2 SOG1 (18.92MW) auto-tripped at 2336H. Ongoing investigation on cause of tripping. | CVIS
3/21/2022 10:22:01 PM | LEYTE ACC-03/21/22: ORMOC CS, 350kV HVDC manually blocked/deblocked at 2209H/2219H, on normal flow per RTD | CVIS
3/21/2022 6:13:40 PM | LRCC-03/21/2022 18:13: Naga-Tayabas 230kV L2 restored at 1802H (Planned Outage). [WEBSMS] | CLUZ
3/21/2022 6:03:37 PM | VRCC-03/21/2022 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2103MW, PK=1825MW, RR=40MW, NetOpMargin: EVE=238 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, TVI = 169 MW [WEBSMS] | CVIS
3/21/2022 5:53:12 PM | LRCC-03/21/2022 17:34: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12448MW, PK=10419MW, RR=415MW, NetOpMargin: EVE=1614 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: GMEC2 at 300MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/21/2022 1:12:08 PM | VRCC-03/21/2022 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2315MW, PK=1880MW, RR=40MW, NetOpMargin: PM=395, EVE=238 Highest Unit O/L: TVI U @ 169 MW Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, TVI = 169 MW [WEBSMS] | CVIS
3/21/2022 12:48:59 PM | LRCC-03/21/2022 12:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12844MW, PK=11305MW, RR=449MW, NetOpMargin: PM=1090, EVE=1644 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: GMEC2 at 300MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/21/2022 11:42:10 AM | MRCC-03/21/2022 11:30: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2841MW, PK=1960MW, RR=59MW, NetOpMargin: PM=803, EVE=890 Highest Unit O/L: GNPOWER Unit 2 & Unit 4 @ 138MW each unit. Derated Plant: Ag1@55MW, Ag2@140MW, Ag4@156MW, Ag5@54MW, Ag6@53MW, Ag7@26MW, Pul4@149MW, MGPP@75MW, STEAG@0.0MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@100MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/21/2022 9:24:21 AM | NEGROS ACC: 03/21/2022, PGPP1 U2 re-online at 0902H. | CVIS
3/21/2022 9:02:15 AM | LRCC-03/21/2022 08:57: Nagsaag-Casecnan 230kV Line 1 de-energized at 0855H. (Planned Outage) [WEBSMS] | CLUZ
3/21/2022 8:52:10 AM | PANAY ACC-03/21/22 08:43: DINGLE SS, Dingle-Natividad 69 kV L (5LI1DIN-NTV), TIME IN: 08:39:00, RELAY: Z1, C-N, WEATHER: FAIR. Cause under investigation. | CVIS
3/21/2022 8:42:08 AM | PANAY ACC-03/21/22 08:36: DINGLE SS, Dingle-Natividad 69 kV L (5LI1DIN-NTV)(4.7MW), TIME OUT: 08:33:00, RELAY: Z1, C-N, WEATHER: FAIR. Cause under investigation. | CVIS
3/21/2022 8:15:20 AM | LEYTE ACC-03/21/22 08:18: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 0751H/001H on reverse power flow per RTD. Weather: Cloudy. | CVIS
3/21/2022 7:52:00 AM | NEGROS ACC: 03/21/2022, PGPP1 U2(31.16MW) auto tripped at 0744H, on going investigation. | CVIS
3/21/2022 6:22:47 AM | VRCC-03/21/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2414MW, PK=1870MW, RR=40MW, NetOpMargin: AM=504, PM=394, EVE=237 Highest Unit O/L: TVI U1 at 169 MW, Derated Plant: EDC at 396 MW, PEDC at 234 MW, TVI at 169 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW [WEBSMS] | CVIS
3/21/2022 6:22:45 AM | LRCC-03/21/2022 05:45: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12899MW, PK=10492MW, RR=439MW, NetOpMargin: AM=1968, PM=1343, EVE=1741 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW and SLTEC 1 at 91MW [WEBSMS] | CLUZ
3/20/2022 12:35:42 PM | LEYTE ACC-03/20/22 12:40: ORMOC SS, 69kV Baybay Feeder re-energized at 1204H, back to normal operation. Weather: Rainy. | CVIS
3/20/2022 11:25:34 AM | LEYTE ACC-03/20/22 11:28: ORMOC SS, 69kV Baybay Feeder de-energized at 1104H as per customers request. Load=25.2MW. Duration: 1100H-1200H. Weather: Fair. | CVIS
3/20/2022 11:02:06 AM | LEYTE ACC-03/20/22 11:04: KANANGA CSS, EDC-UMPP unit #4 cut-in to the system at 1042H, Generator failed ground voltage regulator indication. Weather: Fair. | CVIS
3/20/2022 10:38:39 AM | LEYTE ACC-03/20/22 10:46: KANANGA CSS, EDC-UMPP unit #1 tripped at 1028H, under assessment. Gen load=24.96MW. Weather: Fair. | CVIS
3/20/2022 10:28:34 AM | LRCC-03/20/2022 10:05: Santiago-Tuguegarao 230kV Line restored at 1004H. (Planned Outage) [WEBSMS] | CLUZ
3/20/2022 8:18:39 AM | PANAY ACC 3/20/2022: Panay-Negros on islanding operation at 0728H due to PMS of Negros-Cebu 138kv submarine cable. | CVIS
3/20/2022 8:00:05 AM | LEYTE ACC-03/20/22 07:49: ORMOC SS, Victoria - Tolosa - Mayorga 69kV Line portion isolated at 0633H, pre-arranged activity (0601H-1800H). Weather: Fair. | CVIS
3/20/2022 8:00:03 AM | NEGROS ACC: 03/20/2022, 138kV Amlan-Samboan Line 2 de- energized at 0737H due to APMS. | CVIS
3/20/2022 8:00:02 AM | VRCC-03/20/2022 07:31: 138KV Amlan-Samboan line 2 manually open @0728H scheduled PMS ( Cebu-Negros on islanding operation ). [WEBSMS] | CVIS
3/20/2022 7:18:46 AM | NEGROS ACC: 03/20/2022, Bacolod S/S 69kV Bus 1 de-energized at 0617H to conduct commissioning of 5-04CB04BCL & 5-04CB24BCL as per P&E request. | CVIS
3/20/2022 7:18:43 AM | LRCC-03/20/2022 07:07: Cabanatuan-Pantabangan 230kV Line de-energized at 0705H. (Planned Outage) [WEBSMS] | CLUZ
3/20/2022 7:18:41 AM | LRCC-03/20/2022 06:40: La Trinidad-Bauang 230kV Line 1 de-energized at 0640H. (Planned Outage) [WEBSMS] | CLUZ
3/20/2022 6:37:22 AM | NEGROS ACC: 03/20/2022, 138kV Amlan-Mabinay L2 de-energized at 0609H due to maintenance activity.Load of Line 2 transferred to Line 1. | CVIS
3/20/2022 6:37:19 AM | LRCC-03/20/2022 06:19: San Jose-Tayabas 500kV Line 1 de-energized at 0611H. (Planned Outage) [WEBSMS] | CLUZ
3/20/2022 6:37:18 AM | LRCC-03/20/2022 06:11: San Jose-Tayabas 230kV Line 1 de-energized at 0611H. (Planned Outage) [WEBSMS] | CLUZ
3/20/2022 6:06:01 AM | VRCC-03/20/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2388MW, PK=1543MW, RR=62MW, NetOpMargin: AM=783, PM=730, EVE=285 Highest Unit O/L: TVI U1 at 169 MW, Derated Plant: EDC at 396 MW, PEDC at 234 MW, TVI at 169 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW [WEBSMS] | CVIS
3/20/2022 6:05:58 AM | LRCC-03/20/2022 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12669MW, PK=8424MW, RR=347MW, NetOpMargin: AM=3898, PM=3686, EVE=2726 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: GMEC2 at 300MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/20/2022 5:29:04 AM | LRCC-03/20/2022 05:26: Weather Update: Issued at 0400H, Easterlies affecting Central and Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
3/20/2022 4:55:32 AM | LRCC-03/20/2022 04:53: Santiago-Tuguegarao 230kV Line de-energized at 0438H (Planned Outage) [WEBSMS] | CLUZ
3/20/2022 3:27:02 AM | LRCC-03/20/2022 03:23: QPPL on line at 0315H, on commissioning test. [WEBSMS] | CLUZ
3/20/2022 12:19:25 AM | LEYTE ACC-03/20/22 00:26: ORMOC CONVERTER STATION SS,350kV Leyte Luzon,Blocked/Deblocked at 0000H/0012H,on normal Power flow per RTD. WEATHER: FAIR | CVIS
3/19/2022 10:58:58 PM | VRCC-03/19/2022 22:57: CEBU SS 138 KV Bus 1 energized at 2241H [WEBSMS] | CVIS
3/19/2022 10:45:32 PM | VRCC-03/19/2022 22:43: Cebu-Colon 138kV Line 1 energized at 2239H, P&E Activity completed [WEBSMS] | CVIS
3/19/2022 10:22:05 PM | PANAY ACC-03/19/22 22:08: SAN JOSE SS, San Jose-Hamtic 69 kV L (5LI1SJB-HAM), TIME OUT: 22:02:00, TIME IN: 22:07:00, RELAY: OC2 ROC2 phase B, Z1, BN, 5.594kms., Load: 3.24MW, WEATHER: FAIR; Momentary line fault. | CVIS
3/19/2022 8:11:23 PM | VRCC-03/19/2022 20:05: Magdugo SS 230 KV Bus 2 energized at 1947H P&E activity completed [WEBSMS] | CVIS
3/19/2022 7:06:40 PM | LRCC-03/19/2022 19:02: San Lorenzo-Avion 230kV Line restored at 1901H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 6:23:08 PM | VRCC-03/19/2022 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2107MW, PK=1843MW, RR=40MW, NetOpMargin: EVE=224 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, TVI = 169 MW [WEBSMS] | CVIS
3/19/2022 6:06:43 PM | NEGROS ACC: 03/19/2022, 138kV Amlan-Pondol Line 1 energized at 1721H after completion of planned maintenance activity. | CVIS
3/19/2022 6:06:42 PM | NEGROS ACC: 03/19/2022, 138kV Amlan-Pondol Line 1 energized at 1721H after completion of planned maintenance activity. | CVIS
3/19/2022 6:06:39 PM | LRCC-03/19/2022 17:23: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12246MW, PK=9731MW, RR=380MW, NetOpMargin: EVE=2135 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: GMEC2 at 300MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/19/2022 5:06:57 PM | NEGROS ACC: 03/19/2022, 69kV Kabankalan-La Castellana Sub T/L restored at 1701H after emergency replacement of broken cross-arm at structure no. 61. Customer-owned and maintained line. | CVIS
3/19/2022 5:06:56 PM | NEGROS ACC: 03/19/2022, 69kV Kabankalan-La Castellana Sub T/L restored at 1701H after emergency replacement of broken cross-arm at structure no. 61. Customer-owned and maintained line. | CVIS
3/19/2022 4:56:53 PM | LEYTE ACC-03/19/22: STA. RITA SS, 69kV Quinapondan Feeder re-energized at 1653H, APMS of customer TR (Bagolibas SS) finished, WEATHER: FAIR | CVIS
3/19/2022 4:56:52 PM | LEYTE ACC-03/19/22: STA. RITA SS, 69kV Quinapondan Feeder re-energized at 1653H, APMS of customer TR (Bagolibas SS) finished, WEATHER: FAIR | CVIS
3/19/2022 4:43:28 PM | NEGROS ACC: 03/19/2022, 69kV Kabankalan-La Castellana Sub T/L (11.40MW) emergency shutdown at 1637H as per customers(NOCECO) request to facilitate replacement of broken cross-arm at structure no. 61. Customer-owned and maintained line. | CVIS
3/19/2022 4:43:26 PM | NEGROS ACC: 03/19/2022, 69kV Kabankalan-La Castellana Sub T/L (11.40MW) emergency shutdown at 1637H as per customers(NOCECO) request to facilitate replacement of broken cross-arm at structure no. 61. Customer-owned and maintained line. | CVIS
3/19/2022 2:16:32 PM | PANAY ACC-03/19/22 12:53: ILOILO 1 S/S SS, Iloilo 1 138kV BUS 2, TIME IN: 12:47:00, Pre arranged maintenanc | CVIS
3/19/2022 1:19:08 PM | VRCC-03/19/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2297MW, PK=1818MW, RR=40MW, NetOpMargin: PM=439, EVE=186 Highest Unit O/L: TVI U @ 169 MW Derated Plant: EDC = 396 MW, TVI @ 169MW,PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/19/2022 12:50:50 PM | LRCC-03/19/2022 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12541MW, PK=10080MW, RR=400MW, NetOpMargin: PM=2061, EVE=1825 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: GMEC2 at 300MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/19/2022 12:24:03 PM | NEGROS ACC: 03/19/2022, PGPP1 U3 re-online at 1211H. | CVIS
3/19/2022 11:03:23 AM | VRCC-03/19/2022 09:52: TVI u#2 emergency cut-out @0940H, to check possible tube leak. [WEBSMS] | CVIS
3/19/2022 11:03:21 AM | LRCC-03/19/2022 07:36: QPPL online at 0732H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 10:56:46 AM | VRCC-03/19/2022 09:52: TVI u#2 emergency cut-out @0940H, to check possible tube leak. [WEBSMS] | CVIS
3/19/2022 10:56:45 AM | LRCC-03/19/2022 07:36: QPPL online at 0732H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 10:46:44 AM | VRCC-03/19/2022 09:52: TVI u#2 emergency cut-out @0940H, to check possible tube leak. [WEBSMS] | CVIS
3/19/2022 10:46:43 AM | LRCC-03/19/2022 07:36: QPPL online at 0732H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 10:37:28 AM | LRCC-03/19/2022 07:36: QPPL online at 0732H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 10:37:25 AM | VRCC-03/19/2022 09:52: TVI u#2 emergency cut-out @0940H, to check possible tube leak. [WEBSMS] | CVIS
3/19/2022 10:23:20 AM | LEYTE ACC-03/19/22 10:10:ORMOC CONVERTER STATION SS,350kV HVDC Leyte-Luzon,Blocked/Deblocked at 0941H/0951H,on reverse power flow per RTD.WEATHER: FAIR | CVIS
3/19/2022 10:23:14 AM | LRCC-03/19/2022 07:36: QPPL online at 0732H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 10:23:13 AM | LRCC-03/19/2022 06:46: Muntinlupa(Sucat)-Manila(Paco) 230kV Line de-energized at 0644H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 10:15:51 AM | LEYTE ACC-03/19/22 10:10:ORMOC CONVERTER STATION SS,350kV HVDC Leyte-Luzon,Blocked/Deblocked at 0941H/0951H,on reverse power flow per RTD.WEATHER: FAIR | CVIS
3/19/2022 10:15:50 AM | VRCC-03/19/2022 09:52: TVI u#2 emergency cut-out @0940H, to check possible tube leak. [WEBSMS] | CVIS
3/19/2022 10:15:49 AM | LRCC-03/19/2022 07:36: QPPL online at 0732H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 9:59:47 AM | VRCC-03/19/2022 09:52: TVI u#2 emergency cut-out @0940H, to check possible tube leak. [WEBSMS] | CVIS
3/19/2022 9:59:46 AM | VRCC-03/19/2022 05:47: CEBU SS 138KV Bus 1 de-energized at 0540H, P&E request. ECD: 2335H [WEBSMS] | CVIS
3/19/2022 9:59:45 AM | LRCC-03/19/2022 07:36: QPPL online at 0732H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 9:34:25 AM | VRCC-03/19/2022 07:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2494MW, PK=1795MW, RR=40MW, NetOpMargin: AM=659, PM=608, EVE=355 Highest Unit O/L: TVI U @169 MW Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/19/2022 9:34:24 AM | VRCC-03/19/2022 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2494MW, PK=1795MW, RR=57MW, NetOpMargin: AM=642, PM=608, EVE=355 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/19/2022 9:34:23 AM | LRCC-03/19/2022 07:36: QPPL online at 0732H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 8:18:10 AM | PANAY ACC-03/19/22 08:00 STA. BARBARA SS, Sta. Barbara 138/69/13.8 kV T3 (50MVA) (7XF03SBA), TIME OUT: 07:55:00, Pre arranged maintenance, ETR: March 19, 2022- ONWARDS, WEATHER: FAIR | CVIS
3/19/2022 8:18:09 AM | LRCC-03/19/2022 07:36: QPPL online at 0732H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 8:18:08 AM | LRCC-03/19/2022 06:46: Muntinlupa(Sucat)-Manila(Paco) 230kV Line de-energized at 0644H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 7:00:12 AM | PANAY ACC-03/19/22 06:29: STA. BARBARA SS, Sta. Barbara-Ingore 69 kV Line (5LI1SBA-INR), TIME OUT: 06:21:00, Load: 5.5mw, Pre arranged maintenance, ETR: 0800H, WEATHER: FAIR | CVIS
3/19/2022 7:00:11 AM | LRCC-03/19/2022 06:46: Muntinlupa(Sucat)-Manila(Paco) 230kV Line de-energized at 0644H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 6:50:10 AM | VRCC-03/19/2022 06:27: Samboan SS 30MVA TR1 de-energized at 0622H, pre-arranged activity. ECD 1800H. [WEBSMS] | CVIS
3/19/2022 6:50:09 AM | LRCC-03/19/2022 06:46: Muntinlupa(Sucat)-Manila(Paco) 230kV Line de-energized at 0644H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 6:50:08 AM | LRCC-03/19/2022 04:40: Daraga-Bacman 230kV Line 1 restored at 0418H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 6:40:03 AM | VRCC-03/19/2022 06:27: Samboan SS 30MVA TR1 de-energized at 0622H, pre-arranged activity. ECD 1800H. [WEBSMS] | CVIS
3/19/2022 6:40:02 AM | LRCC-03/19/2022 06:23: San Lorenzo-Avion 230kV Line de-energized at 0620H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 6:39:55 AM | LRCC-03/19/2022 06:23: San Lorenzo-Avion 230kV Line de-energized at 0620H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 6:39:54 AM | LRCC-03/19/2022 05:23: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12882MW, PK=9881MW, RR=394MW, NetOpMargin: AM=2607, PM=2234, EVE=2199 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW [WEBSMS] | CLUZ
3/19/2022 6:39:53 AM | VRCC-03/19/2022 06:27: Samboan SS 30MVA TR1 de-energized at 0622H, pre-arranged activity. ECD 1800H. [WEBSMS] | CVIS
3/19/2022 6:39:52 AM | VRCC-03/19/2022 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2494MW, PK=1795MW, RR=57MW, NetOpMargin: AM=642, PM=608, EVE=355 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/19/2022 6:24:24 AM | LEYTE ACC-03/19/22 06:25: ORMOC SS, CMS of Ormoc - Lemon - Tunga 69kV Line de-energized at 0523H, pre-arranged activity (0501H-1700H). Weather: Fair. | CVIS
3/19/2022 6:24:23 AM | LRCC-03/19/2022 06:23: San Lorenzo-Avion 230kV Line de-energized at 0620H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 6:24:22 AM | LRCC-03/19/2022 06:23: San Lorenzo-Avion 230kV Line de-energized at 0620H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 6:14:22 AM | VRCC-03/19/2022 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2494MW, PK=1795MW, RR=57MW, NetOpMargin: AM=642, PM=608, EVE=355 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/19/2022 6:14:21 AM | VRCC-03/19/2022 05:47: CEBU SS 138KV Bus 1 de-energized at 0540H, P&E request. ECD: 2335H [WEBSMS] | CVIS
3/19/2022 6:14:20 AM | LRCC-03/19/2022 05:23: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12882MW, PK=9881MW, RR=394MW, NetOpMargin: AM=2607, PM=2234, EVE=2199 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW [WEBSMS] | CLUZ
3/19/2022 6:11:30 AM | VRCC-03/19/2022 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2494MW, PK=1795MW, RR=57MW, NetOpMargin: AM=642, PM=608, EVE=355 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/19/2022 6:11:29 AM | LRCC-03/19/2022 05:23: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12882MW, PK=9881MW, RR=394MW, NetOpMargin: AM=2607, PM=2234, EVE=2199 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW [WEBSMS] | CLUZ
3/19/2022 6:01:21 AM | VRCC-03/19/2022 05:47: CEBU SS 138KV Bus 1 de-energized at 0540H, P&E request. ECD: 2335H [WEBSMS] | CVIS
3/19/2022 6:01:20 AM | LRCC-03/19/2022 05:23: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12882MW, PK=9881MW, RR=394MW, NetOpMargin: AM=2607, PM=2234, EVE=2199 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW [WEBSMS] | CLUZ
3/19/2022 5:50:53 AM | VRCC-03/19/2022 05:47: CEBU SS 138KV Bus 1 de-energized at 0540H, P&E request. ECD: 2335H [WEBSMS] | CVIS
3/19/2022 5:50:52 AM | LRCC-03/19/2022 05:23: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12882MW, PK=9881MW, RR=394MW, NetOpMargin: AM=2607, PM=2234, EVE=2199 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW [WEBSMS] | CLUZ
3/19/2022 5:50:46 AM | LRCC-03/19/2022 05:23: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12882MW, PK=9881MW, RR=394MW, NetOpMargin: AM=2607, PM=2234, EVE=2199 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; SLTEC 1 @91MW [WEBSMS] | CLUZ
3/19/2022 5:50:44 AM | VRCC-03/19/2022 05:47: CEBU SS 138KV Bus 1 de-energized at 0540H, P&E request. ECD: 2335H [WEBSMS] | CVIS
3/19/2022 4:58:22 AM | LRCC-03/19/2022 04:46: Weather Update: Issued at 0400H: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
3/19/2022 4:58:21 AM | LRCC-03/19/2022 04:40: Daraga-Bacman 230kV Line 1 restored at 0418H. (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 4:57:59 AM | LRCC-03/19/2022 04:46: Weather Update: Issued at 0400H: Easterlies affecting Southern Luzon, Visayas, and Mindanao. [WEBSMS] | CLUZ
3/19/2022 4:57:58 AM | LRCC-03/19/2022 00:50: Ilijan A-3 shutdown at 0045H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 4:36:14 AM | LRCC-03/19/2022 04:35: Sta. Rita 10 change over from gas to oil at 0403H. [WEBSMS] | CLUZ
3/19/2022 4:26:11 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 4:08:02 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 3:58:00 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 3:57:59 AM | LRCC-03/19/2022 00:29: GNPD 1 on line at 0023H (Unplanned Outage). [WEBSMS] | CLUZ
3/19/2022 3:47:56 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 3:44:34 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 3:34:32 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 3:24:28 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 3:24:27 AM | LRCC-03/19/2022 00:03: QPPL on line at 2255H and conduct load rejection test at 2333H (on commissioning test) [WEBSMS] | CLUZ
3/19/2022 3:21:06 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 3:21:05 AM | LRCC-03/19/2022 00:29: GNPD 1 on line at 0023H (Unplanned Outage). [WEBSMS] | CLUZ
3/19/2022 3:11:03 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 3:01:00 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 3:00:59 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 2:57:34 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 2:47:32 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 2:37:30 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 2:34:06 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 2:24:04 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 2:14:02 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 2:10:38 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 2:00:37 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 2:00:36 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 1:50:35 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 1:50:34 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 1:47:11 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 1:47:10 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 1:37:09 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 1:37:08 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 1:27:07 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 1:27:06 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 1:23:53 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 1:23:44 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 1:13:48 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 1:13:42 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 1:03:44 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 1:03:39 AM | LRCC-03/19/2022 01:03: Ilijan A-2 shutdown at 0058H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 1:00:21 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 1:00:20 AM | LRCC-03/19/2022 00:50: Ilijan A-3 shutdown at 0045H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 12:50:17 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 12:50:16 AM | LRCC-03/19/2022 00:50: Ilijan A-3 shutdown at 0045H (Planned Outage) [WEBSMS] | CLUZ
3/19/2022 12:40:12 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 12:40:11 AM | LRCC-03/19/2022 00:29: GNPD 1 on line at 0023H (Unplanned Outage). [WEBSMS] | CLUZ
3/19/2022 12:36:49 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 12:36:48 AM | LRCC-03/19/2022 00:29: GNPD 1 on line at 0023H (Unplanned Outage). [WEBSMS] | CLUZ
3/19/2022 12:26:48 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 12:26:46 AM | LRCC-03/19/2022 00:03: QPPL on line at 2255H and conduct load rejection test at 2333H (on commissioning test) [WEBSMS] | CLUZ
3/19/2022 12:16:44 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 12:16:43 AM | LRCC-03/19/2022 00:03: QPPL on line at 2255H and conduct load rejection test at 2333H (on commissioning test) [WEBSMS] | CLUZ
3/19/2022 12:13:30 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 12:13:20 AM | LRCC-03/19/2022 00:03: QPPL on line at 2255H and conduct load rejection test at 2333H (on commissioning test) [WEBSMS] | CLUZ
3/19/2022 12:03:25 AM | VRCC-03/18/2022 21:05: 230KV Magdugo Bus 1 energized 2059H activity completed. [WEBSMS] | CVIS
3/19/2022 12:03:18 AM | LRCC-03/19/2022 00:03: QPPL on line at 2255H and conduct load rejection test at 2333H (on commissioning test) [WEBSMS] | CLUZ
3/18/2022 2:29:08 PM | VRCC-03/18/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2100MW, RR=40MW, NetOpMargin: PM=285, EVE=335 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/18/2022 2:29:07 PM | LRCC-03/18/2022 12:45: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12294MW, PK=11143MW, RR=436MW, NetOpMargin: PM=1467, EVE=716 Highest Unit O/L: Sual 1 & 2 at 600MW each Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/18/2022 2:29:06 PM | LRCC-03/18/2022 10:50: System Advisory: Dinginin 1 (653MW) tripped at 1027H. Lowest frequency reached 58.905Hz. Affected ALD feeders of NGCP and MERALCO restored at 1042H and 1041H, respectively. [WEBSMS] | CLUZ
3/17/2022 9:05:12 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 9:05:11 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:48:58 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:48:57 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:46:55 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:46:54 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:38:37 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:38:37 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:38:14 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:38:13 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:20:45 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:20:44 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:18:43 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:18:42 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:16:40 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:16:39 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:14:38 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:14:36 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:12:37 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:12:34 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:10:31 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:10:30 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:08:29 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:08:28 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:08:27 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 8:06:26 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:06:25 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:04:23 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:04:22 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:02:20 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:02:20 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:01:25 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:01:24 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:59:22 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:59:21 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:57:17 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:57:16 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:55:14 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:55:13 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:53:11 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:53:10 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:51:08 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:51:07 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:49:05 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:49:04 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:47:01 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:47:00 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:38:53 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:38:52 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:38:32 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:38:31 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:38:30 PM | LRCC-03/17/2022 14:45: Daraga-Bacman 230kV L2 energized in Daraga side at 1442H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 7:28:10 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:28:09 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:28:08 PM | LRCC-03/17/2022 14:45: Daraga-Bacman 230kV L2 energized in Daraga side at 1442H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 7:26:07 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:26:06 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:24:05 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:24:04 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:24:03 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:22:02 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:22:01 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:19:59 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:19:58 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:17:43 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:17:41 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:15:40 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:15:39 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:13:37 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:13:36 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:11:34 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:11:33 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:09:31 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:09:30 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:08:55 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:08:36 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:06:50 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:06:34 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:04:46 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:04:31 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:02:41 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:02:25 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:02:24 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 7:00:38 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:00:18 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:58:33 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:58:15 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:56:28 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:56:12 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:54:23 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:54:08 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:52:18 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:52:06 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:50:13 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:50:03 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:48:08 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:48:01 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:48:00 PM | LRCC-03/17/2022 14:45: Daraga-Bacman 230kV L2 energized in Daraga side at 1442H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 6:46:03 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:45:58 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:38:53 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:38:52 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:36:51 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:36:50 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:34:48 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:34:47 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:32:46 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:32:45 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:30:41 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:30:40 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:28:39 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:28:38 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:26:36 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:26:35 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:24:34 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:24:32 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:22:31 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:22:30 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:21:59 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:21:21 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:19:54 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:19:20 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:17:49 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:17:17 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:15:45 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:15:16 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:13:41 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:13:40 PM | LRCC-03/17/2022 14:45: Daraga-Bacman 230kV L2 energized in Daraga side at 1442H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 6:13:15 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:11:35 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:11:14 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:09:31 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:09:13 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:07:22 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:07:04 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:05:19 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:05:03 PM | VRCC-03/17/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2242MW, PK=1903MW, RR=40MW, NetOpMargin: EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:03:14 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:03:02 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:01:09 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:01:01 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:59:06 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 5:59:00 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:58:55 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:58:13 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 5:48:29 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:25:43 PM | LRCC-03/17/2022 17:24: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12529MW, PK=10423MW, RR=391MW, NetOpMargin: EVE=1715 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 5:23:40 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:23:39 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 5:21:37 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:21:36 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 5:19:35 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:19:34 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 5:19:33 PM | LRCC-03/17/2022 14:45: Daraga-Bacman 230kV L2 energized in Daraga side at 1442H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 5:17:32 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:17:31 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 5:15:30 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:15:28 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 5:13:49 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:13:48 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 5:13:47 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 5:11:44 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:11:43 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 5:11:42 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 5:02:17 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:02:14 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 5:00:13 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:00:11 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:58:11 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:58:09 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:58:08 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:56:09 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:56:06 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:54:05 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:54:03 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:52:01 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:52:01 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:51:03 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:51:00 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:49:01 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:48:59 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:46:59 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:46:57 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:38:51 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:38:47 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:36:45 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:36:43 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:34:41 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:34:40 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:32:39 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:32:38 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:30:37 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:30:36 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:28:34 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:28:33 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:27:46 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:27:41 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:25:44 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:25:38 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:23:43 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:23:36 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:21:42 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:21:34 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:19:41 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:19:30 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:17:40 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:17:28 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:15:38 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:15:25 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:13:37 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:13:23 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:11:36 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:11:18 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:09:16 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:09:15 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:07:12 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:07:11 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:05:08 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:05:07 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:04:16 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:04:14 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:02:12 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:02:10 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 4:00:09 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 4:00:08 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:58:06 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:58:05 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:56:04 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:56:02 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:54:01 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:54:00 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:51:58 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:51:57 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:49:54 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:49:52 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:47:51 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:47:50 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:45:48 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:45:47 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:43:45 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:43:44 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:41:41 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:41:40 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:40:46 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:40:45 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:25:35 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:25:34 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:23:34 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:23:32 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:21:30 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:21:29 PM | LRCC-03/17/2022 15:21: System Advisory: Luzon Grid Highest Peak Load for the year 2022 at 11392MW occurred at 1429H today, Thursday, March 17, 2022. Previous highest peak at 11077MW (March 16, 2022, Wednesday at 1448H) [WEBSMS] | CLUZ
3/17/2022 3:19:28 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:19:27 PM | LRCC-03/17/2022 14:45: Daraga-Bacman 230kV L2 energized in Daraga side at 1442H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 3:17:25 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:17:24 PM | LRCC-03/17/2022 14:45: Daraga-Bacman 230kV L2 energized in Daraga side at 1442H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 3:16:43 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 3:16:37 PM | LRCC-03/17/2022 14:45: Daraga-Bacman 230kV L2 energized in Daraga side at 1442H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 2:53:22 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:53:04 PM | LRCC-03/17/2022 14:45: Daraga-Bacman 230kV L2 energized in Daraga side at 1442H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 2:51:18 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:51:01 PM | LRCC-03/17/2022 14:45: Daraga-Bacman 230kV L2 energized in Daraga side at 1442H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 2:49:13 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:48:59 PM | LRCC-03/17/2022 14:45: Daraga-Bacman 230kV L2 energized in Daraga side at 1442H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 2:47:09 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:46:56 PM | LRCC-03/17/2022 14:45: Daraga-Bacman 230kV L2 energized in Daraga side at 1442H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 2:38:50 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:38:42 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:36:46 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:36:39 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:29:35 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:29:34 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:27:33 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:27:32 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:25:30 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:25:29 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:23:27 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:23:27 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:21:25 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:21:24 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:19:22 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:19:22 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:17:20 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:17:19 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:15:18 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:15:17 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:13:14 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 2:13:13 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:11:10 PM | LEYTE ACC-03/17/22 13:39: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1318H/1328H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/17/2022 2:11:09 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:10:11 PM | LEYTE ACC-03/17/22 13:39: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1318H/1328H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/17/2022 2:10:11 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:08:08 PM | LEYTE ACC-03/17/22 13:39: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1318H/1328H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/17/2022 2:08:07 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:06:05 PM | LEYTE ACC-03/17/22 13:39: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1318H/1328H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/17/2022 2:06:05 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:04:03 PM | LEYTE ACC-03/17/22 13:39: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1318H/1328H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/17/2022 2:04:02 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 2:02:03 PM | LEYTE ACC-03/17/22 13:39: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1318H/1328H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/17/2022 2:02:00 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:59:58 PM | LEYTE ACC-03/17/22 13:39: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1318H/1328H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/17/2022 1:59:57 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:57:55 PM | LEYTE ACC-03/17/22 13:39: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1318H/1328H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/17/2022 1:57:55 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:55:54 PM | LEYTE ACC-03/17/22 13:39: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1318H/1328H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/17/2022 1:55:52 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:53:51 PM | LEYTE ACC-03/17/22 13:39: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1318H/1328H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/17/2022 1:53:50 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:51:48 PM | LEYTE ACC-03/17/22 13:39: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1318H/1328H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/17/2022 1:51:47 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:49:47 PM | LEYTE ACC-03/17/22 13:39: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1318H/1328H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/17/2022 1:49:45 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:47:43 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 1:47:42 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:46:45 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 1:46:43 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:38:34 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 1:38:33 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:36:31 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:36:31 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 1:34:29 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 1:34:28 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:32:26 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:32:26 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 1:30:24 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 1:30:23 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:28:22 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 1:28:21 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:26:19 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 1:26:18 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:24:16 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 1:24:15 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 1:23:22 PM | VRCC-03/17/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2459MW, PK=1994MW, RR=40MW, NetOpMargin: PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit. Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 1:23:20 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 12:59:08 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:59:06 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 12:57:04 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 12:57:04 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:56:07 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:56:06 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 12:54:05 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:54:03 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 12:52:02 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:52:00 PM | LRCC-03/17/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12721MW, PK=11126MW, RR=442MW, NetOpMargin: PM=1153, EVE=1727 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 12:49:59 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:49:58 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:47:57 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:47:55 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:45:55 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:45:53 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:39:45 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:39:44 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:37:42 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:37:41 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:35:40 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:35:39 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:33:37 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:33:36 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:32:55 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:32:53 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:30:51 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:30:49 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:28:47 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:28:44 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:26:42 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:26:40 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:24:37 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:24:35 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:22:32 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:22:30 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:20:30 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:20:25 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:18:27 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:18:20 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:16:24 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:16:14 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:14:20 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:14:09 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:12:16 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:12:05 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:10:13 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:10:01 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:07:52 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:07:15 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:07:14 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:02:49 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:02:48 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 12:00:46 PM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 12:00:45 PM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:58:44 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:58:43 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:56:41 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:56:40 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:54:39 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:54:37 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:52:37 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:52:35 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:50:34 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:50:32 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:48:31 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:48:30 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:46:28 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:46:27 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:39:25 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:39:20 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:37:23 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:37:17 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:35:21 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:35:15 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:33:14 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:33:12 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:31:11 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:31:10 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:29:09 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:29:07 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:27:06 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:27:05 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:25:04 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:25:02 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:23:01 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:23:00 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:20:58 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:20:57 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:20:00 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:19:59 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:17:57 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:17:57 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:15:55 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:15:54 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:13:53 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:13:52 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:11:49 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:11:48 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:09:46 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:09:45 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:07:44 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:07:42 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:05:41 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:05:40 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:03:39 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 11:03:37 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:01:35 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 11:01:35 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 10:59:34 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 10:59:32 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:57:30 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:57:30 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 10:56:14 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 10:56:13 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:55:10 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 10:55:09 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:54:46 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 10:54:45 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:54:36 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 10:54:35 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:52:34 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 10:52:33 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:43:32 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:34:00 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:34:00 AM | PANAY ACC-03/17/22 10:10: PANIT-AN SS, Sigma-Dao 69 kV Line, TIME OUT: 09:09, TIME IN: 10:08, Customer-owned and maintained line. | CVIS
3/17/2022 10:10:00 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:10:00 AM | PANAY ACC-03/17/22 09:14: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN),Load:10MW; TIME OUT: 09:09, TIME IN: 09:13, WEATHER: FAIR, Cause:Under investigation | CVIS
3/17/2022 10:08:00 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:08:00 AM | PANAY ACC-03/17/22 09:14: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN),Load:10MW; TIME OUT: 09:09, TIME IN: 09:13, WEATHER: FAIR, Cause:Under investigation | CVIS
3/17/2022 10:05:00 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:05:00 AM | PANAY ACC-03/17/22 09:14: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN),Load:10MW; TIME OUT: 09:09, TIME IN: 09:13, WEATHER: FAIR, Cause:Under investigation | CVIS
3/17/2022 10:03:00 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:03:00 AM | PANAY ACC-03/17/22 09:14: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN),Load:10MW; TIME OUT: 09:09, TIME IN: 09:13, WEATHER: FAIR, Cause:Under investigation | CVIS
3/17/2022 10:01:00 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 10:01:00 AM | PANAY ACC-03/17/22 09:14: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN),Load:10MW; TIME OUT: 09:09, TIME IN: 09:13, WEATHER: FAIR, Cause:Under investigation | CVIS
3/17/2022 9:59:00 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 9:59:00 AM | PANAY ACC-03/17/22 09:14: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN),Load:10MW; TIME OUT: 09:09, TIME IN: 09:13, WEATHER: FAIR, Cause:Under investigation | CVIS
3/17/2022 9:57:00 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 9:57:00 AM | PANAY ACC-03/17/22 09:14: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN),Load:10MW; TIME OUT: 09:09, TIME IN: 09:13, WEATHER: FAIR, Cause:Under investigation | CVIS
3/17/2022 9:55:00 AM | LRCC-03/17/2022 09:55: Botolan-Hanjin 230kV Line tripped/reclosed at 0949H (Unplanned Outage). [WEBSMS] | CLUZ
3/17/2022 9:55:00 AM | PANAY ACC-03/17/22 09:14: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN),Load:10MW; TIME OUT: 09:09, TIME IN: 09:13, WEATHER: FAIR, Cause:Under investigation | CVIS
3/17/2022 9:53:00 AM | LRCC-03/17/2022 09:10: GNPD 1 on line at 0906H (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 9:53:00 AM | PANAY ACC-03/17/22 09:14: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN),Load:10MW; TIME OUT: 09:09, TIME IN: 09:13, WEATHER: FAIR, Cause:Under investigation | CVIS
3/17/2022 9:51:00 AM | LRCC-03/17/2022 09:10: GNPD 1 on line at 0906H (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 9:51:00 AM | PANAY ACC-03/17/22 09:14: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN),Load:10MW; TIME OUT: 09:09, TIME IN: 09:13, WEATHER: FAIR, Cause:Under investigation | CVIS
3/17/2022 9:49:00 AM | LRCC-03/17/2022 09:10: GNPD 1 on line at 0906H (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 9:49:00 AM | PANAY ACC-03/17/22 09:14: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN),Load:10MW; TIME OUT: 09:09, TIME IN: 09:13, WEATHER: FAIR, Cause:Under investigation | CVIS
3/17/2022 9:47:00 AM | LRCC-03/17/2022 09:10: GNPD 1 on line at 0906H (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 9:47:00 AM | PANAY ACC-03/17/22 09:14: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN),Load:10MW; TIME OUT: 09:09, TIME IN: 09:13, WEATHER: FAIR, Cause:Under investigation | CVIS
3/17/2022 9:45:00 AM | LRCC-03/17/2022 09:10: GNPD 1 on line at 0906H (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 9:45:00 AM | PANAY ACC-03/17/22 09:14: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN),Load:10MW; TIME OUT: 09:09, TIME IN: 09:13, WEATHER: FAIR, Cause:Under investigation | CVIS
3/17/2022 9:16:00 AM | LRCC-03/17/2022 09:10: GNPD 1 on line at 0906H (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 9:14:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 9:13:00 AM | LRCC-03/17/2022 09:10: GNPD 1 on line at 0906H (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 9:12:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 9:11:00 AM | LRCC-03/17/2022 09:10: GNPD 1 on line at 0906H (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 9:09:00 AM | LRCC-03/17/2022 09:06: Daraga-Bacman 230kV L2 de-energized at 0905H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 9:09:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 9:07:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 9:06:00 AM | LRCC-03/17/2022 09:06: Daraga-Bacman 230kV L2 de-energized at 0905H (Planned Outage). [WEBSMS] | CLUZ
3/17/2022 9:04:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 9:04:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 9:02:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 9:02:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:59:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:59:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:57:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:57:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:55:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:55:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:54:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:52:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:52:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:50:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:49:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:48:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:47:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:45:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:45:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:43:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:43:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:41:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:40:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:39:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:38:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:36:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:36:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:34:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:34:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:31:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:31:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:30:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:28:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:28:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:26:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:25:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:23:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:23:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:21:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:21:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:14:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:14:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:12:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:11:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:09:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:09:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:07:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:07:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:06:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:06:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:04:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:04:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:02:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:02:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 8:00:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 8:00:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:58:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:58:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:55:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:55:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:53:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:53:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:50:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:50:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:48:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:48:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:46:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:46:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:44:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:44:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:43:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:41:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:41:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:39:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:39:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:37:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:36:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:34:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:34:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:32:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:31:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:29:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:29:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:27:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:27:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:24:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:24:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:22:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:22:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:20:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:20:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:18:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:18:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:16:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:16:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:14:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:14:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:11:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:11:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:09:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:09:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:07:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:07:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:04:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:04:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:02:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:02:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 7:00:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 7:00:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:58:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:58:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:56:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:56:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:55:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:55:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:53:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:53:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:51:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:50:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:48:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:48:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:46:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:46:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:44:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:43:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:41:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:41:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:38:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:38:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:36:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:36:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:34:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:34:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:32:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:32:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:31:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:29:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:29:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:27:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:27:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:24:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:24:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:22:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:22:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:20:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:20:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:17:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:17:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:15:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:15:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:13:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:13:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:11:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:11:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 6:08:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 6:08:00 AM | VRCC-03/17/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2503MW, PK=1970MW, RR=40MW, NetOpMargin: AM=493, PM=425, EVE=299 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW, PGPP1 at 71 MW [WEBSMS] | CVIS
3/17/2022 5:43:00 AM | LRCC-03/17/2022 05:42: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12195MW, PK=10543MW, RR=422MW, NetOpMargin: AM=1231, PM=771, EVE=1152 Highest Unit O/L: Sual at 600MW Derated Plant: Ilijan A/B at 817MW, GMEC2 at 300MW, Pagbilao 3 at 350MW, SLTEC1 at 91MW [WEBSMS] | CLUZ
3/17/2022 4:22:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 4:21:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 4:19:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 4:17:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 4:15:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 4:13:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 4:11:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 4:09:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 4:07:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 4:04:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 4:02:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 4:00:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 3:58:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 3:57:00 AM | PANAY ACC-03/17/22 03:55: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 03:45:00, TIME IN: 03:50:00, RELAY: Phase A 33.38kms, Load: 2.5mw, Momentary fault, WEATHER: FAIR | CVIS
3/17/2022 2:07:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 2:05:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 2:03:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 2:01:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:59:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:57:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:55:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:53:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:51:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:48:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:46:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:40:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:38:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:35:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:33:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:30:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:28:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:26:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:23:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:21:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:18:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:16:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:14:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:12:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:10:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:08:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:06:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:03:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 1:00:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:58:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:56:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:54:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:52:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:50:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:41:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:39:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:37:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:35:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:33:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:31:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:28:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:26:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:24:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:22:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:21:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:19:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:17:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:15:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:13:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:11:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:09:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:07:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:05:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:03:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/17/2022 12:01:00 AM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:59:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:58:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:56:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:54:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:52:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:50:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:48:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:46:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:39:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:37:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:35:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:34:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:32:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:30:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:28:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:26:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:24:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:22:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:20:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:18:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:16:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:14:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:12:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:11:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:09:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:07:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:05:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:03:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:03:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 11:01:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 11:01:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:59:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:59:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:56:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:56:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:54:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:54:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:52:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:52:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:50:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:50:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:48:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:48:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:47:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:47:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:45:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:45:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:43:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:43:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:41:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:41:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:39:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:39:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:37:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:37:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:35:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:35:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:33:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:33:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:31:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:31:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:29:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:29:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:27:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:27:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:25:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:25:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:24:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:24:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:22:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:22:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:20:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:20:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:18:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:18:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:16:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:16:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:14:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:14:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:12:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:12:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:10:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:10:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:08:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:08:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:06:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:05:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:03:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:03:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 10:01:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 10:01:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 9:58:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 9:58:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 9:56:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 9:56:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 9:54:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 9:54:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 9:52:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 9:52:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 9:50:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 9:50:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 9:48:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 9:48:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 9:46:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 9:46:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 9:38:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 9:38:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 9:15:00 PM | LRCC-03/16/2022 21:08: Santiago-Bayombong 230kV Line 1 restored at 2108H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 9:15:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 9:06:00 PM | LRCC-03/16/2022 20:27: San Lorenzo Module 50 online at 1931H. (On Commissioning) [WEBSMS] | CLUZ
3/16/2022 9:06:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 9:04:00 PM | LRCC-03/16/2022 20:27: San Lorenzo Module 50 online at 1931H. (On Commissioning) [WEBSMS] | CLUZ
3/16/2022 9:04:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 9:02:00 PM | LRCC-03/16/2022 20:27: San Lorenzo Module 50 online at 1931H. (On Commissioning) [WEBSMS] | CLUZ
3/16/2022 9:02:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 9:00:00 PM | LRCC-03/16/2022 20:27: San Lorenzo Module 50 online at 1931H. (On Commissioning) [WEBSMS] | CLUZ
3/16/2022 9:00:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:58:00 PM | LRCC-03/16/2022 20:27: San Lorenzo Module 50 online at 1931H. (On Commissioning) [WEBSMS] | CLUZ
3/16/2022 8:58:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:55:00 PM | LRCC-03/16/2022 20:27: San Lorenzo Module 50 online at 1931H. (On Commissioning) [WEBSMS] | CLUZ
3/16/2022 8:55:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:53:00 PM | LEYTE ACC-03/16/22 20:43: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2021H/2031H on normal power flow per RTD. Weather: Fair. | CVIS
3/16/2022 8:53:00 PM | LRCC-03/16/2022 20:27: San Lorenzo Module 50 online at 1931H. (On Commissioning) [WEBSMS] | CLUZ
3/16/2022 8:51:00 PM | LEYTE ACC-03/16/22 20:43: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2021H/2031H on normal power flow per RTD. Weather: Fair. | CVIS
3/16/2022 8:51:00 PM | LRCC-03/16/2022 20:27: San Lorenzo Module 50 online at 1931H. (On Commissioning) [WEBSMS] | CLUZ
3/16/2022 8:50:00 PM | LEYTE ACC-03/16/22 20:43: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2021H/2031H on normal power flow per RTD. Weather: Fair. | CVIS
3/16/2022 8:50:00 PM | LRCC-03/16/2022 20:27: San Lorenzo Module 50 online at 1931H. (On Commissioning) [WEBSMS] | CLUZ
3/16/2022 8:48:00 PM | LEYTE ACC-03/16/22 20:43: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2021H/2031H on normal power flow per RTD. Weather: Fair. | CVIS
3/16/2022 8:48:00 PM | LRCC-03/16/2022 20:27: San Lorenzo Module 50 online at 1931H. (On Commissioning) [WEBSMS] | CLUZ
3/16/2022 8:46:00 PM | LEYTE ACC-03/16/22 20:43: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2021H/2031H on normal power flow per RTD. Weather: Fair. | CVIS
3/16/2022 8:46:00 PM | LRCC-03/16/2022 20:27: San Lorenzo Module 50 online at 1931H. (On Commissioning) [WEBSMS] | CLUZ
3/16/2022 8:28:00 PM | LRCC-03/16/2022 20:27: San Lorenzo Module 50 online at 1931H. (On Commissioning) [WEBSMS] | CLUZ
3/16/2022 8:28:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:27:00 PM | LRCC-03/16/2022 20:27: San Lorenzo Module 50 online at 1931H. (On Commissioning) [WEBSMS] | CLUZ
3/16/2022 8:25:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 8:25:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:23:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 8:23:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:21:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 8:21:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:19:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 8:19:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:17:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 8:17:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:15:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 8:15:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:13:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 8:13:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:11:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 8:11:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:09:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 8:09:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:07:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 8:07:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:05:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:04:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 8:04:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:02:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 8:02:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 8:00:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 8:00:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 7:58:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 7:58:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 7:56:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 7:56:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 7:54:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 7:54:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 7:52:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 7:52:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 7:50:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 7:50:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 7:41:00 PM | LRCC-03/16/2022 19:34: Santiago-Bayombong 230kV Line 2 restored at 1928H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 7:41:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 7:32:00 PM | LRCC-03/16/2022 18:51: Santiago-Bayombong 230kV Lines 1 and 2 tripped at 1841H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 7:32:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:58:00 PM | LRCC-03/16/2022 18:51: Santiago-Bayombong 230kV Lines 1 and 2 tripped at 1841H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 6:58:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:56:00 PM | LRCC-03/16/2022 18:51: Santiago-Bayombong 230kV Lines 1 and 2 tripped at 1841H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 6:56:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:54:00 PM | LRCC-03/16/2022 18:51: Santiago-Bayombong 230kV Lines 1 and 2 tripped at 1841H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 6:54:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:52:00 PM | LRCC-03/16/2022 18:51: Santiago-Bayombong 230kV Lines 1 and 2 tripped at 1841H. (Unplanned Outage) [WEBSMS] | CLUZ
3/16/2022 6:52:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:50:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:50:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:49:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:49:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:47:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:47:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:45:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:45:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:39:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:39:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:37:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:37:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:35:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:35:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:33:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:33:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:31:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:31:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:29:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:29:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:27:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:27:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:26:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:26:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:24:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:24:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:22:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:22:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:20:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:20:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:18:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:18:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:16:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:16:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:14:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:14:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:12:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:12:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:09:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:09:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:07:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:07:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:05:00 PM | LRCC-03/16/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11373MW, PK=10144MW, RR=392MW, NetOpMargin: EVE=837 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @813MW [WEBSMS] | CLUZ
3/16/2022 6:05:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:03:00 PM | VRCC-03/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2243MW, PK=1929MW, RR=74MW, NetOpMargin: EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:02:00 PM | LEYTE ACC-03/16/22 18:00: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1737H/1747H on reverse power flow per RTD. Weather: Fair. | CVIS
3/16/2022 5:23:00 PM | LRCC-03/16/2022 14:24: Sta. Rita 40 changeover from gas to oil at 1419H. [WEBSMS] | CLUZ
3/16/2022 5:23:00 PM | LRCC-03/16/2022 16:39: San Lorenzo 50 tripped 1634H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 5:23:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 5:21:00 PM | LRCC-03/16/2022 16:39: San Lorenzo 50 tripped 1634H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 5:21:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 5:19:00 PM | LRCC-03/16/2022 16:39: San Lorenzo 50 tripped 1634H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 5:19:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 5:17:00 PM | LRCC-03/16/2022 16:39: San Lorenzo 50 tripped 1634H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 5:17:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 5:15:00 PM | LRCC-03/16/2022 16:39: San Lorenzo 50 tripped 1634H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 5:15:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 5:13:00 PM | LRCC-03/16/2022 16:39: San Lorenzo 50 tripped 1634H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 5:13:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 5:11:00 PM | LRCC-03/16/2022 16:39: San Lorenzo 50 tripped 1634H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 5:11:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 5:09:00 PM | LRCC-03/16/2022 16:39: San Lorenzo 50 tripped 1634H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 5:09:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 5:07:00 PM | LRCC-03/16/2022 16:39: San Lorenzo 50 tripped 1634H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 5:07:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 5:06:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 5:06:00 PM | LRCC-03/16/2022 16:39: San Lorenzo 50 tripped 1634H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 5:06:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:40:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 4:40:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:38:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:38:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:36:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:36:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:34:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:34:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:32:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:32:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:31:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:31:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:29:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:29:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:27:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:27:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:25:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:25:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:23:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:23:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:21:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:21:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:19:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:18:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:17:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:16:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:15:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:14:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:12:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:12:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:10:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:10:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:08:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:08:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:07:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:07:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:05:00 PM | LRCC-03/16/2022 14:24: Sta. Rita 40 changeover from gas to oil at 1419H. [WEBSMS] | CLUZ
3/16/2022 4:05:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:05:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:03:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:03:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 4:01:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 4:01:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:59:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:59:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:57:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:57:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:55:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:55:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:53:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:53:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:51:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:51:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:49:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:49:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:47:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:47:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:45:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:45:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:44:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:44:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:42:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:42:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:40:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 3:40:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:40:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:38:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:38:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:36:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:36:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:34:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:34:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:32:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 3:32:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:32:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:30:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:30:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:28:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:28:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:27:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 3:25:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:25:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:23:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:23:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:21:00 PM | LRCC-03/16/2022 14:24: Sta. Rita 40 changeover from gas to oil at 1419H. [WEBSMS] | CLUZ
3/16/2022 3:21:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:21:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:02:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:02:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 3:00:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 3:00:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:58:00 PM | LRCC-03/16/2022 14:58: San Lorenzo 50 on line 1450H (on commissioning). [WEBSMS] | CLUZ
3/16/2022 2:58:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:56:00 PM | LRCC-03/16/2022 14:24: Sta. Rita 40 changeover from gas to oil at 1419H. [WEBSMS] | CLUZ
3/16/2022 2:56:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:54:00 PM | LRCC-03/16/2022 14:24: Sta. Rita 40 changeover from gas to oil at 1419H. [WEBSMS] | CLUZ
3/16/2022 2:54:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:52:00 PM | LRCC-03/16/2022 14:24: Sta. Rita 40 changeover from gas to oil at 1419H. [WEBSMS] | CLUZ
3/16/2022 2:52:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:50:00 PM | LRCC-03/16/2022 14:24: Sta. Rita 40 changeover from gas to oil at 1419H. [WEBSMS] | CLUZ
3/16/2022 2:50:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:48:00 PM | LRCC-03/16/2022 14:24: Sta. Rita 40 changeover from gas to oil at 1419H. [WEBSMS] | CLUZ
3/16/2022 2:48:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:47:00 PM | LRCC-03/16/2022 14:24: Sta. Rita 40 changeover from gas to oil at 1419H. [WEBSMS] | CLUZ
3/16/2022 2:47:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:45:00 PM | LRCC-03/16/2022 14:24: Sta. Rita 40 changeover from gas to oil at 1419H. [WEBSMS] | CLUZ
3/16/2022 2:45:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:42:00 PM | LRCC-03/16/2022 14:24: Sta. Rita 40 changeover from gas to oil at 1419H. [WEBSMS] | CLUZ
3/16/2022 2:42:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:24:00 PM | LRCC-03/16/2022 14:24: Sta. Rita 40 changeover from gas to oil at 1419H. [WEBSMS] | CLUZ
3/16/2022 2:24:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:23:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 2:22:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:21:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 2:19:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 2:19:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:17:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 2:17:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:15:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 2:15:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:13:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 2:13:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:11:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 2:11:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:09:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 2:09:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:07:00 PM | LRCC-03/16/2022 10:13: GNPD 1 tripped at 1005H, lowest frequency at 58.855Hz (Unplanned Outage). [WEBSMS] | CLUZ
3/16/2022 2:07:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 2:07:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:05:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 2:05:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:03:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 2:03:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:01:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 2:01:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 2:00:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 2:00:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:58:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:58:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:56:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:56:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:54:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:54:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:52:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:51:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:49:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:49:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:47:00 PM | LRCC-03/16/2022 10:13: GNPD 1 tripped at 1005H, lowest frequency at 58.855Hz (Unplanned Outage). [WEBSMS] | CLUZ
3/16/2022 1:47:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:47:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:45:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:45:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:39:00 PM | LRCC-03/16/2022 10:13: GNPD 1 tripped at 1005H, lowest frequency at 58.855Hz (Unplanned Outage). [WEBSMS] | CLUZ
3/16/2022 1:39:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:39:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:37:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:37:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:36:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:36:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:34:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:34:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:32:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:32:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:30:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:30:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:28:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:28:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:26:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:26:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:24:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:24:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:22:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 1:22:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:22:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:20:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:20:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:18:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:18:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:16:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:16:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:14:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:14:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 1:13:00 PM | LRCC-03/16/2022 10:13: GNPD 1 tripped at 1005H, lowest frequency at 58.855Hz (Unplanned Outage). [WEBSMS] | CLUZ
3/16/2022 1:13:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 1:13:00 PM | VRCC-03/16/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2425MW, PK=2013MW, RR=76MW, NetOpMargin: PM=336, EVE=240 Highest Unit O/L: TVI U @169MW. Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 12:48:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 12:46:00 PM | LRCC-03/16/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11957MW, PK=10861MW, RR=431MW, NetOpMargin: PM=665, EVE=1080 Highest Unit O/L: Sual 1 @600MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 12:38:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 12:36:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 12:35:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 12:33:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 12:31:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 12:25:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 12:23:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 12:21:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 12:19:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 12:17:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 12:10:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 12:06:00 PM | LRCC-03/16/2022 10:13: GNPD 1 tripped at 1005H, lowest frequency at 58.855Hz (Unplanned Outage). [WEBSMS] | CLUZ
3/16/2022 12:06:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 12:02:00 PM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 11:59:00 AM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 11:57:00 AM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 11:55:00 AM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 11:53:00 AM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 11:51:00 AM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 11:49:00 AM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 11:48:00 AM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 11:46:00 AM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 11:44:00 AM | LRCC-03/16/2022 10:13: GNPD 1 tripped at 1005H, lowest frequency at 58.855Hz (Unplanned Outage). [WEBSMS] | CLUZ
3/16/2022 11:44:00 AM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 11:42:00 AM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 11:25:00 AM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 11:01:00 AM | LRCC-03/16/2022 10:13: GNPD 1 tripped at 1005H, lowest frequency at 58.855Hz (Unplanned Outage). [WEBSMS] | CLUZ
3/16/2022 11:01:00 AM | LRCC-03/16/2022 10:40: ALD restored; NGCP at 1024H, Meralco at 1030H during the tripping of GNPD (668MW) at 1005H. [WEBSMS] | CLUZ
3/16/2022 10:21:00 AM | LRCC-03/16/2022 10:13: GNPD 1 tripped at 1005H, lowest frequency at 58.855Hz (Unplanned Outage). [WEBSMS] | CLUZ
3/16/2022 10:19:00 AM | LRCC-03/16/2022 10:13: GNPD 1 tripped at 1005H, lowest frequency at 58.855Hz (Unplanned Outage). [WEBSMS] | CLUZ
3/16/2022 10:17:00 AM | LRCC-03/16/2022 10:13: GNPD 1 tripped at 1005H, lowest frequency at 58.855Hz (Unplanned Outage). [WEBSMS] | CLUZ
3/16/2022 10:15:00 AM | LRCC-03/16/2022 10:13: GNPD 1 tripped at 1005H, lowest frequency at 58.855Hz (Unplanned Outage). [WEBSMS] | CLUZ
3/16/2022 6:10:00 AM | VRCC-03/16/2022 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2445MW, PK=1967MW, RR=40MW, NetOpMargin: AM=438, PM=372, EVE=274 Highest Unit O/L: TVI U @169MW Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 6:08:00 AM | VRCC-03/16/2022 06:07: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2445MW, PK=1967MW, RR=40MW, NetOpMargin: AM=438, PM=372, EVE=274 Highest Unit O/L: TVI U @169MW Derated Plant: EDC = 396 MW, PEDC = 234 MW, LGPP 1 = 80 MW, TPC = 82 MW, KSPC = 103 MW, PGPP 1 = 70 MW [WEBSMS] | CVIS
3/16/2022 5:43:00 AM | LRCC-03/16/2022 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12116MW, PK=10438MW, RR=422MW, NetOpMargin: AM=1256, PM=685, EVE=1110 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @778MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 5:40:00 AM | LRCC-03/16/2022 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12116MW, PK=10438MW, RR=422MW, NetOpMargin: AM=1256, PM=685, EVE=1110 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @778MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/16/2022 4:09:00 AM | MRCC-03/16/2022 04:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2746MW, PK=1930MW, RR=77MW, NetOpMargin: AM=739, PM=672, EVE=815 Highest Unit O/L: GNPK U2 and U4 @ 138MW each. Derated Plant: Ag1@46MW, Ag2@82MW, Ag4@143MW, Ag5@42MW, Ag6@53MW, Ag7@0.0MW, Pul4@131MW, MGPP@75MW, STEAG@100MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@100MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/16/2022 3:51:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 3:49:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 3:47:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 3:45:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 3:43:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 3:41:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 3:39:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 3:37:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 3:35:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 3:33:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 3:31:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 3:29:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 3:28:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 3:26:00 AM | PANAY ACC-03/16/22 03:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:08:00, TIME IN: 03:20:00, RELAY: Z1 BCN 46.38KMS, Load: 19.55mw, under investigation, WEATHER: FAIR | CVIS
3/16/2022 1:07:00 AM | LRCC-03/16/2022 01:06: Malaya 2 shutdown at 0102H. (Planned outage) [WEBSMS] | CLUZ
3/15/2022 8:45:00 PM | LEYTE ACC-03/15/22 20:33: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2008H/2019H on normal power flow per RTD. Weather: Fair. | CVIS
3/15/2022 8:43:00 PM | LEYTE ACC-03/15/22 20:33: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2008H/2019H on normal power flow per RTD. Weather: Fair. | CVIS
3/15/2022 8:41:00 PM | LEYTE ACC-03/15/22 20:33: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2008H/2019H on normal power flow per RTD. Weather: Fair. | CVIS
3/15/2022 8:39:00 PM | LEYTE ACC-03/15/22 20:33: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2008H/2019H on normal power flow per RTD. Weather: Fair. | CVIS
3/15/2022 8:37:00 PM | LEYTE ACC-03/15/22 20:33: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2008H/2019H on normal power flow per RTD. Weather: Fair. | CVIS
3/15/2022 8:35:00 PM | LEYTE ACC-03/15/22 20:33: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2008H/2019H on normal power flow per RTD. Weather: Fair. | CVIS
3/15/2022 8:33:00 PM | LEYTE ACC-03/15/22 20:33: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2008H/2019H on normal power flow per RTD. Weather: Fair. | CVIS
3/15/2022 8:31:00 PM | LEYTE ACC-03/15/22 20:33: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2008H/2019H on normal power flow per RTD. Weather: Fair. | CVIS
3/15/2022 8:24:00 PM | LEYTE ACC-03/15/22 20:33: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 2008H/2019H on normal power flow per RTD. Weather: Fair. | CVIS
3/15/2022 6:54:00 PM | MRCC-03/15/2022 17:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2811MW, PK=1810MW, RR=72MW, NetOpMargin: EVE=929 Highest Unit O/L: GNPK U2 and U4 @ 138MW each. Derated Plant: Ag1@46MW, Ag2@82MW, Ag4@147MW, Ag5@25MW, Ag6@63MW, Ag7@0.0MW, Pul4@131MW, MGPP@75MW, STEAG@200MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@100MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/15/2022 6:22:00 PM | LRCC-03/15/2022 18:20: Nagsaag-Binga 230kV L2 tripped/reclosed at 1747H (Unplanned Outage). [WEBSMS] | CLUZ
3/15/2022 5:58:00 PM | LRCC-03/15/2022 17:55: Nagsaag-Binga 230kV L1 tripped at 1746H (Unplanned Outage). [WEBSMS] | CLUZ
3/15/2022 5:56:00 PM | LRCC-03/15/2022 17:55: Nagsaag-Binga 230kV L1 tripped at 1746H (Unplanned Outage). [WEBSMS] | CLUZ
3/15/2022 5:32:00 PM | LRCC-03/15/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11685MW, PK=10117MW, RR=383MW, NetOpMargin: EVE=1185 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @777MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/15/2022 5:30:00 PM | LRCC-03/15/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11685MW, PK=10117MW, RR=383MW, NetOpMargin: EVE=1185 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @777MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/15/2022 4:20:00 PM | LEYTE ACC-03/15/22 16:06: BABATNGON SS, Babatngon - Abucay 69kV Line restored at 1549H, back to normal operation. Weather: Fair. | CVIS
3/15/2022 4:18:00 PM | LEYTE ACC-03/15/22 16:06: BABATNGON SS, Babatngon - Abucay 69kV Line restored at 1549H, back to normal operation. Weather: Fair. | CVIS
3/15/2022 4:17:00 PM | LEYTE ACC-03/15/22 16:06: BABATNGON SS, Babatngon - Abucay 69kV Line restored at 1549H, back to normal operation. Weather: Fair. | CVIS
3/15/2022 4:08:00 PM | LEYTE ACC-03/15/22 16:06: BABATNGON SS, Babatngon - Abucay 69kV Line restored at 1549H, back to normal operation. Weather: Fair. | CVIS
3/15/2022 4:06:00 PM | LEYTE ACC-03/15/22 16:06: BABATNGON SS, Babatngon - Abucay 69kV Line restored at 1549H, back to normal operation. Weather: Fair. | CVIS
3/15/2022 4:04:00 PM | LEYTE ACC-03/15/22 16:06: BABATNGON SS, Babatngon - Abucay 69kV Line restored at 1549H, back to normal operation. Weather: Fair. | CVIS
3/15/2022 4:02:00 PM | LEYTE ACC-03/15/22 16:06: BABATNGON SS, Babatngon - Abucay 69kV Line restored at 1549H, back to normal operation. Weather: Fair. | CVIS
3/15/2022 4:00:00 PM | LEYTE ACC-03/15/22 16:06: BABATNGON SS, Babatngon - Abucay 69kV Line restored at 1549H, back to normal operation. Weather: Fair. | CVIS
3/15/2022 4:00:00 PM | LRCC-03/15/2022 15:58: Sta. Rita 40 change over from oil to gas at 1536H. [WEBSMS] | CLUZ
3/15/2022 3:54:00 PM | LEYTE ACC-03/15/22 15:57: BABATNGON SS, Babatngon - Abucay 69kV Line tripped at 1536H, ind.: Phase-C & F.D.=18.22kms. Load=45.77MW. Weather: Fair. | CVIS
3/15/2022 3:53:00 PM | LEYTE ACC-03/15/22 15:57: BABATNGON SS, Babatngon - Abucay 69kV Line tripped at 1536H, ind.: Phase-C & F.D.=18.22kms. Load=45.77MW. Weather: Fair. | CVIS
3/15/2022 3:51:00 PM | LEYTE ACC-03/15/22 15:57: BABATNGON SS, Babatngon - Abucay 69kV Line tripped at 1536H, ind.: Phase-C & F.D.=18.22kms. Load=45.77MW. Weather: Fair. | CVIS
3/15/2022 3:49:00 PM | LEYTE ACC-03/15/22 15:57: BABATNGON SS, Babatngon - Abucay 69kV Line tripped at 1536H, ind.: Phase-C & F.D.=18.22kms. Load=45.77MW. Weather: Fair. | CVIS
3/15/2022 3:05:00 PM | LRCC-03/15/2022 15:04: Quezon-Mexico 20kV Line looped at Quezon breaker CB04(8LI1QUE-MEX)QUE upon the repair of compressor motor at 1458H (Unplanned Outage). [WEBSMS] | CLUZ
3/15/2022 2:57:00 PM | MRCC-03/15/2022 11:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2851MW, PK=1990MW, RR=135MW, NetOpMargin: PM=781, EVE=929 Highest Unit O/L: GNPK U2 and U4 @ 138MW each. Derated Plant: Ag1@46MW, Ag2@82MW, Ag4@147MW, Ag5@25MW, Ag6@63MW, Ag7@0.0MW, Pul4@131MW, MGPP@75MW, STEAG@200MW, TSI@270MW, FDC@ 244.5MW, GNPK@276MW, SMCPC@270MW, MCC@100MW, SEC1@105MW, SEC2@105MW. [WEBSMS] | CMIN
3/15/2022 2:16:00 PM | LEYTE ACC-03/15/22 13:35: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1320H/1330H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/15/2022 2:14:00 PM | LEYTE ACC-03/15/22 13:35: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1320H/1330H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/15/2022 2:12:00 PM | LEYTE ACC-03/15/22 13:35: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1320H/1330H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/15/2022 2:10:00 PM | LEYTE ACC-03/15/22 13:35: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1320H/1330H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/15/2022 2:09:00 PM | LEYTE ACC-03/15/22 13:35: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1320H/1330H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/15/2022 2:07:00 PM | LEYTE ACC-03/15/22 13:35: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1320H/1330H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/15/2022 2:05:00 PM | LEYTE ACC-03/15/22 13:35: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1320H/1330H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/15/2022 2:03:00 PM | LEYTE ACC-03/15/22 13:35: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1320H/1330H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/15/2022 2:01:00 PM | LEYTE ACC-03/15/22 13:35: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1320H/1330H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/15/2022 1:59:00 PM | LEYTE ACC-03/15/22 13:35: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1320H/1330H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/15/2022 1:57:00 PM | LEYTE ACC-03/15/22 13:35: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1320H/1330H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/15/2022 1:55:00 PM | LEYTE ACC-03/15/22 13:35: ORMOC CONVERTER STATION SS, 350kV HVDC manually blocked/deblocked at 1320H/1330H, on reverse power flow per RTD. WEATHER: FAIR | CVIS
3/15/2022 1:00:00 PM | VRCC-03/15/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2463MW, PK=1981MW, RR=36MW, NetOpMargin: PM=446, EVE=296 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW [WEBSMS] | CVIS
3/15/2022 9:24:00 AM | VRCC-03/15/2022 09:22: 138 KV Colon - KSPC Line 2 de-energized at 0919H, KSPC request [WEBSMS] | CVIS
3/15/2022 9:21:00 AM | VRCC-03/15/2022 09:22: 138 KV Colon - KSPC Line 2 de-energized at 0919H, KSPC request [WEBSMS] | CVIS
3/15/2022 8:39:00 AM | LRCC-03/15/2022 08:38: Angat Main transformer B de-energized at 0836H (Planned Outage). [WEBSMS] | CLUZ
3/15/2022 8:05:00 AM | LRCC-03/15/2022 08:04: Maximum peak of the year is 10656MW occurred on March 14, 2022 at 1400H. [WEBSMS] | CLUZ
3/15/2022 7:24:00 AM | LRCC-03/15/2022 07:22: Malaya 2 on line at 0717H (Planned Outage). [WEBSMS] | CLUZ
3/15/2022 7:18:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 7:16:00 AM | PANAY ACC-03/15/22 06:23: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 06:22:00, WEATHER: FAIR; To facilitate load transfer of ANTECO Culasi Ss to Nabas Ss. | CVIS
3/15/2022 7:16:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 7:15:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 7:13:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 7:11:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 7:08:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 7:06:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 7:04:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 7:02:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 7:00:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 6:54:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 6:52:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 6:51:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 6:49:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 6:47:00 AM | LRCC-03/15/2022 06:44: Muntinlupa 300MVA T03 restored at 0644H (Planned Outage). [WEBSMS] | CLUZ
3/15/2022 6:47:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 6:45:00 AM | LRCC-03/15/2022 06:44: Muntinlupa 300MVA T03 restored at 0644H (Planned Outage). [WEBSMS] | CLUZ
3/15/2022 6:45:00 AM | PANAY ACC-03/15/22 06:41: NABAS SS, Nabas-Culasi 69 kV L (5LI1NBS-CRD), TIME IN: 06:41:00, WEATHER: FAIR; ANTECO Culasi Ss normalized to Nabas Ss. | CVIS
3/15/2022 6:43:00 AM | PANAY ACC-03/15/22 06:33: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME IN: 06:32:00, WEATHER: FAIR | CVIS
3/15/2022 6:41:00 AM | PANAY ACC-03/15/22 06:33: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME IN: 06:32:00, WEATHER: FAIR | CVIS
3/15/2022 6:39:00 AM | PANAY ACC-03/15/22 06:33: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME IN: 06:32:00, WEATHER: FAIR | CVIS
3/15/2022 6:37:00 AM | PANAY ACC-03/15/22 06:33: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME IN: 06:32:00, WEATHER: FAIR | CVIS
3/15/2022 6:35:00 AM | PANAY ACC-03/15/22 06:33: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME IN: 06:32:00, WEATHER: FAIR | CVIS
3/15/2022 6:33:00 AM | PANAY ACC-03/15/22 06:23: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 06:22:00, WEATHER: FAIR; To facilitate load transfer of ANTECO Culasi Ss to Nabas Ss. | CVIS
3/15/2022 5:58:00 AM | LRCC-03/15/2022 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12310MW, PK=10361MW, RR=408MW, NetOpMargin: AM=1541, PM=1145, EVE=1433 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/15/2022 5:56:00 AM | LRCC-03/15/2022 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12310MW, PK=10361MW, RR=408MW, NetOpMargin: AM=1541, PM=1145, EVE=1433 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @817MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/15/2022 5:56:00 AM | NEGROS ACC: 03/15/2022, PGPP1 U3 (32.8 MW) auto-tripped at 0452H with indication condenser vacuum very Low. | CVIS
3/15/2022 5:54:00 AM | NEGROS ACC: 03/15/2022, PGPP1 U3 (32.8 MW) auto-tripped at 0452H with indication condenser vacuum very Low. | CVIS
3/15/2022 5:52:00 AM | NEGROS ACC: 03/15/2022, PGPP1 U3 (32.8 MW) auto-tripped at 0452H with indication condenser vacuum very Low. | CVIS
3/15/2022 5:50:00 AM | NEGROS ACC: 03/15/2022, PGPP1 U3 (32.8 MW) auto-tripped at 0452H with indication condenser vacuum very Low. | CVIS
3/15/2022 5:48:00 AM | NEGROS ACC: 03/15/2022, PGPP1 U3 (32.8 MW) auto-tripped at 0452H with indication condenser vacuum very Low. | CVIS
3/15/2022 5:46:00 AM | NEGROS ACC: 03/15/2022, PGPP1 U3 (32.8 MW) auto-tripped at 0452H with indication condenser vacuum very Low. | CVIS
3/15/2022 5:44:00 AM | NEGROS ACC: 03/15/2022, PGPP1 U3 (32.8 MW) auto-tripped at 0452H with indication condenser vacuum very Low. | CVIS
3/15/2022 5:42:00 AM | NEGROS ACC: 03/15/2022, PGPP1 U3 (32.8 MW) auto-tripped at 0452H with indication condenser vacuum very Low. | CVIS
3/15/2022 5:41:00 AM | NEGROS ACC: 03/15/2022, PGPP1 U3 (32.8 MW) auto-tripped at 0452H with indication condenser vacuum very Low. | CVIS
3/15/2022 5:39:00 AM | NEGROS ACC: 03/15/2022, PGPP1 U3 (32.8 MW) auto-tripped at 0452H with indication condenser vacuum very Low. | CVIS
3/15/2022 4:32:00 AM | MRCC-03/15/2022 04:30: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2841MW, PK=1900MW, RR=55MW, NetOpMargin: AM=865, PM=805, EVE=927 Highest Unit O/L: GNPOWER U2 & U4 @ 138MW each unit. Derated Plant: Ag1@44MW, Ag2@80MW, Ag4@146MW, Ag5@27MW, Ag6@70MW, Ag7@0MW, Pul4@123MW, MGPP@75MW, STEAG@200MW, FMP@245MW, GNPK@276MW, and MCC@100MW. [WEBSMS] | CMIN
3/15/2022 4:31:00 AM | LRCC-03/15/2022 04:31: San Jose 750MVA T04 restored at 0428H (Planned Outage) [WEBSMS] | CLUZ
3/15/2022 2:26:00 AM | LRCC-03/15/2022 02:26: Quezon breaker CB04(8LI1QUE-MEX)QUE (Quezon-Mexico 20kV Line) de-energized at 0225H (Unplanned Outage). [WEBSMS] | CLUZ
3/14/2022 9:23:00 PM | LRCC-03/14/2022 21:20: San Jose 750MVA T04 de-energized at 2119H (Planned Outage). [WEBSMS] | CLUZ
3/14/2022 9:21:00 PM | LRCC-03/14/2022 21:20: San Jose 750MVA T04 de-energized at 2119H (Planned Outage). [WEBSMS] | CLUZ
3/14/2022 8:40:00 PM | LRCC-03/14/2022 20:39: Muntinlupa 300MVA T03 de-energized at 2039H (Planned Outage). [WEBSMS] | CLUZ
3/14/2022 6:02:00 PM | VRCC-03/14/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2269MW, PK=1882MW, RR=40MW, NetOpMargin: EVE=347 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW [WEBSMS] | CVIS
3/14/2022 6:00:00 PM | VRCC-03/14/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2269MW, PK=1882MW, RR=40MW, NetOpMargin: EVE=347 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW [WEBSMS] | CVIS
3/14/2022 5:28:00 PM | LRCC-03/14/2022 17:26: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11761MW, PK=9968MW, RR=389MW, NetOpMargin: EVE=1404 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @851MW; SAN GABRIEL @211MW [WEBSMS] | CLUZ
3/14/2022 5:26:00 PM | LRCC-03/14/2022 17:26: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11761MW, PK=9968MW, RR=389MW, NetOpMargin: EVE=1404 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @851MW; SAN GABRIEL @211MW [WEBSMS] | CLUZ
3/14/2022 4:34:00 PM | MRCC-03/14/2022 16:32: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2740MW, PK=1770MW, RR=55MW, NetOpMargin: EVE=900 Highest Unit O/L: GNPOWER U2 & U4 @ 138MW each unit. Derated Plant: Ag1@42MW, Ag2@78MW, Ag4@146MW, Ag5@27MW, Ag6@20MW, Ag7@0MW, Pul4@124MW, MGPP@75MW, STEAG@200MW, FMP@245MW, GNPK@276MW, and MCC@100MW. [WEBSMS] | CMIN
3/14/2022 4:00:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:58:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:56:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:54:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:52:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:50:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:49:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:47:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:45:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:43:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:41:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:39:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:37:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:35:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:33:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:31:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:29:00 PM | PANAY ACC-03/14/22 15:19: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 03:11:00 | CVIS
3/14/2022 3:27:00 PM | PANAY ACC-03/14/22 15:08: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME OUT: 03:05:00, Load: 41.8mw, RELAY: Z2 L2L3 BC 22.1KMS, under investigation, WEATHER: FAIR | CVIS
3/14/2022 3:09:00 PM | LEYTE ACC-03/14/22: ORMOC SS, 230kV Ormoc-HVDC Line tripped at 1439H, indications to follow, WEATHER: RAINY | CVIS
3/14/2022 3:07:00 PM | LEYTE ACC-03/14/22: ORMOC SS, 230kV Ormoc-HVDC Line tripped at 1439H, indications to follow, WEATHER: RAINY | CVIS
3/14/2022 3:05:00 PM | LEYTE ACC-03/14/22: ORMOC SS, 230kV Ormoc-HVDC Line tripped at 1439H, indications to follow, WEATHER: RAINY | CVIS
3/14/2022 3:03:00 PM | LEYTE ACC-03/14/22: ORMOC SS, 230kV Ormoc-HVDC Line tripped at 1439H, indications to follow, WEATHER: RAINY | CVIS
3/14/2022 3:02:00 PM | LEYTE ACC-03/14/22: ORMOC SS, 230kV Ormoc-HVDC Line tripped at 1439H, indications to follow, WEATHER: RAINY | CVIS
3/14/2022 3:00:00 PM | LEYTE ACC-03/14/22: ORMOC SS, 230kV Ormoc-HVDC Line tripped at 1439H, indications to follow, WEATHER: RAINY | CVIS
3/14/2022 2:54:00 PM | LEYTE ACC-03/14/22: ORMOC SS, 230kV Ormoc-HVDC Line tripped at 1439H, indications to follow, WEATHER: RAINY | CVIS
3/14/2022 2:52:00 PM | LEYTE ACC-03/14/22: ORMOC SS, 230kV Ormoc-HVDC Line tripped at 1439H, indications to follow, WEATHER: RAINY | CVIS
3/14/2022 2:50:00 PM | LEYTE ACC-03/14/22: ORMOC SS, 230kV Ormoc-HVDC Line tripped at 1439H, indications to follow, WEATHER: RAINY | CVIS
3/14/2022 2:48:00 PM | LEYTE ACC-03/14/22: ORMOC SS, 230kV Ormoc-HVDC Line tripped at 1439H, indications to follow, WEATHER: RAINY | CVIS
3/14/2022 1:01:00 PM | VRCC-03/14/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2475MW, PK=1856MW, RR=36MW, NetOpMargin: PM=583, EVE=359 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW [WEBSMS] | CVIS
3/14/2022 12:23:00 PM | LRCC-03/14/2022 12:21: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12182MW, PK=10540MW, RR=401MW, NetOpMargin: PM=1241, EVE=1569 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @851MW; SAN GABRIEL @211MW [WEBSMS] | CLUZ
3/14/2022 12:21:00 PM | LRCC-03/14/2022 12:21: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12182MW, PK=10540MW, RR=401MW, NetOpMargin: PM=1241, EVE=1569 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @851MW; SAN GABRIEL @211MW [WEBSMS] | CLUZ
3/14/2022 11:06:00 AM | VRCC-03/14/2022 11:05: Daan Bantayan SS 69 KV Lanao Feeder energized at 1057H, with clearance from CEBECO 2 [WEBSMS] | CVIS
3/14/2022 11:04:00 AM | VRCC-03/14/2022 11:05: Daan Bantayan SS 69 KV Lanao Feeder energized at 1057H, with clearance from CEBECO 2 [WEBSMS] | CVIS
3/14/2022 10:58:00 AM | MRCC-03/14/2022 10:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2811MW, PK=1890MW, RR=71MW, NetOpMargin: PM=845, EVE=900 Highest Unit O/L: GNPOWER U2 * U4 @ 138MW each unit. Derated Plant: Ag1@46MW, Ag2@80MW, Ag4@137MW, Ag5@27MW, Ag6@20MW, Ag7@0MW, Pul4@130MW, MGPP@75MW, STEAG@200MW, FMP@245MW, GNPK@276MW, and MCC@100MW. [WEBSMS] | CMIN
3/14/2022 10:12:00 AM | VRCC-03/14/2022 10:11: Daan Bantayan SS 69 KV Lanao Feeder auto-tripped at 0957H with 22.6 MW load, OCR activation (phase AB), weather: fair [WEBSMS] | CVIS
3/14/2022 8:22:00 AM | LRCC-03/14/2022 08:21: Dispatch function transfer from CLACC to LRCC (near NCC gate using Laptop) at 0537H while waiting clearance for entering NCC building. [WEBSMS] | CLUZ
3/14/2022 8:20:00 AM | LRCC-03/14/2022 08:17: Dispatch function of LRCC transfer to CLACC due to earthquake at 0510H. [WEBSMS] | CLUZ
3/14/2022 8:18:00 AM | LRCC-03/14/2022 08:17: Dispatch function of LRCC transfer to CLACC due to earthquake at 0510H. [WEBSMS] | CLUZ
3/14/2022 7:01:00 AM | VRCC-03/14/2022 06:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2508MW, PK=1899MW, RR=56MW, NetOpMargin: AM=553, PM=560, EVE=341 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW [WEBSMS] | CVIS
3/14/2022 6:59:00 AM | VRCC-03/14/2022 06:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2508MW, PK=1899MW, RR=56MW, NetOpMargin: AM=553, PM=560, EVE=341 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW [WEBSMS] | CVIS
3/14/2022 6:08:00 AM | LRCC-03/14/2022 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12320MW, PK=9847MW, RR=395MW, NetOpMargin: AM=2078, PM=1580, EVE=1875 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @91MW; ILJJAN A / B @851MW; SAN GABRIEL @211MW [WEBSMS] | CLUZ
3/14/2022 6:06:00 AM | VRCC-03/14/2022 06:04: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2508MW, PK=1899MW, RR=56MW, NetOpMargin: AM=553, PM=560, EVE=341 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW [WEBSMS] | CVIS
3/14/2022 6:05:00 AM | VRCC-03/14/2022 06:04: GRID UPDATE AS OF 6:00 AM System Condition: YELLOW ALERT CAP=2508MW, PK=1899MW, RR=56MW, NetOpMargin: AM=553, PM=560, EVE=341 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 396 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW [WEBSMS] | CVIS
3/13/2022 9:54:00 PM | VRCC-03/13/2022 21:53: 138 KV Colon-Quiot line energized at 2100H, transformer 100MVA TR2 energized 2141H activity completed. [WEBSMS] | CVIS
3/13/2022 7:01:00 PM | MRCC-03/13/2022 16:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2727MW, PK=1630MW, RR=59MW, NetOpMargin: EVE=1038 Highest Unit O/L: GNPKU2&U4@138MW each; Derated Plant: Ag1@46MW, Ag2@78MW, Ag4@146MW, Ag5@27MW, Ag6@20MW, Ag7@26MW, Pul4@130MW, MGPP@30MW, STEAG@200MW, FMP@245MW, GNPK@276MW, and MCC@100MW. [WEBSMS] | CMIN
3/13/2022 6:18:00 PM | PANAY ACC-03/13/22 17:55: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME IN: 05:49:00, Pre arranged maintenance | CVIS
3/13/2022 6:16:00 PM | PANAY ACC-03/13/22 17:55: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME IN: 05:49:00, Pre arranged maintenance | CVIS
3/13/2022 6:14:00 PM | PANAY ACC-03/13/22 17:55: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME IN: 05:49:00, Pre arranged maintenance | CVIS
3/13/2022 6:12:00 PM | PANAY ACC-03/13/22 17:55: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME IN: 05:49:00, Pre arranged maintenance | CVIS
3/13/2022 6:10:00 PM | PANAY ACC-03/13/22 17:55: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME IN: 05:49:00, Pre arranged maintenance | CVIS
3/13/2022 6:09:00 PM | LRCC-03/13/2022 18:09: Concepcion-San Manuel 230kV Line 1 restored at 1808H (Planned Outage). [WEBSMS] | CLUZ
3/13/2022 6:07:00 PM | PANAY ACC-03/13/22 17:55: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME IN: 05:49:00, Pre arranged maintenance | CVIS
3/13/2022 6:05:00 PM | PANAY ACC-03/13/22 17:55: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME IN: 05:49:00, Pre arranged maintenance | CVIS
3/13/2022 6:03:00 PM | PANAY ACC-03/13/22 17:55: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME IN: 05:49:00, Pre arranged maintenance | CVIS
3/13/2022 6:01:00 PM | PANAY ACC-03/13/22 17:55: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME IN: 05:49:00, Pre arranged maintenance | CVIS
3/13/2022 5:59:00 PM | PANAY ACC-03/13/22 17:55: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME IN: 05:49:00, Pre arranged maintenance | CVIS
3/13/2022 5:57:00 PM | PANAY ACC-03/13/22 17:55: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME IN: 05:49:00, Pre arranged maintenance | CVIS
3/13/2022 5:31:00 PM | LRCC-03/13/2022 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11816MW, PK=8794MW, RR=355MW, NetOpMargin: EVE=2667 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @91MW, GMEC 2 @300MW, Pagbilao 3 @350MW, San Gabriel @210MW & Ilijan @851MW [WEBSMS] | CLUZ
3/13/2022 4:57:00 PM | PANAY ACC-03/13/22 16:30: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME IN: 04:25:00, Pre arranged maintenance | CVIS
3/13/2022 4:55:00 PM | PANAY ACC-03/13/22 16:30: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME IN: 04:25:00, Pre arranged maintenance | CVIS
3/13/2022 4:53:00 PM | PANAY ACC-03/13/22 16:30: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME IN: 04:25:00, Pre arranged maintenance | CVIS
3/13/2022 4:51:00 PM | PANAY ACC-03/13/22 16:30: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME IN: 04:25:00, Pre arranged maintenance | CVIS
3/13/2022 4:49:00 PM | PANAY ACC-03/13/22 16:30: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME IN: 04:25:00, Pre arranged maintenance | CVIS
3/13/2022 4:47:00 PM | PANAY ACC-03/13/22 16:30: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME IN: 04:25:00, Pre arranged maintenance | CVIS
3/13/2022 4:45:00 PM | PANAY ACC-03/13/22 16:30: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME IN: 04:25:00, Pre arranged maintenance | CVIS
3/13/2022 4:43:00 PM | PANAY ACC-03/13/22 16:30: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME IN: 04:25:00, Pre arranged maintenance | CVIS
3/13/2022 4:41:00 PM | PANAY ACC-03/13/22 16:30: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME IN: 04:25:00, Pre arranged maintenance | CVIS
3/13/2022 4:39:00 PM | PANAY ACC-03/13/22 16:30: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME IN: 04:25:00, Pre arranged maintenance | CVIS
3/13/2022 3:22:00 PM | NEGROS ACC: 03/13/2022: 138KV Mabinay-Kabankalan L2 energized at 1454H after completion of maintenance activities | CVIS
3/13/2022 3:20:00 PM | NEGROS ACC: 03/13/2022: 138KV Mabinay-Kabankalan L2 energized at 1454H after completion of maintenance activities | CVIS
3/13/2022 3:18:00 PM | NEGROS ACC: 03/13/2022: 138KV Mabinay-Kabankalan L2 energized at 1454H after completion of maintenance activities | CVIS
3/13/2022 3:16:00 PM | NEGROS ACC: 03/13/2022: 138KV Mabinay-Kabankalan L2 energized at 1454H after completion of maintenance activities | CVIS
3/13/2022 3:07:00 PM | NEGROS ACC: 03/13/2022: 138KV Mabinay-Kabankalan L2 energized at 1454H after completion of maintenance activities | CVIS
3/13/2022 3:06:00 PM | NEGROS ACC: 03/13/2022: 138KV Mabinay-Kabankalan L2 energized at 1454H after completion of maintenance activities | CVIS
3/13/2022 3:04:00 PM | NEGROS ACC: 03/13/2022: 138KV Mabinay-Kabankalan L2 energized at 1454H after completion of maintenance activities | CVIS
3/13/2022 1:48:00 PM | MRCC-03/13/2022 12:16: GRID UPDATE AS OF 1:00 PM System Condition: CAP=2755MW, PK=1400MW, RR=52MW, NetOpMargin: PM=1303, EVE=1038 Highest Unit O/L: GNPKU2&U4@138MW each; Derated Plant: Ag1@40MW, Ag2@80MW, Ag4@137MW, Ag5@27MW, Ag6@20MW, Ag7@26MW, Pul4@122MW, MGPP@30MW, STEAG@200MW, FMP@245MW, GNPK@276MW, and MCC@100MW. [WEBSMS] | CMIN
3/13/2022 11:29:00 AM | LRCC-03/13/2022 11:29: San Jose-Taytay 230kV Line 2 restored at 1128H (Planned Outage). [WEBSMS] | CLUZ
3/13/2022 8:02:00 AM | LEYTE ACC-03/13/22 07:45:CALBAYOG SS, Palanas-Catarman-Allen-Laoang 69kV L,tripped/restored,0726H/0730H,Phase AB, fd=94.0kms,load=10.5mw, WEATHER: FAIR | CVIS
3/13/2022 8:00:00 AM | LEYTE ACC-03/13/22 07:45:CALBAYOG SS, Palanas-Catarman-Allen-Laoang 69kV L,tripped/restored,0726H/0730H,Phase AB, fd=94.0kms,load=10.5mw, WEATHER: FAIR | CVIS
3/13/2022 7:58:00 AM | LEYTE ACC-03/13/22 07:45:CALBAYOG SS, Palanas-Catarman-Allen-Laoang 69kV L,tripped/restored,0726H/0730H,Phase AB, fd=94.0kms,load=10.5mw, WEATHER: FAIR | CVIS
3/13/2022 7:56:00 AM | LEYTE ACC-03/13/22 07:45:CALBAYOG SS, Palanas-Catarman-Allen-Laoang 69kV L,tripped/restored,0726H/0730H,Phase AB, fd=94.0kms,load=10.5mw, WEATHER: FAIR | CVIS
3/13/2022 7:54:00 AM | LEYTE ACC-03/13/22 07:45:CALBAYOG SS, Palanas-Catarman-Allen-Laoang 69kV L,tripped/restored,0726H/0730H,Phase AB, fd=94.0kms,load=10.5mw, WEATHER: FAIR | CVIS
3/13/2022 7:52:00 AM | LEYTE ACC-03/13/22 07:45:CALBAYOG SS, Palanas-Catarman-Allen-Laoang 69kV L,tripped/restored,0726H/0730H,Phase AB, fd=94.0kms,load=10.5mw, WEATHER: FAIR | CVIS
3/13/2022 7:41:00 AM | LEYTE ACC-03/13/22 07:45:CALBAYOG SS, Palanas-Catarman-Allen-Laoang 69kV L,tripped/restored,0726H/0730H,Phase AB, fd=94.0kms,load=10.5mw, WEATHER: FAIR | CVIS
3/13/2022 7:39:00 AM | LEYTE ACC-03/13/22 07:45:CALBAYOG SS, Palanas-Catarman-Allen-Laoang 69kV L,tripped/restored,0726H/0730H,Phase AB, fd=94.0kms,load=10.5mw, WEATHER: FAIR | CVIS
3/13/2022 7:39:00 AM | LRCC-03/13/2022 07:38: San Jose-Taytay 230kV Line 2 de-energized at 0737H (Planned Outage). [WEBSMS] | CLUZ
3/13/2022 7:37:00 AM | LEYTE ACC-03/13/22 07:45:CALBAYOG SS, Palanas-Catarman-Allen-Laoang 69kV L,tripped/restored,0726H/0730H,Phase AB, fd=94.0kms,load=10.5mw, WEATHER: FAIR | CVIS
3/13/2022 7:35:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:33:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:31:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:29:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:27:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:25:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:23:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:22:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:20:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:18:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:16:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:14:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:12:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:10:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:08:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:06:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:04:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:02:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 7:00:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:58:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:56:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:54:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:52:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:50:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:48:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:46:00 AM | NEGROS ACC: 03/13/2022: 138KV Mabinay-Kabankalan L2 de-energized at 0620H to conduct APMS and correction of defects of TL and its associated HVE including protection and secondary devices. Load of L2 transferred to L1. | CVIS
3/13/2022 6:46:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:44:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:42:00 AM | PANAY ACC-03/13/22 06:16: NABAS SS, Malay 69/13.2 kV T1 (30MVA) (CO) (5XF01MLA), TIME OUT: 06:12:00, TIME IN: , RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:42:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:40:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:38:00 AM | LRCC-03/13/2022 06:38: Concepcion-San Manuel 230kV Line 1 de-energized at 0637H (Planned Outage). [WEBSMS] | CLUZ
3/13/2022 6:38:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:36:00 AM | PANAY ACC-03/13/22 06:25: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 06:21:00, RELAY: NONE, WEATHER: FAIR. Pre-arranged Maintenance. | CVIS
3/13/2022 6:14:00 AM | LRCC-03/13/2022 06:13: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12403MW, PK=8498MW, RR=332MW, NetOpMargin: AM=3573, PM=3568, EVE=2702 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLTEC 1 @91MW, GMEC 2 @300MW, Pagbilao 3 @350MW, San Gabriel @210MW & Ilijan @851MW [WEBSMS] | CLUZ
3/13/2022 5:49:00 AM | VRCC-03/13/2022 05:46: 138 KV Colon-Quiot line de-energized at 0545H, pre arranged. [WEBSMS] | CVIS
3/13/2022 5:47:00 AM | VRCC-03/13/2022 05:46: 138 KV Colon-Quiot line de-energized at 0545H, pre arranged. [WEBSMS] | CVIS
3/13/2022 5:46:00 AM | VRCC-03/13/2022 05:46: 138 KV Colon-Quiot line de-energized at 0545H, pre arranged. [WEBSMS] | CVIS
3/13/2022 5:42:00 AM | VRCC-03/13/2022 05:39: Quiot SS. 100 MVA TR 2 de-energized at 0532H, pre arranged. [WEBSMS] | CVIS
3/13/2022 5:40:00 AM | VRCC-03/13/2022 05:39: Quiot SS. 100 MVA TR 2 de-energized at 0532H, pre arranged. [WEBSMS] | CVIS
3/13/2022 4:49:00 AM | VRCC-03/13/2022 04:47: Cebu SS. 69 KV Cebu-VECO L2 de-energized at 0418H, customers request. [WEBSMS] | CVIS
3/13/2022 4:47:00 AM | VRCC-03/13/2022 04:47: Cebu SS. 69 KV Cebu-VECO L2 de-energized at 0418H, customers request. [WEBSMS] | CVIS
3/13/2022 4:43:00 AM | MRCC-03/13/2022 04:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2769MW, PK=1390MW, RR=56MW, NetOpMargin: AM=1323, PM=1299, EVE=1032 Highest Unit O/L: GNPOWER Unit#2 & Unit#4 @ 138MW each unit. Derated Plant: Ag1@40MW, Ag2@80MW, Ag4@139MW, Ag5@27MW, Ag6@20MW, Ag7@26MW, Pul4@120MW, MGPP@30MW, STEAG@200MW, FMP@245MW, GNPK@276MW, and MCC@100MW. [WEBSMS] | CMIN
3/12/2022 10:37:00 PM | LRCC-03/12/2022 22:36: Hermosa-Mexico 230kV Line 2 restored at 2236H. (Planned Outage) [WEBSMS] | CLUZ
3/12/2022 7:57:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy - San Carlos line section restored at 1934H | CVIS
3/12/2022 7:55:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy - San Carlos line section restored at 1934H | CVIS
3/12/2022 7:53:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy - San Carlos line section restored at 1934H | CVIS
3/12/2022 7:51:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy - San Carlos line section restored at 1934H | CVIS
3/12/2022 7:49:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy - San Carlos line section restored at 1934H | CVIS
3/12/2022 7:47:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy - San Carlos line section restored at 1934H | CVIS
3/12/2022 7:44:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy - San Carlos line section restored at 1934H | CVIS
3/12/2022 7:42:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy - San Carlos line section restored at 1934H | CVIS
3/12/2022 7:40:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy - San Carlos line section restored at 1934H | CVIS
3/12/2022 7:38:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy - San Carlos line section restored at 1934H | CVIS
3/12/2022 7:36:00 PM | VRCC-03/12/2022 19:36: 34.5 KV Carcon-Sangi L1 & Sangi-2nd lift line energized at 1930H and 1933H. [WEBSMS] | CVIS
3/12/2022 7:35:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy-San Carlos line section (4.85 MW) auto-tripped at 1905H with indication Z3 ABC START, 112.5 km. SACASUN isolated. | CVIS
3/12/2022 7:33:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy-San Carlos line section (4.85 MW) auto-tripped at 1905H with indication Z3 ABC START, 112.5 km. SACASUN isolated. | CVIS
3/12/2022 7:31:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy-San Carlos line section (4.85 MW) auto-tripped at 1905H with indication Z3 ABC START, 112.5 km. SACASUN isolated. | CVIS
3/12/2022 7:29:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy-San Carlos line section (4.85 MW) auto-tripped at 1905H with indication Z3 ABC START, 112.5 km. SACASUN isolated. | CVIS
3/12/2022 7:27:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy-San Carlos line section (4.85 MW) auto-tripped at 1905H with indication Z3 ABC START, 112.5 km. SACASUN isolated. | CVIS
3/12/2022 7:25:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy-San Carlos line section (4.85 MW) auto-tripped at 1905H with indication Z3 ABC START, 112.5 km. SACASUN isolated. | CVIS
3/12/2022 7:23:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy-San Carlos line section (4.85 MW) auto-tripped at 1905H with indication Z3 ABC START, 112.5 km. SACASUN isolated. | CVIS
3/12/2022 7:21:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy-San Carlos line section (4.85 MW) auto-tripped at 1905H with indication Z3 ABC START, 112.5 km. SACASUN isolated. | CVIS
3/12/2022 7:19:00 PM | NEGROS ACC: 03/12/2022, 69kV Bindoy-San Carlos line section (4.85 MW) auto-tripped at 1905H with indication Z3 ABC START, 112.5 km. SACASUN isolated. | CVIS
3/12/2022 6:46:00 PM | VRCC-03/12/2022 18:44: 34.5KV Carcon-Sangi Line 2 energized & line 3 energized at 1838H. TPC1A synchronized 1836H. [WEBSMS] | CVIS
3/12/2022 6:44:00 PM | VRCC-03/12/2022 18:44: 34.5KV Carcon-Sangi Line 2 energized & line 3 energized at 1838H. TPC1A synchronized 1836H. [WEBSMS] | CVIS
3/12/2022 6:30:00 PM | LEYTE ACC-03/12/22 18:15: CALBAYOG SS, 69kV Calabayog-Palanas Cara-Catarman line energized at 1741H, while 69kV Palanas Cara-Allen-Lao-ang line energized at 1747H and 69kV Calbayog-Bliss line energized at 1801H. Completed pre-arranged activity. WEATHER: FAIR | CVIS
3/12/2022 6:28:00 PM | LEYTE ACC-03/12/22 18:15: CALBAYOG SS, 69kV Calabayog-Palanas Cara-Catarman line energized at 1741H, while 69kV Palanas Cara-Allen-Lao-ang line energized at 1747H and 69kV Calbayog-Bliss line energized at 1801H. Completed pre-arranged activity. WEATHER: FAIR | CVIS
3/12/2022 6:26:00 PM | LEYTE ACC-03/12/22 18:15: CALBAYOG SS, 69kV Calabayog-Palanas Cara-Catarman line energized at 1741H, while 69kV Palanas Cara-Allen-Lao-ang line energized at 1747H and 69kV Calbayog-Bliss line energized at 1801H. Completed pre-arranged activity. WEATHER: FAIR | CVIS
3/12/2022 6:25:00 PM | LEYTE ACC-03/12/22 18:15: CALBAYOG SS, 69kV Calabayog-Palanas Cara-Catarman line energized at 1741H, while 69kV Palanas Cara-Allen-Lao-ang line energized at 1747H and 69kV Calbayog-Bliss line energized at 1801H. Completed pre-arranged activity. WEATHER: FAIR | CVIS
3/12/2022 6:03:00 PM | LRCC-03/12/2022 18:03: Muntinlupa (Sucat) - Binan 230kV Line 2 restored at 1802H (Planned Outage) [WEBSMS] | CLUZ
3/12/2022 5:55:00 PM | VRCC-03/12/2022 17:54: 34.5KV Carcon-Sangi Line 1 energized at 1733H. [WEBSMS] | CVIS
3/12/2022 5:51:00 PM | LRCC-03/12/2022 17:49: Muntinlupa (Sucat) 230V Bus 1 restored at 1747H (Planned Outage) [WEBSMS] | CLUZ
3/12/2022 5:45:00 PM | LEYTE ACC-03/12/22 16:38: CALBAYOG SS, Calbayog 138/69/13.8 kV T (50MVA) energized at 1824H. WEATHER: FAIR | CVIS
3/12/2022 5:44:00 PM | LEYTE ACC-03/12/22 16:38: CALBAYOG SS, Calbayog 138/69/13.8 kV T (50MVA) energized at 1824H. WEATHER: FAIR | CVIS
3/12/2022 5:42:00 PM | LEYTE ACC-03/12/22 16:38: CALBAYOG SS, Calbayog 138/69/13.8 kV T (50MVA) energized at 1824H. WEATHER: FAIR | CVIS
3/12/2022 5:40:00 PM | LEYTE ACC-03/12/22 16:38: CALBAYOG SS, Calbayog 138/69/13.8 kV T (50MVA) energized at 1824H. WEATHER: FAIR | CVIS
3/12/2022 5:38:00 PM | LEYTE ACC-03/12/22 16:38: CALBAYOG SS, Calbayog 138/69/13.8 kV T (50MVA) energized at 1824H. WEATHER: FAIR | CVIS
3/12/2022 5:36:00 PM | LEYTE ACC-03/12/22 16:38: CALBAYOG SS, Calbayog 138/69/13.8 kV T (50MVA) energized at 1824H. WEATHER: FAIR | CVIS
3/12/2022 5:33:00 PM | LEYTE ACC-03/12/22 16:38: CALBAYOG SS, Calbayog 138/69/13.8 kV T (50MVA) energized at 1824H. WEATHER: FAIR | CVIS
3/12/2022 5:31:00 PM | LEYTE ACC-03/12/22 16:38: CALBAYOG SS, Calbayog 138/69/13.8 kV T (50MVA) energized at 1824H. WEATHER: FAIR | CVIS
3/12/2022 5:29:00 PM | LEYTE ACC-03/12/22 16:38: CALBAYOG SS, Calbayog 138/69/13.8 kV T (50MVA) energized at 1824H. WEATHER: FAIR | CVIS
3/12/2022 5:23:00 PM | LRCC-03/12/2022 17:21: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11650MW, PK=9765MW, RR=373MW, NetOpMargin: EVE=1512 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @86MW; ILJJAN A / B @851MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/12/2022 5:21:00 PM | LRCC-03/12/2022 17:21: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11650MW, PK=9765MW, RR=373MW, NetOpMargin: EVE=1512 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @86MW; ILJJAN A / B @851MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/12/2022 4:36:00 PM | MRCC-03/12/2022 16:33: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2817MW, PK=1700MW, RR=48MW, NetOpMargin: EVE=1049 Highest Unit O/L: GNPOWER Unit 2 & Unit 4 @ 138MW each unit Derated Plant: Ag1@46MW, Ag2@78MW, Ag4@146MW, Ag5@27MW, Ag6@63MW, Ag7@26MW, Pul4@130MW, MGPP@75MW, STEAG@200MW, FMP@245MW, GNPK@276MW, and MCC@100MW. [WEBSMS] | CMIN
3/12/2022 4:09:00 PM | NEGROS ACC: 03/12/2022: 138kV Mabinay-Kabankalan Line 1 energized at 1540H after completion of APMS . | CVIS
3/12/2022 4:07:00 PM | NEGROS ACC: 03/12/2022: 138kV Mabinay-Kabankalan Line 1 energized at 1540H after completion of APMS . | CVIS
3/12/2022 4:05:00 PM | NEGROS ACC: 03/12/2022: 138kV Mabinay-Kabankalan Line 1 energized at 1540H after completion of APMS . | CVIS
3/12/2022 3:55:00 PM | NEGROS ACC: 03/12/2022: 138kV Mabinay-Kabankalan Line 1 energized at 1540H after completion of APMS . | CVIS
3/12/2022 3:53:00 PM | NEGROS ACC: 03/12/2022: 138kV Mabinay-Kabankalan Line 1 energized at 1540H after completion of APMS . | CVIS
3/12/2022 3:51:00 PM | NEGROS ACC: 03/12/2022: 138kV Mabinay-Kabankalan Line 1 energized at 1540H after completion of APMS . | CVIS
3/12/2022 3:49:00 PM | VRCC-03/12/2022 15:48: Magdugo SS 230KV Bus 1 energized at 1532H, P & E activity completed. [WEBSMS] | CVIS
3/12/2022 12:58:00 PM | MRCC-03/12/2022 11:35: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2884MW, PK=1650MW, RR=46MW, NetOpMargin: PM=1168, EVE=1049 Highest Unit O/L: GNPOWER U2 & U4 @ 138MW each unit. Derated Plant: Ag1@46MW, Ag2@80MW, Ag4@143MW, Ag5@27MW, Ag6@63MW, Ag7@26MW, Pul4@132MW, MGPP@75MW, STEAG@200MW, FMP@245MW, GNPK@276MW, and MCC@100MW. [WEBSMS] | CMIN
3/12/2022 12:54:00 PM | MRCC-03/12/2022 10:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2884MW, PK=1650MW, RR=46MW, NetOpMargin: PM=1168, EVE=1049 Highest Unit O/L: GNPOWER U2 & U4 @ 138MW each unit. Derated Plant: Ag1@46MW, Ag2@80MW, Ag4@143MW, Ag5@27MW, Ag6@63MW, Ag7@26MW, Pul4@132MW, MGPP@75MW, STEAG@200MW, FMP@245MW, GNPK@276MW, and MCC@100MW. [WEBSMS] | CMIN
3/12/2022 12:53:00 PM | MRCC-03/12/2022 10:47: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2884MW, PK=1650MW, RR=46MW, NetOpMargin: PM=1168, EVE=1049 Highest Unit O/L: GNPOWER U2 & U4 @ 138MW each unit. Derated Plant: Ag1@46MW, Ag2@80MW, Ag4@143MW, Ag5@27MW, Ag6@63MW, Ag7@26MW, Pul4@132MW, MGPP@75MW, STEAG@200MW, FMP@245MW, GNPK@276MW, and MCC@100MW. [WEBSMS] | CMIN
3/12/2022 10:38:00 AM | LEYTE ACC-03/12/22 10:22:ORMOC SS,Sepalco & Soleq Solar PP,cut-in at 0939H & 0943H respectively.WEATHER: FAIR | CVIS
3/12/2022 10:36:00 AM | LEYTE ACC-03/12/22 10:22:ORMOC SS,Sepalco & Soleq Solar PP,cut-in at 0939H & 0943H respectively.WEATHER: FAIR | CVIS
3/12/2022 10:34:00 AM | LEYTE ACC-03/12/22 10:22:ORMOC SS,Sepalco & Soleq Solar PP,cut-in at 0939H & 0943H respectively.WEATHER: FAIR | CVIS
3/12/2022 10:33:00 AM | LEYTE ACC-03/12/22 10:22:ORMOC SS,Sepalco & Soleq Solar PP,cut-in at 0939H & 0943H respectively.WEATHER: FAIR | CVIS
3/12/2022 10:31:00 AM | LEYTE ACC-03/12/22 10:22:ORMOC SS,Sepalco & Soleq Solar PP,cut-in at 0939H & 0943H respectively.WEATHER: FAIR | CVIS
3/12/2022 10:29:00 AM | LEYTE ACC-03/12/22 10:22:ORMOC SS,Sepalco & Soleq Solar PP,cut-in at 0939H & 0943H respectively.WEATHER: FAIR | CVIS
3/12/2022 10:27:00 AM | LEYTE ACC-03/12/22 10:22:ORMOC SS,Sepalco & Soleq Solar PP,cut-in at 0939H & 0943H respectively.WEATHER: FAIR | CVIS
3/12/2022 10:25:00 AM | LEYTE ACC-03/12/22 10:22:ORMOC SS,Sepalco & Soleq Solar PP,cut-in at 0939H & 0943H respectively.WEATHER: FAIR | CVIS
3/12/2022 10:23:00 AM | LEYTE ACC-03/12/22 10:22:ORMOC SS,Sepalco & Soleq Solar PP,cut-in at 0939H & 0943H respectively.WEATHER: FAIR | CVIS
3/12/2022 10:21:00 AM | LEYTE ACC-03/12/22 10:22:ORMOC SS,Sepalco & Soleq Solar PP,cut-in at 0939H & 0943H respectively.WEATHER: FAIR | CVIS
3/12/2022 10:19:00 AM | LEYTE ACC-03/12/22 10:22:ORMOC SS,Sepalco & Soleq Solar PP,cut-in at 0939H & 0943H respectively.WEATHER: FAIR | CVIS
3/12/2022 10:17:00 AM | LEYTE ACC-03/12/22 10:22:ORMOC SS,Sepalco & Soleq Solar PP,cut-in at 0939H & 0943H respectively.WEATHER: FAIR | CVIS
3/12/2022 10:15:00 AM | LEYTE ACC-03/12/22 10:22:ORMOC SS,Sepalco & Soleq Solar PP,cut-in at 0939H & 0943H respectively.WEATHER: FAIR | CVIS
3/12/2022 10:13:00 AM | LEYTE ACC-03/12/22 10:15:Correction,ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV Line tripped/restored at 0924H/0937H,EF Inverse tripped, total load=33.14mw, . WEATHER: FAIR | CVIS
3/12/2022 10:10:00 AM | LEYTE ACC-03/12/22 10:15:Correction,ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV Line tripped/restored at 0924H/0937H,EF Inverse tripped, total load=33.14mw, . WEATHER: FAIR | CVIS
3/12/2022 10:09:00 AM | LEYTE ACC-03/12/22 10:15:Correction,ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV Line tripped/restored at 0924H/0937H,EF Inverse tripped, total load=33.14mw, . WEATHER: FAIR | CVIS
3/12/2022 10:07:00 AM | LEYTE ACC-03/12/22 10:15:Correction,ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV Line tripped/restored at 0924H/0937H,EF Inverse tripped, total load=33.14mw, . WEATHER: FAIR | CVIS
3/12/2022 9:57:00 AM | LEYTE ACC-03/12/22 09:51:ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV Line tripped/energized, at 1926H/1937H,Under assessment, WEATHER: FAIR | CVIS
3/12/2022 9:55:00 AM | LEYTE ACC-03/12/22 09:51:ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV Line tripped/energized, at 1926H/1937H,Under assessment, WEATHER: FAIR | CVIS
3/12/2022 9:53:00 AM | LEYTE ACC-03/12/22 09:51:ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV Line tripped/energized, at 1926H/1937H,Under assessment, WEATHER: FAIR | CVIS
3/12/2022 9:51:00 AM | LEYTE ACC-03/12/22 09:51:ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV Line tripped/energized, at 1926H/1937H,Under assessment, WEATHER: FAIR | CVIS
3/12/2022 9:49:00 AM | LEYTE ACC-03/12/22 09:51:ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV Line tripped/energized, at 1926H/1937H,Under assessment, WEATHER: FAIR | CVIS
3/12/2022 9:47:00 AM | LEYTE ACC-03/12/22 09:51:ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV Line tripped/energized, at 1926H/1937H,Under assessment, WEATHER: FAIR | CVIS
3/12/2022 9:46:00 AM | LEYTE ACC-03/12/22 09:51:ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV Line tripped/energized, at 1926H/1937H,Under assessment, WEATHER: FAIR | CVIS
3/12/2022 9:44:00 AM | LEYTE ACC-03/12/22 09:51:ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV Line tripped/energized, at 1926H/1937H,Under assessment, WEATHER: FAIR | CVIS
3/12/2022 9:42:00 AM | LEYTE ACC-03/12/22 09:51:ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV Line tripped/energized, at 1926H/1937H,Under assessment, WEATHER: FAIR | CVIS
3/12/2022 9:02:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 9:00:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:59:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:57:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:55:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:53:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:51:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:49:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:47:00 AM | VRCC-03/12/2022 08:45: Magdugo SS 230KV Bus 1 de-energized at 0809H, P & E request. ECD: 1700H [WEBSMS] | CVIS
3/12/2022 8:45:00 AM | VRCC-03/12/2022 08:45: Magdugo SS 230KV Bus 1 de-energized at 0809H, P & E request. ECD: 1700H [WEBSMS] | CVIS
3/12/2022 8:43:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:41:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:39:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:37:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:36:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:34:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:31:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:29:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:27:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:25:00 AM | PANAY ACC-03/12/22 08:15: SAN JOSE SS, San Jose-Bugasong-Culasi 69 kV L (5LI1SJB-CRD), TIME OUT: 08:00:00, TIME IN: 08:12:00, RELAY: Z1 AIDED TRIP PHASE C 32.47KMS, Load: 3.9mw, under investigation, WEATHER: FAIR | CVIS
3/12/2022 8:23:00 AM | LEYTE ACC-03/12/22 08:30: CALBAYOG SS,Deenergized 138/69kV 50MVA Transformer at 0806H,Pre arranged per PANR No. PANR VRCC-2022-03-0009,6am-6pm.WEATHER: FAIR | CVIS
3/12/2022 8:00:00 AM | LEYTE ACC-03/12/22 06:59:CALBAYOG SS,Palanas-Cara-Allen-Lao-ang and Calbayog 69 KVL Deenergized at 0614H & 0617H respectively,Pre arranged per PANR No. PANR VRCC-2022-03-0009,6am-6pm,load=18.7mw WEATHER: FAIR | CVIS
3/12/2022 7:58:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:56:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:54:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:52:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:50:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:49:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:47:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:45:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:43:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:41:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:39:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:36:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:34:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:32:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:30:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:28:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:26:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:24:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:22:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:20:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:18:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:16:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:14:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:11:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:03:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:02:00 AM | PANAY ACC-03/12/22 07:01: SAN JOSE SS, San Jose-Bugasong-Culasi 69kV L, TIME IN: 06:53:00, Pre arranged maintenance, Load transfer of ANTECO Culasi SS to San Jose SS | CVIS
3/12/2022 7:00:00 AM | PANAY ACC-03/12/22 07:35: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 06:30:00, Load: 2.61mw, Pre arranged maintenance | CVIS
3/12/2022 6:58:00 AM | PANAY ACC-03/12/22 07:35: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 06:30:00, Load: 2.61mw, Pre arranged maintenance | CVIS
3/12/2022 6:56:00 AM | PANAY ACC-03/12/22 07:35: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 06:30:00, Load: 2.61mw, Pre arranged maintenance | CVIS
3/12/2022 6:54:00 AM | PANAY ACC-03/12/22 06:19: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME OUT: 06:11:00, Load: 1.96mw, Pre arranged maintenance, Facilitate Load transfer to San Jose SS | CVIS
3/12/2022 6:52:00 AM | LEYTE ACC-03/12/22 06:59:CALBAYOG SS,Palanas-Cara-Allen-Lao-ang and Calbayog 69 KVL Deenergized at 0614H & 0617H respectively,Pre arranged per PANR No. PANR VRCC-2022-03-0009,6am-6pm,load=18.7mw WEATHER: FAIR | CVIS
3/12/2022 6:50:00 AM | LEYTE ACC-03/12/22 06:47:CALBAYOG SS,Calbayog-Bliss 69kV Line,Deenergized at 0602H,while Samelco 1(San Agustin SS)load transferred via Paranas SS,at 0611H,load=1.8mw,Pre arranged per PANR No. PANR VRCC-2022-03-0009,6am-6pm,WEATHER: Cloudy | CVIS
3/12/2022 6:50:00 AM | LRCC-03/12/2022 06:49: Muntinlupa (Sucat) - Binan 230kV Line 2 de-energized at 0645H (Planned Outage) [WEBSMS] | CLUZ
3/12/2022 6:47:00 AM | LEYTE ACC-03/12/22 06:47:CALBAYOG SS,Calbayog-Bliss 69kV Line,Deenergized at 0602H,while Samelco 1(San Agustin SS)load transferred via Paranas SS,at 0611H,load=1.8mw,Pre arranged per PANR No. PANR VRCC-2022-03-0009,6am-6pm,WEATHER: Cloudy | CVIS
3/12/2022 6:45:00 AM | LEYTE ACC-03/12/22 06:47:CALBAYOG SS,Calbayog-Bliss 69kV Line,Deenergized at 0602H,while Samelco 1(San Agustin SS)load transferred via Paranas SS,at 0611H,load=1.8mw,Pre arranged per PANR No. PANR VRCC-2022-03-0009,6am-6pm,WEATHER: Cloudy | CVIS
3/12/2022 6:43:00 AM | LEYTE ACC-03/12/22 06:47:CALBAYOG SS,Calbayog-Bliss 69kV Line,Deenergized at 0602H,while Samelco 1(San Agustin SS)load transferred via Paranas SS,at 0611H,load=1.8mw,Pre arranged per PANR No. PANR VRCC-2022-03-0009,6am-6pm,WEATHER: Cloudy | CVIS
3/12/2022 6:41:00 AM | NEGROS ACC: 03/12/2022, 138kV Mabinay-Kabankalan Line 1(72.18MW) de-energized at 0621H due to APMS. Load of Line 1 transferred to Line 2. | CVIS
3/12/2022 6:39:00 AM | NEGROS ACC: 03/12/2022, 138kV Mabinay-Kabankalan Line 1(72.18MW) de-energized at 0621H due to APMS. Load of Line 1 transferred to Line 2. | CVIS
3/12/2022 6:38:00 AM | NEGROS ACC: 03/12/2022, 138kV Mabinay-Kabankalan Line 1(72.18MW) de-energized at 0621H due to APMS. Load of Line 1 transferred to Line 2. | CVIS
3/12/2022 6:36:00 AM | NEGROS ACC: 03/12/2022, 138kV Mabinay-Kabankalan Line 1(72.18MW) de-energized at 0621H due to APMS. Load of Line 1 transferred to Line 2. | CVIS
3/12/2022 6:34:00 AM | NEGROS ACC: 03/12/2022, 138kV Mabinay-Kabankalan Line 1(72.18MW) de-energized at 0621H due to APMS. Load of Line 1 transferred to Line 2. | CVIS
3/12/2022 6:32:00 AM | NEGROS ACC: 03/12/2022, 138kV Mabinay-Kabankalan Line 1(72.18MW) de-energized at 0621H due to APMS. Load of Line 1 transferred to Line 2. | CVIS
3/12/2022 6:30:00 AM | NEGROS ACC: 03/12/2022, 138kV Mabinay-Kabankalan Line 1(72.18MW) de-energized at 0621H due to APMS. Load of Line 1 transferred to Line 2. | CVIS
3/12/2022 6:28:00 AM | NEGROS ACC: 03/12/2022, 138kV Mabinay-Kabankalan Line 1(72.18MW) de-energized at 0621H due to APMS. Load of Line 1 transferred to Line 2. | CVIS
3/12/2022 6:22:00 AM | LRCC-03/12/2022 06:21: Mexico-Hermosa 230kV Line 2 de-energized at 0620H. (Planned Outage) [WEBSMS] | CLUZ
3/12/2022 5:32:00 AM | MRCC-03/12/2022 04:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2876MW, PK=1635MW, RR=46MW, NetOpMargin: AM=1176, PM=1168, EVE=1049 Highest Unit O/L: GNPKU2&U4@138MW each; Derated Plant: Ag1@46MW, Ag2@80MW, Ag4@139MW, Ag5@27MW, Ag6@63MW, Ag7@26MW, Pul4@132MW, MGPP@75MW, STEAG@200MW, FMP@245MW, GNPK@276MW, and MCC@100MW. [WEBSMS] | CMIN
3/11/2022 6:57:00 PM | PANAY ACC-03/11/22 18:22: BUENAVISTA SS, Buenavista-Zaldivar 69kV Line, TIME OUT: 18:18:00, RELAY: OCR phase B, Customer Owned Line | CVIS
3/11/2022 6:55:00 PM | PANAY ACC-03/11/22 18:22: BUENAVISTA SS, Buenavista-Zaldivar 69kV Line, TIME OUT: 18:18:00, RELAY: OCR phase B, Customer Owned Line | CVIS
3/11/2022 6:53:00 PM | PANAY ACC-03/11/22 18:22: BUENAVISTA SS, Buenavista-Zaldivar 69kV Line, TIME OUT: 18:18:00, RELAY: OCR phase B, Customer Owned Line | CVIS
3/11/2022 6:50:00 PM | PANAY ACC-03/11/22 18:22: BUENAVISTA SS, Buenavista-Zaldivar 69kV Line, TIME OUT: 18:18:00, RELAY: OCR phase B, Customer Owned Line | CVIS
3/11/2022 6:48:00 PM | PANAY ACC-03/11/22 18:22: BUENAVISTA SS, Buenavista-Zaldivar 69kV Line, TIME OUT: 18:18:00, RELAY: OCR phase B, Customer Owned Line | CVIS
3/11/2022 6:46:00 PM | PANAY ACC-03/11/22 18:22: BUENAVISTA SS, Buenavista-Zaldivar 69kV Line, TIME OUT: 18:18:00, RELAY: OCR phase B, Customer Owned Line | CVIS
3/11/2022 6:44:00 PM | PANAY ACC-03/11/22 18:22: BUENAVISTA SS, Buenavista-Zaldivar 69kV Line, TIME OUT: 18:18:00, RELAY: OCR phase B, Customer Owned Line | CVIS
3/11/2022 6:42:00 PM | PANAY ACC-03/11/22 18:22: BUENAVISTA SS, Buenavista-Zaldivar 69kV Line, TIME OUT: 18:18:00, RELAY: OCR phase B, Customer Owned Line | CVIS
3/11/2022 6:40:00 PM | PANAY ACC-03/11/22 18:22: BUENAVISTA SS, Buenavista-Zaldivar 69kV Line, TIME OUT: 18:18:00, RELAY: OCR phase B, Customer Owned Line | CVIS
3/11/2022 6:38:00 PM | PANAY ACC-03/11/22 18:22: BUENAVISTA SS, Buenavista-Zaldivar 69kV Line, TIME OUT: 18:18:00, RELAY: OCR phase B, Customer Owned Line | CVIS
3/11/2022 6:36:00 PM | PANAY ACC-03/11/22 18:22: BUENAVISTA SS, Buenavista-Zaldivar 69kV Line, TIME OUT: 18:18:00, RELAY: OCR phase B, Customer Owned Line | CVIS
3/11/2022 6:35:00 PM | PANAY ACC-03/11/22 18:22: BUENAVISTA SS, Buenavista-Zaldivar 69kV Line, TIME OUT: 18:18:00, RELAY: OCR phase B, Customer Owned Line | CVIS
3/11/2022 6:33:00 PM | PANAY ACC-03/11/22 18:22: BUENAVISTA SS, Buenavista-Zaldivar 69kV Line, TIME OUT: 18:18:00, RELAY: OCR phase B, Customer Owned Line | CVIS
3/11/2022 6:01:00 PM | VRCC-03/11/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2279MW, PK=1837MW, RR=40MW, NetOpMargin: EVE=402 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 389MW, KSPC at 103MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW. [WEBSMS] | CVIS
3/11/2022 5:51:00 PM | LRCC-03/11/2022 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12060MW, PK=9687MW, RR=345MW, NetOpMargin: EVE=2028 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @72MW; ILJJAN A / B @851MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/11/2022 5:06:00 PM | MRCC-03/11/2022 17:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2795MW, PK=1750MW, RR=49MW, NetOpMargin: EVE=975 Highest Unit O/L: GNPKU2&U4@138MW each; Derated Plant: Ag1@30MW, Ag2@79MW, Ag4@140MW, Ag5@27MW, Ag6@63MW, Ag7@26MW, Pul4@130MW, MGPP@75MW, STEAG@200MW, FMP@245MW, GNPK@276MW, and MCC@100MW. [WEBSMS] | CMIN
3/11/2022 2:35:00 PM | MRCC-03/11/2022 11:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2868MW, PK=1875MW, RR=52MW, NetOpMargin: PM=0, EVE=0 Highest Unit O/L: GNPKU2&U4@138MW each; Derated Plant: Ag1@25MW, Ag2@80MW, Ag4@144MW, Ag5@27MW, Ag6@63MW, Ag7@21MW, Pul4@131MW, MGPP@73MW, STEAG@200MW, FMP@245MW, GNPK@276MW, and MCC@100MW. [WEBSMS] | CMIN
3/11/2022 1:01:00 PM | VRCC-03/11/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2403MW, PK=1895MW, RR=40MW, NetOpMargin: PM=468, EVE=365 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 389MW, KSPC at 103MW, TPC at 82MW, PGPP1 at 71MW, PEDC at 234MW, LGPP at 80MW. [WEBSMS] | CVIS
3/11/2022 12:45:00 PM | LRCC-03/11/2022 12:44: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12325MW, PK=10350MW, RR=395MW, NetOpMargin: PM=1580, EVE=2134 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @72MW; ILJJAN A / B @851MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/11/2022 6:34:00 AM | NEGROS ACC: 03/11/2022, PGPP1 U3(37.4MW) auto tripped at 0603H due to condenser vacuum very low. | CVIS
3/11/2022 6:32:00 AM | NEGROS ACC: 03/11/2022, PGPP1 U3(37.4MW) auto tripped at 0603H due to condenser vacuum very low. | CVIS
3/11/2022 6:30:00 AM | NEGROS ACC: 03/11/2022, PGPP1 U3(37.4MW) auto tripped at 0603H due to condenser vacuum very low. | CVIS
3/11/2022 6:28:00 AM | NEGROS ACC: 03/11/2022, PGPP1 U3(37.4MW) auto tripped at 0603H due to condenser vacuum very low. | CVIS
3/11/2022 6:25:00 AM | NEGROS ACC: 03/11/2022, PGPP1 U3(37.4MW) auto tripped at 0603H due to condenser vacuum very low. | CVIS
3/11/2022 6:23:00 AM | NEGROS ACC: 03/11/2022, PGPP1 U3(37.4MW) auto tripped at 0603H due to condenser vacuum very low. | CVIS
3/11/2022 6:21:00 AM | NEGROS ACC: 03/11/2022, PGPP1 U3(37.4MW) auto tripped at 0603H due to condenser vacuum very low. | CVIS
3/11/2022 6:19:00 AM | NEGROS ACC: 03/11/2022, PGPP1 U3(37.4MW) auto tripped at 0603H due to condenser vacuum very low. | CVIS
3/11/2022 6:17:00 AM | NEGROS ACC: 03/11/2022, PGPP1 U3(37.4MW) auto tripped at 0603H due to condenser vacuum very low. | CVIS
3/11/2022 6:15:00 AM | NEGROS ACC: 03/11/2022, PGPP1 U3(37.4MW) auto tripped at 0603H due to condenser vacuum very low. | CVIS
3/11/2022 6:06:00 AM | VRCC-03/11/2022 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2484MW, PK=1873MW, RR=59MW, NetOpMargin: AM=552, PM=505, EVE=369 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 389MW, KSPC at 103MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW. [WEBSMS] | CVIS
3/11/2022 5:05:00 AM | LRCC-03/11/2022 05:04: Binan-Balibago 115kV Line restored at 0459H. (Planned Outage) [WEBSMS] | CLUZ
3/11/2022 12:05:00 AM | LRCC-03/11/2022 00:05: Dona Imelda(Araneta) - Kamuning 115kV Line de-energized at 0002H. (Planned Outage) [WEBSMS] | CLUZ
3/10/2022 6:02:00 PM | VRCC-03/10/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2293MW, PK=1853MW, RR=40MW, NetOpMargin: EVE=400 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 389MW, KSPC at 103MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW. [WEBSMS] | CVIS
3/10/2022 6:00:00 PM | LRCC-03/10/2022 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11720MW, PK=9448MW, RR=345MW, NetOpMargin: EVE=1927 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @71MW; ILJJAN A / B @851MW; SAN GABRIEL @211MW [WEBSMS] | CLUZ
3/10/2022 6:00:00 PM | VRCC-03/10/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2293MW, PK=1853MW, RR=40MW, NetOpMargin: EVE=400 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 389MW, KSPC at 103MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW. [WEBSMS] | CVIS
3/10/2022 5:59:00 PM | LRCC-03/10/2022 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11720MW, PK=9448MW, RR=345MW, NetOpMargin: EVE=1927 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @71MW; ILJJAN A / B @851MW; SAN GABRIEL @211MW [WEBSMS] | CLUZ
3/10/2022 2:25:00 PM | LEYTE ACC-03/10/22 14:17: BABATNGON SS, Babatngon 69kV BUS 2 re-energized at 1358H, back to normal operation. Weather: Cloudy. | CVIS
3/10/2022 2:23:00 PM | LEYTE ACC-03/10/22 14:17: BABATNGON SS, Babatngon 69kV BUS 2 re-energized at 1358H, back to normal operation. Weather: Cloudy. | CVIS
3/10/2022 2:21:00 PM | LEYTE ACC-03/10/22 14:17: BABATNGON SS, Babatngon 69kV BUS 2 re-energized at 1358H, back to normal operation. Weather: Cloudy. | CVIS
3/10/2022 2:19:00 PM | LEYTE ACC-03/10/22 14:17: BABATNGON SS, Babatngon 69kV BUS 2 re-energized at 1358H, back to normal operation. Weather: Cloudy. | CVIS
3/10/2022 2:17:00 PM | LEYTE ACC-03/10/22 14:17: BABATNGON SS, Babatngon 69kV BUS 2 re-energized at 1358H, back to normal operation. Weather: Cloudy. | CVIS
3/10/2022 2:15:00 PM | LEYTE ACC-03/10/22 14:17: BABATNGON SS, Babatngon 69kV BUS 2 re-energized at 1358H, back to normal operation. Weather: Cloudy. | CVIS
3/10/2022 2:13:00 PM | LEYTE ACC-03/10/22 14:17: BABATNGON SS, Babatngon 69kV BUS 2 re-energized at 1358H, back to normal operation. Weather: Cloudy. | CVIS
3/10/2022 2:10:00 PM | LEYTE ACC-03/10/22 14:17: BABATNGON SS, Babatngon 69kV BUS 2 re-energized at 1358H, back to normal operation. Weather: Cloudy. | CVIS
3/10/2022 2:08:00 PM | LEYTE ACC-03/10/22 14:17: BABATNGON SS, Babatngon 69kV BUS 2 re-energized at 1358H, back to normal operation. Weather: Cloudy. | CVIS
3/10/2022 1:15:00 PM | LEYTE ACC-03/10/22 13:00: BABATNGON SS, Babatngon 69kV BUS 2 isolated at 1243H, emergency request by O & M. Duration: 1230H-1400H. Weather: Cloudy. | CVIS
3/10/2022 1:12:00 PM | LEYTE ACC-03/10/22 13:00: BABATNGON SS, Babatngon 69kV BUS 2 isolated at 1243H, emergency request by O & M. Duration: 1230H-1400H. Weather: Cloudy. | CVIS
3/10/2022 1:10:00 PM | LEYTE ACC-03/10/22 13:00: BABATNGON SS, Babatngon 69kV BUS 2 isolated at 1243H, emergency request by O & M. Duration: 1230H-1400H. Weather: Cloudy. | CVIS
3/10/2022 1:08:00 PM | LEYTE ACC-03/10/22 13:00: BABATNGON SS, Babatngon 69kV BUS 2 isolated at 1243H, emergency request by O & M. Duration: 1230H-1400H. Weather: Cloudy. | CVIS
3/10/2022 1:06:00 PM | LEYTE ACC-03/10/22 13:00: BABATNGON SS, Babatngon 69kV BUS 2 isolated at 1243H, emergency request by O & M. Duration: 1230H-1400H. Weather: Cloudy. | CVIS
3/10/2022 1:04:00 PM | VRCC-03/10/2022 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2499MW, PK=1950MW, RR=58MW, NetOpMargin: PM=491, EVE=400 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 389MW, KSPC at 103MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW. [WEBSMS] | CVIS
3/10/2022 1:02:00 PM | LEYTE ACC-03/10/22 13:00: BABATNGON SS, Babatngon 69kV BUS 2 isolated at 1243H, emergency request by O & M. Duration: 1230H-1400H. Weather: Cloudy. | CVIS
3/10/2022 1:00:00 PM | LEYTE ACC-03/10/22 13:00: BABATNGON SS, Babatngon 69kV BUS 2 isolated at 1243H, emergency request by O & M. Duration: 1230H-1400H. Weather: Cloudy. | CVIS
3/10/2022 12:58:00 PM | LEYTE ACC-03/10/22 13:00: BABATNGON SS, Babatngon 69kV BUS 2 isolated at 1243H, emergency request by O & M. Duration: 1230H-1400H. Weather: Cloudy. | CVIS
3/10/2022 12:56:00 PM | LEYTE ACC-03/10/22 13:00: BABATNGON SS, Babatngon 69kV BUS 2 isolated at 1243H, emergency request by O & M. Duration: 1230H-1400H. Weather: Cloudy. | CVIS
3/10/2022 12:54:00 PM | LEYTE ACC-03/10/22 13:00: BABATNGON SS, Babatngon 69kV BUS 2 isolated at 1243H, emergency request by O & M. Duration: 1230H-1400H. Weather: Cloudy. | CVIS
3/10/2022 12:54:00 PM | LRCC-03/10/2022 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12166MW, PK=10089MW, RR=410MW, NetOpMargin: PM=1667, EVE=2019 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @71MW; ILJJAN A / B @851MW; SAN GABRIEL @211MW [WEBSMS] | CLUZ
3/10/2022 12:53:00 PM | LEYTE ACC-03/10/22 13:00: BABATNGON SS, Babatngon 69kV BUS 2 isolated at 1243H, emergency request by O & M. Duration: 1230H-1400H. Weather: Cloudy. | CVIS
3/10/2022 12:53:00 PM | LRCC-03/10/2022 12:52: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12166MW, PK=10089MW, RR=410MW, NetOpMargin: PM=1667, EVE=2019 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; SLTEC 1 @71MW; ILJJAN A / B @851MW; SAN GABRIEL @211MW [WEBSMS] | CLUZ
3/10/2022 9:13:00 AM | LRCC-03/10/2022 09:12: Quezon 300MVA T08 de-energized at 0910H (Unplanned Outage). [WEBSMS] | CLUZ
3/10/2022 7:40:00 AM | PANAY ACC-03/10/22 07:20: ILOILO 1 S/S SS, 138kV Iloilo-PEDC L1, TIME OUT: 07:17:00, Customer Request(PEDC). ETR 3/30/2022 @ (0600H) | CVIS
3/10/2022 7:32:00 AM | NEGROS ACC: 03/10/2022, 69kV Sipalay-Mambaroto Sub T/L restored at 0727H after replacement of busted L.A.. Customer owned and maintained line. | CVIS
3/10/2022 6:48:00 AM | LRCC-03/10/2022 06:47: Dasmarinas 300MVA T02 (T05 Old No.) restored at 0626H (Planned Outage) [WEBSMS] | CLUZ
3/10/2022 6:01:00 AM | VRCC-03/10/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2535MW, PK=1952MW, RR=40MW, NetOpMargin: AM=543, PM=491, EVE=400 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 389 MW, PEDC at 234 MW, KSPC at 103 MW, TPC at 82 MW, LGPP at 80 MW [WEBSMS] | CVIS
3/10/2022 5:54:00 AM | LRCC-03/10/2022 05:53: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12332MW, PK=9917MW, RR=401MW, NetOpMargin: AM=2014, PM=1707, EVE=2039 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW, Pagbilao 3 @350MW, San Gabriel @210MW, Ilijan @851MW [WEBSMS] | CLUZ
3/10/2022 5:17:00 AM | LRCC-03/10/2022 05:15: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 465 km West of Zamboanga City or 255 km South Southwest of Puerto Princesa City (7.6?N, 117.9?E). Shear Line affecting Visayas. Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
3/10/2022 3:44:00 AM | NEGROS ACC: 03/10/2022, 69kV Bindoy-San Carlos Line energized at 0341H. | CVIS
3/10/2022 3:33:00 AM | NEGROS ACC: 03/10/2022, 69kV Bindoy-San Carlos Line(1.2MW) section de-energized at 0330H as per customers(NORECO 1) request to isolate Guihulngan S/S to rectify Power fuse cut-out. SACASUN isolated. | CVIS
3/10/2022 2:46:00 AM | PANAY ACC-03/10/22 02:36: STA. BARBARA SS, Miagao-Hamtic 69kV L (5LIMIA-HAM), TIME IN: 02:33:00, RELAY: L2-3, 42.7km., WEATHER: RAINY. Sustained Fault. | CVIS
3/10/2022 2:44:00 AM | PANAY ACC-03/10/22 02:04: STA. BARBARA SS, Miagao-Hamtic 69kV L (5LIMIA-HAM), TIME OUT: 01:59:00, RELAY: L2-3, 42.7km., WEATHER: RAINY. Cause under investigation. | CVIS
3/10/2022 12:29:00 AM | NEGROS ACC: 03/10/2022, 69kV Sipalay-Mambaroto Sub T/L(3.81MW) auto tripped at 0010H with ind.; CN 872m. Customer owned and maintained line. | CVIS
3/10/2022 12:13:00 AM | LRCC-03/10/2022 00:11: San Jose-Taytay 230kV L1 restored at 0011H (Planned Outage). [WEBSMS] | CLUZ
3/10/2022 12:12:00 AM | LRCC-03/10/2022 00:11: San Jose-Taytay 230kV L1 restored at 0011H (Planned Outage). [WEBSMS] | CLUZ
3/10/2022 12:06:00 AM | PANAY ACC-03/10/22 00:07: ILOILO 1 S/S SS, PEDC U_2, TIME IN: 12:01:00, WEATHER: FAIR | CVIS
3/10/2022 12:06:00 AM | VRCC-03/10/2022 00:05: KSPC Unit 2 cut-out at 0000H for APMS, ECD: March 29, 2022 [WEBSMS] | CVIS
3/9/2022 11:27:00 PM | NEGROS ACC: 03/09/2022, 69kV Kabankalan-La Castellana Sub T/L(9.92MW) auto tripped at 2315H with ind.; Z1 AN 23.5KM. Restored at 2323H. Customer owned and maintained line. | CVIS
3/9/2022 10:12:00 PM | LRCC-03/09/2022 22:12: Dasmarinas 300MVA T02 (T05 Old No.) de-energized at 2211H (Planned Outage). [WEBSMS] | CLUZ
3/9/2022 9:53:00 PM | PANAY ACC-03/09/22 21:45: PEDC U_2, TIME OUT: 21:44:00, Autotripped due to High Vibration | CVIS
3/9/2022 9:12:00 PM | NEGROS ACC: 03/09/2022: 69kV Calumangan-San Enrique Line section restored at 2108H. | CVIS
3/9/2022 8:33:00 PM | LRCC-03/09/2022 20:32: San Jose-Taytay 230kV L1 de-energized at 2030H (Planned Outage). [WEBSMS] | CLUZ
3/9/2022 8:13:00 PM | NEGROS ACC: 03/09/2022: 69kV Bacolod-Calumangan Line section restored at 2010H, ABS Calumangan opened isolating 69kV Calumangan-San Enrique Line section. CENPRI, SNBP & ISLASOL II isolated. | CVIS
3/9/2022 8:09:00 PM | NEGROS ACC: 03/09/2022, 138kV Amlan-PGPP1 Line 1 energized at 1947H after commissioning and energization of main 2 protection relay. | CVIS
3/9/2022 7:21:00 PM | NEGROS ACC: 03/09/2022: 69kV Bacolod-San Enrique Sub T/L (30.35 MW) auto tripped at 1906H with ind. Z3 L1L2L3; 24.6KM. CENPRI, SNBP & ISLASOL II isolated. | CVIS
3/9/2022 5:44:00 PM | LRCC-03/09/2022 17:44: Santiago-Magat 230kV Line 2 energized at 1742H at Santiago side only (Planned Outage). [WEBSMS] | CLUZ
3/9/2022 1:24:00 PM | LRCC-03/09/2022 13:22: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12384MW, PK=10129MW, RR=395MW, NetOpMargin: PM=1860, EVE=1705 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW, Pagbilao 3 @350MW, San Gabriel @210MW, Ilijan @851MW [WEBSMS] | CLUZ
3/9/2022 1:11:00 PM | VRCC-03/09/2022 13:11: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2608MW, PK=1927MW, RR=40MW, NetOpMargin: PM=641, EVE=536 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 383MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW [WEBSMS] | CVIS
3/9/2022 10:09:00 AM | LRCC-03/09/2022 10:08: GMEC 1 @290MW tripped at 1003H. Lowest frequency is 59.247Hz (Unplanned Outage) [WEBSMS] | CLUZ
3/9/2022 10:07:00 AM | LRCC-03/09/2022 10:06: SLTEC 1 online at 1003H (Unplanned Outage) [WEBSMS] | CLUZ
3/9/2022 9:26:00 AM | LEYTE ACC-03/09/22 09:33: ORMOC SS, Victoria - Sepalco SPP 69kV Line re-energized at 0919H after closing Victoria Abs #3. Weather: Rainy. | CVIS
3/9/2022 7:21:00 AM | LRCC-03/09/2022 07:21: Santiago-Magat 230kV Line 2 de-energized at 0717H (Planned Outage). [WEBSMS] | CLUZ
3/9/2022 6:03:00 AM | VRCC-03/09/2022 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2613MW, PK=1875MW, RR=40MW, NetOpMargin: AM=698, PM=641, EVE=536 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 383MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW [WEBSMS] | CVIS
3/9/2022 5:59:00 AM | LRCC-03/09/2022 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12723MW, PK=10227MW, RR=410MW, NetOpMargin: AM=2086, PM=1751, EVE=2031 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW; PAGBILAO 3 @350MW; ILJJAN A / B @851MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
3/9/2022 1:57:00 AM | LRCC-03/09/2022 01:56: SLTEC Unit 1 tripped at 0153H (Unplanned outage). [WEBSMS] | CLUZ
3/8/2022 10:38:00 PM | PANAY ACC-03/08/22 22:30: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW), TIME OUT: 10:00:00, TIME IN: 10:23:00, Customers request to conduct clearing of bamboo at Brgy. Avila, Buenavista, Guimaras | CVIS
3/8/2022 7:32:00 PM | LRCC-03/08/2022 19:33: Santiago-Magat 230kV Line 1 restored at 1932H (Planned Outage). [WEBSMS] | CLUZ
3/8/2022 6:43:00 PM | PANAY ACC-03/08/22 18:43: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW), TIME IN: 8:40:00, RELAY: Phase C, Z3, 6.73km., Differential Trip, WEATHER: FAIR. Cause under investigation. | CVIS
3/8/2022 6:41:00 PM | LEYTE ACC-03/08/22 18:47:ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69 kV L,energized up to ABS#1 Tunga at 1754H & ABS#1 Tunga energized at 1826H up to ABS San Isidro while While Sepalco Solar Plant still isolated,WEATHER: FAIR | CVIS
3/8/2022 6:39:00 PM | PANAY ACC-03/08/22 18:20: BUENAVISTA SS, Buenavista-San Lorenzo 69kv Line (CO) (5LI1BVI-SLW)(37.1MW), TIME OUT: 06:17:00, RELAY: Phase C, Z3, 6.73km., Differential Trip, WEATHER: FAIR. Cause under investigation. | CVIS
3/8/2022 6:17:00 PM | VRCC-03/08/2022 18:16: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2380MW, PK=1892MW, RR=76MW, NetOpMargin: EVE=412 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 350MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW. [WEBSMS] | CVIS
3/8/2022 5:30:00 PM | LRCC-03/08/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12144MW, PK=9625MW, RR=323MW, NetOpMargin: EVE=2196 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @280MW, Pagbilao 3 @350MW, San Gabriel @210MW, Ilijan @851MW [WEBSMS] | CLUZ
3/8/2022 4:41:00 PM | LEYTE ACC-03/08/22 16:47: ORMOC SS,Ormoc-Lemon-Tolosa-San Isidro 69kV L,tripped at 1629H,Under assesment, WEATHER: FAIR | CVIS
3/8/2022 1:21:00 PM | LRCC-03/08/2022 13:21: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12745MW, PK=10557MW, RR=363MW, NetOpMargin: PM=1825, EVE=2303 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GMEC 2 @300MW, Pagbilao 3 @350MW, San Gabriel @210MW, Ilijan @851MW [WEBSMS] | CLUZ
3/8/2022 1:13:00 PM | VRCC-03/08/2022 13:13: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2565MW, PK=1927MW, RR=40MW, NetOpMargin: PM=598, EVE=412 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 350MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW. [WEBSMS] | CVIS
3/8/2022 12:24:00 PM | LRCC-03/08/2022 12:23: Hermosa-Malolos 230kV Line tripped at 1205H. Restored at 1218H (Unplanned Outage) [WEBSMS] | CLUZ
3/8/2022 7:15:00 AM | LRCC-03/08/2022 07:14: Santiago-Magat 230kV Line 1 de-energized at 0712H (Planned Outage) [WEBSMS] | CLUZ
3/8/2022 5:33:00 AM | LRCC-03/08/2022 05:33: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 100 km East Southeast of Davao City, Davao del Sur (6.8?N, 126.6?E). Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
3/7/2022 10:16:00 PM | LRCC-03/07/2022 22:15: Dasmarinas 300MVA T01 de-energized at 2211H (Planned Outage). [WEBSMS] | CLUZ
3/7/2022 9:09:00 PM | LRCC-03/07/2022 20:57: Correction; GMEC 2 on line at 2031H (Unplanned Outage). [WEBSMS] | CLUZ
3/7/2022 9:09:00 PM | LRCC-03/07/2022 21:00: GMEC 2 tripped at 2042H (Unplanned Outage). [WEBSMS] | CLUZ
3/7/2022 9:09:00 PM | LRCC-03/07/2022 21:05: GMEC 2 on line at 2103H (Unplanned Outage). [WEBSMS] | CLUZ
3/7/2022 9:09:00 PM | NEGROS ACC: 03/07/2022, SACASUN NORTH Line transferred to 69kV Amlan-San Carlos Sub T/L at 1911H. | CVIS
3/7/2022 8:45:00 PM | LRCC-03/07/2022 20:44: GNPD 2 on line at 2031H (Unplanned Outage). [WEBSMS] | CLUZ
3/7/2022 6:32:00 PM | LRCC-03/07/2022 18:11: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12033MW, PK=9634MW, RR=364MW, NetOpMargin: EVE=2035 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Pagbilao 3 @345MW, San Gabriel at 211MW & Iljan @851MW [WEBSMS] | CLUZ
3/7/2022 6:02:00 PM | VRCC-03/07/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2359MW, PK=1883MW, RR=40MW, NetOpMargin: EVE=436 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 357MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW [WEBSMS] | CVIS
3/7/2022 1:41:00 PM | VRCC-03/07/2022 13:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2574MW, PK=1961MW, RR=76MW, NetOpMargin: PM=537, EVE=436 Highest Unit O/L: TVI U at 169MW/unit. Derated Plant: EDC at 357MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW [WEBSMS] | CVIS
3/7/2022 1:02:00 PM | LRCC-03/07/2022 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12500MW, PK=10139MW, RR=404MW, NetOpMargin: PM=1957, EVE=2246 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Calaca 1 @220MW, Pagbilao 3 @345MW, San Gabriel at 211MW & Iljan @851MW [WEBSMS] | CLUZ
3/7/2022 10:25:00 AM | LRCC-03/07/2022 10:23: SLTEC 1 online at 1015H (Unplanned Outage) [WEBSMS] | CLUZ
3/7/2022 7:47:00 AM | LRCC-03/07/2022 07:46: For info: Sta Rita Module 20 completed fuel changeover from gas to oil at 0734H due to natural gas supply restriction. [WEBSMS] | CLUZ
3/7/2022 7:00:00 AM | LRCC-03/07/2022 06:43: SLTEC 1 @121MW tripped at 0638H. Lowest Frequency is 59.97Hz coming from 60.31Hz (Unplanned Outage) [WEBSMS] | CLUZ
3/7/2022 6:39:00 AM | LRCC-03/07/2022 06:35: Dona Imelda(Araneta) - Kamuning 115kV Line restored at 0634H. (Planned Outage) [WEBSMS] | CLUZ
3/7/2022 6:04:00 AM | VRCC-03/07/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2595MW, PK=1905MW, RR=58MW, NetOpMargin: AM=632, PM=537, EVE=436 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 357MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW [WEBSMS] | CVIS
3/7/2022 5:30:00 AM | LRCC-03/07/2022 05:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=13018MW, PK=9832MW, RR=398MW, NetOpMargin: AM=2788, PM=2388, EVE=2699 Highest Unit O/L: Dinginin at 668MW Derated Plant: Pagbilao 3 at 345MW, San Gabriel at 211MW [WEBSMS] | CLUZ
3/7/2022 12:06:00 AM | LRCC-03/07/2022 00:05: Dona Imelda(Araneta) - Kamuning 115kV Line de-energized at 0002H. (Planned Outage) [WEBSMS] | CLUZ
3/6/2022 11:36:00 PM | LRCC-03/06/2022 23:35: SCPC Unit 4 offline at 2330H. (Planned Outage) [WEBSMS] | CLUZ
3/6/2022 11:27:00 PM | VRCC-03/06/2022 23:27: Quiot SS. 100 MVA TR 1 energized at 2325H, pre arranged, P & E activity [WEBSMS] | CVIS
3/6/2022 11:01:00 PM | VRCC-03/06/2022 23:01: 138kV Cebu-Quiot line energized at 2300H, pre-arranged activity. [WEBSMS] | CVIS
3/6/2022 10:20:00 PM | LRCC-03/06/2022 22:07: Mexico-Hermosa 230kV Line 2 restored at 2206H. (Unplanned Outage) [WEBSMS] | CLUZ
3/6/2022 9:53:00 PM | LRCC-03/06/2022 21:53: Mexico-Hermosa 230kV Line 1 restored at 2140H. (Unplanned Outage) [WEBSMS] | CLUZ
3/6/2022 9:25:00 PM | LRCC-03/06/2022 21:24: Mexico-Hermosa 230kV Line 1 tripped at 2113H. (Unplanned Outage) [WEBSMS] | CLUZ
3/6/2022 7:15:00 PM | LRCC-03/06/2022 19:13: Ilijan GT2-1 online at 1910H. (Planned Outage) [WEBSMS] | CLUZ
3/6/2022 6:35:00 PM | LRCC-03/06/2022 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12057MW, PK=9015MW, RR=345MW, NetOpMargin: EVE=2697 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Pagbilao 3 @340MW [WEBSMS] | CLUZ
3/6/2022 6:35:00 PM | VRCC-03/06/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2357MW, PK=1775MW, RR=71MW, NetOpMargin: EVE=511 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 347MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW [WEBSMS] | CVIS
3/6/2022 5:52:00 PM | LRCC-03/06/2022 17:44: Ilijan ST2 online at 1743H (Unplanned Outage) [WEBSMS] | CLUZ
3/6/2022 5:32:00 PM | LRCC-03/06/2022 17:04: Quezon - San Jose 230kV Line 1 restored at 1703H (Planned Outage) [WEBSMS] | CLUZ
3/6/2022 4:55:00 PM | LEYTE ACC-03/06/22 16:58: PARANAS SS, 69kV Samelco-2 ABS (ABS before transformer of Samelco 2) manually closed at 1643H as per customers request, serving power to Samelco 2 (Paranas S/s). Weather: Rainy. | CVIS
3/6/2022 4:55:00 PM | LRCC-03/06/2022 16:17: SLTEC 1 online at 1615H (Unplanned Outage) [WEBSMS] | CLUZ
3/6/2022 4:55:00 PM | LRCC-03/06/2022 16:31: Concepcion-San Manuel 230kV line 2 restored at 1628H (Planned Outage) [WEBSMS] | CLUZ
3/6/2022 4:55:00 PM | NEGROS ACC: 03/06/2022, Bacolod SS 69kV Bus 2 energized at 1636H after PMS. | CVIS
3/6/2022 4:55:00 PM | VRCC-03/06/2022 16:51: 230 KV Tabango-DaanBantayan Line 1 energized at 1649H, Note:Daanbantayan reactor 2 (50 MVAr) remain open needs further repair. [WEBSMS] | CVIS
3/6/2022 3:55:00 PM | LRCC-03/06/2022 15:45: Tayabas-Mauban 230kV Line 1 restored at 1544H (Planned Outage). [WEBSMS] | CLUZ
3/6/2022 3:55:00 PM | LRCC-03/06/2022 15:52: Ilijan GT2-2 online at 1549H (Unplanned Outage) [WEBSMS] | CLUZ
3/6/2022 3:55:00 PM | PANAY ACC-03/06/22 15:46: STA. BARBARA SS, Sta. Barbara-PEDC 138 kV L2 (CO) Breaker (7-03CB04SBA (OLD)), TIME IN: 03:43:00 Pre arranged maintenance | CVIS
3/6/2022 3:54:00 PM | LRCC-03/06/2022 15:34: San Lorenzo 230kV Bus B restored at 1532H (Planned Outage). [WEBSMS] | CLUZ
3/6/2022 3:54:00 PM | LRCC-03/06/2022 15:45: Tayabas-Mauban 230kV Line 1 restored at 1544H (Planned Outage). [WEBSMS] | CLUZ
3/6/2022 1:25:00 PM | LRCC-03/06/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12570MW, PK=8308MW, RR=323MW, NetOpMargin: PM=3939, EVE=2725 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Pagbilao 3 @340MW [WEBSMS] | CLUZ
3/6/2022 1:00:00 PM | VRCC-03/06/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2527MW, PK=1595MW, RR=40MW, NetOpMargin: PM=892, EVE=506 Highest Unit O/L: TVI U at 169MW/unit Derated Plant: EDC at 342MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW [WEBSMS] | CVIS
3/6/2022 10:53:00 AM | VRCC-03/06/2022 06:06: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2496MW, PK=1553MW, RR=54MW, NetOpMargin: AM=889, PM=807, EVE=444 Highest Unit O/L: TVI U2 at 169MW Derated Plant: EDC at 369MW, TPC at 82MW, PEDC at 234MW, LGPP at 80MW [WEBSMS] | CVIS
3/6/2022 10:53:00 AM | VRCC-03/06/2022 08:39: Quiot SS. 100 MVA TR 1 de energized at 0837H, pre arranged, P & E activity. [WEBSMS] | CVIS
3/6/2022 10:53:00 AM | VRCC-03/06/2022 09:53: 230 KV DaanBantayan-Tabango Line 1 de-energized at 0952H, pre arranged. [WEBSMS] | CVIS
3/6/2022 8:25:00 AM | LRCC-03/06/2022 07:24: San Lorenzo 230kV Bus B de-energized at 0721H (Planned Outage). [WEBSMS] | CLUZ
3/6/2022 8:25:00 AM | LRCC-03/06/2022 07:28: Tayabas-Mauban 230kV Line 1 de-energized at 0727H (Planned Outage). [WEBSMS] | CLUZ
3/6/2022 8:25:00 AM | LRCC-03/06/2022 07:33: Quezon - San Jose 230kV Line 1 de-energized at 0731H (Planned Outage). [WEBSMS] | CLUZ
3/6/2022 8:24:00 AM | LRCC-03/06/2022 07:16: Hermosa-Mexico 230kV Line 2 de-energized at 0702H. (Unplanned Outage) [WEBSMS] | CLUZ
3/6/2022 8:24:00 AM | LRCC-03/06/2022 07:24: San Lorenzo 230kV Bus B de-energized at 0721H (Planned Outage). [WEBSMS] | CLUZ
3/6/2022 7:10:00 AM | LRCC-03/06/2022 07:10: Hermosa-Mexico 230kV Line 2 de-energized at 0702H. (Planned Outage) [WEBSMS] | CLUZ
3/6/2022 6:43:00 AM | LRCC-03/06/2022 06:11: Concepcion-San Manuel 230kV line 2 de-energized at 0608H (Planned Outage) [WEBSMS] | CLUZ
3/6/2022 5:51:00 AM | LRCC-03/06/2022 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12637MW, PK=9104MW, RR=318MW, NetOpMargin: AM=3215, PM=3031, EVE=2230 Highest Unit O/L: Dinginin at 668MW Derated Plant: Pagbilao 3 at 345MW [WEBSMS] | CLUZ
3/5/2022 9:07:00 PM | LRCC-03/05/2022 21:06: Hermosa-Mexico 230kV Line 1 restored at 2105H. (Planned Outage) [WEBSMS] | CLUZ
3/5/2022 7:21:00 PM | LRCC-03/05/2022 19:21: San Esteban-Bakun 230kV Line restored at 1920H. (Planned Outage) [WEBSMS] | CLUZ
3/5/2022 5:27:00 PM | LRCC-03/05/2022 17:26: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11430MW, PK=9332MW, RR=379MW, NetOpMargin: EVE=1719 Highest Unit O/L: Sual 1 & 2 @600MW Derated Plant: GNPD 1 @501MW & Pagbilao 3 @340MW [WEBSMS] | CLUZ
3/5/2022 4:50:00 PM | LRCC-03/05/2022 16:50: San Juan 230kV Bus 2 restored at 1649H (Planned Outage) [WEBSMS] | CLUZ
3/5/2022 3:12:00 PM | LRCC-03/05/2022 15:11: Limay-BCCPP 230kV Line 1 restored at 1511H (Planned Outage) [WEBSMS] | CLUZ
3/5/2022 2:08:00 PM | LRCC-03/05/2022 14:08: Mexico-San Rafael 230kV Line 2 restored at 1406H (Unplanned Outage) [WEBSMS] | CLUZ
3/5/2022 1:14:00 PM | LRCC-03/05/2022 13:13: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11953MW, PK=9396MW, RR=379MW, NetOpMargin: PM=2178, EVE=1591 Highest Unit O/L: Sual 1 & 2 @600MW Derated Plant: GNPD 1 @501MW & Pagbilao 3 @340MW [WEBSMS] | CLUZ
3/5/2022 7:57:00 AM | LRCC-03/05/2022 07:58: Limay-BCCPP 230kV Line 1 de-energized at 0756H (Planned Outage) [WEBSMS] | CLUZ
3/5/2022 7:25:00 AM | LRCC-03/05/2022 07:23: San Juan 230kV Bus 2 de-energized at 0719H (Planned Outage) [WEBSMS] | CLUZ
3/5/2022 7:24:00 AM | LRCC-03/05/2022 07:23: San Juan 230kV Bus 2 de-energized at 0719H (Planned Outage) [WEBSMS] | CLUZ
3/5/2022 6:40:00 AM | LRCC-03/05/2022 06:39: Bauang-Bakun 230kV Line & San Esteban-Bakun 230kV Line de-energized at 0636H & 0638H, respectively (Planned Outage) [WEBSMS] | CLUZ
3/5/2022 6:39:00 AM | LRCC-03/05/2022 06:39: Bauang-Bakun 230kV Line & San Esteban-Bakun 230kV Line de-energized at 0636H & 0638H, respectively (Planned Outage) [WEBSMS] | CLUZ
3/5/2022 6:29:00 AM | LRCC-03/05/2022 06:29: Hermosa-Mexico 230kV Line 1 de-energized at 0625H (Planned Outage) [WEBSMS] | CLUZ
3/5/2022 6:10:00 AM | LRCC-03/05/2022 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11997MW, PK=9226MW, RR=369MW, NetOpMargin: AM=2402, PM=2152, EVE=1502 Highest Unit O/L: Sual 1 & 2 at 647MW Derated Plant: Dinginin at 501MW, Pagbilao 3 at 340MW [WEBSMS] | CLUZ
3/5/2022 5:41:00 AM | LRCC-03/05/2022 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11997MW, PK=11993MW, RR=369MW, NetOpMargin: AM=2402, PM=2152, EVE=1502 Highest Unit O/L: Sual 1 & 2 at 647MW Derated Plant: Dinginin 1 at 501MW, Pagbilao 3 at 340MW [WEBSMS] | CLUZ
3/5/2022 4:21:00 AM | LRCC-03/05/2022 04:21: San Jose - Angat 115kV Line 2 de-energized at 0411H (Planned Outage). [WEBSMS] | CLUZ
3/4/2022 7:30:00 PM | LRCC-03/04/2022 19:28: San Lorenzo 60 online at 1917H (Unplanned Outage). [WEBSMS] | CLUZ
3/4/2022 7:25:00 PM | LRCC-03/04/2022 19:24: Ilijan 500kV Bus 2 restored at 1922H (Planned Outage). [WEBSMS] | CLUZ
3/4/2022 5:44:00 PM | LRCC-03/04/2022 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12057MW, PK=9733MW, RR=389MW, NetOpMargin: EVE=1935 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: GMEC 2 at 305MW, Pagbilao 3 at 335MW [WEBSMS] | CLUZ
3/4/2022 12:27:00 PM | LRCC-03/04/2022 12:26: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12526MW, PK=10395MW, RR=411MW, NetOpMargin: PM=1720, EVE=1993 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: GMEC 2 at 305MW, Pagbilao 3 at 335MW [WEBSMS] | CLUZ
3/3/2022 5:53:00 PM | LRCC-03/03/2022 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12034MW, PK=9593MW, RR=363MW, NetOpMargin: EVE=2078 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 890MW, San Gabriel at 210MW, GMEC 2 at 300MW [WEBSMS] | CLUZ
3/3/2022 3:51:00 PM | LRCC-03/03/2022 15:50: Sta. Rita 20 change over from fuel to gas at 1524H. [WEBSMS] | CLUZ
3/3/2022 2:53:00 PM | LRCC-03/03/2022 14:52: San Gabriel on line at 1447H (Unplanned Outage). [WEBSMS] | CLUZ
3/3/2022 2:14:00 PM | LRCC-03/03/2022 14:12: SLTEC 1 online at 1402H (Unplanned Outage). [WEBSMS] | CLUZ
3/3/2022 12:57:00 PM | LRCC-03/03/2022 12:55: San Gabriel tripped at 1250H, lowest frequency reach at 59.523Hz (Unplanned Outage). [WEBSMS] | CLUZ
3/3/2022 12:21:00 PM | LRCC-03/03/2022 12:21: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12453MW, PK=10295MW, RR=402MW, NetOpMargin: PM=1756, EVE=2201 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, San Gabriel at 210MW, GMEC 2 at 300MW, Sta. Rita 40 at 220MW [WEBSMS] | CLUZ
3/3/2022 11:53:00 AM | LRCC-03/03/2022 11:52: Ilijan B2 shutdown at 1140H (Planned Outage). [WEBSMS] | CLUZ
3/3/2022 8:29:00 AM | LRCC-03/03/2022 08:28: Maximum peak of the year is 10345MW occurred on March 2, 2022 at 1418H. [WEBSMS] | CLUZ
3/3/2022 6:24:00 AM | LRCC-03/03/2022 06:24: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12753MW, PK=10103MW, RR=392MW, NetOpMargin: AM=2258, PM=2019, EVE=2359 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, San Gabriel at 210MW, GMEC 2 at 300MW, Sta. Rita 40 at 220MW [WEBSMS] | CLUZ
3/2/2022 9:58:00 PM | LRCC-03/02/2022 21:57: Ilijan A1 online at 2155H. (Unplanned Outage) [WEBSMS] | CLUZ
3/2/2022 5:46:00 PM | LRCC-03/02/2022 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12190MW, PK=9813MW, RR=376MW, NetOpMargin: EVE=2001 Highest Unit O/L: Dinginin @ 668MW Derated Plant: GMEC2 @ 305MW, Pagbilao 3 @ 340MW, Ilijan A/B @ 851MW, San Gabriel @ 210MW, Sta. Rita 40 @ 220MW [WEBSMS] | CLUZ
3/2/2022 3:51:00 PM | LRCC-03/02/2022 15:50: Laoag-Currimao 115kV Line restored at 1533H (Planned Outage). [WEBSMS] | CLUZ
3/2/2022 3:50:00 PM | LRCC-03/02/2022 15:50: Laoag-Currimao 115kV Line restored at 1533H (Planned Outage). [WEBSMS] | CLUZ
3/2/2022 10:22:00 AM | LRCC-03/02/2022 10:20: Balsik-Olongapo restored at 1014H (Unplanned Outage). [WEBSMS] | CLUZ
3/2/2022 9:31:00 AM | LRCC-03/02/2022 09:31: Balsik-Olongapo tripped at 0915H (Unplanned Outage) [WEBSMS] | CLUZ
3/2/2022 8:09:00 AM | LRCC-03/02/2022 08:08: Laoag-Currimao 115kV Line de-energized at 0806H (Planned Outage). [WEBSMS] | CLUZ
3/2/2022 5:56:00 AM | LRCC-03/02/2022 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12650MW, PK=10057MW, RR=390MW, NetOpMargin: AM=2203, PM=1860, EVE=2131 Highest Unit O/L: Dinginin @ 668MW Derated Plant: GMEC2 @ 305MW, Pagbilao 3 @ 340MW, Ilijan A/B @ 778MW, San Gabriel @ 210MW, Sta. Rita 40 @ 220MW [WEBSMS] | CLUZ
3/1/2022 5:44:00 PM | LRCC-03/01/2022 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12244MW, PK=9660MW, RR=370MW, NetOpMargin: EVE=2214 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 305MW, Masinloc 1 at 300MW, Pagbilao 3 at 335MW, SLTEC 2 at 50MW, Ilijan at 778MW, Sta Rita 40 at 220MW and San Gabriel at 210MW [WEBSMS] | CLUZ
3/1/2022 3:24:00 PM | LRCC-03/01/2022 15:23: Kalayaan 2 on line at 1520H (Unplanned Outage). [WEBSMS] | CLUZ
3/1/2022 2:32:00 PM | LRCC-03/01/2022 14:31: Kalayaan 2 at 90MW tripped at 1422H, lowest frequency reach is 60.03Hz (Unplanned Outage). [WEBSMS] | CLUZ
3/1/2022 12:20:00 PM | LRCC-03/01/2022 12:18: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12675MW, PK=9894MW, RR=398MW, NetOpMargin: PM=2383, EVE=2590 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 305MW, Masinloc 1 at 300MW, Pagbilao 3 at 335MW, SLTEC 2 at 40MW, Ilijan at 778MW, Sta Rita 40 at 220MW and San Gabriel at 210MW [WEBSMS] | CLUZ
3/1/2022 6:06:00 AM | LRCC-03/01/2022 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12694MW, PK=9706MW, RR=390MW, NetOpMargin: AM=2598, PM=2310, EVE=2549 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 305MW, Masinloc 1 at 300MW, Pagbilao 3 at 335MW, SLTEC 2 at 25MW, Ilijan at 778MW, Sta Rita 40 at 220MW and San Gabriel at 210MW [WEBSMS] | CLUZ
3/1/2022 6:05:00 AM | LRCC-03/01/2022 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12694MW, PK=9706MW, RR=390MW, NetOpMargin: AM=2598, PM=2310, EVE=2549 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 305MW, Masinloc 1 at 300MW, Pagbilao 3 at 335MW, SLTEC 2 at 25MW, Ilijan at 778MW, Sta Rita 40 at 220MW and San Gabriel at 210MW [WEBSMS] | CLUZ
3/1/2022 5:24:00 AM | LRCC-03/01/2022 05:22: Weather Update: Trough of Low Pressure Area affecting the southern section of Mindanao. Metro Manila and the rest of the country will have partly cloudy to cloudy skies with isolated rainshowers or thunderstorms. [WEBSMS] | CLUZ
3/1/2022 5:23:00 AM | LRCC-03/01/2022 05:22: Weather Update: Trough of Low Pressure Area affecting the southern section of Mindanao. Metro Manila and the rest of the country will have partly cloudy to cloudy skies with isolated rainshowers or thunderstorms. [WEBSMS] | CLUZ
2/28/2022 7:35:00 PM | LRCC-02/28/2022 19:35: Ilijan B GT-2 online at 1927H. (Unplanned Outage) [WEBSMS] | CLUZ
2/28/2022 7:23:00 PM | LRCC-02/28/2022 19:23: Balsik 230kV Bus 1 commissioning and energization was completed at 1921H. [WEBSMS] | CLUZ
2/28/2022 6:36:00 PM | LRCC-02/28/2022 18:34: Balsik 230kV Bus 1 energized at 1832H. (On-going commissioning and energization) [WEBSMS] | CLUZ
2/28/2022 5:41:00 PM | LRCC-02/28/2022 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11777MW, PK=9478MW, RR=372MW, NetOpMargin: EVE=1927 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Pagbilao 3 at 335MW, Masinloc 1 at 300MW, Ilijan at 580MW, GMEC 2 at 240MW, SLTEC 2 at 20MW [WEBSMS] | CLUZ
2/28/2022 12:57:00 PM | LRCC-02/28/2022 12:56: Ilijan A1 offline at 1212H. (Unplanned Outage) [WEBSMS] | CLUZ
2/28/2022 12:50:00 PM | LRCC-02/28/2022 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12178MW, PK=9930MW, RR=394MW, NetOpMargin: PM=1854, EVE=2161 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Pagbilao 3 at 335MW, Masinloc 1 at 300MW, Ilijan at 580MW, GMEC 2 at 300MW, SLTEC 2 at 11MW, SLPGC 2 at 130MW, Sta Rita 10 at 161MW and Sta Rita 40 at 161MW [WEBSMS] | CLUZ
2/28/2022 11:17:00 AM | LRCC-02/28/2022 11:15: San Gabriel online at 1111H (Unplanned Outage). [WEBSMS] | CLUZ
2/28/2022 7:01:00 AM | LRCC-02/28/2022 07:00: Mauban-QPPL 230kV Line 2 restored at 0649H (Planned Outage). [WEBSMS] | CLUZ
2/28/2022 6:04:00 AM | LRCC-02/28/2022 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11811MW, PK=9587MW, RR=375MW, NetOpMargin: AM=1849, PM=1653, EVE=1788 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Pagbilao 3 at 335MW, Masinloc 1 at 300MW, Ilijan at 603MW, GMEC 2 at 300MW, SLTEC 2 at 11MW, SLPGC 2 at 130MW, Sta Rita 10 at 161MW and Sta Rita 40 at 161MW [WEBSMS] | CLUZ
2/28/2022 5:29:00 AM | LRCC-02/28/2022 05:28: Mexico-Hermosa 230kV line restored at 2227H. (Unplanned Outage) [WEBSMS] | CLUZ
2/27/2022 11:19:00 PM | LRCC-02/27/2022 23:18: Muntinlupa(Sucat)-Filinvest 115kV line restored at 2318H. (Planned Outage) [WEBSMS] | CLUZ
2/27/2022 11:08:00 PM | LRCC-02/27/2022 23:06: For info: SLTEC Unit 2 online at 2230H. (Unplanned Outage) [WEBSMS] | CLUZ
2/27/2022 9:06:00 PM | LRCC-02/27/2022 21:04: Mexico-Hermosa 230kV 1 line tried to energize from Hermosa side at 2051H but tripped with SOTF relay indication. (On-going restoration from an unplanned outage.) The system frequency reached 60.491Hz during the incident. [WEBSMS] | CLUZ
2/27/2022 8:01:00 PM | LRCC-02/27/2022 20:01: Commissioning of San Rafael(CND) 100MVA T01 upgraded transformer protection system was completed at 1959H. [WEBSMS] | CLUZ
2/27/2022 7:47:00 PM | LRCC-02/27/2022 19:45: San Rafael(CND) 100MVA T01 energized at 1943H. On-going commissioning of upgraded transformer protection system. [WEBSMS] | CLUZ
2/27/2022 6:46:00 PM | LRCC-02/27/2022 18:45: San Rafael(CND) 230kV Bus 2 energized at 1843H. (Planned Outage) [WEBSMS] | CLUZ
2/27/2022 5:51:00 PM | LRCC-02/27/2022 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11178MW, PK=9078MW, RR=337MW, NetOpMargin: EVE=1763 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 603MW, Pagbilao 3 at 335MW, Masinloc 1 at 300MW, GMEC 2 at 300MW, Sta. Rita 10 and 40 at 161MW each, San Lorenzo 60 at 105MW, SLPGC 2 at 75MW [WEBSMS] | CLUZ
2/27/2022 5:00:00 PM | LRCC-02/27/2022 16:57: Lumban-Malaya 230kV Line 2 restored at 1655H. (Planned Outage) [WEBSMS] | CLUZ
2/27/2022 12:53:00 PM | LRCC-02/27/2022 12:51: Sual Unit 1 online at 1248H. (Planned Outage) [WEBSMS] | CLUZ
2/27/2022 12:41:00 PM | LRCC-02/27/2022 12:40: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10880MW, PK=8308MW, RR=318MW, NetOpMargin: PM=1374, EVE=1474 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 603MW, Pagbilao 1 at 210MW, Pagbilao 3 at 335MW, Masinloc 1 at 300MW, GMEC 2 at 300MW, Sta. Rita 10 and 40 at 161MW each, SLPGC 2 at 75MW [WEBSMS] | CLUZ
2/27/2022 9:36:00 AM | LRCC-02/27/2022 09:35: Mexico - Hermosa 230kV Line 1 de-energized at 0934H. (Unplanned Outage) [WEBSMS] | CLUZ
2/27/2022 9:20:00 AM | LRCC-02/27/2022 09:18: Mexico - Hermosa 230kV Line 2 restored at 0917H. (Planned Outage) [WEBSMS] | CLUZ
2/27/2022 9:19:00 AM | LRCC-02/27/2022 09:18: Mexico - Hermosa 230kV Line 2 restored at 0917H. (Planned Outage) [WEBSMS] | CLUZ
2/27/2022 8:32:00 AM | LRCC-02/27/2022 08:31: Mauban-QPPL 230kV Line 2 de-energized at 0757H (Planned Outage). [WEBSMS] | CLUZ
2/27/2022 7:45:00 AM | LRCC-02/27/2022 07:45: San Rafael 230kV Bus 2 de-energized at 0742H (Planned Outage). [WEBSMS] | CLUZ
2/27/2022 7:25:00 AM | LRCC-02/27/2022 07:24: Mexico-Hermosa 230kV Line 2 de-energized at 0721H. (Planned Outage) [WEBSMS] | CLUZ
2/27/2022 6:41:00 AM | LRCC-02/27/2022 06:40: Quezon 300MVA T08 restored at 0621H. (Planned Outage) [WEBSMS] | CLUZ
2/27/2022 6:40:00 AM | LRCC-02/27/2022 06:39: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=10984MW, PK=8434MW, RR=315MW, NetOpMargin: AM=1354, PM=1276, EVE=1109 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, Pagbilao 3 at 335MW, Masinloc 1 at 300MW, Ilijan at 603MW, Sta Rita 10 at 161MW and Sta Rita 40 at 161MW [WEBSMS] | CLUZ
2/27/2022 5:57:00 AM | LRCC-02/27/2022 05:56: Weather Update: Easterlies affecting the country. Metro Manila and the rest of the country will be partly cloudy to cloudy skies with isolated rainshowers or thunderstorms. [WEBSMS] | CLUZ
2/27/2022 1:37:00 AM | LRCC-02/27/2022 01:36: Hermosa-Mexico 230kV line 1 restored at 0134H. (Planned Outage) [WEBSMS] | CLUZ
2/27/2022 12:20:00 AM | LRCC-02/27/2022 00:18: Muntinlupa-Filinvest 115kV line de-energized at 0018H. (Planned Outage) [WEBSMS] | CLUZ
2/26/2022 7:13:00 PM | LRCC-02/26/2022 19:12: San Lorenzo Module 60 online at 1908H. (Unplaned Outage) [WEBSMS] | CLUZ
2/26/2022 6:36:00 PM | LRCC-02/26/2022 18:34: San Lorenzo Module 60 tripped at 1826H (Unplanned Outage). [WEBSMS] | CLUZ
2/26/2022 5:46:00 PM | LRCC-02/26/2022 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10118MW, PK=8608MW, RR=1152MW, NetOpMargin: EVE=1152 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 603MW, Pagbilao 3 at 335MW, Masinloc 1 at 300MW, GMEC 2 at 300MW, Sta. Rita 10 and 40 at 161MW each, SLPGC 2 at 75MW [WEBSMS] | CLUZ
2/26/2022 5:02:00 PM | LRCC-02/26/2022 17:00: Lumban-Malaya 230kV Line 1 restored at 1654H. (Planned Outage) [WEBSMS] | CLUZ
2/26/2022 1:16:00 PM | LRCC-02/26/2022 13:16: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10637MW, PK=8816MW, RR=358MW, NetOpMargin: PM=1463, EVE=1095 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 603MW, Pagbilao 3 at 335MW, Masinloc 1 at 300MW, GMEC 2 at 300MW, Sta. Rita 10 and 40 at 161MW each, SLPGC 2 at 75MW [WEBSMS] | CLUZ
2/26/2022 1:10:00 PM | LRCC-02/26/2022 13:09: Sta. Rita 30 offline at 1301H (Unplanned Outage) [WEBSMS] | CLUZ
2/26/2022 9:19:00 AM | LRCC-02/26/2022 09:18: Mexico-Hermosa 230kV Line 1 de-energized at 0918H (Planned Outage). [WEBSMS] | CLUZ
2/26/2022 7:30:00 AM | LRCC-02/26/2022 07:29: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=10938MW, PK=8733MW, RR=0MW, NetOpMargin: AM=913, PM=730, EVE=1189 Highest Unit O/L: GNPD 1 @668MW Derated Plant: GN POWER 2 @300MW; MASINLOC 1 @280MW; PAGBILAO 3 @335MW; SLPGC 2 @75MW; ILJJAN A / B @603MW; STA RITA 10 @161MW; STA RITA 40 @161MW [WEBSMS] | CLUZ
2/26/2022 3:06:00 AM | LRCC-02/26/2022 03:05: Dasmarinas - Ilijan 500kV Line restored at 0301H (Planned Outage) [WEBSMS] | CLUZ
2/26/2022 12:12:00 AM | LRCC-02/26/2022 00:12: Dasmarinas-Ilijan 500kV Line de-energized at 0012H (Planned Outage). [WEBSMS] | CLUZ
2/25/2022 11:16:00 PM | LRCC-02/25/2022 23:14: Binan 300MVA T03 restored at 2313H (Planned Outage). [WEBSMS] | CLUZ
2/25/2022 10:21:00 PM | LRCC-02/25/2022 22:19: San Lorenzo Module 60 offline at 2213H (Planned Outage) [WEBSMS] | CLUZ
2/25/2022 6:20:00 PM | LRCC-02/25/2022 18:20: San Lorenzo Module 60 on-line at 1817H (Unplanned Outage) [WEBSMS] | CLUZ
2/25/2022 5:52:00 PM | LRCC-02/25/2022 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10600MW, PK=8959MW, RR=364MW, NetOpMargin: EVE=1277 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: GMEC 2 at 300MW, Masinloc 1 at 300MW, Pagbilao 3 at 335MW, Ilijan at 603MW, Sta Rita 10 at 161MW, Sta Rita 40 at 161MW and SLPGC 2 at 75MW [WEBSMS] | CLUZ
2/25/2022 4:07:00 PM | LRCC-02/25/2022 16:06: SLTEC 2 tripped at 1603H from 81MW. (Unplanned Outage) [WEBSMS] | CLUZ
2/25/2022 3:20:00 PM | LRCC-02/25/2022 15:18: San Lorenzo Module 60 tripped at 1516H from 74MW. The lowest frequency is 59.85Hz. (Unplanned Outage) [WEBSMS] | CLUZ
2/25/2022 3:04:00 PM | LRCC-02/25/2022 15:02: Bolo(Kadampat)-Sual 230kV line 1 looped at Sual side at 1501H. (Unplanned Outage) [WEBSMS] | CLUZ
2/25/2022 2:36:00 PM | LRCC-02/25/2022 14:35: Bolo(Kadampat)-Sual 230kV line 1 unlooped at Sual side at 1432H. An unplanned outage to facilitate refilling of Sual PCB CB04(8LI1SUA-BLZ)SUA. [WEBSMS] | CLUZ
2/25/2022 2:35:00 PM | LRCC-02/25/2022 14:35: Bolo(Kadampat)-Sual 230kV line 1 unlooped at Sual side at 1432H. An unplanned outage to facilitate refilling of Sual PCB CB04(8LI1SUA-BLZ)SUA. [WEBSMS] | CLUZ
2/25/2022 11:41:00 AM | LRCC-02/25/2022 11:39: San Lorenzo Module 60 online at 1134H. (Planned Outage) [WEBSMS] | CLUZ
2/25/2022 6:51:00 AM | LRCC-02/25/2022 06:50: Hermosa-Balsik 230kV tie line 1 commissioning and energization was completed at 0648H. [WEBSMS] | CLUZ
2/25/2022 6:40:00 AM | LRCC-02/25/2022 06:38: Hermosa-Balsik 230kV Tie line 1 looped at 0637H. (On-going Commissioning and Energization) [WEBSMS] | CLUZ
2/25/2022 6:03:00 AM | LRCC-02/25/2022 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11073MW, PK=8881MW, RR=354MW, NetOpMargin: AM=1838, PM=1592, EVE=1112 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 603MW, Masinloc 1 at 300MW, GMEC 1 at 150MW, GMEC 2 at 300MW, Sta. Rita 10 and 20 at 161MW each, SLPGC 2 at 75MW, SLTEC 2 at 65MW [WEBSMS] | CLUZ
2/25/2022 5:22:00 AM | LRCC-02/25/2022 05:20: Hermosa 230kV Bus 2 restored at 0519H (Planned Outage). [WEBSMS] | CLUZ
2/25/2022 5:10:00 AM | LRCC-02/25/2022 05:09: Weather Update: Trough of Low Pressure Area affecting Mindanao. Shear line affecting the eastern section of Northern Luzon. [WEBSMS] | CLUZ
2/25/2022 3:58:00 AM | LRCC-02/25/2022 03:57: Taytay(Dolores) 300MVA T03 & 115kV Bus 2 energized at 0354H and 0353H, respectively (Planned Outage). [WEBSMS] | CLUZ
2/25/2022 12:16:00 AM | LRCC-02/25/2022 00:15: Taytay(Dolores) 300MVA T03 & 115kV Bus 2 de-energized at 0014H and 0011H, respectively (Planned Outage). [WEBSMS] | CLUZ
2/24/2022 11:38:00 PM | LRCC-02/24/2022 23:37: San Gabriel offline at 2333H (Unplanned Outage) [WEBSMS] | CLUZ
2/24/2022 7:01:00 PM | LRCC-02/24/2022 19:00: Quezon(Balintawak) 115kV Bus 2 restored at 1813H. (Unplanned Outage) [WEBSMS] | CLUZ
2/24/2022 6:13:00 PM | LRCC-02/24/2022 18:13: Quezon(Balintawak) 115kV Bus 2 de-energized at 1759H. (Unplanned Outage) [WEBSMS] | CLUZ
2/24/2022 5:42:00 PM | LRCC-02/24/2022 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11278MW, PK=9321MW, RR=362MW, NetOpMargin: EVE=1595 Highest Unit O/L: GNPD 1 at 668MW Derated Plant: Pagbilao 3 at 335MW, Masinloc 1 at 300MW, San Gabriel at 210MW, and SLTEC 2 at 40MW [WEBSMS] | CLUZ
2/24/2022 2:56:00 PM | LRCC-02/24/2022 14:55: Muntinlupa-Filinvest 115kV line looped at 1453H(Muntinlupa side). (Unplanned Outage) [WEBSMS] | CLUZ
2/24/2022 2:50:00 PM | LRCC-02/24/2022 14:48: Muntinlupa-Filinvest 115kV line auto-tripped at both sides/autoreclosed at Filinvest side at 1443H. (Unplanned Outage) [WEBSMS] | CLUZ
2/24/2022 1:09:00 PM | LRCC-02/24/2022 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11620MW, PK=9819MW, RR=375MW, NetOpMargin: PM=1426, EVE=1647 Highest Unit O/L: GNPD Unit 1 at 668MW Derated Plant: Pagbilao 3 at 335MW, Masinloc 1 at 300MW, SLTEC 2 at 35MW, and San Gabriel at 210MW [WEBSMS] | CLUZ
2/24/2022 5:49:00 AM | LRCC-02/24/2022 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11641MW, PK=9653MW, RR=384MW, NetOpMargin: AM=1604, PM=1547, EVE=1621 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MASINLOC 1 @300MW; PAGBILAO 3 @335MW; SLTEC 2 @25MW; ILJJAN A / B @1024MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
2/24/2022 1:40:00 AM | LRCC-02/24/2022 01:37: SCPC Unit 2 synchronized at 0132H (Planned outage). [WEBSMS] | CLUZ
2/24/2022 1:39:00 AM | LRCC-02/24/2022 01:37: SCPC Unit 2 synchronized at 0132H (Planned outage). [WEBSMS] | CLUZ
2/24/2022 12:01:00 AM | LRCC-02/23/2022 23:59: Sual Unit 1 shutdown at 2340H (Planned outage). [WEBSMS] | CLUZ
2/23/2022 11:59:00 PM | LRCC-02/23/2022 23:58: SLPGC Unit 2 synchronized at 2205H (Unplanned outage). [WEBSMS] | CLUZ
2/23/2022 9:24:00 PM | LRCC-02/23/2022 21:22: SLPGC 2 (20MW) tripped at 2113H (Unplanned Outage) [WEBSMS] | CLUZ
2/23/2022 9:22:00 PM | LRCC-02/23/2022 21:21: Dona Imelda(Araneta) 230kV Bus 1 de-energized at 2121H (Planned Outage). [WEBSMS] | CLUZ
2/23/2022 7:12:00 PM | LRCC-02/23/2022 19:11: SLPGC 2 online at 1907H (Planned Outage) [WEBSMS] | CLUZ
2/23/2022 6:52:00 PM | LRCC-02/23/2022 18:51: Ilijan B1 online at 1849 (Unplanned Outage). [WEBSMS] | CLUZ
2/23/2022 5:57:00 PM | LRCC-02/23/2022 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11410MW, PK=9288MW, RR=370MW, NetOpMargin: EVE=1752 Highest Unit O/L: GNPD Unit 1 at 668MW Derated Plant: Pagbilao 3 at 335MW, Masinloc 1 at 300MW and San Gabriel at 210MW(due to natural gas supply restriction) [WEBSMS] | CLUZ
2/23/2022 5:33:00 PM | LRCC-02/23/2022 17:32: Naga-Tayabas 230kV line 2 restored at 1731H. (Planned Outage) [WEBSMS] | CLUZ
2/23/2022 1:27:00 PM | LRCC-02/23/2022 13:25: SLTEC Unit 2 online at 1323H. (Unplanned Outage) [WEBSMS] | CLUZ
2/23/2022 12:46:00 PM | LRCC-02/23/2022 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11764MW, PK=9699MW, RR=375MW, NetOpMargin: PM=1690, EVE=1742 Highest Unit O/L: GNPD Unit 1 at 668MW Derated Plant: Pagbilao 3 at 335MW, Masinloc 1 at 300MW and San Gabriel at 210MW(due to gas supply restriction) [WEBSMS] | CLUZ
2/23/2022 6:14:00 AM | LRCC-02/23/2022 06:13: Naga-Tayabas 230kV line 2 de-energized at 0610H. (Planned Outage) [WEBSMS] | CLUZ
2/23/2022 6:12:00 AM | LRCC-02/23/2022 06:11: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11999MW, PK=9594MW, RR=375MW, NetOpMargin: AM=2030, PM=1745, EVE=1904 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MASINLOC 1 @300MW; PAGBILAO 3 @335MW [WEBSMS] | CLUZ
2/22/2022 9:31:00 PM | LRCC-02/22/2022 21:30: Dona Imelda(Araneta) 230kV Bus 2 de-energized at 2129H (Planned Outage). [WEBSMS] | CLUZ
2/22/2022 2:03:00 PM | LRCC-02/22/2022 14:03: Ilijan B-1 shutdown at 1400H. (Unplanned Outage) [WEBSMS] | CLUZ
2/22/2022 9:59:00 AM | LRCC-02/22/2022 09:57: Ilijan A-2 online at 0954H. (Unplanned Outage) [WEBSMS] | CLUZ
2/22/2022 5:24:00 AM | LRCC-02/22/2022 05:22: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11603MW, PK=9987MW, RR=375MW, NetOpMargin: AM=1241, PM=931, EVE=1239 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @300MW, Pagbilao 3 @335MW, Ilijan @ 887MW & San Gabriel @210MW [WEBSMS] | CLUZ
2/22/2022 4:59:00 AM | LRCC-02/22/2022 04:58: Weather Update: Shear Line affecting the eastern section of Visayas. Northeast Monsoon affecting Luzon and the rest of Visayas. [WEBSMS] | CLUZ
2/21/2022 5:50:00 PM | LRCC-02/21/2022 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11413MW, PK=9389MW, RR=371MW, NetOpMargin: EVE=1653 Highest Unit O/L: GNPD 1 @668MW Derated Plant: PAGBILAO 3 @335MW; ILJJAN A / B @888MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
2/21/2022 12:57:00 PM | LRCC-02/21/2022 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11753MW, PK=9998MW, RR=375MW, NetOpMargin: PM=1380, EVE=1615 Highest Unit O/L: GNPD 1 @668MW Derated Plant: PAGBILAO 3 @335MW; ILJJAN A / B @888MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
2/21/2022 5:59:00 AM | LRCC-02/21/2022 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11865MW, PK=9759MW, RR=389MW, NetOpMargin: AM=1717, PM=1507, EVE=1630 Highest Unit O/L: GNPD Unit 1 at 668MW Derated Plant: Pagbilao 3 at 335MW, Ilijan at 888MW and San Gabriel at 210MW [WEBSMS] | CLUZ
2/21/2022 5:43:00 AM | LRCC-02/21/2022 05:42: Weather Update: Northeast Monsoon affecting Luzon. Metro Manila and the rest of Luzon will have partly cloudy to cloudy skies with isolated light rains. The rest of the country will experience partly cloudy to cloudy skies with isolated rainshowers or thunderstorms. [WEBSMS] | CLUZ
2/21/2022 1:10:00 AM | LRCC-02/21/2022 01:09: Commissioning and energization of new protection system for Mexico-San Rafael(CND) 230kV line 1 was completed at 0108H. [WEBSMS] | CLUZ
2/21/2022 12:48:00 AM | LRCC-02/21/2022 00:48: Mexico-San Rafael(CND) 230kV line 1 looped at 0046H. On-going commissioning and energization of new protection system. [WEBSMS] | CLUZ
2/21/2022 12:27:00 AM | LRCC-02/21/2022 00:25: Commissioning of New Main 2 Protection for San Jose-Tayabas 500kV line 2 was completed at 0022H. [WEBSMS] | CLUZ
2/21/2022 12:25:00 AM | LRCC-02/21/2022 00:23: San Jose-Tayabas 500kV line 2 commissioning of New Main 2 Protection was completed at 0022H. [WEBSMS] | CLUZ
2/21/2022 12:06:00 AM | LRCC-02/21/2022 00:04: San Jose-Tayabas 500kV line 2 looped at 0002H. On-going commissioning of New Main 2 Protection. [WEBSMS] | CLUZ
2/21/2022 12:05:00 AM | LRCC-02/21/2022 00:04: San Jose-Tayabas 500kV line 2 looped at 0002H. On-going commissioning of New Main 2 Protection. [WEBSMS] | CLUZ
2/20/2022 6:51:00 PM | LRCC-02/20/2022 18:50: Subic 55MVA T01 energized at 1847H (Planned Outage). [WEBSMS] | CLUZ
2/20/2022 6:10:00 PM | LRCC-02/20/2022 18:08: Bacnotan-CIP II 69kV line restored at 1805H. (Planned Outage) [WEBSMS] | CLUZ
2/20/2022 5:46:00 PM | LRCC-02/20/2022 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11193MW, PK=8755MW, RR=333MW, NetOpMargin: EVE=2105 Highest Unit O/L: GNPD 1 @668MW Derated Plant: PAGBILAO 3 @335MW; ILJJAN A / B @888MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
2/20/2022 3:40:00 PM | LRCC-02/20/2022 15:38: Sta Rita 10 offline at 1257H (Unplanned Outage). [WEBSMS] | CLUZ
2/20/2022 3:30:00 PM | LRCC-02/20/2022 15:29: Sta Rita 10 online at 1526H (Unplanned Outage). [WEBSMS] | CLUZ
2/20/2022 10:56:00 AM | LRCC-02/20/2022 10:54: GMEC 2 tripped at 1052H (Unplanned Outage). Lowest frequency = 59.754Hz. [WEBSMS] | CLUZ
2/20/2022 10:45:00 AM | LRCC-02/20/2022 10:43: Sta Rita 10 online at 1041H (Unplanned Outage). [WEBSMS] | CLUZ
2/20/2022 10:26:00 AM | LRCC-02/20/2022 10:25: GMEC 2 online at 1021H (Unplanned Outage). [WEBSMS] | CLUZ
2/20/2022 8:52:00 AM | LRCC-02/20/2022 08:52: Sta Rita 10 tripped at 0844H, Lowest Frequency =59.679Hz (Unplanned Outage) [WEBSMS] | CLUZ
2/20/2022 8:07:00 AM | LRCC-02/20/2022 08:06: San Jose-Tayabas 500kV Line 2 de-energized at 0805H (Planned Outage). [WEBSMS] | CLUZ
2/20/2022 7:40:00 AM | LRCC-02/20/2022 07:39: Sta Rita 10 online at 0728H (Planned Outage) [WEBSMS] | CLUZ
2/20/2022 6:48:00 AM | LRCC-02/20/2022 06:48: San Rafael 230kV Bus 1 de-energized at 0647H (Planned Outage). [WEBSMS] | CLUZ
2/20/2022 5:33:00 AM | LRCC-02/20/2022 05:32: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
2/20/2022 5:32:00 AM | LRCC-02/20/2022 05:32: Weather Update: Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
2/20/2022 1:07:00 AM | LRCC-02/20/2022 01:05: Dasmarinas-Tayabas 500kV Line restored at 0105H (Planned Outage) [WEBSMS] | CLUZ
2/20/2022 12:51:00 AM | LRCC-02/20/2022 00:50: Sta Rita 10 shutdown at 0048H (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 10:15:00 PM | LRCC-02/19/2022 22:13: Dasmarinas-Tayabas 500kV Line de-energized at 2206H (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 9:40:00 PM | LRCC-02/19/2022 21:40: Subic(Enron) 55MVA Main Unit Transformer No. 2 restored at 2136H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 5:56:00 PM | LRCC-02/19/2022 17:54: Malaya-Ingrid 230kV line 2 restored at 1753H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 5:55:00 PM | LRCC-02/19/2022 17:54: Malaya-Ingrid 230kV line 2 restored at 1753H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 5:53:00 PM | LRCC-02/19/2022 17:51: Malaya 230kV Bus 1 energized at 1751H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 4:48:00 PM | LRCC-02/19/2022 16:47: Lumban-Bay(Makban) 230kV line 1 restored at 1646H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 4:44:00 PM | LRCC-02/19/2022 16:42: Lumban 230kV Bus 2 energized at 1639H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 1:08:00 PM | LRCC-02/19/2022 13:06: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10844MW, PK=8991MW, RR=361MW, NetOpMargin: PM=1493, EVE=1202 Highest Unit O/L: GNPD Unit 1 at 668MW Derated Plant: Pagbilao 3 at 335MW, Ilijan at 888MW, and San Gabriel at 210MW [WEBSMS] | CLUZ
2/19/2022 10:38:00 AM | LRCC-02/19/2022 10:37: Malaya-Ingrid 230kV line de-energized at 1029H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 10:37:00 AM | LRCC-02/19/2022 10:37: Malaya-Ingrid 230kV line de-energized at 1029H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 10:31:00 AM | LRCC-02/19/2022 10:29: Malaya 230kV Bus 1 de-energized at 1029H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 10:30:00 AM | LRCC-02/19/2022 10:29: Malaya 230kV Bus 1 de-energized at 1029H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 10:20:00 AM | LRCC-02/19/2022 10:19: San Lorenzo Module 50 Main Unit Transformer de-energized at 1014H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 8:29:00 AM | LRCC-02/19/2022 08:29: Lumban 230kV Bus 2 de-energized at 0828H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 8:25:00 AM | LRCC-02/19/2022 08:25: Lumban-Bay(Makban) 230kV line 1 de-energized at 0823H. (Planned Outage) [WEBSMS] | CLUZ
2/19/2022 5:52:00 AM | LRCC-02/19/2022 05:51: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=10902MW, PK=8861MW, RR=357MW, NetOpMargin: AM=1684, PM=1544, EVE=1156 Highest Unit O/L: GNPD 1 @668MW Derated Plant: PAGBILAO 3 @335MW; ILJJAN A / B @888MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
2/18/2022 6:50:00 PM | LRCC-02/18/2022 18:49: SLPGC 230kV Bus 2 and Calaca-SLPGC 230kV Line 2 restored at 1848H and 1849H, respectively (Planned Outage). [WEBSMS] | CLUZ
2/18/2022 5:44:00 PM | LRCC-02/18/2022 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10860MW, PK=9283MW, RR=364MW, NetOpMargin: EVE=1213 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SCPC 4 @110MW, Pagbilao 3 @335MW, Ilijan @888MW & San Gabriel @210MW [WEBSMS] | CLUZ
2/18/2022 5:34:00 PM | LRCC-02/18/2022 17:31: Daraga-Bacman 230kV Line 1 restored at 1731H (Planned Outage) [WEBSMS] | CLUZ
2/18/2022 5:32:00 PM | LRCC-02/18/2022 17:29: Ilijan A3 (ST1) online at 1727H (Unplanned Outage) [WEBSMS] | CLUZ
2/18/2022 5:31:00 PM | LRCC-02/18/2022 17:29: Ilijan A3 (ST1) online at 1727H (Unplanned Outage) [WEBSMS] | CLUZ
2/18/2022 2:49:00 PM | LRCC-02/18/2022 14:47: GMEC 1 emergency shutdown at 1443H (Unplanned Outage) [WEBSMS] | CLUZ
2/18/2022 2:43:00 PM | LRCC-02/18/2022 14:43: Ilijan Block A Main transformer & Ilijan 500kV Bus B energized at 1442H & 1438H, respectively (Unplanned Outage) [WEBSMS] | CLUZ
2/18/2022 1:16:00 PM | LRCC-02/18/2022 13:14: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11255MW, PK=9847MW, RR=389MW, NetOpMargin: PM=1019, EVE=1418 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SCPC 4 @110MW, Pagbilao 3 @335MW & San Gabriel @210MW [WEBSMS] | CLUZ
2/18/2022 10:14:00 AM | LRCC-02/18/2022 10:13: Correction: Ilijan Block A Main transformer & Ilijan 500kV Bus B de-energized at 1009H & 1010H, respectively (Unplanned Outage) [WEBSMS] | CLUZ
2/18/2022 10:14:00 AM | LRCC-02/18/2022 10:13: Ilijan Block A Main transformer & Ilijan 230kV Bus B de-energized at 1009H & 1010H, respectively (Unplanned Outage) [WEBSMS] | CLUZ
2/18/2022 8:51:00 AM | LRCC-02/18/2022 08:50: Ilijan A3 (ST1) de-energized at 0845H (Unplanned Outage) [WEBSMS] | CLUZ
2/18/2022 8:50:00 AM | LRCC-02/18/2022 08:50: Ilijan A3 (ST1) de-energized at 0845H (Unplanned Outage) [WEBSMS] | CLUZ
2/18/2022 6:21:00 AM | LRCC-02/18/2022 06:20: Daraga-Bacman 230kV Line 1 de-energized at 0619H (Planned Outage) [WEBSMS] | CLUZ
2/18/2022 5:17:00 AM | LRCC-02/18/2022 05:15: Weather Update: Northeast Monsoon affecting Northern Luzon. Metro Manila and the rest of the country will have partly cloudy to cloudy skies with isolated rainshowers or thunderstorms. [WEBSMS] | CLUZ
2/18/2022 4:19:00 AM | LRCC-02/18/2022 04:17: Bacman Unit 3 online at 0351H (Unplanned Outage). [WEBSMS] | CLUZ
2/17/2022 11:33:00 PM | LRCC-02/17/2022 23:32: Binan-Balibago 115kV line de-energized at 2332H. (Planned Outage) [WEBSMS] | CLUZ
2/17/2022 5:42:00 PM | LRCC-02/17/2022 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11147MW, PK=9385MW, RR=370MW, NetOpMargin: EVE=1668 Highest Unit O/L: GNPD 1 @668MW Derated Plant: PAGBILAO 3 @335MW; ILJJAN A / B @888MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
2/17/2022 4:01:00 PM | LRCC-02/17/2022 16:01: Ilijan B1 online at 1559H (Unplanned Outage). [WEBSMS] | CLUZ
2/17/2022 1:09:00 PM | LRCC-02/17/2022 13:09: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11488MW, PK=10013MW, RR=396MW, NetOpMargin: PM=1079, EVE=1375 Highest Unit O/L: GNPD 1 @668MW Derated Plant: PAGBILAO 3 @335MW; SLPGC 1 @135MW; ILJJAN A / B @888MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
2/17/2022 10:19:00 AM | LRCC-02/17/2022 10:18: Commissioning of Hermosa-Balsik 230kV Tie Line 1 completed at 1014H. [WEBSMS] | CLUZ
2/17/2022 7:14:00 AM | LRCC-02/17/2022 07:13: Commissioning of Malaya 300MVA T01 main protection and BFR completed at 0705H. [WEBSMS] | CLUZ
2/17/2022 6:15:00 AM | LRCC-02/17/2022 06:14: Daraga-Bacman 230kV Line 2 de-energized at 0614H (Planned Outage). [WEBSMS] | CLUZ
2/17/2022 6:01:00 AM | LRCC-02/17/2022 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11471MW, PK=9719MW, RR=389MW, NetOpMargin: AM=1363, PM=1146, EVE=1502 Highest Unit O/L: GNPD 1 @668MW Derated Plant: SLPGC 1 @125MW, Pagbilao 3 @330MW, San Gabriel @210MW & Iljan @888MW [WEBSMS] | CLUZ
2/17/2022 3:57:00 AM | LRCC-02/17/2022 03:55: Malaya 300MVA TO1 energized & looped at 0257H & 0352H, respectively. Ongoing commissioning of New Main protection & BFR. [WEBSMS] | CLUZ
2/17/2022 2:42:00 AM | LRCC-02/17/2022 02:42: GMEC 2 emergency shutdown at 0240H (Unplanned Outage) [WEBSMS] | CLUZ
2/16/2022 9:19:00 PM | LRCC-02/16/2022 21:18: New Balsik-Hermosa 230kV Tie Line 1 successfully energized & looped at 2049H & 2118H, respectively. On going commissioning test [WEBSMS] | CLUZ
2/15/2022 6:16:00 AM | LRCC-02/15/2022 06:14: Lumban-Bay 230kV Line 2 de-energized at 0611H (Planned Outage). [WEBSMS] | CLUZ
2/14/2022 5:31:00 PM | LRCC-02/14/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11214MW, PK=9255MW, RR=366MW, NetOpMargin: EVE=1593 Highest Unit O/L: Sual 1 & 2 @600MW Derated Plant: GNPD 1 @499MW, Masinloc 1 @240MW, Pagbilao 3 @ 330MW , San Gabriel @210MW & Iljan @888MW [WEBSMS] | CLUZ
2/14/2022 9:40:00 AM | LRCC-02/14/2022 09:38: San Gabriel shutdown at 0936H (Unplanned Outage) [WEBSMS] | CLUZ
2/14/2022 1:46:00 AM | LRCC-02/14/2022 01:46: Mexico-San Rafael 230KV Line energized and looped at 0141H (Planned Outage), on-going commisioning. [WEBSMS] | CLUZ
2/13/2022 11:53:00 PM | LRCC-02/13/2022 23:52: MUNTINLUPA-FILINVEST 115KV LINE ENERGIZED AND LOOPED AT 2351H (Planned Outage) [WEBSMS] | CLUZ
2/13/2022 11:15:00 PM | LRCC-02/13/2022 23:14: MUNTINLUPA-FILINVEST 115KV LINE DE-ENERGIZED AT 2314H (Planned Outage) [WEBSMS] | CLUZ
2/13/2022 5:49:00 PM | LRCC-02/13/2022 17:46: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11693MW, PK=8166MW, RR=322MW, NetOpMargin: EVE=3205 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1/2 @240MW & Iljan @851MW [WEBSMS] | CLUZ
2/13/2022 5:37:00 PM | LRCC-02/13/2022 17:35: Calaca-Malamig (Sta Rosa) 230kV Line restored at 1735H (Unplanned Outage) [WEBSMS] | CLUZ
2/13/2022 3:47:00 PM | LRCC-02/13/2022 15:45: Hermosa 230kV Bus 2 restored at 1543H (Planned Outage). [WEBSMS] | CLUZ
2/13/2022 3:04:00 PM | LRCC-02/13/2022 15:03: For info: Reported cause of tripping of Calaca-Malamig (Sta Rosa) 230kV Line was detached insulator Phase C at tower 118 along Brgy. Imus, Calaca, Batangas [WEBSMS] | CLUZ
2/13/2022 12:25:00 PM | LRCC-02/13/2022 12:23: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12166MW, PK=7979MW, RR=303MW, NetOpMargin: PM=3884, EVE=3043 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1 @240MW & Iljan @851MW [WEBSMS] | CLUZ
2/13/2022 11:22:00 AM | LRCC-02/13/2022 11:20: Binga-Ambuklao 230kV Line 1 tripped at Ambukao side only at 1103H. Looped at 1118H (Unplanned Outage) [WEBSMS] | CLUZ
2/13/2022 6:42:00 AM | LRCC-02/13/2022 06:41: Nagsaag 600MVA TO2 de-energized at 0640H (Planned Outage) [WEBSMS] | CLUZ
2/13/2022 5:53:00 AM | LRCC-02/13/2022 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12158MW, PK=8493MW, RR=304MW, NetOpMargin: AM=3361, PM=3370, EVE=2432 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, Masinloc 1 at 290MW, Masinloc 3 at 200MW, GMEC 2 at 150MW [WEBSMS] | CLUZ
2/13/2022 5:52:00 AM | LRCC-02/13/2022 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12158MW, PK=8493MW, RR=304MW, NetOpMargin: AM=3361, PM=3370, EVE=2432 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 851MW, Masinloc 1 at 290MW, Masinloc 3 at 200MW, GMEC 2 at 150MW [WEBSMS] | CLUZ
2/13/2022 2:35:00 AM | LRCC-02/13/2022 02:35: Cabanatuan - San Rafael(CND) 230kV Line 1 energized and looped at 0232H. (On-going commissioning) [WEBSMS] | CLUZ
2/13/2022 2:01:00 AM | LRCC-02/13/2022 01:59: For info: San Gabriel on emergency shutdown at 0037H due to Malampaya gas restriction. [WEBSMS] | CLUZ
2/13/2022 12:00:00 AM | LRCC-02/12/2022 23:59: Bolo 600MVA T01 de-energized at 2357H. (Unplanned Outage) [WEBSMS] | CLUZ
2/12/2022 9:19:00 PM | LRCC-02/12/2022 21:18: Malaya 230kV Bus B restored at 2117H. (Planned Outage) [WEBSMS] | CLUZ
2/12/2022 8:08:00 PM | LRCC-02/12/2022 20:07: GMEC Unit 2 online at 2001H. (Unplanned Outage) [WEBSMS] | CLUZ
2/12/2022 6:54:00 PM | LRCC-02/12/2022 18:52: Masinloc Unit 3 online at 1846H. (Unplanned Outage) [WEBSMS] | CLUZ
2/12/2022 5:59:00 PM | LRCC-02/12/2022 17:57: Dasmarinas-Amadeo 230kV Line 1 restored at 1757H (Planned Outage). [WEBSMS] | CLUZ
2/12/2022 5:24:00 PM | LRCC-02/12/2022 17:23: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11096MW, PK=8818MW, RR=333MW, NetOpMargin: EVE=1945 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Pagbilao 3 @ 330MW, Masinloc 1 @290MW, San Gabriel @250MW & Iljan @851MW [WEBSMS] | CLUZ
2/12/2022 3:53:00 PM | LRCC-02/12/2022 15:51: Masinloc 3 tripped at 298MW at 1546H (Unplanned Outage). [WEBSMS] | CLUZ
2/12/2022 12:31:00 PM | LRCC-02/12/2022 12:29: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11640MW, PK=8780MW, RR=337MW, NetOpMargin: PM=2523, EVE=2250 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Pagbilao 3 @ 231MW, Masinloc 1/2 @240MW/330MW, San Gabriel @210MW & Iljan @850MW [WEBSMS] | CLUZ
2/12/2022 7:28:00 AM | LRCC-02/12/2022 07:26: Hermosa 230kV Bus 2 de-energized at 0724H (Planned Outage). [WEBSMS] | CLUZ
2/12/2022 7:20:00 AM | LRCC-02/12/2022 07:19: Dasmarinas-Amadeo 230kV Line 1 de-energized at 0716H (Planned Outage). [WEBSMS] | CLUZ
2/12/2022 7:19:00 AM | LRCC-02/12/2022 07:19: Dasmarinas-Amadeo 230kV Line 1 de-energized at 0716H (Planned Outage). [WEBSMS] | CLUZ
2/12/2022 5:55:00 AM | LRCC-02/12/2022 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11719MW, PK=8801MW, RR=333MW, NetOpMargin: AM=2585, PM=2415, EVE=2427 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Pagbilao 3 @ 231MW, Masinloc 1/2 @240MW/330MW, San Gabriel @210MW & Iljan @888MW [WEBSMS] | CLUZ
2/12/2022 5:51:00 AM | LRCC-02/12/2022 05:49: Weather Update: Shear line affecting Southern Luzon and Visayas. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CLUZ
2/11/2022 10:44:00 PM | LRCC-02/11/2022 22:42: Malaya 230kV Bus B de-energized at 2236H (Planned Outage) [WEBSMS] | CLUZ
2/11/2022 10:38:00 PM | LRCC-02/11/2022 22:35: Malaya 300MVA TO1 de-energized at 2232H (Planned Outage) [WEBSMS] | CLUZ
2/11/2022 10:37:00 PM | LRCC-02/11/2022 22:35: Malaya 300MVA TO1 de-energized at 2232H (Planned Outage) [WEBSMS] | CLUZ
2/11/2022 5:31:00 PM | LRCC-02/11/2022 17:29: Nagsaag-Casecnan 230kV L2 restored at 1728H (Planned Outage). [WEBSMS] | CLUZ
2/11/2022 5:25:00 PM | LRCC-02/11/2022 17:23: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10995MW, PK=9039MW, RR=327MW, NetOpMargin: EVE=1589 Highest Unit O/L: Dinginin 1 at 668MW Derated Plant: Ilijan A/B at 850MW, San Gabriel at 250MW [WEBSMS] | CLUZ
2/11/2022 3:45:00 PM | LRCC-02/11/2022 15:43: Balintawak T03 de-energized at 1541H (Unplanned Outage). [WEBSMS] | CLUZ
2/11/2022 2:06:00 PM | LRCC-02/11/2022 14:05: SBPL on line at 1357H (Unplanned Outage). [WEBSMS] | CLUZ
2/11/2022 6:14:00 AM | LRCC-02/11/2022 06:12: Nagsaag-Casecnan 230kV L2 de-energized at 0610H (Planned Outage). [WEBSMS] | CLUZ
2/10/2022 5:43:00 PM | LRCC-02/10/2022 17:41: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11538MW, PK=9338MW, RR=329MW, NetOpMargin: EVE=1871 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 2 @320MW, San Gabriel @210MW & Iljan @888MW [WEBSMS] | CLUZ
2/10/2022 4:07:00 PM | LRCC-02/10/2022 16:05: GMEC 2 (GN Power 2) emergency shutdown at 1600H due to air heater tube leak (Unplanned Outage) [WEBSMS] | CLUZ
2/10/2022 1:01:00 PM | LRCC-02/10/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12164MW, PK=9654MW, RR=335MW, NetOpMargin: PM=2175, EVE=2114 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 2 @320MW, GMEC 2 (GN Power 2) @135MW, San Gabriel @210MW & Iljan @888MW [WEBSMS] | CLUZ
2/10/2022 12:58:00 PM | LRCC-02/10/2022 12:58: Gumaca-Labo 230kV Line 1 restored at 1244H (Planne Outage) [WEBSMS] | CLUZ
2/10/2022 8:55:00 AM | LRCC-02/10/2022 08:54: Sual 2 online at 0847H (Unplanned Outage) [WEBSMS] | CLUZ
2/10/2022 6:00:00 AM | LRCC-02/10/2022 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11536MW, PK=9701MW, RR=375MW, NetOpMargin: AM=1460, PM=1274, EVE=1370 Highest Unit O/L: GNPD 1 at 668MW, Derated Plant: Ilijan A/B at 888MW, San Gabriel at 210MW, , GMEC 2 at 135MW [WEBSMS] | CLUZ
2/10/2022 5:24:00 AM | LRCC-02/10/2022 05:22: Weather Update: As of 4:00AM ; Northeast Monsoon affecting Extreme Northern Luzon. Trough of Low Pressure Area affecting the eastern section of Mindanao. [WEBSMS] | CLUZ
2/10/2022 5:23:00 AM | LRCC-02/10/2022 05:22: Weather Update: As of 4:00AM ; Northeast Monsoon affecting Extreme Northern Luzon. Trough of Low Pressure Area affecting the eastern section of Mindanao. [WEBSMS] | CLUZ
2/10/2022 4:46:00 AM | LRCC-02/10/2022 04:46: Binan-Balibago 115kV Line energized at 0444H (Planned Outage) [WEBSMS] | CLUZ
2/9/2022 11:40:00 PM | LRCC-02/09/2022 23:39: Binan-Balibago 115kV Line de-energized at 2336H (Planned Outage) [WEBSMS] | CLUZ
2/9/2022 11:22:00 PM | LRCC-02/09/2022 23:22: Sual 2 Unit 2 Emergency Shutdown at 2315H. (Unplanned Outage) [WEBSMS] | CLUZ
2/9/2022 9:33:00 PM | LRCC-02/09/2022 21:33: Pagbilao Unit 2 online at 2129H. (Unplanned Outage) [WEBSMS] | CLUZ
2/9/2022 3:59:00 PM | LRCC-02/09/2022 15:59: Gumaca-Labo 230kV Line 2 restored at 1556H. (Planned Outage) [WEBSMS] | CLUZ
2/9/2022 12:50:00 PM | LRCC-02/09/2022 12:49: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11750MW, PK=9718MW, RR=375MW, NetOpMargin: PM=1658, EVE=1566 Highest Unit O/L: GNPD at 668MW Derated Plant: Ilijan A/B at 888MW, San Gabriel at 210MW, GMEC 2 at 135MW [WEBSMS] | CLUZ
2/9/2022 12:34:00 PM | LRCC-02/09/2022 12:33: GMEC Unit 1 offline at 1232H. (Unplanned Outage) [WEBSMS] | CLUZ
2/9/2022 6:17:00 AM | LRCC-02/09/2022 06:15: Gumaca-Labo 230kV Line 2 de-energized at 0613H. (Planned Outage) [WEBSMS] | CLUZ
2/9/2022 5:49:00 AM | LRCC-02/09/2022 05:48: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11668MW, PK=9740MW, RR=375MW, NetOpMargin: AM=1553, PM=1487, EVE=1606 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1/2 @180MW/240MW, GMEC 2 (GN Power 2) @135MW, San Gabriel @210MW & Iljan @888MW [WEBSMS] | CLUZ
2/9/2022 5:14:00 AM | LRCC-02/09/2022 05:14: Binan-Balibago 115kV Line restored at 0512H (Planned Outage) [WEBSMS] | CLUZ
2/9/2022 4:37:00 AM | LRCC-02/09/2022 04:36: Dona Imelda (Araneta)-Valencia-Kamuning 115kV restored at 0433H (Planned Outage [WEBSMS] | CLUZ
2/9/2022 1:13:00 AM | LRCC-02/09/2022 01:10: Bolo-Masinloc 230kV Line 1 restored at 0109H (Planned Outage) [WEBSMS] | CLUZ
2/9/2022 1:12:00 AM | LRCC-02/09/2022 01:10: Bolo-Masinloc 230kV Line 1 restored at 0109H (Planned Outage) [WEBSMS] | CLUZ
2/8/2022 11:37:00 PM | LRCC-02/08/2022 23:36: Binan-Balibago 115kV Line de-energized at 2334H (Planned Outage) [WEBSMS] | CLUZ
2/8/2022 11:13:00 PM | LRCC-02/08/2022 23:11: Bolo-Masinloc 230kV Line 1 de-energized at 2308H (Planned Outage) [WEBSMS] | CLUZ
2/8/2022 9:09:00 PM | LRCC-02/08/2022 21:08: Dona Imelda (Araneta)-Valencia-Kamuning 115kV de-energized at 2102H (Planned Outage) [WEBSMS] | CLUZ
2/8/2022 7:11:00 PM | LRCC-02/08/2022 19:09: Pagbilao Unit 2 (262MW) tripped at 1902H. Lowest frequency is 59.315Hz.(Unplanned Outage). [WEBSMS] | CLUZ
2/8/2022 6:17:00 PM | LRCC-02/08/2022 18:15: Tayabas - Mauban 230kV Line 2 restored at 1813H. (Unplanned Outage) [WEBSMS] | CLUZ
2/8/2022 5:28:00 PM | LRCC-02/08/2022 17:27: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10959MW, PK=9353MW, RR=344MW, NetOpMargin: EVE=1262 Highest Unit O/L: GNPD at 668MW Derated Plant: Plant: Ilijan A/B at 888MW, San Gabriel at 210MW, Masinloc 1 at 205MW, Masinloc 2 at 200MW, GMEC 2 at 145MW [WEBSMS] | CLUZ
2/8/2022 2:52:00 PM | LRCC-02/08/2022 14:51: Tayabas - Mauban 230kV Line 2 tripped at 1445H. (Unplanned Outage). [WEBSMS] | CLUZ
2/8/2022 2:51:00 PM | LRCC-02/08/2022 14:51: Tayabas - Mauban 230kV Line 2 tripped at 1445H. (Unplanned Outage). [WEBSMS] | CLUZ
2/8/2022 12:25:00 PM | LRCC-02/08/2022 12:24: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11336MW, PK=9717MW, RR=375MW, NetOpMargin: PM=1244, EVE=1451 Highest Unit O/L: GNPD at 668MW Derated Plant: Ilijan A/B at 888MW, San Gabriel at 210MW, Masinloc 1 at 205MW, Masinloc 2 at 200MW, GMEC 2 at 145MW [WEBSMS] | CLUZ
2/8/2022 10:15:00 AM | LRCC-02/08/2022 10:14: Pagbilao Unit 2 (97MW) tripped at 1007H. Lowest frequency is 59.638Hz.(Unplanned Outage). [WEBSMS] | CLUZ
2/8/2022 8:47:00 AM | LRCC-02/08/2022 08:45: Pagbilao Unit 2 online at 0835H. (Unplanned Outage) [WEBSMS] | CLUZ
2/8/2022 8:46:00 AM | LRCC-02/08/2022 08:45: Pagbilao Unit 2 online at 0835H. (Unplanned Outage) [WEBSMS] | CLUZ
2/8/2022 5:57:00 AM | LRCC-02/08/2022 05:56: Binan-Balibago 115kV Line restored at 0554H. (Planned Outage) [WEBSMS] | CLUZ
2/8/2022 5:33:00 AM | LRCC-02/08/2022 05:33: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11788MW, PK=9385MW, RR=376MW, NetOpMargin: AM=2028, PM=1706, EVE=1817 Highest Unit O/L: GNPD at 668MW Derated Plant: Ilijan A/B at 888MW, San Gabriel at 210MW, Masinloc 1 at 205MW, Masinloc 2 at 200MW, GMEC 2 at 145MW [WEBSMS] | CLUZ
2/7/2022 11:33:00 PM | LRCC-02/07/2022 23:32: Pagbilao Unit 2 (106MW) tripped at 2329H. Lowest frequency is 59.515Hz. [WEBSMS] | CLUZ
2/7/2022 9:14:00 PM | LRCC-02/07/2022 21:13: Dona Imelda(Araneta)-Kamuning 115kV Line de-energized at 2111H. (Planned Outage) [WEBSMS] | CLUZ
2/7/2022 8:03:00 PM | LRCC-02/07/2022 20:03: Pagbilao Unit 2 online at 1954H. (Unplanned Outage) [WEBSMS] | CLUZ
2/7/2022 5:20:00 PM | LRCC-02/07/2022 17:18: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10964MW, PK=8989MW, RR=349MW, NetOpMargin: EVE=1626 Highest Unit O/L: GNPD at 668MW Derated Plant: Ilijan A/B at 888MW, Masinloc 1 at 205MW, Masinloc 2 at 200MW, GMEC 2 at 145MW [WEBSMS] | CLUZ
2/7/2022 12:21:00 PM | LRCC-02/07/2022 12:20: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11350MW, PK=9385MW, RR=375MW, NetOpMargin: PM=1590, EVE=1373 Highest Unit O/L: GNPD at 668MW Derated Plant: Ilijan A/B at 888MW, Masinloc 1 at 205MW, Masinloc 2 at 200MW, GMEC 2 at 145MW [WEBSMS] | CLUZ
2/7/2022 11:49:00 AM | LRCC-02/07/2022 11:47: Casecnan-Nagsaag 230kV L2 energized up to jumper looped at Casecnan side restored at 1144H (Planned Outage). [WEBSMS] | CLUZ
2/7/2022 8:44:00 AM | LRCC-02/07/2022 08:42: Casecnan-Nagsaag 230kV L2 de-energized at 0838H (Planned Outage). [WEBSMS] | CLUZ
2/7/2022 8:28:00 AM | LRCC-02/07/2022 08:28: Pagbilao 2 tripped at 272MW at 0819H, lowest frequency at 59.3Hz (Uplanned Outage). [WEBSMS] | CLUZ
2/7/2022 5:48:00 AM | LRCC-02/07/2022 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11728MW, PK=9344MW, RR=369MW, NetOpMargin: AM=2015, PM=1790, EVE=1935 Highest Unit O/L: GNPD at 668MW Derated Plant: Ilijan A/B at 888MW, Masinloc 1 at 205MW, Masinloc 2 at 200MW, GMEC 2 at 145MW [WEBSMS] | CLUZ
2/7/2022 12:54:00 AM | LRCC-02/07/2022 00:52: Pagbilao Unit 2 online at 0051H. (Unplanned Outage) [WEBSMS] | CLUZ
2/6/2022 11:45:00 PM | LRCC-02/06/2022 23:44: Correction: San Gabriel offline at 2329H. (Unplanned Outage) [WEBSMS] | CLUZ
2/6/2022 11:33:00 PM | LRCC-02/06/2022 23:32: San Gabriel offline at 2329H. (Planned Outage) [WEBSMS] | CLUZ
2/6/2022 8:44:00 PM | LRCC-02/06/2022 20:42: GMEC Unit 2 online at 2041H. (Unplanned Outage) [WEBSMS] | CLUZ
2/6/2022 6:07:00 PM | LRCC-02/06/2022 18:07: San Jose 300MVA T02 restored at 1804H. (Planned Outage) [WEBSMS] | CLUZ
2/6/2022 3:28:00 PM | LRCC-02/06/2022 15:27: Pagbilao 2 @352MW tripped at 1524H. Lowest System Frequency is 59.072Hz (Unplanned Outage) [WEBSMS] | CLUZ
2/6/2022 2:43:00 PM | LRCC-02/06/2022 14:41: Calaca-Bi?an 230kV Line energized @ 1441H (Planned Outage) [WEBSMS] | CLUZ
2/6/2022 2:42:00 PM | LRCC-02/06/2022 14:41: Calaca-Bi?an 230kV Line energized @ 1441H (Planned Outage) [WEBSMS] | CLUZ
2/6/2022 12:30:00 PM | LRCC-02/06/2022 12:28: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12072MW, PK=7707MW, RR=304MW, NetOpMargin: PM=4061, EVE=2956 Highest Unit O/L: GNPD at 668MW Derated Plant: Ilijan A/B at 888MW, San Gabriel at 210MW, Masinloc 1 at 205MW, Masinloc 2 at 290MW, Sta. Rita 10 & 20 at 170MW, SLPGC 1 at 90MW [WEBSMS] | CLUZ
2/6/2022 6:52:00 AM | LRCC-02/06/2022 06:29: Calaca-Bi?an 230kV Line de-energized @ 0629H (Planned Outage) [WEBSMS] | CLUZ
2/6/2022 5:38:00 AM | LRCC-02/06/2022 05:37: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11820MW, PK=8193MW, RR=306MW, NetOpMargin: AM=3321, PM=3091, EVE=2243 Highest Unit O/L: GNPD at 668MW Derated Plant: Ilijan A/B at 888MW, San Gabriel at 210MW, Masinloc 1 at 205MW, Masinloc 2 at 290MW, Sta. Rita 10 & 20 at 170MW, SLPGC 1 at 90MW [WEBSMS] | CLUZ
2/3/2022 7:10:00 AM | LRCC-02/03/2022 07:09: Naga-Labo 230kV L1 de-energized at 0708H (Planned Outage). [WEBSMS] | CLUZ
2/3/2022 5:42:00 AM | LRCC-02/03/2022 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11679MW, PK=9191MW, RR=352MW, NetOpMargin: AM=2136, PM=1834, EVE=1991 Highest Unit O/L: GNPD at 668MW Derated Plant: Ilijan A/B at 888MW, San Gabriel at 210MW, Masinloc 1 at 200MW, Masinloc 2 at 200MW, Masinloc 3 at 270MW, GNPower 1 at 240MW, Sta. Rita 10 & 20 at 170MW each [WEBSMS] | CLUZ
2/3/2022 5:30:00 AM | LRCC-02/03/2022 05:28: Binan-Balibago 115kV Line restored at 0527H. (Planned Outage) [WEBSMS] | CLUZ
2/3/2022 12:21:00 AM | LRCC-02/03/2022 00:19: GNPower Unit 1 online at 0017H. (Unplanned Outage) [WEBSMS] | CLUZ
2/2/2022 11:33:00 PM | LRCC-02/02/2022 23:33: Binan-Balibago 115kV Line de-energized at 2331H. (Planned Outage) [WEBSMS] | CLUZ
2/2/2022 5:51:00 PM | LRCC-02/02/2022 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11102MW, PK=8852MW, RR=275MW, NetOpMargin: EVE=1975 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MASINLOC 1 @210MW; MASINLOC 2 @290MW; MASINLOC 3 @250MW; ILJJAN A / B @888MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
2/2/2022 1:07:00 PM | LRCC-02/02/2022 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11598MW, PK=9345MW, RR=379MW, NetOpMargin: PM=1874, EVE=1952 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MASINLOC 1 @260MW; MASINLOC 2 @290MW; MASINLOC 3 @250MW; ILJJAN A / B @888MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
1/30/2022 9:18:00 AM | LRCC-01/30/2022 09:17: Tayabas 600MVA T01de-energized at 0914H. (Planned Outage) [WEBSMS] | CLUZ
1/30/2022 9:17:00 AM | LRCC-01/30/2022 09:17: Tayabas 600MVA T01de-energized at 0914H. (Planned Outage) [WEBSMS] | CLUZ
1/30/2022 8:20:00 AM | LRCC-01/30/2022 08:19: Las Pinas(Zapote) 300MVA T01 de-energized at 0818H. (Planned Outage) [WEBSMS] | CLUZ
1/30/2022 8:11:00 AM | LRCC-01/30/2022 08:10: Hermosa 230kV Bus 2 de-energized at 0810H. (Planned Outage) [WEBSMS] | CLUZ
1/30/2022 7:10:00 AM | LRCC-01/30/2022 07:09: Naga-Daraga 230kV line de-energized at 0706H. (Planned Outage) [WEBSMS] | CLUZ
1/30/2022 6:49:00 AM | LRCC-01/30/2022 06:48: Dasmarinas-MEC-Rosario 115kV line de-energized at 0647H. (Planned Outage) [WEBSMS] | CLUZ
1/30/2022 6:02:00 AM | LRCC-01/30/2022 06:01: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11540MW, PK=8614MW, RR=312MW, NetOpMargin: AM=2614, PM=2535, EVE=1822 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MASINLOC 1 @300MW; MASINLOC 2 @300MW; MASINLOC 3 @250MW; ILJJAN A / B @888MW; STA RITA 30 @220MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
1/30/2022 4:47:00 AM | LRCC-01/30/2022 04:47: Tayabas 600MVA T04 restored at 0446H (Planned Outage). [WEBSMS] | CLUZ
1/30/2022 1:56:00 AM | LRCC-01/30/2022 01:55: Calauan 230kV Bus 1 restored at 0151H (Planned Outage). [WEBSMS] | CLUZ
1/29/2022 11:43:00 PM | LRCC-01/29/2022 23:43: Calauan 230kV Bus 1 de-energized at 2340H (Planned Outage). [WEBSMS] | CLUZ
1/29/2022 7:30:00 PM | LRCC-01/29/2022 19:30: Naga-Tiwi A 230kV line restored at 1929H (Planned Outage). [WEBSMS] | CLUZ
1/29/2022 5:47:00 PM | LRCC-01/29/2022 17:47: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10735MW, PK=9194MW, RR=357 MW, NetOpMargin: EVE=1184 Highest Unit O/L: GNPD Unit 1 at 668MW Derated Plant: Masinloc 1 at 300MW, Masinloc 2 at 300MW, Masinloc 3 at 250MW, Ilijan at 888MW and San Gabriel at 210MW [WEBSMS] | CLUZ
1/29/2022 12:39:00 PM | LRCC-01/29/2022 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11221MW, PK=8955MW, RR=373MW, NetOpMargin: PM=1894, EVE=1050 Highest Unit O/L: GNPD Unit 1 at 668MW Derated Plant: Masinloc 1 at 300MW, Masinloc 2 at 300MW, Masinloc 3 at 250MW, Ilijan at 888MW and San Gabriel at 210MW [WEBSMS] | CLUZ
1/29/2022 9:28:00 AM | LRCC-01/29/2022 09:27: Pagbilao 230kV Bus 2 de-energized at 0925H. (Planned Outage) [WEBSMS] | CLUZ
1/29/2022 8:12:00 AM | LRCC-01/29/2022 08:09: Gamu 230kV Bus 2 de-energized at 0807H. (Planned Outage) [WEBSMS] | CLUZ
1/29/2022 7:42:00 AM | LRCC-01/29/2022 07:41: San Jose - Taytay 230kV Line 1 de-energized at 0737H. (Planned Outage) [WEBSMS] | CLUZ
1/29/2022 6:15:00 AM | LRCC-01/29/2022 06:14: Bantay PCB 6-01CB04BAN closed at 0610H, Currimao-Bantay 115kV line was looped. Integration of New BFR completed. [WEBSMS] | CLUZ
1/29/2022 6:15:00 AM | LRCC-01/29/2022 06:14: Hermosa-SBMA 230kV line de-energized at 0613H. (Planned Outage) [WEBSMS] | CLUZ
1/29/2022 6:09:00 AM | LRCC-01/29/2022 06:08: Naga-Tiwi A 230kV line de-energized at 0607H. (Planned Outage) [WEBSMS] | CLUZ
1/29/2022 5:32:00 AM | LRCC-01/29/2022 05:31: Batangas-San Lorenzo 230kV L1 restored at 0531H (Planned Outage). [WEBSMS] | CLUZ
1/29/2022 4:00:00 AM | LRCC-01/29/2022 03:59: Quezon 300MVA T03 restored at 0359H (Planned Outage). [WEBSMS] | CLUZ
1/29/2022 3:59:00 AM | LRCC-01/29/2022 03:59: Quezon 300MVA T03 restored at 0359H (Planned Outage). [WEBSMS] | CLUZ
1/29/2022 1:06:00 AM | LRCC-01/29/2022 01:06: SLTEC 1 online at 0045H (Unplanned Outage). [WEBSMS] | CLUZ
1/28/2022 11:36:00 PM | LRCC-01/28/2022 23:36: Quezon 300MVA T03 de-energized at 2335H (Planned Outage). [WEBSMS] | CLUZ
1/28/2022 11:08:00 PM | LRCC-01/28/2022 23:07: Batangas-San Lorenzo 230kV L1 de-energized at 2305H (Planned Outage). [WEBSMS] | CLUZ
1/28/2022 6:33:00 PM | LRCC-01/28/2022 18:32: Hermosa-Calaguiman 69kV Line de-energized at 1830H (Planned Outage). [WEBSMS] | CLUZ
1/28/2022 5:46:00 PM | LRCC-01/28/2022 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10610MW, PK=9439MW, RR=348MW, NetOpMargin: EVE=823 Highest Unit O/L: GNPD Unit 1 at 668MW Derated Plant: Masinloc 1 at 300MW, Masinloc 2 at 300MW, Ilijan at 888MW, Sta Rita 10 at 80MW and Masinloc 3 at 80MW [WEBSMS] | CLUZ
1/28/2022 2:55:00 PM | LRCC-01/28/2022 14:54: Masinloc Unit 3 online at 1448H. (Unplanned Outage) [WEBSMS] | CLUZ
1/28/2022 1:38:00 PM | LRCC-01/28/2022 13:34: Daraga-Tiwi A 230kV line auto-tripped/auto-reclosed at Daraga side at 1329H. The line is still un-looped at Tiwi A side. (Unplanned Outage) [WEBSMS] | CLUZ
1/28/2022 1:38:00 PM | LRCC-01/28/2022 13:36: Daraga-Tiwi A 230kV line was looped at Tiwi A side at 1335H. (Unplanned Outage) [WEBSMS] | CLUZ
1/28/2022 1:16:00 PM | LRCC-01/28/2022 13:14: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10979MW, PK=9831MW, RR=376MW, NetOpMargin: PM=772, EVE=987 Highest Unit O/L: GNPD Unit 1 at 668MW Derated Plant: Masinloc 1 at 300MW, Masinloc 2 at 300MW and Ilijan at 888MW [WEBSMS] | CLUZ
1/28/2022 8:17:00 AM | LRCC-01/28/2022 08:15: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11119MW, PK=9596MW, RR=364MW, NetOpMargin: AM=1159, PM=945, EVE=1173 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MASINLOC 1 @300MW; MASINLOC 2 @300MW; ILJJAN A / B @888MW [WEBSMS] | CLUZ
1/28/2022 8:05:00 AM | LRCC-01/28/2022 08:05: Pagbilao Unit 2 online at 0801H (Unplanned outage) [WEBSMS] | CLUZ
1/28/2022 6:14:00 AM | LRCC-01/28/2022 06:12: Correction: Bantay PCB 6-01CB24BAN opened at 0603H. Bantay-Currimao 115kV line on floating status. (Planned Outage) [WEBSMS] | CLUZ
1/28/2022 6:07:00 AM | LRCC-01/28/2022 06:07: Bantay PCB 6-03CB24BAN opened at 0603H. Bantay-Currimao 115kV line on floating status. (Planned Outage) [WEBSMS] | CLUZ
1/27/2022 6:00:00 PM | LRCC-01/27/2022 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10441MW, PK=9373MW, RR=355MW, NetOpMargin: EVE=713 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MASINLOC 1 @300MW; MASINLOC 2 @300MW; ILJJAN A / B @888MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
1/27/2022 12:58:00 PM | LRCC-01/27/2022 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10733MW, PK=9659MW, RR=376MW, NetOpMargin: PM=698, EVE=792 Highest Unit O/L: GNPD 1 @668MW Derated Plant: Masinloc 1/2 @290MW/300MW, San Gabriel @210MW & Iljan @888MW [WEBSMS] | CLUZ
1/27/2022 12:14:00 PM | LRCC-01/27/2022 12:13: Pagbilao 2 @381MW tripped at 1204H. Lowest Frequency at 59.044Hz. No ALD (Unplanned Outage) [WEBSMS] | CLUZ
1/27/2022 10:48:00 AM | LRCC-01/27/2022 10:46: SLTEC 1 @95MW tripped at 1033H. Lowest System Frequency is 59.562Hz (Unplanned Outage) [WEBSMS] | CLUZ
1/27/2022 6:44:00 AM | LRCC-01/27/2022 06:42: Lumban-Gumaca 230kV Line 2 de-energized at 0642H (Planned Outage) [WEBSMS] | CLUZ
1/27/2022 5:46:00 AM | LRCC-01/27/2022 05:46: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data at 190 km South Southwest of Puerto Princesa City, Palawan (8.1N, 118.3E). Shear Line affecting the eastern section of Northern Luzon. [WEBSMS] | CLUZ
1/27/2022 5:36:00 AM | LRCC-01/27/2022 05:35: Masinloc Unit 3 on-line at 0531H. (Extended Outage) [WEBSMS] | CLUZ
1/27/2022 4:16:00 AM | LRCC-01/27/2022 04:15: Binan-Balibago 115kV line restored at 0414H. Planned Outage. [WEBSMS] | CLUZ
1/26/2022 11:39:00 PM | LRCC-01/26/2022 23:38: Binan-Balibago 115kV line de-energized at 2333H. Planned Outage [WEBSMS] | CLUZ
1/26/2022 5:57:00 PM | LRCC-01/26/2022 17:57: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10564MW, PK=8901MW, RR=357MW, NetOpMargin: EVE=1306 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GNPD 1 @636MW; MASINLOC 1 @300MW; MASINLOC 2 @300MW; SCPC 3 @95MW; ILJJAN A / B @888MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
1/26/2022 5:22:00 PM | LRCC-01/26/2022 17:21: Lumban - Gumaca 230kV Line 1 energized at 1718H. [WEBSMS] | CLUZ
1/26/2022 12:57:00 PM | LRCC-01/26/2022 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10812MW, PK=9383MW, RR=372MW, NetOpMargin: PM=1057, EVE=1042 Highest Unit O/L: GNPD 1 @668MW Derated Plant: MASINLOC 1 @300MW; MASINLOC 2 @300MW; SCPC 3 @95MW; ILIJAN B @288MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
1/26/2022 6:43:00 AM | LRCC-01/26/2022 06:42: Lumban - Gumaca 230kV Line 1 de-energized at 0638H. (Planned Outage) [WEBSMS] | CLUZ
1/26/2022 6:42:00 AM | LRCC-01/26/2022 06:42: Lumban - Gumaca 230kV Line 1 de-energized at 0638H. (Planned Outage) [WEBSMS] | CLUZ
1/26/2022 6:15:00 AM | LRCC-01/26/2022 06:14: Binan 300MVA T01 restored at 0614H. (Planned Outage) [WEBSMS] | CLUZ
1/26/2022 6:06:00 AM | LRCC-01/26/2022 05:36: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data in the vicinity of Tayasan, Negros Oriental (9.9?N, 123.0?E). Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
1/25/2022 10:08:00 PM | LRCC-01/25/2022 22:06: Binan 300MVA T01 de-energized at 2206H. (Planned Outage) [WEBSMS] | CLUZ
1/25/2022 5:51:00 PM | LRCC-01/25/2022 17:50: Santiago 230kV Bus 2 energized at 1748H. Planned Outage [WEBSMS] | CLUZ
1/25/2022 5:49:00 PM | LRCC-01/25/2022 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10448MW, PK=9063MW, RR=363MW, NetOpMargin: EVE=1022 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Masinloc 1 at 300MW, Masinloc 2 at 300MW, Ilijan at 888MW, San Gabriel at 210MW and GNPD 1 at 155MW [WEBSMS] | CLUZ
1/25/2022 3:38:00 PM | LRCC-01/25/2022 15:37: Dasmarinas-TMC(Ternate) 115kV line energized at 1534H. (Planned Outage) [WEBSMS] | CLUZ
1/25/2022 3:36:00 PM | LRCC-01/25/2022 15:35: Dasmarinas-TMC(Ternate) 115kV line energized at 1634H. (Planned Outage) [WEBSMS] | CLUZ
1/25/2022 1:02:00 PM | LRCC-01/25/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10597MW, PK=9311MW, RR=363MW, NetOpMargin: PM=923, EVE=757 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Masinloc 1 at 300MW, Masinloc 2 at 300MW, Ilijan at 888MW and San Gabriel at 210MW [WEBSMS] | CLUZ
1/25/2022 12:42:00 PM | LRCC-01/25/2022 12:41: GNPD Unit 1 on-line at 1234H. (Extended Outage) [WEBSMS] | CLUZ
1/25/2022 10:22:00 AM | LRCC-01/25/2022 10:21: New Naga PCB 8-05CB24NAG was energized at 1019H. [WEBSMS] | CLUZ
1/25/2022 9:50:00 AM | LRCC-01/25/2022 09:48: San Gabriel on-line at 0946H. (Planned Outage) [WEBSMS] | CLUZ
1/25/2022 9:07:00 AM | LRCC-01/25/2022 09:05: Dasmarinas-TMC(Ternate) 115kV line de-energized at 0903H. (Planned Outage) [WEBSMS] | CLUZ
1/25/2022 8:06:00 AM | LRCC-01/25/2022 08:05: Santiago 230kV Bus 2 de-energized at 0804H. (Planned Outage) [WEBSMS] | CLUZ
1/25/2022 5:58:00 AM | LRCC-01/25/2022 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=10522MW, PK=9360MW, RR=375MW, NetOpMargin: AM=787, PM=741, EVE=648 Highest Unit O/L: SUAL 1 @647MW Derated Plant: MASINLOC 1 @290MW; MASINLOC 2 @300MW; ILJJAN A / B @888MW [WEBSMS] | CLUZ
1/25/2022 5:04:00 AM | LRCC-01/25/2022 04:32: Weather Update: At 3:00 AM today, the Low Pressure Area (LPA) was estimated based on all available data in the vicinity of Talacogon, Agusan del Sur (8.3?N, 125.8?E). [WEBSMS] | CLUZ
1/24/2022 7:26:00 PM | LRCC-01/24/2022 19:24: SBMA-Subic Solar Power 230kV Line restored at 1921H (Planned Outage). [WEBSMS] | CLUZ
1/24/2022 5:37:00 PM | LRCC-01/24/2022 17:36: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10092MW, PK=9083MW, RR=335MW, NetOpMargin: EVE=674 Highest Unit O/L: Sual 1 @647MW Derated Plant: Masinloc 1/2 @290MW/300MW, & Iljan @888MW [WEBSMS] | CLUZ
1/24/2022 12:18:00 PM | LRCC-01/24/2022 12:18: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10516MW, PK=9498MW, RR=360MW, NetOpMargin: PM=658, EVE=1024 Highest Unit O/L: Sual 1 @647MW Derated Plant: Masinloc 1/2 @280MW/300MW, & Iljan @888MW [WEBSMS] | CLUZ
1/24/2022 6:50:00 AM | LRCC-01/24/2022 06:50: Muntinlupa(Sucat) 300MVA TO1 restored at 0646H. (Unplanned Outage) [WEBSMS] | CLUZ
1/24/2022 6:26:00 AM | LRCC-01/24/2022 06:25: Binan 300MVA T02 restored at 0615H. (Planned Outage) [WEBSMS] | CLUZ
1/24/2022 4:59:00 AM | LRCC-01/24/2022 04:59: Muntinlupa(Sucat) 300MVA TO1 energized at 230kV (high) side at 0454H. Transformer is under observation. (Unplanned Outage) [WEBSMS] | CLUZ
1/24/2022 1:39:00 AM | LRCC-01/24/2022 01:37: Muntinlupa(Sucat) 300MVA TO1 tripped at 0134H. (Unplanned Outage) [WEBSMS] | CLUZ
1/24/2022 1:38:00 AM | LRCC-01/24/2022 01:37: Muntinlupa(Sucat) 300MVA TO1 tripped at 0134H. (Unplanned Outage) [WEBSMS] | CLUZ
1/24/2022 12:42:00 AM | LRCC-01/24/2022 00:42: Muntinlupa(Sucat) 300MVA TO1 restored at 0040H. (Planned Outage) [WEBSMS] | CLUZ
1/23/2022 10:40:00 PM | LRCC-01/23/2022 22:40: Binan 300MVA T02 de-energized at 2239H. (Planned Outage) [WEBSMS] | CLUZ
1/23/2022 10:15:00 PM | LRCC-01/23/2022 22:15: San Lorenzo-Avion 230kV Line restored at 2214H. (Planned Outage) [WEBSMS] | CLUZ
1/23/2022 8:40:00 PM | LRCC-01/23/2022 20:40: San Lorenzo-Batangas 230kV Line 2 restored at 2039H. (Planned Outage) [WEBSMS] | CLUZ
1/23/2022 6:02:00 PM | LRCC-01/23/2022 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=9798MW, PK=8319MW, RR=303MW, NetOpMargin: EVE=1176 Highest Unit O/L: SUAL 1 @647MW Derated Plant: MASINLOC 1 @290MW; MASINLOC 2 @300MW; ILJJAN A / B @888MW [WEBSMS] | CLUZ
1/23/2022 5:14:00 PM | LRCC-01/23/2022 17:02: Naga-Tiwi Plant A 230kV Line energized at 1702H (Planned Outage). [WEBSMS] | CLUZ
1/23/2022 4:52:00 PM | LRCC-01/23/2022 16:50: Hermosa - BCCP 230kV Line 1 energized at 1649H (Planned Outage). [WEBSMS] | CLUZ
1/23/2022 3:42:00 PM | LRCC-01/23/2022 15:41: Bantay 115kV Bus 2 energized at 1541H (Planned Outage). [WEBSMS] | CLUZ
1/23/2022 2:30:00 PM | LRCC-01/23/2022 14:30: Pagbilao 230kV Bus 1 restored at 1428H (Planned Outage) [WEBSMS] | CLUZ
1/23/2022 10:19:00 AM | LRCC-01/23/2022 10:18: Mexico-Cabanatuan 230kV Line tripped at 1015H (Unplanned Outage). [WEBSMS] | CLUZ
1/23/2022 8:27:00 AM | LRCC-01/23/2022 08:26: SLPGC 1 offine at 0823H (Unplanned Outage). [WEBSMS] | CLUZ
1/23/2022 8:26:00 AM | LRCC-01/23/2022 08:26: SLPGC 1 offine at 0823H (Unplanned Outage). [WEBSMS] | CLUZ
1/23/2022 6:34:00 AM | LRCC-01/23/2022 06:33: Bantay 115kV Bus 2 de-energized at 0633H (Planned Outage) [WEBSMS] | CLUZ
1/23/2022 6:08:00 AM | LRCC-01/23/2022 06:08: Hermosa - BCCP 230kV Line 1 de-energized at 0605H (Planned Outage) [WEBSMS] | CLUZ
1/23/2022 5:22:00 AM | LRCC-01/23/2022 05:22: Weather Update: At 3:00 AM today, a Low Pressure Area (LPA) was estimated based on all available data at 965 km East of Mindanao (6.2?N, 134.5?E). [WEBSMS] | CLUZ
1/23/2022 5:17:00 AM | LRCC-01/23/2022 05:15: Muntinlupa 300MVA TO1 de-energized at 0513H (Planned Outage) [WEBSMS] | CLUZ
1/23/2022 5:16:00 AM | LRCC-01/23/2022 05:15: Muntinlupa 300MVA TO1 de-energized at 0513H (Planned Outage) [WEBSMS] | CLUZ
1/23/2022 2:13:00 AM | LRCC-01/23/2022 02:13: Kalayaan 2 tripped as pump (-152MW) at 0205H. Highest Frequency is 60.488Hz (Unplanned Outage) [WEBSMS] | CLUZ
1/22/2022 11:53:00 PM | LRCC-01/22/2022 23:51: SBMA 230kV Bus 1 restored at 2350H. (Planned Outage) [WEBSMS] | CLUZ
1/22/2022 8:25:00 PM | LRCC-01/22/2022 20:25: Hermosa-Balsik 230kV Tie Line 2 and Balsik 230kV Bus 2 restored at 2022H. (Planned Outage) [WEBSMS] | CLUZ
1/22/2022 7:19:00 PM | LRCC-01/22/2022 19:18: Hermosa 230kV Bus 1 restored at 1915H. (Planned Outage) [WEBSMS] | CLUZ
1/22/2022 6:59:00 PM | LRCC-01/22/2022 18:59: GN Power 2 @130MW tripped at 1849H. Lowest frequency is 59.46Hz (Unplanned Outage) [WEBSMS] | CLUZ
1/22/2022 12:47:00 PM | LRCC-01/22/2022 12:46: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10570MW, PK=8322MW, RR=330MW, NetOpMargin: PM=1918, EVE=1365 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Ilijan A/B at 888MW, San Gabriel at 210MW, GNPower 2 at 150MW, Masinloc 1 at 250MW, Masinloc 2 at 300MW, SLPGC at 145MW [WEBSMS] | CLUZ
1/22/2022 8:25:00 AM | LRCC-01/22/2022 08:23: Pagbilao 230kV Bus 1 de-energized at 0823H. (Planned Outage) [WEBSMS] | CLUZ
1/22/2022 7:22:00 AM | LRCC-01/22/2022 07:22: San Lorenzo-Avion 230kV Line de-energized at 0720H. (Planned Outage) [WEBSMS] | CLUZ
1/22/2022 6:42:00 AM | LRCC-01/22/2022 06:41: Balsik 230kV Bus 2 de-energized at 0640H. (Planned Outage) [WEBSMS] | CLUZ
1/22/2022 6:40:00 AM | LRCC-01/22/2022 06:38: Hermosa 230kV Bus 1 de-energized at 0637H. (Planned Outage) [WEBSMS] | CLUZ
1/22/2022 6:40:00 AM | LRCC-01/22/2022 06:39: Hermosa-Balsik 230kV Tie Line 2 de-energized at 0639H. (Planned Outage) [WEBSMS] | CLUZ
1/22/2022 5:47:00 AM | LRCC-01/22/2022 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=10557MW, PK=8413MW, RR=334MW, NetOpMargin: AM=1810, PM=1853, EVE=1340 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GN POWER 2 @150MW; MASINLOC 1 @250MW; MASINLOC 2 @300MW; ILJJAN A / B @888MW [WEBSMS] | CLUZ
1/22/2022 1:01:00 AM | LRCC-01/22/2022 01:00: Pagbilao 1 online at 0053H (Unplanned Outage). [WEBSMS] | CLUZ
1/22/2022 12:33:00 AM | LRCC-01/22/2022 00:33: San Gabriel offline at 0031H (Planned Outage). [WEBSMS] | CLUZ
1/21/2022 5:44:00 PM | LRCC-01/21/2022 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=9945MW, PK=8695MW, RR=323MW, NetOpMargin: EVE=927 Highest Unit O/L: Sual 1 @647MW Derated Plant: Masinloc 1/2 @250MW/290MW, San Gabriel @210MW & Iljan @888MW [WEBSMS] | CLUZ
1/21/2022 12:23:00 PM | LRCC-01/21/2022 12:23: Kalayaan 3 @178MW tripped at 1215H. Lowest Frequency is 59.609Hz (Unplanned Outage) [WEBSMS] | CLUZ
1/21/2022 10:14:00 AM | LRCC-01/21/2022 10:12: Pagbilao 2 online at 1011H (Unplanned Outage) [WEBSMS] | CLUZ
1/21/2022 6:48:00 AM | LRCC-01/21/2022 06:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=9832MW, PK=8602MW, RR=342MW, NetOpMargin: AM=888, PM=864, EVE=730 Highest Unit O/L: Sual 1 at 647MW Derated Plant: San Gabriel at 210MW, Ilijan A/B at 888MW, Masinloc 1 at 300MW, Masinloc 2 at 290MW, Sta. Rita 10 at 160MW, Sta. Rita 20 at 160MW [WEBSMS] | CLUZ
1/21/2022 5:53:00 AM | LRCC-01/21/2022 05:53: Binan-Balibago 115kV Line restored at 0552H. (Planned Outage) [WEBSMS] | CLUZ
1/21/2022 5:27:00 AM | LRCC-01/21/2022 05:26: Pagbilao Units 1 & 2 (339MW and 152MW respectively) tripped simultaneously with Pagbilao-Tayabas 230kV Line 2 at 0510H. Lowest frequency is 59.048H. No ALD occurred. (Unplanned Outage) [WEBSMS] | CLUZ
1/20/2022 11:34:00 PM | LRCC-01/20/2022 23:32: Binan-Balibago 115kV Line de-energized at 2331H. (Planned Outage) [WEBSMS] | CLUZ
1/20/2022 6:20:00 PM | LRCC-01/20/2022 18:01: Bantay 115kV Bus 1 restored at 1800H. (Planned Outage) [WEBSMS] | CLUZ
1/20/2022 6:20:00 PM | LRCC-01/20/2022 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10089MW, PK=8489MW, RR=332MW, NetOpMargin: EVE=1268 Highest Unit O/L: SUAL 1 @647MW Derated Plant: MASINLOC 1 @300MW; MASINLOC 2 @90MW; ILJJAN A / B @851MW; STA RITA 10 @160MW; STA RITA 20 @160MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
1/20/2022 5:58:00 PM | LRCC-01/20/2022 17:58: Limay-BCCPP 230kV Line 1 restored at 1756H. (Planned Outage) [WEBSMS] | CLUZ
1/20/2022 3:11:00 PM | LRCC-01/20/2022 15:10: Naga-Tiwi C 230 kV L1 restored at 1509H (Planned Outage). [WEBSMS] | CLUZ
1/20/2022 2:25:00 PM | LRCC-01/20/2022 14:24: Tiwi C 230kV Bus 2 restored at 1420H(Planned Outage). [WEBSMS] | CLUZ
1/20/2022 1:07:00 PM | LRCC-01/20/2022 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10345MW, PK=8577MW, RR=341MW, NetOpMargin: PM=1427, EVE=1314 Highest Unit O/L: SUAL 1 @647MW Derated Plant: MASINLOC 1 @300MW; MASINLOC 2 @280MW; ILJJAN A / B @851MW; STA RITA 10 @160MW; STA RITA 20 @160MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
1/20/2022 1:06:00 PM | LRCC-01/20/2022 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10345MW, PK=8577MW, RR=341MW, NetOpMargin: PM=1427, EVE=1314 Highest Unit O/L: SUAL 1 @647MW Derated Plant: MASINLOC 1 @300MW; MASINLOC 2 @280MW; ILJJAN A / B @851MW; STA RITA 10 @160MW; STA RITA 20 @160MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
1/20/2022 9:55:00 AM | LRCC-01/20/2022 09:54: Quezon - Mexico 230kV Line tripped at 0951H (Unplanned Outage). [WEBSMS] | CLUZ
1/20/2022 7:56:00 AM | LRCC-01/20/2022 07:55: Tiwi C 230kV Bus 2 de-energized at 0754H(Planned Outage). [WEBSMS] | CLUZ
1/20/2022 7:12:00 AM | LRCC-01/20/2022 07:11: Limay-BCCPP 230kV Line 1 de-energized at 0710H (Planned Outage). [WEBSMS] | CLUZ
1/20/2022 5:40:00 AM | LRCC-01/20/2022 05:40: Weather Update: Shear Line affecting the eastern section of Southern Luzon. Northeast Monsoon affecting the rest of Luzon. [WEBSMS] | CLUZ
1/20/2022 4:24:00 AM | LRCC-01/20/2022 04:24: Binan-Balibago 115kV Line energized at 0422H (Planned Outage) [WEBSMS] | CLUZ
1/20/2022 3:41:00 AM | LRCC-01/20/2022 03:40: San Lorenzo 60 offline at 0339H. (Planned Outage) [WEBSMS] | CLUZ
1/19/2022 11:26:00 PM | LRCC-01/19/2022 23:26: Binan-Balibago 115kV Line de-energized at 2325H (Planned Outage) [WEBSMS] | CLUZ
1/19/2022 8:15:00 PM | LRCC-01/19/2022 20:14: Malaya 2 offline at 2012H. (On Commissioning Test) [WEBSMS] | CLUZ
1/19/2022 6:00:00 PM | LRCC-01/19/2022 17:59: Naga - Tayabas 230kV Line 2 restored at 1758H. (Planned Outage) [WEBSMS] | CLUZ
1/19/2022 5:29:00 PM | LRCC-01/19/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10822MW, PK=8458MW, RR=338MW, NetOpMargin: EVE=2026 Highest Unit O/L: Sual 1 at 647MW Derated Plant: San Gabriel at 210MW, Ilijan A/B at 695MW, Masinloc 1 at 300MW, Masinloc 2 at 300MW, Sta. Rita 10 at 180MW [WEBSMS] | CLUZ
1/19/2022 3:54:00 PM | LRCC-01/19/2022 15:54: SBPL online at 1547H. (Unplanned Outage) [WEBSMS] | CLUZ
1/19/2022 9:11:00 AM | LRCC-01/19/2022 09:10: SBPL online at 0859H. (Planned Outage) [WEBSMS] | CLUZ
1/19/2022 7:28:00 AM | LRCC-01/19/2022 07:28: Naga - Tayabas 230kV Line 2 de-energized at 0727H. (Planned Outage) [WEBSMS] | CLUZ
1/19/2022 6:36:00 AM | LRCC-01/19/2022 06:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=10330MW, PK=8525MW, RR=348MW, NetOpMargin: AM=1457, PM=1412, EVE=1334 Highest Unit O/L: SUAL 1 @647MW Derated Plant: GN POWER 2 @307MW; MASINLOC 1 @300MW; MASINLOC 2 @300MW; ILJJAN A / B @581MW; STA RITA 30 @220MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
1/18/2022 11:47:00 PM | VRCC-01/18/2022 23:46: Energized back 69Kv Naga-Sibonga line @2345H. [WEBSMS] | CVIS
1/18/2022 11:41:00 PM | VRCC-01/18/2022 23:40: 69Kv Naga-Sibonga line auto tripped @2333H with load of 11.9Mw customers fault. [WEBSMS] | CVIS
1/18/2022 10:03:00 PM | LEYTE ACC-01/18/22 22:13: CALBAYOG SS, Catarman - Lao-ang 69kV Line re-energized at 2158H. 69kV Norsamelco Feeder back to its normal line configuration. Weather: Fair. | CVIS
1/18/2022 7:05:00 PM | LEYTE ACC-01/18/22 19:15: CALBAYOG SS, 69kV PCB Palanas Cara emergency opened/closed at 1853H/1857H as per VOMs request. Load=16.0MW. Weather: Cloudy. | CVIS
1/18/2022 5:44:00 PM | LRCC-01/18/2022 17:43: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=9969MW, PK=8264MW, RR=336MW, NetOpMargin: EVE=1369 Highest Unit O/L: Sual 1 @647MW Derated Plant: Masinloc 1/2 @300MW each, Sta Rita 30 @220MW,San Gabriel @210MW & Iljan A/B @401MW/180MW [WEBSMS] | CLUZ
1/18/2022 3:37:00 PM | VRCC-01/18/2022 15:36: 138 KV Colon - Calongcalong Line 1 energized from Calongcalong SS at 1524H, closed at 1535H in Colon SS [WEBSMS] | CVIS
1/18/2022 7:51:00 AM | LEYTE ACC-01/18/22 07:53: ORMOC SS,Ormoc-Simangan-Baybay 69 kV L,Deenergized /Energized at 0700H/0706H,load=20.19mw, while Leyeco IV (Hilongos) load transferred back to Maasin SS AT 0735H back to normal configuration. WEATHER: Cloudy | CVIS
1/18/2022 7:41:00 AM | PANAY ACC-01/18/22 07:50: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 07:29:00, TIME IN: 07:36:00, RELAY: Trip BN Z1, 198kms., Ld: 19.4MW; WEATHER: FAIR, Momentary line fault. | CVIS
1/18/2022 7:13:00 AM | LRCC-01/18/2022 07:12: Naga-Tayabas 230kV Line 1 de-energized at 0708H (Planned Outage) [WEBSMS] | CLUZ
1/18/2022 6:36:00 AM | VRCC-01/18/2022 06:36: 230KV TVI-Magdugo line 2 manually open @0630H to facilitate maintenance activity, pre-arranged customers request. [WEBSMS] | CVIS
1/18/2022 6:11:00 AM | VRCC-01/18/2022 06:11: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2353MW, PK=1693MW, RR=0MW, NetOpMargin: AM=660, PM=572, EVE=492 Highest Unit O/L: PCPC U@ 135 MW Derated Plant: EDC = 340 MW, PEDC = 164 MW [WEBSMS] | CVIS
1/18/2022 5:46:00 AM | LRCC-01/18/2022 05:46: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=10508MW, PK=8739MW, RR=346MW, NetOpMargin: AM=1423, PM=1331, EVE=1196 Highest Unit O/L: Sual 1 at 647MW Derated Plant: San Gabriel at 210MW, Ilijan A/B at 581MW, Masinloc 1 at 300MW, Masinloc 2 at 300MW, Sta. Rita 20 at 220MW [WEBSMS] | CLUZ
1/18/2022 4:23:00 AM | VRCC-01/18/2022 04:24: CEDC unit# 1 cut-in @0355H. [WEBSMS] | CVIS
1/17/2022 8:18:00 PM | LEYTE ACC-01/17/22 20:26: ORMOC CONVERTER STATION SS,350kV HVDC Leyte-Luzon,Blocked/Deblocked at 1953H/2004H, L1 to Parallel to Ground on normal flow per RTD, WEATHER: FAIR | CVIS
1/17/2022 5:10:00 PM | VRCC-01/17/2022 17:10: 138 KV Cebu - Colon Line 2 energized from Cebu SS at 1645H, closed at 1705H at Colon SS [WEBSMS] | CVIS
1/17/2022 2:04:00 PM | LEYTE ACC-01/17/22 14:10: MAASIN SS, 69kV Maasin-Baybay Line,energized at 1353H up to DS03 Of PCB Hilongos, WEATHER:Fair | CVIS
1/17/2022 1:11:00 PM | LRCC-01/17/2022 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10081MW, PK=8908MW, RR=354MW, NetOpMargin: PM=819, EVE=824 Highest Unit O/L: SUAL 1 @647MW Derated Plant: MASINLOC 1 @300MW; MASINLOC 2 @300MW; ILJJAN A / B @581MW; STA RITA 30 @220MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
1/17/2022 1:00:00 PM | VRCC-01/17/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2002MW, PK=1734MW, RR=0MW, NetOpMargin: PM=268, EVE=67 Highest Unit O/L: PCPC at 135 MW, Derated Plant: EDC at 340 MW, PEDC at 164 MW, CEDC at 164 MW, KSPC at 163 MW [WEBSMS] | CVIS
1/17/2022 10:34:00 AM | PANAY ACC-01/17/22 10:26: DINGLE SS, Dingle-Sta. Barbara 138 kV L1 (7LI1DIN-SBA), TIME IN: 10:23:00, RELAY: NONE, WEATHER: FAIR. Scheduled Corrective Maintenance. | CVIS
1/17/2022 10:04:00 AM | VRCC-01/17/2022 10:03: SO initiated Market Intervention at 1942H December 16, 2021 lifted at 1001H January 17, 2022 [WEBSMS] | CVIS
1/17/2022 8:35:00 AM | LEYTE ACC-01/17/22 08:43: MAASIN SS, Nasaug-Sogod-St. Bernard 69 kV Line tripped/restored at 0825H/0830H,Phase AN, load=1.73mw, WEATHER: FAIR | CVIS
1/17/2022 8:28:00 AM | PANAY ACC-01/17/22 08:16: DINGLE SS, Dingle-Sta. Barbara 138 kV L1 (7LI1DIN-SBA), TIME OUT: 08:12:00, RELAY: NONE, WEATHER: FAIR. Scheduled Corrective Maintenance. | CVIS
1/17/2022 6:32:00 AM | VRCC-01/17/2022 06:05: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2102MW, PK=1741MW, RR=0MW, NetOpMargin: AM=361, PM=322, EVE=121 Highest Unit O/L: PCPC U@ 135 MW Derated Plant: EDC = 340 MW, PEDC = 164 MW, CEDC = 164 MW [WEBSMS] | CVIS
1/17/2022 6:00:00 AM | LRCC-01/17/2022 05:43: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=10245MW, PK=8964MW, RR=349MW, NetOpMargin: AM=932, PM=892, EVE=870 Highest Unit O/L: Sual 1 @647MW Derated Plant: Masinloc 1/2 @300MW each, Sta Rita 30 @220MW,San Gabriel @210MW & Iljan A/B @401MW/180MW [WEBSMS] | CLUZ
1/17/2022 5:29:00 AM | LRCC-01/17/2022 05:27: Weather Update: Shear Line affecting the eastern section of Mindanao. Northeast Monsoon affecting the rest of the country. [WEBSMS] | CLUZ
1/16/2022 10:47:00 PM | LRCC-01/16/2022 22:46: For info: Sta Rita Module 20 completed fuel changeover from gas to oil at 2242H. [WEBSMS] | CLUZ
1/16/2022 10:01:00 PM | LRCC-01/16/2022 21:43: Sta Rita 40 online at 2142H (Planned Outage) [WEBSMS] | CLUZ
1/16/2022 8:22:00 PM | VRCC-01/16/2022 20:22: 138KV Colon - Cebu line 3 energized 1948H. [WEBSMS] | CVIS
1/16/2022 7:52:00 PM | LEYTE ACC-01/16/22 20:00: MAASIN SS, ABS San Miguel - St. Bernard 69 kV L restored at 1943H,Pre arranged completed per PANR No.TLOS V_LEY-2022-01-0003. WEATHER: FAIR | CVIS
1/16/2022 6:56:00 PM | LRCC-01/16/2022 18:55: Mexico - Quezon(Balintawak) 230kV Line restored at 1842H. (Planned Outage) [WEBSMS] | CLUZ
1/16/2022 6:03:00 PM | VRCC-01/16/2022 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1880MW, PK=1632MW, RR=0MW, NetOpMargin: EVE=248 Highest Unit O/L: PCPC U@ 135 MW Derated Plant: EDC = 340 MW, PEDC = 164 MW, CEDC = 164 MW [WEBSMS] | CVIS
1/16/2022 5:35:00 PM | LRCC-01/16/2022 17:35: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=9554MW, PK=7967MW, RR=313MW, NetOpMargin: EVE=1274 Highest Unit O/L: Sual 1 at 647MW Derated Plant: San Gabriel at 210MW, Ilijan A/B at 581MW, Masinloc 1 at 300MW, Masinloc 2 at 300MW [WEBSMS] | CLUZ
1/16/2022 5:01:00 PM | LEYTE ACC-01/16/22 17:09: MAASIN SS,69kV PCB Soleco closed at 1656H up to ABS San Miguel back to normal configuration, WEATHER: FAIR | CVIS
1/16/2022 4:35:00 PM | NEGROS ACC: 01/16/2022, 34.5kV Amlan-AHEP Line energized at 1615H after completion of maintenance activities | CVIS
1/16/2022 4:12:00 PM | LEYTE ACC-01/16/22 16:17:ORMOC SS,Tolosa-San Isidro 69 kV L,Deenergized /Energized,1538H/1549H,to effect the opening of ABS San Isidro back to normal configuration, load=2.8mw, WEATHER: FAIR | CVIS
1/16/2022 3:43:00 PM | PANAY ACC-01/16/22 15:40: STA. BARBARA SS, Sta. Barbara-Tigbauan 69kV Line, TIME OUT: 03:29:00, TIME IN: 03:33:00, Load: 25.2mw, Manually open to facilitate closing of 69kv ABS Tigbauan-Miag-ao tl | CVIS
1/16/2022 2:07:00 PM | LRCC-01/16/2022 14:07: Tayabas - Pagbilao 230kV Line 1 restored at 1406H. (Planned Outage) [WEBSMS] | CLUZ
1/16/2022 1:14:00 PM | VRCC-01/16/2022 12:56: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2035MW, PK=1460MW, RR=0MW, NetOpMargin: PM=575, EVE=248 Highest Unit O/L: PCPC @ 135 MW Derated Plant: EDC = 340 MW, PEDC = 164 MW, CEDC = 164 MW [WEBSMS] | CVIS
1/16/2022 12:51:00 PM | LRCC-01/16/2022 12:50: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=9756MW, PK=7415MW, RR=332MW, NetOpMargin: PM=2009, EVE=1391 Highest Unit O/L: Sual 1 at 647MW Derated Plant: San Gabriel at 210MW, Ilijan A/B at 581MW, Masinloc 1 at 300MW, Masinloc 2 at 300MW [WEBSMS] | CLUZ
1/16/2022 12:20:00 PM | PANAY ACC-01/16/22 12:18: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line(25.45MW) (5LI1SBA-SJD), TIME IN: 12:14:00, RELAY: NONE, WEATHER: FAIR. 69kV Tigbauan - Miag-ao Line section remained open due to failed energization after line clearing | CVIS
1/16/2022 12:18:00 PM | LRCC-01/16/2022 12:16: Botolan - Labrador 230kV Line restored at 1216H. (Planned Outage) [WEBSMS] | CLUZ
1/16/2022 12:06:00 PM | PANAY ACC-01/16/22 12:03: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME OUT: 12:00:00, RELAY: NONE, WEATHER: FAIR. Open to process restoration of Tigbauan - Miag-ao Line section. | CVIS
1/16/2022 11:59:00 AM | LEYTE ACC-01/16/22 12:06: MAASIN SS, Maasin-Nasaug 69 kV L,Energized at 1139H while PCB Soleco closed up to STR# 178-D,loc at Brgy. Pandan So. Leyte, per PANR No. TLOS V_LEY-2022-01-0003, WEATHER: FAIR | CVIS
1/16/2022 11:37:00 AM | LRCC-01/16/2022 11:16: Botolan 230kV Bus 2 restored at 1115H. (Planned Outage) [WEBSMS] | CLUZ
1/16/2022 8:25:00 AM | LEYTE ACC-01/16/22 07:30: MAASIN SS,Maasin-Nasaug 69 kV L,Deenergized at 0709H,Pre arranged per PANR No. TLOS V_LEY-2022-01-0002, 7am-5pm.load=1.51mw,WEATHER: FAIR | CVIS
1/16/2022 8:22:00 AM | PANAY ACC-01/16/22 07:48: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME IN: 07:44:00, RELAY: M1: Z3, L2-E, 34.3km.; M2, Z3, Trip B - N, 34.31km., WEATHER: FAIR. Open ABS at Tigbauan,to isolate Tigbauan - Miag-ao Line & restored Sta. Barbara - Tigbauan Line. | CVIS
1/16/2022 7:38:00 AM | LRCC-01/16/2022 07:36: Botolan 230kV Bus 2 de-energized at 0735H. (Planned Outage) [WEBSMS] | CLUZ
1/16/2022 7:36:00 AM | LRCC-01/16/2022 07:35: Botolan - Labrador 230kV Line de-energized at 0734H. (Planned Outage) [WEBSMS] | CLUZ
1/16/2022 7:21:00 AM | LEYTE ACC-01/16/22 07:30: MAASIN SS,Maasin-Nasaug 69 kV L,Deenergized at 0709H,Pre arranged per PANR No. TLOS V_LEY-2022-01-0002, 7am-5pm.load=1.51mw,WEATHER: FAIR | CVIS
1/16/2022 7:21:00 AM | PANAY ACC-01/16/22 07:14: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (29.8MW)(5LI1SBA-SJD), TIME OUT: 07:10:00, RELAY: M1: Z3, L2-E, 34.3km.; M2, Z3, Trip B - N, 34.31km., WEATHER: FAIR. Cause under investigation. | CVIS
1/16/2022 6:39:00 AM | LEYTE ACC-01/16/22 06:46: ORMOC SS, Tolosa-San Isidro 69 kV L,Deenergized/Energized at 0613H/0616H,Pre arranged per PANR No.TLOS V_LEY-2022-01-0003,6am-6pm,load=5.0mw,WEATHER: RAINY | CVIS
1/16/2022 6:33:00 AM | NEGROS ACC: 01/16/2022, 34.5kV Amlan-AHEP Line de-energized at 0621H to conduct woodpole replacement and correction of defects. AHEP (0.89MW) isolated | CVIS
1/16/2022 6:10:00 AM | LRCC-01/16/2022 06:10: Mexico - Quezon(Balintawak) 230kV Line de-energized at 0609H. (Planned Outage) [WEBSMS] | CLUZ
1/16/2022 6:08:00 AM | VRCC-01/16/2022 06:08: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2124MW, PK=1440MW, RR=0MW, NetOpMargin: AM=684, PM=575, EVE=248 Highest Unit O/L: PCPC@ 135MW Derated Plant: EDC = 340 MW, PEDC = 164 MW, CEDC = 164 MW [WEBSMS] | CVIS
1/16/2022 4:42:00 AM | VRCC-01/16/2022 04:41: 50MVA TR7 at Naga SS energized at 0437H corrective maintenance activity completed.. [WEBSMS] | CVIS
1/16/2022 3:22:00 AM | VRCC-01/16/2022 03:22: 50MVA TR7 at Naga SS de-energized at 0315H for corrective maintenance. ECD: 0800H. [WEBSMS] | CVIS
1/16/2022 1:23:00 AM | PANAY ACC-01/16/22 01:20: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 01:14:00, TIME IN: 01:19:00, RELAY: Z1, BN, 369.9kms., WEATHER: FAIR; Momentary line fault. | CVIS
1/15/2022 6:14:00 PM | VRCC-01/15/2022 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1902MW, PK=1584MW, RR=0MW, NetOpMargin: EVE=0 Highest Unit O/L: PCPC@ 135MW Derated Plant: EDC = 340 MW, PEDC = 164 MW, CEDC = 164 MW, TVI = 70 MW [WEBSMS] | CVIS
1/15/2022 4:53:00 PM | LRCC-01/15/2022 16:52: Sual 230kV Bus 2 restored at 1649H. (Planned Outage) [WEBSMS] | CLUZ
1/15/2022 2:44:00 PM | LRCC-01/15/2022 14:43: Tayabas - Pagbilao 230kV Line 2 restored at 1437H. (Planned Outage) [WEBSMS] | CLUZ
1/15/2022 2:13:00 PM | VRCC-01/15/2022 14:14: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2118MW, PK=1605MW, RR=0MW, NetOpMargin: PM=513, EVE=318 Highest Unit O/L: PCPC @ 135 MW Derated Plant: EDC = 340 MW, PEDC = 164 MW, CEDC = 164 MW, TVI = 70 MW [WEBSMS] | CVIS
1/15/2022 1:04:00 PM | NEGROS ACC: 01/15/2022, 69kV Bacolod-Alijis Sub-T/L restored at 1248H. Customer-owned and maintained line. | CVIS
1/15/2022 12:40:00 PM | LRCC-01/15/2022 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=9932MW, PK=7603MW, RR=338MW, NetOpMargin: PM=1991, EVE=1795 Highest Unit O/L: Sual 1 at 647MW Derated Plant: San Gabriel at 210MW, Ilijan A/B at 581MW, Masinloc 1 at 300MW, Masinloc 2 at 300MW [WEBSMS] | CLUZ
1/15/2022 12:39:00 PM | LRCC-01/15/2022 12:38: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=9932MW, PK=7603MW, RR=338MW, NetOpMargin: PM=1991, EVE=1795 Highest Unit O/L: Sual 1 at 647MW Derated Plant: San Gabriel at 210MW, Ilijan A/B at 581MW, Masinloc 1 at 300MW, Masinloc 2 at 300MW [WEBSMS] | CLUZ
1/15/2022 12:02:00 PM | PANAY ACC-01/15/22 12:01: ILOILO 1 S/S SS, Iloilo - Lapaz 1 69 kV Line (CO) (5LI1ILO-LZ1), TIME IN: 11:58:00 | CVIS
1/15/2022 11:30:00 AM | VRCC-01/15/2022 11:30: KSPC unit#2 re-cut-in @1124H. [WEBSMS] | CVIS
1/15/2022 10:38:00 AM | NEGROS ACC: 01/15/2022, 69kV Bacolod-Alijis Sub-T/L (20.14MW) auto-tripped at 1029H with indication Z1 L1-E, 2.8km. Customer-owned and maintained line. | CVIS
1/15/2022 8:45:00 AM | VRCC-01/15/2022 08:28: KSPC unit# 2 cut-in @0743H but tripped @0822H with load of 25MW. [WEBSMS] | CVIS
1/15/2022 8:17:00 AM | LRCC-01/15/2022 08:17: Sual 230kV Bus 2 de-energized at 0816H. (Planned Outage) [WEBSMS] | CLUZ
1/15/2022 7:30:00 AM | PANAY ACC-01/15/22 06:07: ILOILO 1 S/S SS, Iloilo - Lapaz 1 69 kV Line (CO) (5LI1ILO-LZ1), TIME OUT: 06:02:00, Load absorbed by PPC1, ETR: 1800H, WEATHER: FAIR | CVIS
1/15/2022 6:24:00 AM | LRCC-01/15/2022 06:21: Tayabas - Pagbilao 230kV Line 2 de-energized at 0620H. (Planned Outage) [WEBSMS] | CLUZ
1/15/2022 6:03:00 AM | VRCC-01/15/2022 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2053MW, PK=1560MW, RR=0MW, NetOpMargin: AM=493, PM=410, EVE=215 Highest Unit O/L: PCPC U3 @ 135 MW. Derated Plant: EDC = 340 MW, PEDC = 164 MW, CEDC = 164 MW, KSPC = 103 MW [WEBSMS] | CVIS
1/15/2022 6:02:00 AM | LRCC-01/15/2022 05:30: Weather Update: Shear Line affecting the eastern section of Mindanao. Northeast Monsoon affecting the rest of the country. [WEBSMS] | CLUZ
1/15/2022 6:02:00 AM | LRCC-01/15/2022 05:40: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=9846MW, PK=7864MW, RR=341MW, NetOpMargin: AM=1641, PM=1775, EVE=1092 Highest Unit O/L: Sual 1 @647MW Derated Plant: Masinloc 1/2 @300MW each, San Gabriel @210MW & Iljan A/B @401MW/180MW [WEBSMS] | CLUZ
1/15/2022 4:57:00 AM | VRCC-01/15/2022 04:57: THVI unit #1 cut-out from the system at 0232H scheduled maintenance. [WEBSMS] | CVIS
1/15/2022 3:41:00 AM | LRCC-01/15/2022 03:15: Correction: Sta Rita Module 40 offline at 0238H. (Unplanned Outage) [WEBSMS] | CLUZ
1/15/2022 2:48:00 AM | LRCC-01/15/2022 02:46: For info: Sta Rita Module 20 completed fuel changeover from oil to natural gas at 0243H. [WEBSMS] | CLUZ
1/15/2022 2:41:00 AM | LRCC-01/15/2022 02:39: Sta Rita Module 30 offline at 0238H. (Unplanned Outage) [WEBSMS] | CLUZ
1/14/2022 11:29:00 PM | LRCC-01/14/2022 23:08: Dasmarinas-Rosario 115kV Line restored at 2306H (Unplanned Outage) [WEBSMS] | CLUZ
1/14/2022 6:49:00 PM | LRCC-01/14/2022 18:47: Dasmarinas-Rosario 115kV Line tripped at 1840H (Unplanned Outage) [WEBSMS] | CLUZ
1/14/2022 6:20:00 PM | VRCC-01/14/2022 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1856MW, PK=1729MW, RR=0MW, NetOpMargin: EVE=127 Highest Unit O/L: PCPC U3 @ 135 MW Derated Plant: EDC = 340 MW, PEDC = 164 MW, CEDC = 164 MW, KSPC = 103 MW, TVI = 70 MW [WEBSMS] | CVIS
1/14/2022 5:51:00 PM | LRCC-01/14/2022 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=9810MW, PK=7946MW, RR=331MW, NetOpMargin: EVE=1533 Highest Unit O/L: SUAL 1 @647MW Derated Plant: MASINLOC 1 @300MW; MASINLOC 2 @300MW; ILJJAN A / B @581MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
1/14/2022 3:18:00 PM | VRCC-01/14/2022 14:13: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2068MW, PK=1733MW, RR=0MW, NetOpMargin: PM=335, EVE=127 Highest Unit O/L: PCPC @ 135 MW Derated Plant: EDC = 340 MW, PEDC = 164 MW, CEDC = 164 MW, KSPC = 103 MW, TVI = 70 MW [WEBSMS] | CVIS
1/14/2022 1:13:00 PM | LRCC-01/14/2022 13:07: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10120MW, PK=8547MW, RR=352MW, NetOpMargin: PM=1221, EVE=872 Highest Unit O/L: SUAL 1 @647MW Derated Plant: MASINLOC 1 @300MW; MASINLOC 2 @300MW; ILJJAN A / B @581MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
1/14/2022 10:23:00 AM | LEYTE ACC-01/14/22: PARANAS SS, 69kV Taft Feeder (up to ABS Cabong) tripped/restored at 1017H/1019H, RELAY: phase CN, 105.34kms, load=8.4MW, WEATHER: FAIR | CVIS
1/14/2022 9:41:00 AM | LRCC-01/14/2022 09:19: Commissioning of Calamba New 300MVA T01 completed at 0917H. [WEBSMS] | CLUZ
1/14/2022 9:41:00 AM | LRCC-01/14/2022 09:21: Calamba New 300MVA T02 energized/looped at high side (230kV) at 0918H(Commissioning test). [WEBSMS] | CLUZ
1/14/2022 8:00:00 AM | LRCC-01/14/2022 08:00: Calamba New 300MVA T01 energized/looped at high side (230kV) at 0757H(Commissioning test). [WEBSMS] | CLUZ
1/14/2022 7:58:00 AM | LEYTE ACC-01/14/22: ORMOC SS, 69kV Ormoc-Simangan-Baybay, tripped/restored at 0748H/0754H, RELAY: phase ABC, OC Inv. Trip in M2(Sifang CSC-211), load=20.8MW, WEATHER: FAIR | CVIS
1/14/2022 7:53:00 AM | PANAY ACC-01/14/22 07:43: DINGLE SS, Dingle-Sta. Barbara 138 kV L2 (7LI2DIN-SBA), TIME IN: 07:39:00 | CVIS
1/14/2022 6:40:00 AM | PANAY ACC-01/14/22 06:13: DINGLE SS, Dingle-Sta. Barbara 138 kV L2 (7LI2DIN-SBA), TIME OUT: 06:08:00, Corrective maintenance, ETR: 10:00:00, WEATHER: FAIR | CVIS
1/14/2022 6:40:00 AM | VRCC-01/14/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2104MW, PK=1745MW, RR=0MW, NetOpMargin: AM=359, PM=335, EVE=127 Highest Unit O/L: PCPC at 135 MW, Derated Plant: EDC at 340 MW, PEDC at 164 MW, CEDC at 164 MW, KSPC at 103 MW, TVI at 70 MW [WEBSMS] | CVIS
1/14/2022 5:58:00 AM | LRCC-01/14/2022 05:57: Calamba New 300MVA TO2 energized via low side (115kV) at 0542H. On-going commissioning test. [WEBSMS] | CLUZ
1/14/2022 5:49:00 AM | LRCC-01/14/2022 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=10093MW, PK=8673MW, RR=351MW, NetOpMargin: AM=1069, PM=1000, EVE=977 Highest Unit O/L: Sual 1 @647MW Derated Plant: Masinloc 1/2 @270MW/300MW, San Gabriel @210MW & Iljan A/B @401MW/180MW [WEBSMS] | CLUZ
1/14/2022 5:18:00 AM | LRCC-01/14/2022 05:10: Weather Update: Shear Line affecting the eastern section of Mindanao. Northeast Monsoon affecting Luzon and Visayas. [WEBSMS] | CLUZ
1/14/2022 4:42:00 AM | LEYTE ACC-01/14/22 04:41: ORMOC SS, 69kV Ormoc-Simangan-Baybay line tripped at 0425H, Indications: O/C Inverse Trip, load=17MW. Restored per clearance from Line Engineer at 0436H. WEATHER: FAIR | CVIS
1/14/2022 12:11:00 AM | LRCC-01/14/2022 00:10: Kalayaan 4 tripped as pump (-160MW) at 0001H while ongoing start-up of Kalayaan 3 as pump. System Frequency at 60.565Hz [WEBSMS] | CLUZ
1/13/2022 6:07:00 PM | VRCC-01/13/2022 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1859MW, PK=1625MW, RR=0MW, NetOpMargin: EVE=234 Highest Unit O/L: PCPC at 135 MW. Derated Plant: EDC at 340 MW, PEDC at 164 MW, CEDC at 164 MW, KSPC at 103 MW, TVI at 70 MW [WEBSMS] | CVIS
1/13/2022 5:44:00 PM | LRCC-01/13/2022 17:31: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=9797MW, PK=8356MW, RR=345MW, NetOpMargin: EVE=1096 Highest Unit O/L: Sual 1 at 647MW Derated Plant: San Gabriel at 210MW, Ilijan A/B at 581MW, Masinloc 1 at 270MW, Masinloc 2 at 300MW, Sta. Rita 30 at 200MW [WEBSMS] | CLUZ
1/13/2022 1:04:00 PM | VRCC-01/13/2022 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2077MW, PK=1653MW, RR=0MW, NetOpMargin: PM=424, EVE=113 Highest Unit O/L: PCPC at 135 MW. Derated Plant: EDC at 340 MW, PEDC at 164 MW, CEDC at 164 MW, KSPC at 103 MW, TVI at 70 MW [WEBSMS] | CVIS
1/13/2022 10:05:00 AM | LRCC-01/13/2022 10:04: For info: Sta Rita Module 40 completed fuel changeover from oil to natural gas at 0940H. [WEBSMS] | CLUZ
1/13/2022 10:04:00 AM | LRCC-01/13/2022 10:04: For info: Sta Rita Module 40 completed fuel changeover from oil to natural gas at 0940H. [WEBSMS] | CLUZ
1/12/2022 11:06:00 PM | LRCC-01/12/2022 23:05: San Jose - Camarin 115kV Line de-energized at 2302H. (Planned Outage) [WEBSMS] | CLUZ
1/12/2022 5:56:00 PM | LRCC-01/12/2022 17:54: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=9846MW, PK=8645MW, RR=354MW, NetOpMargin: EVE=847 Highest Unit O/L: Sual 1 @647MW Derated Plant: Masinloc 1/2 @260MW/300MW, San Gabriel @210MW & Iljan A/B @401MW/180MW [WEBSMS] | CLUZ
1/12/2022 12:58:00 PM | LRCC-01/12/2022 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10168MW, PK=8979MW, RR=371MW, NetOpMargin: PM=818, EVE=817 Highest Unit O/L: Sual 1 @647MW Derated Plant: Masinloc 1/2 @230MW/300MW, San Gabriel @210MW & Iljan A/B @401MW/180MW [WEBSMS] | CLUZ
1/12/2022 10:00:00 AM | NEGROS ACC: 01/12/2022, 69kV Sipalay-Mambaroto Sub T/L restored at 0958H. Customer owned and maintained line. | CVIS
1/12/2022 9:57:00 AM | NEGROS ACC: 01/12/2022, 69kV Sipalay-Mambaroto Sub T/L (1.19MW) auto-tripped at 0942H with indication CN, 7.093km. Customer owned and maintained line. | CVIS
1/12/2022 9:38:00 AM | LRCC-01/12/2022 09:36: Tiwi A-C 230kV Tie Line 1 de-energized at 0934H (Planned Outage) [WEBSMS] | CLUZ
1/12/2022 9:38:00 AM | LRCC-01/12/2022 09:37: Tiwi C 230kV Bus 1 de-energized at 0936H (Planned Outage) [WEBSMS] | CLUZ
1/8/2022 3:44:00 AM | LRCC-01/08/2022 03:43: For info: Sta. Rita 20 completed fuel changeover from oil to natural gas at 0336H due to increase in Natural gas supply allocation. [WEBSMS] | CLUZ
1/8/2022 2:50:00 AM | LRCC-01/08/2022 02:50: Sta. Rita Module 30 Shutdown (Planned Outage) [WEBSMS] | CLUZ
1/8/2022 12:25:00 AM | LRCC-01/08/2022 00:24: Pagbilao 3 offline at 0006H. (Planned Outage) [WEBSMS] | CLUZ
1/8/2022 12:03:00 AM | PANAY ACC-01/07/22 23:56: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN), TIME OUT: 11:55:00, RELAY: Z2 CN 28.01kms. load=6.2MW, WEATHER: FAIR; Under investigation. | CVIS
1/7/2022 7:24:00 PM | NEGROS ACC: 01/07/2022, 69kV Kabankalan-La Castellana Sub T/L restored at 1921H. Customer-owned and maintained line. | CVIS
1/7/2022 6:01:00 PM | VRCC-01/07/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1740MW, PK=1499MW, RR=0MW, NetOpMargin: EVE=241 Highest Unit O/L: PCPC at 135MW Derated Plant: EDC at 320MW, KSPC at 103MW, CEDC at 164MW, PEDC at 164MW. [WEBSMS] | CVIS
1/7/2022 5:52:00 PM | NEGROS ACC: 01/07/2022, 69kV Kabankalan-La Castellana Sub T/L (4.89MW) auto-tripped at 1747H with indication Z1 L2L3, 22.5km. Customer-owned and maintained line. | CVIS
1/7/2022 5:51:00 PM | NEGROS ACC: 01/07/2022, 69kV Kabankalan-La Castellana Sub T/L (4.89MW) auto-tripped at 1747H with indication Z1 L2L3, 22.5km. Customer-owned and maintained line. | CVIS
1/7/2022 5:49:00 PM | LEYTE ACC-01/07/22 17:54: ORMOC SS, Tolosa-San Isidro 69 kV L Manually opened/closed,1727H/1736H, per O&M request to effect the closing of ABS #2 Javier back to normal configuration,load=4.25mw, WEATHER: FAIR | CVIS
1/7/2022 5:39:00 PM | LRCC-01/07/2022 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10987MW, PK=8706MW, RR=343MW, NetOpMargin: EVE=1938 Highest Unit O/L: Sual 1 @647MW Derated Plant: Masinloc 2 @130MW, San Gabriel @210MW & Iljan A/B @425MW/270MW [WEBSMS] | CLUZ
1/7/2022 5:30:00 PM | NEGROS ACC: 01/07/2022, 69kV Kabankalan-La Castellana Sub T/L restored at 1725H. Customer-owned and maintained line. | CVIS
1/7/2022 5:26:00 PM | NEGROS ACC: 01/07/2022, 69kV Kabankalan-La Castellana Sub T/L (4.92MW) auto-tripped at 1719H with indication Z1 L2L3, 22.4 km. Customer-owned and maintained line. | CVIS
1/7/2022 4:12:00 PM | LRCC-01/07/2022 16:11: Gamu-Tuguegarao 230kV Line tripped and reclosed both side at 1604H. (Unplanned Outage) [WEBSMS] | CLUZ
1/7/2022 1:51:00 PM | LRCC-01/07/2022 13:50: For info: San Lorenzo 50 completed fuel changeover from oil to natural gas at 1345H due to increase in Natural gas supply allocation. [WEBSMS] | CLUZ
1/7/2022 1:01:00 PM | LRCC-01/07/2022 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11341MW, PK=8783MW, RR=335MW, NetOpMargin: PM=2223, EVE=2088 Highest Unit O/L: Sual 1 @647MW Derated Plant: Masinloc 2 @130MW, San Gabriel @210MW & Iljan A/B @425MW/270MW [WEBSMS] | CLUZ
1/7/2022 1:01:00 PM | VRCC-01/07/2022 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=1921MW, PK=1344MW, RR=0MW, NetOpMargin: PM=577, EVE=241 Highest Unit O/L: PCPC at 135MW Derated Plant: EDC at 310MW, KSPC at 103MW, CEDC at 164MW, PEDC at 164MW. [WEBSMS] | CVIS
1/7/2022 1:00:00 PM | LRCC-01/07/2022 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11341MW, PK=8783MW, RR=335MW, NetOpMargin: PM=2223, EVE=2088 Highest Unit O/L: Sual 1 @647MW Derated Plant: Masinloc 2 @130MW, San Gabriel @210MW & Iljan A/B @425MW/270MW [WEBSMS] | CLUZ
1/7/2022 12:34:00 PM | LRCC-01/07/2022 12:34: San Gabriel online at 1232H (Unplanned outage) [WEBSMS] | CLUZ
1/7/2022 12:22:00 PM | LEYTE ACC-01/07/22 12:29: MAASIN SS, Maasin-Nasaug 69 kV L,Energized at 1214H,Customers activity completed the Repair of Soleco 13.2kV Distribution line. WEATHER: FAIR | CVIS
1/7/2022 11:47:00 AM | LRCC-01/07/2022 11:45: For info: Sta Rita 10 completed the fuel changeover from oil to natural gas at 1139H due to increase in Natural gas supply allocation. [WEBSMS] | CLUZ
1/7/2022 11:46:00 AM | LRCC-01/07/2022 11:45: For info: Sta Rita 10 completed the fuel changeover from oil to natural gas at 1139H due to increase in Natural gas supply allocation. [WEBSMS] | CLUZ
1/7/2022 11:44:00 AM | LRCC-01/07/2022 11:44: San Gabriel shutdown at 1142H to transfer natural gas supply meter. (unplanned outage) [WEBSMS] | CLUZ
1/7/2022 10:53:00 AM | LRCC-01/07/2022 10:52: For info: San Lorenzo 60 completed the fuel changeover from oil to natural gas at 1042H due to increase in Natural gas supply allocation. [WEBSMS] | CLUZ
1/7/2022 8:24:00 AM | LEYTE ACC-01/07/22 08:33:MAASIN SS,Maasin-Nasaug 69 kV L, Deenergized at 0817H,Per Customers request to effect the Repair of Soleco 13.2kV Distribution line,load=1.12mw, WEATHER: Cloudy | CVIS
1/7/2022 6:49:00 AM | PANAY ACC-01/07/22 06:08: ILOILO 1 S/S , 138kV Iloilo 1-PEDC Line 3, TIME OUT: 06:00:00, Customers request, ETR: 1600H | CVIS
1/7/2022 5:48:00 AM | LRCC-01/07/2022 05:47: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11344MW, PK=8651MW, RR=335MW, NetOpMargin: AM=2358, PM=2194, EVE=2126 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Masinloc 2 at 135MW, Ilijan A/B at 270MW/270MW, and San Gabriel at 375MW [WEBSMS] | CLUZ
1/7/2022 5:22:00 AM | LRCC-01/07/2022 05:22: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
1/7/2022 4:47:00 AM | LRCC-01/07/2022 04:46: Bacman Unit 1 online (Unplanned Outage) [WEBSMS] | CLUZ
1/6/2022 7:56:00 PM | LEYTE ACC-01/06/22 20:01:ORMOC SS,Tolosa-San Isidro 69 kV L,Deenergized/Energized at 1919H/1924,but failed Z2, Phase BN, fd=40.48kms,load=5.2mw, reclosed back at 1928H up to ABS#2 Javier, WEATHER:Cloudy | CVIS
1/6/2022 6:00:00 PM | VRCC-01/06/2022 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1691MW, PK=1417MW, RR=0MW, NetOpMargin: EVE=274 Highest Unit O/L: PCPC at 135MW Derated Plant: EDC at 320MW, KSPC at 103MW, CEDC at 164MW, TPC1A at 20MW, PEDC at 164MW [WEBSMS] | CVIS
1/6/2022 5:30:00 PM | LRCC-01/06/2022 17:29: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10925MW, PK=8666MW, RR=342MW, NetOpMargin: EVE=1916 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 240MW, Ilijan A/B at 540MW, San Gabriel at 375MW, Masinloc 2 at 135MW [WEBSMS] | CLUZ
1/6/2022 4:33:00 PM | NEGROS ACC: 01/06/2022, 138kV Amlan-Mabinay L2 energized at 1623H after completion of maintenance activities. | CVIS
1/6/2022 4:33:00 PM | VRCC-01/06/2022 16:33: TPC1A cut in at 1630H, initial load of 8MW. [WEBSMS] | CVIS
1/6/2022 3:28:00 PM | LEYTE ACC-01/06/22 15:06: MARSHALLING SS,EDC-Malitbog unit #3 cut-in at 1514H,capability increased back to 355.0mw. WEATHER: FAIR | CVIS
1/6/2022 2:58:00 PM | LEYTE ACC-01/06/22 15:06: MARSHALLING SS,EDC-Malitbog unit #3 tripped at 1451H,load=66.6mw, under assesment. WEATHER: FAIR | CVIS
1/6/2022 1:03:00 PM | VRCC-01/06/2022 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=1834MW, PK=1329MW, RR=0MW, NetOpMargin: PM=505, EVE=254 Highest Unit O/L: PCPC at 135MW Derated Plant: EDC at 320MW, KSPC at 103MW, CEDC at 164MW, PEDC at 164MW [WEBSMS] | CVIS
1/6/2022 12:39:00 PM | LRCC-01/06/2022 12:39: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11128MW, PK=8930MW, RR=349MW, NetOpMargin: PM=1849, EVE=1964 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 240MW, Ilijan A/B at 540MW, San Gabriel at 375MW, Masinloc 2 at 135MW [WEBSMS] | CLUZ
1/6/2022 10:46:00 AM | NEGROS ACC: 01/06/2022, 138kV Amlan-Mabinay L2 de-energized at 1031H to conduct troubleshooting of relay at Mabinay SS | CVIS
1/6/2022 6:00:00 AM | VRCC-01/06/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=1875MW, PK=1339MW, RR=0MW, NetOpMargin: AM=536, PM=499, EVE=334 Highest Unit O/L: PCPC at 135MW. Derated Plant: EDC at 320MW, KSPC at 103MW, CEDC at 164MW, PEDC at 164MW [WEBSMS] | CVIS
1/6/2022 5:43:00 AM | LRCC-01/06/2022 05:41: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=10911MW, PK=8651MW, RR=344MW, NetOpMargin: AM=1916, PM=1747, EVE=1681 Highest Unit O/L: Sual 1 @647MW Derated Plant: Masinloc 2 @135MW, Calaca 1 @210MW, San Gabriel @250MW & Iljan A/B @161MW each block [WEBSMS] | CLUZ
1/6/2022 5:26:00 AM | LRCC-01/06/2022 05:26: Weather Update: Northeast Monsoon affecting Northern Luzon. [WEBSMS] | CLUZ
1/6/2022 4:59:00 AM | VRCC-01/06/2022 04:58: 230KV Daanbantayan-Tabango line 2 energized at 0452H, under corrective maintenance activity completed. [WEBSMS] | CVIS
1/6/2022 2:57:00 AM | VRCC-01/06/2022 02:57: 230KV Daanbantayan-Tabango line 2 de-energized at 0010H, under corrective maintenance, pre-arranged activity. ECD: 0600H [WEBSMS] | CVIS
1/6/2022 12:45:00 AM | LEYTE ACC-01/06/22 00:53:TABANGO SS,Daan Bantayan-Tabango 230kV Sub.Cable L2,Deenergized at 0010H,Pre arranged per PANR No.VRCC-2022-01-002,(0100-0600H), WEATHER: FAIR | CVIS
1/5/2022 9:58:00 PM | LRCC-01/05/2022 21:57: For info: Sta Rita Module 30 completed the fuel changeover from gas to oil at 2145H due to Malampaya gas supply restriction. [WEBSMS] | CLUZ
1/5/2022 7:52:00 PM | LEYTE ACC-01/05/22 19:58: ORMOC SS, Tolosa - Mabuhay - Javier 69kV Line portion re-energized at 1946H. Still isolated Javier - San Isidro up to Str. #178-D 60kV Line. Weather: Cloudy. | CVIS
1/5/2022 7:48:00 PM | VRCC-01/05/2022 19:46: Visayas Spot Peak as of Jan. 5, 2022, 1416 MW at 1345H, previous spot peak 2224 MW at 1400H on May 16, 2019. [WEBSMS] | CVIS
1/5/2022 5:46:00 PM | LRCC-01/05/2022 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10945MW, PK=8702MW, RR=347MW, NetOpMargin: EVE=1896 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 210MW, Masinloc 2 at 135MW, Ilijan A/B at 180MW/360MW, and San Gabriel at 375MW [WEBSMS] | CLUZ
1/5/2022 3:06:00 PM | VRCC-01/05/2022 15:06: Turn over dispatch functions of PB4 operation from VRCC to Bohol ACC at 1450H due to availability of Cisco IP phone. [WEBSMS] | CVIS
1/5/2022 1:47:00 PM | LRCC-01/05/2022 13:46: Mexico-Balintawak(Quezon) 230kV line auto-tripped at 1341H. (Unplanned Outage) [WEBSMS] | CLUZ
1/5/2022 1:45:00 PM | LEYTE ACC-01/05/22 13:47: ORMOC SS, 69kV PCB Tolosa (Tolosa-Mabuhay-San Isidro 69kV Line) tripped at 1327H, ind.: Z2, B/C & 33.64kms. Load=5.1MW. Weather: Rainy. | CVIS
1/5/2022 12:10:00 PM | LRCC-01/05/2022 12:09: For info: Sta Rita Module 10 and San Lorenzo Module 50 completed the fuel changeover from gas to oil at 1155H due to Malampaya gas supply restriction. [WEBSMS] | CLUZ
1/5/2022 12:00:00 PM | NEGROS ACC: 01/05/2022, Bacolod-San Enrique 69 kV T/L restored at 1156H. | CVIS
1/5/2022 11:38:00 AM | LRCC-01/05/2022 11:38: San Gabriel offline at 1133H. Affected by the Malampaya gas supply restriction. [WEBSMS] | CLUZ
1/5/2022 11:15:00 AM | LRCC-01/05/2022 11:14: For info: Sta Rita Module 20 completed the fuel changeover from gas to oil at 1109H due to Malampaya gas supply restriction. [WEBSMS] | CLUZ
1/5/2022 11:14:00 AM | LRCC-01/05/2022 11:14: For info: Sta Rita Module 20 completed the fuel changeover from gas to oil at 1109H due to Malampaya gas supply restriction. [WEBSMS] | CLUZ
1/5/2022 10:56:00 AM | NEGROS ACC: 01/05/2022, 69KV Bacolod-San Enrique Sub T/L(23.58MW)auto tripped at 1047H with ind.; Z2 L1L2L3 11.7KM.CENPRI, ISLASOL II and SNBP isolated. | CVIS
1/5/2022 10:47:00 AM | LRCC-01/05/2022 10:46: For info: Sta Rita Module 40 completed the fuel changeover from gas to oil at 1042H due to Malampaya gas supply restriction. [WEBSMS] | CLUZ
1/5/2022 8:00:00 AM | LRCC-01/05/2022 07:59: Meralco Mauban 50MVA T01 de-energized at 0757H. (Planned Outage) [WEBSMS] | CLUZ
1/5/2022 7:48:00 AM | LRCC-01/05/2022 07:47: Mauban-SBPL 230kV line 2 de-energized at 0741H. (Planned Outage) [WEBSMS] | CLUZ
1/5/2022 6:01:00 AM | VRCC-01/05/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=1859MW, PK=1160MW, RR=0MW, NetOpMargin: AM=699, PM=658, EVE=489 Highest Unit O/L: PCPC at 135 MW Derated Plant: EDC at 320 MW, KSPC at 103 MW, CEDC 164 MW, PEDC at 164 MW [WEBSMS] | CVIS
1/5/2022 5:51:00 AM | LRCC-01/05/2022 05:50: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11494MW, PK=8810MW, RR=343MW, NetOpMargin: AM=2341, PM=2274, EVE=2082 Highest Unit O/L: Sual 1 @647MW Derated Plant: Calaca 1 @200MW, San Gabriel @210MW & Iljan A/B @347MW/348MW [WEBSMS] | CLUZ
1/5/2022 5:15:00 AM | LRCC-01/05/2022 05:15: Weather Update: Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
1/4/2022 5:05:00 PM | LEYTE ACC-1/4/2022: KANANGA CS, EDC-Malitbog unit #1 cut-in to the system at 1623H. Weather: Cloudy. | CVIS
1/4/2022 12:34:00 PM | LRCC-01/04/2022 12:33: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11470MW, PK=8761MW, RR=352MW, NetOpMargin: PM=2357, EVE=2475 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 180MW, Ilijan A/B at 695MW, San Gabriel at 210MW [WEBSMS] | CLUZ
1/4/2022 12:30:00 PM | 01/04/2022 ACC Bohol | CVIS
1/4/2022 12:17:00 PM | PB 104 Units 1&2 isolated and on houseload at 1200H | CVIS
1/4/2022 10:44:00 AM | Garcia-Tagbilaran 69kV energized at 1038H | CVIS
1/4/2022 7:05:00 AM | LRCC-01/04/2022 07:04: Bantay 115kV Bus 1 de-energized at 0702H. (Planned Outage) [WEBSMS] | CLUZ
1/4/2022 5:28:00 AM | LEYTE ACC-01/04/22 05:25: ORMOC SS, EDC-Malitbog unit no. 1 emergency cut-out at 0512H. WEATHER: Fair. | CVIS
1/4/2022 5:24:00 AM | LRCC-01/04/2022 05:23: Weather Update: Northeast Monsoon affecting the country. [WEBSMS] | CLUZ
1/4/2022 2:10:00 AM | LRCC-01/04/2022 02:09: Araneta(Dona Imelda)-Sta Mesa 115kV line 2 was Energized at 0152H. (Planned Outage) [WEBSMS] | CLUZ
1/3/2022 11:16:00 PM | LRCC-01/03/2022 23:15: Araneta(Dona Imelda)-Sta Mesa 115kV line 2 was de-energized at 2314H. (Planned Outage) [WEBSMS] | CLUZ
1/3/2022 11:15:00 PM | LRCC-01/03/2022 23:15: Araneta(Dona Imelda)-Sta Mesa 115kV line 2 was de-energized at 2314H. (Planned Outage) [WEBSMS] | CLUZ
1/3/2022 6:56:00 PM | LRCC-01/03/2022 18:55: San Manuel-San Manuel BESS 69kV line restored at 1854H. (Planned Outage) [WEBSMS] | CLUZ
1/3/2022 6:56:00 PM | VRCC-01/03/2022 18:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1633MW, PK=1422MW, RR=0MW, NetOpMargin: EVE=231 Highest Unit O/L: PCPC at 135 MW. Derated Plant: EDC at 300 MW, KSPC at 103 MW, CEDC at 164 MW, PEDC at 164 MW [WEBSMS] | CVIS
1/3/2022 6:45:00 PM | NEGROS ACC: 01/03/2022, 138kV Amlan-Mabinay L2 energized at 1836H. | CVIS
1/3/2022 5:49:00 PM | LRCC-01/03/2022 17:42: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11078MW, PK=8167MW, RR=344MW, NetOpMargin: EVE=2567 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 182MW, Ilijan A/B at 695MW, San Gabriel at 210MW [WEBSMS] | CLUZ
1/3/2022 5:24:00 PM | LRCC-01/03/2022 17:22: Sta. Rita Module 20 online at 1721H. (Unplanned Outage) [WEBSMS] | CLUZ
1/3/2022 1:17:00 PM | VRCC-01/03/2022 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=1770MW, PK=1384MW, RR=0MW, NetOpMargin: PM=386, EVE=231 Highest Unit O/L: PCPC at 135 MW. Derated Plant: EDC at 300 MW, KSPC at 103 MW, CEDC at 164 MW, PEDC at 164 MW [WEBSMS] | CVIS
1/3/2022 12:56:00 PM | LRCC-01/03/2022 12:34: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11069MW, PK=8416MW, RR=335MW, NetOpMargin: PM=2318, EVE=2311 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 185MW, Ilijan A/B at 695MW, San Gabriel at 210MW [WEBSMS] | CLUZ
1/3/2022 12:25:00 PM | PANAY ACC-01/03/22 12:22: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 12:18:00, TIME IN: 12:21:00, WEATHER: FAIR; As per request by AKELCO. | CVIS
1/3/2022 11:14:00 AM | PANAY ACC-01/03/22 10:30: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 10:29:00, TIME IN: , WEATHER: FAIR; Emergency request by AKELCO. | CVIS
1/3/2022 11:14:00 AM | PANAY ACC-01/03/22 10:39: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME IN: 10:38:00, WEATHER: FAIR | CVIS
1/3/2022 10:32:00 AM | LRCC-01/03/2022 10:30: San Manuel-San Manuel BESS 69kV line de-energized at 1029H. [WEBSMS] | CLUZ
1/3/2022 10:32:00 AM | LRCC-01/03/2022 10:31: San Manuel-San Manuel BESS 69kV line de-energized at 1029H. (Planned Outage) [WEBSMS] | CLUZ
1/3/2022 6:21:00 AM | VRCC-01/03/2022 06:15: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=1781MW, PK=1381MW, RR=0MW, NetOpMargin: AM=400, PM=386, EVE=231 Highest Unit O/L: PCPC at 135 MW Derated Plant: EDC at 300 MW, KSPC at 103 MW, CEDC at 164 MW, PEDC at 164 MW [WEBSMS] | CVIS
1/3/2022 5:54:00 AM | LRCC-01/03/2022 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11265MW, PK=8633MW, RR=350MW, NetOpMargin: AM=2282, PM=2245, EVE=2304 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Ilijan at 695MW, Calaca 1 at 185MW, and San Gabriel at 210MW [WEBSMS] | CLUZ
1/3/2022 5:21:00 AM | LRCC-01/03/2022 05:20: Weather Update: Shear Line affecting the eastern sections of Visayas and Mindanao. Northeast Monsoon affecting the rest of the country. [WEBSMS] | CLUZ
1/3/2022 5:20:00 AM | LRCC-01/03/2022 05:20: Weather Update: Shear Line affecting the eastern sections of Visayas and Mindanao. Northeast Monsoon affecting the rest of the country. [WEBSMS] | CLUZ
1/3/2022 3:42:00 AM | PANAY ACC-01/03/22 03:41: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME IN: 03:37:00 | CVIS
1/3/2022 3:40:00 AM | PANAY ACC-01/03/22 03:27: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 03:20:00, Load: 14.5mw, customers request to conduct emergency repair of blown out fuse cut-out at AKELCO Altavas SS | CVIS
1/3/2022 1:14:00 AM | LEYTE ACC-01/03/22 01:13: ORMOC SS, 69kV Ormoc-Lemon-Tolosa-San Isidro line tripped at 0100H, EF Inverse trip, load=21.1MW. Restored per clearance from Line Engineer at 0106H. WEATHER: FAIR | CVIS
1/2/2022 9:23:00 PM | VRCC-01/02/2022 21:22: 34.5 KV CARCON - SANGI L1 and L2 energized at 2118H and 2119H respectively. [WEBSMS] | CVIS
1/2/2022 8:29:00 PM | VRCC-01/02/2022 20:29: 34.5 KV CARCON - SANGI L1 and L2 tripped at 2006 H ,with indication @ CARCON for L2 ,Phase BG FD =35.63 KM Load 4.5 MW [WEBSMS] | CVIS
1/2/2022 7:08:00 PM | VRCC-01/02/2022 19:08: 30 MVA Transformer # 1 at Samboan SS energized at 1903H, heat soaking. [WEBSMS] | CVIS
1/2/2022 6:52:00 PM | PANAY ACC-01/02/22 18:46: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD)(35.58MW), TIME IN: 18:44H, RELAY: M1: Z1, 0.4km.; M2: Z1, Trip B - n, 611.7meters., WEATHER: FAIR. Cause: Busted L.A at ILECO 1 Tapping Point of their 69kV Line for Iloilo International Airport. | CVIS
1/2/2022 6:14:00 PM | LRCC-01/02/2022 18:13: San Manuel-San Manuel BESS 69kV line restored at 1800H. (Planned Outage) [WEBSMS] | CLUZ
1/2/2022 6:09:00 PM | PANAY ACC-01/02/22 18:18: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD), TIME OUT: 06:02:00, RELAY: M1: Z1, 0.4km.; M2: Z1, Trip B - N, 611.7meters., WEATHER: FAIR | CVIS
1/2/2022 6:09:00 PM | VRCC-01/02/2022 18:09: 138KV Colon-Samboan Line 1 energized at 1741H, parallel operation with Line 2 at 1754 on normal operation. [WEBSMS] | CVIS
1/2/2022 6:07:00 PM | VRCC-01/02/2022 18:06: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1653MW, PK=1063MW, RR=0MW, NetOpMargin: EVE=590 Highest Unit O/L: PCPC at 135MW. Derated Plant: EDC at 300MW, KSPC at 103MW, CEDC at 164MW, PEDC at 164MW. OUTAGE: TVI U at 338MW, TPC1A at 82MW. [WEBSMS] | CVIS
1/2/2022 6:01:00 PM | LRCC-01/02/2022 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10823MW, PK=7197MW, RR=271MW, NetOpMargin: EVE=3355 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 185MW, Ilijan A/B at 695MW, San Gabriel at 210MW [WEBSMS] | CLUZ
1/2/2022 1:25:00 PM | VRCC-01/02/2022 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=1770MW, PK=1005MW, RR=0MW, NetOpMargin: PM=765, EVE=590 Highest Unit O/L: PCPC at 135MW. Derated Plant: EDC at 300MW, KSPC at 103MW, CEDC at 164MW, PEDC at 164MW. OUTAGE: TVI U at 338MW, TPC1A at 82MW. [WEBSMS] | CVIS
1/2/2022 12:54:00 PM | LRCC-01/02/2022 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11143MW, PK=6570MW, RR=244MW, NetOpMargin: PM=4328, EVE=2518 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 185MW, Ilijan A/B at 695MW, San Gabriel at 210MW [WEBSMS] | CLUZ
1/2/2022 9:31:00 AM | LRCC-01/02/2022 09:09: San Manuel-San Manuel BESS 69kV line de-energized at 0908H. (Planned Outage) [WEBSMS] | CLUZ
1/2/2022 6:18:00 AM | LRCC-01/02/2022 05:52: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11189MW, PK=7416MW, RR=247MW, NetOpMargin: AM=3526, PM=3587, EVE=2513 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Ilijan at 695MW, Calaca 1 at 185MW and San Gabriel at 210MW [WEBSMS] | CLUZ
1/2/2022 6:18:00 AM | VRCC-01/02/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=1781MW, PK=1005MW, RR=0MW, NetOpMargin: AM=776, PM=765, EVE=590 Highest Unit O/L: PCPC at 135MW Derated Plant: EDC at 300MW, KSPC at 103MW, CEDC at 164MW, PEDC at 164MW. OUTAGE: TVI U at 338MW, TPC1A at 82MW. [WEBSMS] | CVIS
1/2/2022 5:40:00 AM | LRCC-01/02/2022 05:38: Weather Update: Northeast Monsoon affecting the whole country. [WEBSMS] | CLUZ
1/1/2022 11:46:00 PM | NEGROS ACC: 01/01/2022, 69kV Kabankalan-La Castellana Sub T/L (1.85 MW) auto-tripped at 2335H with indication Z1 L1L3, 18.2 km. Restored at 2339H. Customer-owned and maintained line. | CVIS
1/1/2022 10:48:00 PM | LRCC-01/01/2022 22:27: Dolores(Taytay) 300MVA T04 restored at 2218H. (Unplanned Outage) [WEBSMS] | CLUZ
1/1/2022 10:48:00 PM | LRCC-01/01/2022 22:39: San Manuel-San Manuel BESS 69kV line restored at 2234H. (Planned Outage) [WEBSMS] | CLUZ
1/1/2022 10:07:00 PM | LRCC-01/01/2022 21:45: Dolores(Taytay) 300MVA T04 de-energized at 2142H. (Unplanned Outage) [WEBSMS] | CLUZ
1/1/2022 6:02:00 PM | VRCC-01/01/2022 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1628MW, PK=1107MW, RR=0MW, NetOpMargin: EVE=521 Highest Unit O/L: PCPC at 135 MW Derated Plant: EDC at 300 MW , CEDC at 164 MW, PEDC at 164 MW, KSPC at 103 MW [WEBSMS] | CVIS
1/1/2022 5:31:00 PM | LRCC-01/01/2022 17:28: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10656MW, PK=6519MW, RR=275MW, NetOpMargin: EVE=3862 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 185MW, Ilijan A/B at 695MW, San Gabriel at 210MW [WEBSMS] | CLUZ
1/1/2022 5:30:00 PM | LRCC-01/01/2022 17:28: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10656MW, PK=6519MW, RR=275MW, NetOpMargin: EVE=3862 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 185MW, Ilijan A/B at 695MW, San Gabriel at 210MW [WEBSMS] | CLUZ
1/1/2022 1:42:00 PM | VRCC-01/01/2022 13:41: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=1767MW, PK=940MW, RR=0MW, NetOpMargin: PM=827, EVE=521 Highest Unit O/L: PCPC at 135 MW Derated Plant: PEDC at 164 MW, CEDC at 164 MW, KSPC at 103 MW, EDC at 300 MW [WEBSMS] | CVIS
1/1/2022 1:01:00 PM | LRCC-01/01/2022 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10921MW, PK=6093MW, RR=254MW, NetOpMargin: PM=4501, EVE=2715 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 185MW, Ilijan A/B at 695MW, San Gabriel at 210MW [WEBSMS] | CLUZ
1/1/2022 1:00:00 PM | LRCC-01/01/2022 12:59: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10921MW, PK=6093MW, RR=254MW, NetOpMargin: PM=4501, EVE=2715 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 185MW, Ilijan A/B at 695MW, San Gabriel at 210MW [WEBSMS] | CLUZ
1/1/2022 12:20:00 PM | NEGROS ACC: 01/01/2022, 34.5KV Amlan-AHEP Line restored at 1213H. | CVIS
1/1/2022 7:12:00 AM | LRCC-01/01/2022 05:29: Weather Update: Shear Line affecting Visayas and the northeastern portion of Mindanao. Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
1/1/2022 7:12:00 AM | LRCC-01/01/2022 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=10957MW, PK=6820MW, RR=246MW, NetOpMargin: AM=3890, PM=3690, EVE=2713 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Ilijan at 695MW, Calaca 1 at 200MW and SLTEC 1 at 48MW [WEBSMS] | CLUZ
1/1/2022 7:11:00 AM | VRCC-01/01/2022 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=1792MW, PK=922MW, RR=0MW, NetOpMargin: AM=870, PM=827, EVE=521 Highest Unit O/L: PCPC at 135MW Derated Plant: EDC at 300MW, KSPC at 103MW, CEDC at 164MW, PEDC at 164MW. OUTAGE: TVI at 338MW, TPC1A at 82MW. [WEBSMS] | CVIS
1/1/2022 5:30:00 AM | LRCC-01/01/2022 05:29: Weather Update: Shear Line affecting Visayas and the northeastern portion of Mindanao. Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
1/1/2022 12:55:00 AM | PANAY ACC-01/01/22 00:37: PEDC U3 (150MW) OUT:0035H; due to APMS; ETA:01/30/2022 @ 2400H | CVIS
1/1/2022 12:49:00 AM | PANAY ACC-01/01/22 00:37: PEDC U3 (150MW) OUT:0035H; due to APMS; ETA:01/30/2022 @ 2400H | CVIS
12/31/2021 6:04:00 PM | VRCC-12/31/2021 18:03: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1784MW, PK=1227MW, RR=0MW, NetOpMargin: EVE=557 Highest Unit O/L: PEDC U # 3 at 150 MW Derated Plant: EDC at 300 MW, KSPC at 103 MW, CEDC at 264 MW [WEBSMS] | CVIS
12/31/2021 5:32:00 PM | LRCC-12/31/2021 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10773MW, PK=7012MW, RR=274MW, NetOpMargin: EVE=3487 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 185MW, Ilijan A/B at 695MW, Masinloc 3 at 140MW, San Gabriel at 210MW [WEBSMS] | CLUZ
12/31/2021 1:35:00 PM | VRCC-12/31/2021 13:17: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=1915MW, PK=1134MW, RR=0MW, NetOpMargin: PM=781, EVE=557 Highest Unit O/L: PEDC U # 3 at 150 MW Derated Plant: EDC at 300 MW, KSPC at 103 MW , CEDC at 164 MW [WEBSMS] | CVIS
12/31/2021 1:05:00 PM | LRCC-12/31/2021 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11170MW, PK=6737MW, RR=406MW, NetOpMargin: PM=4160, EVE=3390 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 185MW, Ilijan A/B at 737MW, Masinloc 3 at 140MW, San Gabriel at 210MW [WEBSMS] | CLUZ
12/31/2021 12:43:00 PM | LRCC-12/31/2021 12:42: Sta. Rita Module 40 online at 1238H. (Unplanned Outage) [WEBSMS] | CLUZ
12/31/2021 12:37:00 PM | VRCC-12/31/2021 12:35: CEBECO 3 Pinamungajan feeder energized at 1217H [WEBSMS] | CVIS
12/31/2021 10:28:00 AM | LRCC-12/31/2021 10:26: Taytay(Dolores) 300MVA T04 restored at 1026H. (Unplanned Outage) [WEBSMS] | CLUZ
12/31/2021 10:28:00 AM | LRCC-12/31/2021 10:27: Mexico-Quezon(Balintawak) 230kV line restored at 1026H. (Planned Outage) [WEBSMS] | CLUZ
12/31/2021 8:42:00 AM | LRCC-12/31/2021 08:40: Taytay(Dolores) 300MVA T04 tripped at 0833H. (Unplanned Outage) [WEBSMS] | CLUZ
12/31/2021 8:35:00 AM | LEYTE ACC-12/31/21 08:26: KANANGA CS, EDC-Mahanagdong B unit #3 cut-in to the system at 0811H. Weather: Cloudy. | CVIS
12/31/2021 8:08:00 AM | LRCC-12/31/2021 08:07: Taytay(Dolores) 300MVA T05 de-energized at 0806H. (Planned Outage) [WEBSMS] | CLUZ
12/31/2021 7:46:00 AM | LEYTE ACC-12/31/21 07:52: PB 104, Black start dispatch for PB 104 at 0740H. Weather: Cloudy. | CVIS
12/31/2021 7:11:00 AM | LRCC-12/31/2021 07:10: Mexico-Quezon(Balintawak) 230kV line de-energized at 0706H. (Planned Outage) [WEBSMS] | CLUZ
12/31/2021 6:01:00 AM | VRCC-12/31/2021 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=1942MW, PK=1091MW, RR=0MW, NetOpMargin: AM=851, PM=781, EVE=557 Highest Unit O/L: PEDC U3 at 150MW Derated Plant: EDC at 300MW, KSPC at 103MW, CEDC at 164MW. OUTAGE: TVI at 338MW, TPC1A at 82MW. [WEBSMS] | CVIS
12/31/2021 5:59:00 AM | LRCC-12/31/2021 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11044MW, PK=7820MW, RR=274MW, NetOpMargin: AM=2950, PM=3069, EVE=2676 Highest Unit O/L: SUAL 1 @647MW Derated Plant: CALACA 1 @190MW; MASINLOC 3 @140MW; ILJJAN A / B @737MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
12/30/2021 6:08:00 PM | LRCC-12/30/2021 18:06: Daraga-Bacman 230kV line 1 looped at Daraga side at 1800H. (Unplanned Outage) [WEBSMS] | CLUZ
12/30/2021 6:06:00 PM | LRCC-12/30/2021 18:05: Daraga-Bacman 230kV line tripped at Daraga side at 1751H. (Unplanned Outage) [WEBSMS] | CLUZ
12/30/2021 6:04:00 PM | VRCC-12/30/2021 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1736MW, PK=1254MW, RR=0MW, NetOpMargin: EVE=482 Highest Unit O/L: PEDC at 150 MW Derated Plant: EDC at 300 MW [WEBSMS] | CVIS
12/30/2021 5:58:00 PM | LRCC-12/30/2021 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10715MW, PK=7199MW, RR=308MW, NetOpMargin: EVE=3208 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Masinloc 3 at 140MW, Ilijan at 737MW, San Gabriel at 210MW, Calaca 1 at 200MW and SLTEC 1 at 48MW [WEBSMS] | CLUZ
12/30/2021 5:58:00 PM | LRCC-12/30/2021 17:45: San Jose 750MVA T05 restored at 1744H. (Planned Outage) [WEBSMS] | CLUZ
12/30/2021 5:58:00 PM | LRCC-12/30/2021 17:50: San Jose-Tayabas 500kV line 2 restored at 1750H. (Planned Outage) [WEBSMS] | CLUZ
12/30/2021 5:58:00 PM | NEGROS ACC: 12/30/2021, 69kV Amlan- Montesol-Bindoy Line Section energized at 1601H. | CVIS
12/30/2021 5:58:00 PM | NEGROS ACC: 12/30/2021, 69kV Amlan- Montesol-Binoy Line Section energized at 1601H. | CVIS
12/30/2021 5:58:00 PM | NEGROS ACC: 12/30/2021, 69kV Amlan-Montesol Line section(1.2MW) de-energized at 1556H to facilitate energization of 69KV Montesol-Bindoy Line Section.Montesol(2.29MW) & CABI isolated. | CVIS
12/30/2021 2:53:00 PM | LRCC-12/30/2021 14:52: Taytay(Dolores) 300MVA T02 restored at 1451H. (Planned Outage) [WEBSMS] | CLUZ
12/30/2021 1:36:00 PM | LEYTE ACC-12/30/21: ORMOC SS, 69kV Tolosa-San Isidro Line (extended up to SOLECO Sogod Ss)tripped/restored at 1308H/1316H, RELAY: z2, phase BN, 36.8kms, WEATHER: RAINY | CVIS
12/30/2021 1:13:00 PM | LRCC-12/30/2021 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11091MW, PK=7266MW, RR=280MW, NetOpMargin: PM=3545, EVE=2858 Highest Unit O/L: Sual 1at 647MW Derated Plant: Masinloc 3 at 140MW, Ilijan at 737MW, San Gabriel at 210MW and Calaca 1 at 200MW [WEBSMS] | CLUZ
12/30/2021 1:06:00 PM | VRCC-12/30/2021 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=1928MW, PK=1165MW, RR=0MW, NetOpMargin: PM=763, EVE=482 Highest Unit O/L: PEDC at 150 MW Derated Plant: EDC at 300 MW [WEBSMS] | CVIS
12/30/2021 12:49:00 PM | LEYTE ACC-12/30/21: ORMOC SS, 69kV Tolosa-San Isidro (extended up to SOLECO Sogod Ss) tripped/restored at 1233H/1242H, RELAY: z2, phase BN, 31.84kms, load=4.0MW, WEATHER: RAINY | CVIS
12/30/2021 12:48:00 PM | LEYTE ACC-12/30/21: ORMOC SS, 69kV Tolosa-San Isidro (extended up to SOLECO Sogod Ss) tripped/restored at 1233H/1242H, RELAY: z2, phase BN, 31.84kms, load=4.0MW, WEATHER: RAINY | CVIS
12/30/2021 10:50:00 AM | VRCC-12/30/2021 10:50: 34.5 KV Sangi - CEBECO 3 tripped at 1041H [WEBSMS] | CVIS
12/30/2021 9:58:00 AM | LRCC-12/30/2021 09:57: Calaca-SLPGC 230kV line 2 and SLPGC 230kV Bus 2 de-energized at 0946H and 0949H respectively. (Planned Outage) [WEBSMS] | CLUZ
12/30/2021 9:21:00 AM | LRCC-12/30/2021 09:20: Bauang-Bacnotan 230kV line restored at 0918H. (Planned Outage) [WEBSMS] | CLUZ
12/30/2021 8:18:00 AM | LRCC-12/30/2021 08:18: Taytay(Dolores) 300MVA T02 de-energized at 0816H. (Planned Outage) [WEBSMS] | CLUZ
12/30/2021 7:21:00 AM | VRCC-12/30/2021 07:20: Lapulapu GIS feeder 2 Manual open at 0630 H , reclosed at 0710H load 1.2 MW customers request [WEBSMS] | CVIS
12/30/2021 7:18:00 AM | LRCC-12/30/2021 07:14: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11055MW, PK=7069MW, RR=340MW, NetOpMargin: AM=3722, PM=3835, EVE=2847 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 200MW, Ilijan A/B at 737MW, Masinloc 3 at 140MW, San Gabriel at 210MW [WEBSMS] | CLUZ
12/30/2021 7:17:00 AM | LRCC-12/30/2021 07:14: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11055MW, PK=7069MW, RR=340MW, NetOpMargin: AM=3722, PM=3835, EVE=2847 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Calaca 1 at 200MW, Ilijan A/B at 737MW, Masinloc 3 at 140MW, San Gabriel at 210MW [WEBSMS] | CLUZ
12/30/2021 6:34:00 AM | LRCC-12/30/2021 06:28: San Jose 750MVA T05 de-energized at 0626H. (Planned Outage) [WEBSMS] | CLUZ
12/30/2021 6:26:00 AM | LRCC-12/30/2021 06:24: San Jose-Tayabas 500kV line 2 de-energized at 0623H. (Planned Outage) [WEBSMS] | CLUZ
12/30/2021 6:13:00 AM | VRCC-12/30/2021 06:10: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=1961MW, PK=1089MW, RR=36MW, NetOpMargin: AM=872, PM=763, EVE=482 Highest Unit O/L: PEDC U3 @ 150 MW Derated Plant: EDC = 321 MW [WEBSMS] | CVIS
12/30/2021 5:12:00 AM | LRCC-12/30/2021 05:10: Bauang-Bacnotan 230kV Line de-energized at 0510H. (Planned Outage) [WEBSMS] | CLUZ
12/30/2021 12:34:00 AM | LRCC-12/30/2021 00:32: SLPGC Unit 2 offline at 0028H. (Planned Outage) [WEBSMS] | CLUZ
12/29/2021 11:50:00 PM | LRCC-12/29/2021 23:48: Sual 2 offline at 2344H. (Planned Outage) [WEBSMS] | CLUZ
12/29/2021 11:15:00 PM | LRCC-12/29/2021 23:14: Lumban-Bay 230kV Line 1 restored at 2311H. (Planned Outage) [WEBSMS] | CLUZ
12/29/2021 9:22:00 PM | LEYTE ACC-12/29/21 21:28: MAASIN SS, Maasin-Nasaug 69 kV L energized up to Soleco ABS#1 at 2054H while Soleco ABS#1 closed at 2108H with clearance from O&M & Soleco GM ,WEATHER: Cloudy | CVIS
12/29/2021 9:13:00 PM | LRCC-12/29/2021 21:11: Limay 100MVA T02 energized (high side) at 2104H. (Commissioning Test) [WEBSMS] | CLUZ
12/29/2021 6:32:00 PM | LRCC-12/29/2021 18:30: Taytay (Dolores) 300MVA T04 restored at 1828H. (Planned Outage) [WEBSMS] | CLUZ
12/29/2021 6:30:00 PM | VRCC-12/29/2021 18:28: 138 KV Colon-Cebu L1 energized at 1828H. [WEBSMS] | CVIS
12/29/2021 6:01:00 PM | VRCC-12/29/2021 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1714MW, PK=1314MW, RR=0MW, NetOpMargin: EVE=400 Highest Unit O/L: PEDC U3 at 150MW Derated Plant: EDC at 300MW, KSPC at 103MW, CEDC at 164MW. OUTAGE: TVI at 338MW, TPC1A at 82MW. [WEBSMS] | CVIS
12/29/2021 5:56:00 PM | LRCC-12/29/2021 17:53: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11550MW, PK=8090MW, RR=329MW, NetOpMargin: EVE=3131 Highest Unit O/L: SUAL 1 @647MW Derated Plant: CALACA 1 @200MW; MASINLOC 3 @140MW; SUAL 2 @590MW; ILJJAN A / B @737MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
12/29/2021 5:48:00 PM | LEYTE ACC-12/29/21 17:50:PARANAS SS,Unload Cabong SS at 1644H load=5.2mw, to effect opening of ABS Cabong load transferred back to Paranas SS at 1730H back to normal configuration.WEATHER: FAIR | CVIS
12/29/2021 4:02:00 PM | LRCC-12/29/2021 16:01: Lumban - Gumaca 230kV Line 1 restored at 1600H (Planned Outage) [WEBSMS] | CLUZ
12/29/2021 3:35:00 PM | NEGROS ACC: 12/29/2021, 69KV Sipalay-Mambaroto Sub T/L restored at 1529H. | CVIS
12/29/2021 2:40:00 PM | LRCC-12/29/2021 14:38: Taytay (Dolores) 300MVA T04 de-energized at 1438H (Planned Outage) [WEBSMS] | CLUZ
12/29/2021 2:10:00 PM | LRCC-12/29/2021 14:08: Taytay (Dolores) 300MVA T03 restored at 1358H (Planned Outage) [WEBSMS] | CLUZ
12/29/2021 1:06:00 PM | VRCC-12/29/2021 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=1714MW, PK=1200MW, RR=0MW, NetOpMargin: PM=514, EVE=400 Highest Unit O/L: PEDC U3 at 150MW Derated Plant: EDC at 300MW, KSPC at 103MW, CEDC at 164MW. OUTAGE: TVI at 338MW, TPC1A at 82MW. [WEBSMS] | CVIS
12/29/2021 12:59:00 PM | LRCC-12/29/2021 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11864MW, PK=8093MW, RR=336MW, NetOpMargin: PM=3435, EVE=3030 Highest Unit O/L: SUAL 1 @647MW Derated Plant: CALACA 1 @200MW; MASINLOC 3 @140MW; SUAL 2 @590MW; ILJJAN A / B @737MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
12/29/2021 11:52:00 AM | LEYTE ACC-12/29/21 12:00: PARANAS SS,Paranas- ABS Nato line tripped/restored 1136H/1146H, Z2, Phase AN, fd=78.94kms, load=3.6mw,WEATHER:Cloudy/Windy | CVIS
12/29/2021 5:19:00 AM | LRCC-12/29/2021 05:18: Weather Update: Shear Line affecting Visayas and the northeastern section of Mindanao. Northeast Monsoon affecting Luzon. [WEBSMS] | CLUZ
12/29/2021 2:09:00 AM | NEGROS ACC: 12/29/2021, 69kV Amlan-Montesol Line section(2.17MW) auto tripped at 0154H with ind.; Z2 AN DELAY 28.88KM. | CVIS
12/29/2021 1:14:00 AM | NEGROS ACC: 12/29/2021, 69kV Amlan-Montesol Line section(2.3MW) auto tripped at 0054H with ind.; Z2 AN DELAY 29.06KM. Restored at 0107H. | CVIS
12/29/2021 12:04:00 AM | LRCC-12/29/2021 00:04: Hermosa 230kV Bus 1 energized at 0001H. (Planned Outage) [WEBSMS] | CLUZ
12/28/2021 11:17:00 PM | LRCC-12/28/2021 23:16: Taytay(Dolores)-Pinagbuhatan 115kV line and Taytay(Dolores) 115kV Bus 2 de-energized at 2308H and 2313H respectively. (Planned Outage) [WEBSMS] | CLUZ
12/28/2021 9:15:00 PM | LEYTE ACC-12/28/21 21:22:PARANAS SS,69kV ABS Cabong closed at 2104H load transferred Cabong SS via Sta Rita SS. WEATHER: Cloudy | CVIS
12/28/2021 8:11:00 PM | LRCC-12/28/2021 20:10: Hermosa 230kV Bus 1 de-energized at 2008H. (Planned Outage) [WEBSMS] | CLUZ
12/28/2021 6:17:00 PM | LRCC-12/28/2021 18:16: Currimao-Currimao Solar 69kV line de-energized at 1814H. (Planned Outage) [WEBSMS] | CLUZ
12/28/2021 6:15:00 PM | LEYTE ACC-12/28/21 18:22:PARANAS SS,Paranas-Borongan-Quinapondan 69kV L,69kV Taft feeder energized back up to ABS Nato at 1804H,WEATHER: RAINY | CVIS
12/28/2021 6:00:00 PM | VRCC-12/28/2021 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1631MW, PK=1324MW, RR=0MW, NetOpMargin: EVE=307 Highest Unit O/L: PEDC U3 at 150MW Derated Plant: EDC at 300MW, KSPC at 103MW, CEDC at 82MW. OUTAGE: TVI at 338, TPC1A at 82MW. [WEBSMS] | CVIS
12/28/2021 5:58:00 PM | LRCC-12/28/2021 17:58: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11476MW, PK=8086MW, RR=330MW, NetOpMargin: EVE=3060 Highest Unit O/L: SUAL 1 @647MW Derated Plant: MASINLOC 3 @140MW; SUAL 2 @590MW; ILJJAN A / B @737MW; SAN GABRIEL @210MW [WEBSMS] | CLUZ
12/28/2021 4:49:00 PM | LEYTE ACC-12/28/21 16:56:PARANAS SS,Paranas-Borongan-Quinapondan 69 kV L ,tripped at 1639H Z2, Phase AN, 78.8kms,load=8.6mw,reclosed at 1641H but failed, WEATHER: RAINY | CVIS
12/28/2021 4:45:00 PM | LRCC-12/28/2021 16:43: Limay - Batangas II (BPC) 230kV Line 2 restored at 1642H (Planned Outage) [WEBSMS] | CLUZ
12/28/2021 4:27:00 PM | LEYTE ACC-12/28/21 16:33: MAASIN SS,69kV ABS San Isidro closed at 1530H up to Str.# 178-B while 10MVA Sogod SS energized at 1607H. WEATHER: Rainy | CVIS
12/28/2021 4:09:00 PM | NEGROS ACC: 12/28/2021, 69kV Amlan-Montesol Line section energized at 1604H. | CVIS
12/28/2021 4:07:00 PM | VRCC-12/28/2021 16:05: 138 KV Colon-Cebu L1 re energized at 1602H. [WEBSMS] | CVIS
12/28/2021 3:47:00 PM | NEGROS ACC: 12/28/2021, 69kV Amlan-Bais Line section( 2.56MW) de-energized at 1544H to facilitate energization of 69kV Bais-Montesol Line Section, close DSW at Bais. | CVIS
12/28/2021 3:45:00 PM | NEGROS ACC: 12/28/2021, 69kV Amlan-Bais Line section( 2.56MW) de-energized at 1544H to facilitate energization of 69kV Bais-Montesol Line Section, close DSW at Bais. | CVIS
12/28/2021 3:26:00 PM | PANAY ACC-12/28/21 15:07: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD),Load:35.9MW; TIME OUT: 15:02, TIME IN: 15:07, RELAY: Z3 AN at 37.21kms, Cause: Under investigation | CVIS
12/28/2021 3:16:00 PM | PANAY ACC-12/28/21 15:07: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD),Load:35.9MW; TIME OUT: 15:02, TIME IN: 15:07, RELAY: Z3 AN at 37.21kms, Cause: Under investigation | CVIS
12/28/2021 3:14:00 PM | PANAY ACC-12/28/21 15:07: STA. BARBARA SS, Sta. Barbara-Miagao 69 kV Line (5LI1SBA-SJD),Load:35.9MW; TIME OUT: 15:02, TIME IN: 15:07, RELAY: Z3 AN at 37.21kms, Cause: Under investigation | CVIS
12/28/2021 2:42:00 PM | VRCC-12/28/2021 14:42: Compostela SS. 150 MVA TR 5 and TR 6 energized at 1439H and 1440H, respectively. [WEBSMS] | CVIS
12/28/2021 12:44:00 PM | LEYTE ACC-12/28/21 12:53: ORMOC SS, Tolosa-Mabuhay-San Isidro 69kV Line re-energized at 1238H, emergency repair completed. Weather: Rainy. | CVIS
12/28/2021 12:44:00 PM | LRCC-12/28/2021 12:43: Sta. Rita 40 offline at 1234H (Unplanned Outage). [WEBSMS] | CLUZ
12/28/2021 11:26:00 AM | LRCC-12/28/2021 11:24: Sta. Rita 20 (161MW) tripped at 1121H (Unplanned Outage). Lowest freq =59.49Hz. [WEBSMS] | CLUZ
12/28/2021 10:19:00 AM | VRCC-12/28/2021 10:18: Calongcalong bus 2 energized at 1014H. Colon-Cebu L2L3 earthing engaged at 1002H, Colon-Calongcalong earthing engaged at 1010H. [WEBSMS] | CVIS
12/28/2021 10:01:00 AM | VRCC-12/28/2021 10:00: 69 KV Naga-Sibonga line tripped/energized at 0938H/0956H. [WEBSMS] | CVIS
12/28/2021 9:59:00 AM | VRCC-12/28/2021 09:58: 69 KV Naga-Sibonga line energized at 0956H. [WEBSMS] | CVIS
12/28/2021 9:55:00 AM | VRCC-12/28/2021 09:54: 69 KV Naga-Sibonga line tripped L=3.92MW, ind:Z1, CA, 9.3 km. [WEBSMS] | CVIS
12/28/2021 9:49:00 AM | VRCC-12/28/2021 09:48: 138 KV Colon-Cebu L1 tripped at 0943H w/a load of 49MW, ind retrieval on progress. [WEBSMS] | CVIS
12/28/2021 9:12:00 AM | VRCC-12/28/2021 09:11: 138 KV Colon-Cebu L1 re energized at 0909H, diff trip ind, w/ clearance from O & M. [WEBSMS] | CVIS
12/28/2021 8:58:00 AM | VRCC-12/28/2021 08:57: 138 KV Colon-Cebu L1 tripped at 0850H w/a load of 39MW, ind retrieval on progress. [WEBSMS] | CVIS
12/28/2021 8:56:00 AM | VRCC-12/28/2021 08:55: Toledo Solar generates 5MW at 0844H. [WEBSMS] | CVIS
12/28/2021 8:46:00 AM | LRCC-12/28/2021 08:45: Taytay (Dolores) 115kV Bus 2 restored at 0844H (Planned Outage) [WEBSMS] | CLUZ
12/28/2021 8:11:00 AM | LRCC-12/28/2021 08:10: Limay - Batangas II (BPC) 230kV Line 2 de-energized at 0810H (Planned Outage) [WEBSMS] | CLUZ
12/28/2021 8:09:00 AM | LEYTE ACC-12/28/21 08:17: ORMOC SS, Tolosa-Mabuhay-San Isidro 69kV Line emergency de-energized at 0727H as per requested by Visayas O & M. Load=3.3MW. Weather: Rainy. | CVIS
12/28/2021 6:00:00 AM | VRCC-12/28/2021 05:59: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=1879MW, PK=1273MW, RR=36MW, NetOpMargin: AM=606, PM=556, EVE=361 Highest Unit O/L: PCPC @ 135 MW Derated Plant: EDC = 300 MW [WEBSMS] | CVIS
12/28/2021 1:08:00 AM | LRCC-12/28/2021 01:06: Hermosa 230kV Bus 2 restored at 0106H. (Planned Outage) [WEBSMS] | CLUZ
12/28/2021 1:07:00 AM | LRCC-12/28/2021 01:06: Hermosa 230kV Bus 2 restored at 0106H. (Planned Outage) [WEBSMS] | CLUZ
12/28/2021 12:10:00 AM | LRCC-12/28/2021 00:09: San Gabriel online at 0007H. (Unplanned Outage) [WEBSMS] | CLUZ
12/27/2021 11:02:00 PM | LRCC-12/27/2021 23:00: Sta Rita-San Lorenzo 230kV Bus A & B tie Breakers were opened at 2254H, unlooping Sta Rita CCPP and San Lorenzo CCPP. This is in preparation for the synchronization of San Gabriel CCPP. Meanwhile, paralleling of Batangas 300MVA T04 and T05 was completed at 2259H. [WEBSMS] | CLUZ
12/27/2021 6:49:00 PM | LRCC-12/27/2021 18:48: Hermosa 230kV Bus 2 de-energized at 1848H. (Planned Outage) [WEBSMS] | CLUZ
12/27/2021 6:01:00 PM | LRCC-12/27/2021 17:59: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11952MW, PK=8280MW, RR=323MW, NetOpMargin: EVE=3349 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Masinloc 3 at 140MW, Ilijan at 945MW, and Sual 2 at 590MW [WEBSMS] | CLUZ
12/27/2021 6:01:00 PM | VRCC-12/27/2021 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1632MW, PK=1203MW, RR=0MW, NetOpMargin: EVE=429 Highest Unit O/L: PEDC U3 at 150MW Derated Plant: EDC at 300MW, KSPC at 103MW, CEDC at 82MW. OUTAGE: TVI at 338MW, TPC1A at 82MW. [WEBSMS] | CVIS
12/27/2021 5:51:00 PM | LEYTE ACC-12/27/2021 17:49: ORMOC SS, Javier - San Isidro 69kV line portion re-energized at 1743H. 69kV Tunga Feeder back to its normal line configuration. Wether: Fair. | CVIS
12/27/2021 5:33:00 PM | VRCC-12/27/2021 17:31: 138 KV Colon-Cebu L1 energized at 1730H. [WEBSMS] | CVIS
12/27/2021 5:04:00 PM | LRCC-12/27/2021 17:02: Olongapo-SBMA 230kV line restored at 1659H. (Planned Outage) [WEBSMS] | CLUZ
12/27/2021 5:03:00 PM | LRCC-12/27/2021 17:02: Olongapo-SBMA 230kV line restored at 1659H. (Planned Outage) [WEBSMS] | CLUZ
12/27/2021 4:40:00 PM | LRCC-12/27/2021 16:38: Araneta(Dona Imelda) 115kV Bus 2 energized at 1636H. For 24H soaking. (Planned Outage) [WEBSMS] | CLUZ
12/27/2021 4:30:00 PM | VRCC-12/27/2021 16:29: Sibonga load end 5 MVA energized at 1424H. [WEBSMS] | CVIS
12/27/2021 4:12:00 PM | LRCC-12/27/2021 16:11: Araneta(Dona Imelda) 300MVA T03 restored at 1607H. (Planned Outage) [WEBSMS] | CLUZ
12/27/2021 4:04:00 PM | VRCC-12/27/2021 16:04: 138 KV Colon-Cebu L1 tripped at 1601H w/a load of 54MW, at Colon ss, diff trip ind. [WEBSMS] | CVIS
12/27/2021 4:01:00 PM | NEGROS ACC: 12/27/2021, 69KV Mabinay-Bayawan Sub T/L fully restored 1557H. | CVIS
12/27/2021 3:58:00 PM | NEGROS ACC: 12/27/2021, 69KV Mabinay-Bayawan Sub T/L fully restored 1557H. | CVIS
12/27/2021 3:23:00 PM | VRCC-12/27/2021 15:20: 138 KV Colon-Cebu L1 energized at 1519H. [WEBSMS] | CVIS
12/27/2021 3:21:00 PM | NEGROS ACC: 12/27/2021, 69KV Mabinay-Bayawan Sub T/L(0.38MW) de-energized at 1515H to facilitate closing of loop to energize Bayawan S/S. | CVIS
12/27/2021 3:03:00 PM | VRCC-12/27/2021 15:02: 138 KV Colon-Cebu L1 tripped at 1456H w/a load of 56MW, at Colon ss, diff trip ind. [WEBSMS] | CVIS
12/27/2021 2:10:00 PM | VRCC-12/27/2021 14:08: 138 KV Mandaue-Lapulapu Line 1 energized at 1407H, double circuit. [WEBSMS] | CVIS
12/27/2021 1:21:00 PM | LRCC-12/27/2021 13:20: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12158MW, PK=8412MW, RR=348MW, NetOpMargin: PM=3398, EVE=2402 Highest Unit O/L: Sual at 647MW Derated Plant: Masinloc 3 at 140MW, Ilijan at 945MW and Sual 2 at 590MW [WEBSMS] | CLUZ
12/27/2021 1:00:00 PM | VRCC-12/27/2021 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=1632MW, PK=1117MW, RR=0MW, NetOpMargin: PM=515, EVE=429 Highest Unit O/L: PEDC U3 at 150MW Derated Plant: EDC at 300MW, KSPC at 103MW, CEDC at 82MW. OUTAGE:TVI 1&2 at 338MW, TPC1A at 82MW. [WEBSMS] | CVIS
12/27/2021 11:07:00 AM | VRCC-12/27/2021 11:02: 138 KV Cebu-Mandaue L1 energized at 1100H, double circuit. [WEBSMS] | CVIS
12/27/2021 10:39:00 AM | LRCC-12/27/2021 10:37: For info: Batangas 300MVA T04 and T05 un-paralleled at 1026H. San Lorenzo-Sta Rita 230kV Bus A and Bus B tie breakers were closed at 1028H and 1029H respectively. Purpose: Enhanced reliability for Batangas 230kV corridor while San Gabriel is on shutdown. [WEBSMS] | CLUZ
12/27/2021 9:52:00 AM | LRCC-12/27/2021 09:51: Tayabas-Mauban 230kV line 2 de-energized at 0950H. (Planned Outage) [WEBSMS] | CLUZ
12/27/2021 9:28:00 AM | LRCC-12/27/2021 09:26: Tayabas-Mauban 230kV line 1 restored at 0924H. (Planned Outage) [WEBSMS] | CLUZ
12/27/2021 8:02:00 AM | NEGROS ACC: 12/27/2021: 69kV Mabinay-Kabankalan Sub T/L energized at 0758H. | CVIS
12/27/2021 8:00:00 AM | LEYTE ACC-12/27/21 08:08: STA. RITA SS, Sta. Rita-Quinapondan 69kV Line up to ABS Cabong tripped/restored at 0745H/0749H, ind.: Phase-A/N & F.D.=95.77kms. Load=3.6MW. Weather: Fair. | CVIS
12/27/2021 6:26:00 AM | LEYTE ACC-12/27/21 06:33: ORMOC SS, Tolosa-Mabuhay-San Isidro 69kV Line tripped/restored at 2330H/0613H, ind.: Z1, AB & 11.3kms. Note: Delayed restoration due to NO Operator on duty at PCB Station. Weather: Fair. | CVIS
12/27/2021 4:22:00 AM | LRCC-12/27/2021 04:21: Bacman Unit 1 (50MW) tripped at 0401H, lowest frequency at 59.78Hz [WEBSMS] | CLUZ
12/27/2021 4:02:00 AM | LRCC-12/27/2021 04:01: Sta. Rita Module 10 online at 0358H (Unplanned Outage) [WEBSMS] | CLUZ
12/27/2021 2:33:00 AM | LRCC-12/27/2021 02:32: Limay - BCCPP 230kV line 2 looped at Limay side at 0231H (Unplanned Outage) [WEBSMS] | CLUZ
12/26/2021 9:18:00 PM | VRCC-12/26/2021 21:18: KSPC Unit # 1 cut in at 2113H [WEBSMS] | CVIS
12/26/2021 7:39:00 PM | NEGROS ACC: 12/26/2021, 69KV Mabinay-Kabankalan Sub T/L(0.0MW) auto tripped at 1931H with ind.; Z1 AN 16.88KM. Test energized but failed. | CVIS
12/26/2021 5:50:00 PM | LRCC-12/26/2021 17:49: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11571MW, PK=7869MW, RR=308MW, NetOpMargin: EVE=3394 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Masinloc 1 at 250MW, Masinloc 3 at 140MW, Ilijan at 945MW and Sual 2 at 590MW [WEBSMS] | CLUZ
12/26/2021 5:46:00 PM | VRCC-12/26/2021 17:44: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1551MW, PK=1117MW, RR=36MW, NetOpMargin: EVE=434 Highest Unit O/L: TVI U1 @ 166 MW Derated Plant: EDC = 321 MW [WEBSMS] | CVIS
12/26/2021 3:05:00 PM | LRCC-12/26/2021 15:04: Sta Rita Module 10 offline at 1503H. (Unplanned Outage) [WEBSMS] | CLUZ
12/26/2021 2:51:00 PM | VRCC-12/26/2021 14:50: 138KV Colon-Naga line @1449H. [WEBSMS] | CVIS
12/26/2021 2:19:00 PM | VRCC-12/26/2021 14:17: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=1743MW, PK=941MW, RR=36MW, NetOpMargin: PM=802, EVE=434 Highest Unit O/L: TVI U1 @ 166 MW Derated Plant: EDC = 321 MW [WEBSMS] | CVIS
12/26/2021 1:24:00 PM | LEYTE ACC-12/26/21: ORMOC SS, 69kV PCB Tolosa tripped/restored at 1310H/1317H, z2, phase AN, 59.12kms. Line testing along Javier-San Isidro ongoing, WEATHER: RAINY | CVIS
12/26/2021 1:06:00 PM | LRCC-12/26/2021 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12168MW, PK=7516MW, RR=287MW, NetOpMargin: PM=4365, EVE=3332 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Masinloc 1 at 250MW, Masinloc 3 at 140MW, Ilijan at 945MW and Sual 2 at 590MW [WEBSMS] | CLUZ
12/26/2021 11:27:00 AM | VRCC-12/26/2021 11:27: 230KV Magdugo-TVI line 2 energized @1124H. [WEBSMS] | CVIS
12/26/2021 11:08:00 AM | LEYTE ACC-12/26/21: ORMOC SS, 69kV PCB Tolosa tripped/restored at 1058H/1104H, RELAY: z1, phase AB, 8.2kms, WEATHER: RAINY | CVIS
12/26/2021 9:39:00 AM | VRCC-12/26/2021 09:38: 138KV Colon-KSPC line 1 energized @0933H. [WEBSMS] | CVIS
12/26/2021 8:28:00 AM | LRCC-12/26/2021 08:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12190MW, PK=6879MW, RR=294MW, NetOpMargin: AM=5017, PM=4659, EVE=3784 Highest Unit O/L: SUAL 1 @647MW Derated Plant: MASINLOC 1 @250MW, MASINLOC 3 @120MW, SUAL 2 @590MW, ILJJAN A / B @945MW [WEBSMS] | CLUZ
12/26/2021 8:24:00 AM | LRCC-12/26/2021 08:23: Limay-BCCPP 230kV Line 2 de-energized at 0809H (Planned Outage). [WEBSMS] | CLUZ
12/26/2021 6:01:00 AM | VRCC-12/26/2021 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=1776MW, PK=939MW, RR=0MW, NetOpMargin: AM=837, PM=802, EVE=434 Highest Unit O/L: PEDC U # 3 at 150 MW Derated Plant: EDC at 321 MW [WEBSMS] | CVIS
12/25/2021 5:57:00 PM | VRCC-12/25/2021 17:56: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1540MW, PK=1063MW, RR=36MW, NetOpMargin: EVE=477 Highest Unit O/L: TVI U1 @ 166 MW Derated Plant: EDC = 321 MW [WEBSMS] | CVIS
12/25/2021 5:53:00 PM | LRCC-12/25/2021 17:51: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11864MW, PK=7014MW, RR=267MW, NetOpMargin: EVE=4583 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Masinloc 1 at 250MW, Masinloc 3 at 140MW, Ilijan at 945MW and Sual 2 at 590MW [WEBSMS] | CLUZ
12/25/2021 5:19:00 PM | LEYTE ACC-12/25/21 17:00: ORMOC SS, 69kV Ormoc-Simangan-Baybay feeder extended up to Hilongos ABS 2, energized Leyeco IV (Hilongos) at 1630H. WEATHER: FAIR | CVIS
12/25/2021 4:55:00 PM | LRCC-12/25/2021 16:54: Dona Imelda-Kamuning 115kV line restored at 1651H. (Planned Outage) [WEBSMS] | CLUZ
12/25/2021 4:31:00 PM | LEYTE ACC-12/25/21 16:15: PARANAS SS, 69kV Paranas-Catbalogan line tripped at 1609H, phase CN, 60.47kms., Z1, load=8.4MW. Restored at 1610H. WEATHER: FAIR | CVIS
12/25/2021 8:37:00 AM | LRCC-12/25/2021 08:36: Araneta(Dona Imelda) 115kV Bus 1 de-energized at 0835H. (Planned Outage) [WEBSMS] | CLUZ
12/25/2021 6:31:00 AM | NEGROS ACC: 12/25/2021, 69kV Naga-Overflow Line section (1.28MW) de-energized at 0626H to facilitate shifting back to 69kV Kabankalan-Sipalay Sub TL. | CVIS
12/25/2021 6:31:00 AM | NEGROS ACC: 12/25/2021, 69kV Naga-Overflow Line section energized at 0628H, line section shifted back to 69kV Kabankalan-Sipalay Sub TL. | CVIS
12/25/2021 6:18:00 AM | LRCC-12/25/2021 05:56: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12415MW, PK=7514MW, RR=237MW, NetOpMargin: AM=4663, PM=4375, EVE=3957 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Sual 2 at 590MW, Ilijan A/B at 945MW, Masinloc 1 at 250MW [WEBSMS] | CLUZ
12/25/2021 6:18:00 AM | VRCC-12/25/2021 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=1777MW, PK=899MW, RR=0MW, NetOpMargin: AM=878, PM=826, EVE=477 Highest Unit O/L: PEDC U # 3 at 150 MW Derated Plant: EDC at 321 MW [WEBSMS] | CVIS
12/25/2021 12:34:00 AM | VRCC-12/25/2021 00:33: CEDC U # 2 cut in to the system at 0026H [WEBSMS] | CVIS
12/24/2021 11:28:00 PM | VRCC-12/24/2021 23:05: 138 KV Colon - Cebu Line 1 tripped at 2259 H. [WEBSMS] | CVIS
12/24/2021 11:28:00 PM | VRCC-12/24/2021 23:17: 138 KV Colon - Cebu energized at 2313H. [WEBSMS] | CVIS
12/24/2021 10:59:00 PM | LRCC-12/24/2021 22:58: Bolo - Sual 230kV Line 2 restored at 2257H. (Unplanned Outage) [WEBSMS] | CLUZ
12/24/2021 7:47:00 PM | VRCC-12/24/2021 19:47: 138 KV Cebu - Colon L1 energized at 1943H [WEBSMS] | CVIS
12/24/2021 7:22:00 PM | VRCC-12/24/2021 19:22: 138 KV Cebu - Colon L1 tripped at 1913H [WEBSMS] | CVIS
12/24/2021 7:14:00 PM | VRCC-12/24/2021 19:12: 138 KV Naga - TPVI L1 energized at 1909 H [WEBSMS] | CVIS
12/24/2021 6:30:00 PM | LEYTE ACC-12/24/21 18:25: ORMOC SS, 69kV Tolosa-San Isidro line tripped at 1808H, phase ABC, 6.3kms., load=5.8MW. Restored per clearance from Line Engineer at 1819H. WEATHER: FAIR | CVIS
12/24/2021 5:54:00 PM | LRCC-12/24/2021 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=12004MW, PK=8245MW, RR=330MW, NetOpMargin: EVE=3429 Highest Unit O/L: SUAL 1 @647MW Derated Plant: MASINLOC 1 @250MW; SUAL 2 @590MW; ILJJAN A / B @945MW [WEBSMS] | CLUZ
12/24/2021 5:41:00 PM | VRCC-12/24/2021 17:35: 69KV Mandaue-GIS F1 & F4 energized @1731H & 1732H respectively. [WEBSMS] | CVIS
12/24/2021 5:14:00 PM | LRCC-12/24/2021 17:14: Bolo - Sual 230kV Line 2 tripped at 1709H (Unplanned Outage). [WEBSMS] | CLUZ
12/24/2021 2:03:00 PM | LEYTE ACC-12/25/21: SOLEQ and SEPALCO per advise from RCC, to start generating with their PPC enabled at 5MW limit starting 1300H. SOLEQ first inverter cut-in at 1248H. ABS 3 Victoria closed at 1307H and SEPALCO 51CB4 closed at 1314H | CVIS
12/24/2021 1:43:00 PM | VRCC-12/24/2021 13:40: 230KV Magdugo -TVI line 1 energized @1337H. [WEBSMS] | CVIS
12/24/2021 1:01:00 PM | LRCC-12/24/2021 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12346MW, PK=8033MW, RR=357MW, NetOpMargin: PM=3956, EVE=2639 Highest Unit O/L: SUAL 1 @647MW Derated Plant: MASINLOC 1 @250MW; SUAL 2 @590MW; ILJJAN A / B @945MW [WEBSMS] | CLUZ
12/24/2021 12:56:00 PM | VRCC-12/24/2021 12:55: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=1611MW, PK=1043MW, RR=36MW, NetOpMargin: PM=568, EVE=271 Highest Unit O/L: TVI U1 @ 166 MW Derated Plant: EDC = 321 MW [WEBSMS] | CVIS
12/24/2021 11:38:00 AM | VRCC-12/24/2021 11:38: 34.5KV Sangi-Carcon line 2 energized @1115H. [WEBSMS] | CVIS
12/24/2021 11:28:00 AM | VRCC-12/24/2021 11:27: 138KV Samboan-Colon line 2 energized @1116H, One grid Cebu-Negros synchronized @ Colon SS 1118H. [WEBSMS] | CVIS
12/24/2021 10:02:00 AM | VRCC-12/24/2021 10:00: 138KV Daanlungsod-Magdugo line energized @0953H and Magdugo 300MVA TR#2 energized @0955H. [WEBSMS] | CVIS
12/24/2021 9:38:00 AM | VRCC-12/24/2021 09:37: 138KV Cebu-Colon line 1 energized @0932H. [WEBSMS] | CVIS
12/24/2021 8:53:00 AM | VRCC-12/24/2021 08:52: 138KV Colon-KSPC line 2 energized @0848H to provide feedback power to the plant. [WEBSMS] | CVIS
12/24/2021 8:38:00 AM | NEGROS ACC: 12/24/2021, 69kV Kabankalan-Sipalay Sub T/L restored at 0834H. | CVIS
12/24/2021 7:04:00 AM | NEGROS ACC: 12/24/2021, 69kV Naga-Overflow Line section temporarily energized through to 69kV Mabinay-Kabankalan Sub TL at 0659H. | CVIS
12/24/2021 6:56:00 AM | EGROS ACC: 12/24/2021, 69kV Kabankalan-Overflow Line section (1.69MW) de-energizec at 0649H to conduct closing of loop at Tower No. 4 of 69kV Kabankalan-Sipalay Sub TL. | CVIS
12/24/2021 6:06:00 AM | VRCC-12/24/2021 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=1662MW, PK=1033MW, RR=0MW, NetOpMargin: AM=629, PM=568, EVE=271 Highest Unit O/L: PEDC U3 at 150 MW, Derated Plant: EDC at 321 MW [WEBSMS] | CVIS
12/24/2021 5:55:00 AM | LRCC-12/24/2021 05:54: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12259MW, PK=9000MW, RR=360MW, NetOpMargin: AM=2899, PM=2893, EVE=2502 Highest Unit O/L: Sual 1 at 647MW Derated Plant: Masinloc 1 at 250MW, Masinloc 3 at 170MW, Ilijan A/B at 360MW/585MW and Sual 2 at 590MW [WEBSMS] | CLUZ
12/24/2021 4:44:00 AM | LRCC-12/24/2021 04:43: Dona Imelda (Araneta) 300MVA T03 de-energized at 0436H (Planned Outage). [WEBSMS] | CLUZ
12/24/2021 4:42:00 AM | LRCC-12/24/2021 04:36: Dona Imelda-Kamuning 115kV Line de-energized at 0428H (Planned Outage). [WEBSMS] | CLUZ
12/24/2021 4:34:00 AM | LRCC-12/24/2021 04:33: Dona Imelda 115kV Bus 2 de-energized at 0423H (Planned Outage). [WEBSMS] | CLUZ
12/24/2021 4:00:00 AM | LRCC-12/24/2021 03:47: San Gabriel offline at 0345H. (Unplanned Outage) [WEBSMS] | CLUZ
12/24/2021 3:40:00 AM | LRCC-12/24/2021 03:39: San Lorenzo Module 60 online at 0336H. Planned Outage [WEBSMS] | CLUZ
12/23/2021 11:05:00 PM | VRCC-12/23/2021 23:03: Provided feedback power to CEDC at 2300H [WEBSMS] | CVIS
12/23/2021 10:28:00 PM | NEGROS ACC: 12/23/2021, 69kV Mabinay-Tadlong Line section restored at 2221H, loop at str.29 opened isolating 69KV Tadlong-Bayawan Line section. | CVIS
12/23/2021 10:26:00 PM | VRCC-12/23/2021 22:24: 138 KV Calongcalong - Daanlungsod energized at 2222H [WEBSMS] | CVIS
12/23/2021 9:56:00 PM | VRCC-12/23/2021 21:55: 138 KV Colon - AYA (VECO) Line 1 energized at 2150H [WEBSMS] | CVIS
12/23/2021 9:13:00 PM | VRCC-12/23/2021 21:12: 138 KV Toledo - Calongcalong Line energized at 2110H [WEBSMS] | CVIS
12/23/2021 8:13:00 PM | VRCC-12/23/2021 20:13: 138 KV Quiot - Colon Line energized at 2007H [WEBSMS] | CVIS
12/23/2021 6:32:00 PM | LRCC-12/23/2021 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11905MW, PK=9021MW, RR=368MW, NetOpMargin: EVE=2516 Highest Unit O/L: Sual 1 @647MW Derated Plant: Sual 2 @590MW, GN Power 1/2 @165MW/290MW, Masinloc 1 @150MW & Iljan A/B @360MW/585MW [WEBSMS] | CLUZ
12/23/2021 6:32:00 PM | VRCC-12/23/2021 18:08: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=1366MW, PK=1000MW, RR=0MW, NetOpMargin: EVE=366 Highest Unit O/L: PEDC U # 3 at 150 MW Derated Plant: EDC at 300 MW [WEBSMS] | CVIS
12/23/2021 6:31:00 PM | LRCC-12/23/2021 17:52: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11905MW, PK=9021MW, RR=368MW, NetOpMargin: EVE=2516 Highest Unit O/L: Sual 1 @647MW Derated Plant: Sual 2 @590MW, GN Power 1/2 @165MW/290MW, Masinloc 1 @150MW & Iljan A/B @360MW/585MW [WEBSMS] | CLUZ
12/23/2021 5:19:00 PM | NEGROS ACC: 12/23/2021, 69kV Kabankalan-La Castellana Sub T/L energized at 1709H. Customer-owned and maintained line. | CVIS
12/23/2021 4:36:00 PM | NEGROS ACC: 12/23/2021, 69kV Kabankalan-La Castellana Sub T/L de-energized at 1619H as per customer request. Customer-owned and maintained line. | CVIS
12/23/2021 4:17:00 PM | NEGROS ACC: 12/23/2021, 69kV Kabankalan-La Castellana Sub T/L energized at 1608H. Customer-owned and maintained line. | CVIS
12/23/2021 4:05:00 PM | LEYTE ACC-12/23/21 16:00: MARSHALLING SS, EDC-UMPP unit no. 2 cut-in to the system at 1545H. WEATHER: FAIR | CVIS
12/23/2021 3:53:00 PM | VRCC-12/23/2021 15:52: 138 KV Colon - Cebu Line 1 tripped at 1541H, Colon side :Differential trip, voltage protection trip L1 L2 EOC: Cebu side differential trip L1 L2 FD= 23.4 KM Load = 12.3 MW [WEBSMS] | CVIS
12/23/2021 2:42:00 PM | VRCC-12/23/2021 14:41: 69 KV Lapulapu GIS feeder 4 energized at 1439 H [WEBSMS] | CVIS
12/23/2021 2:35:00 PM | VRCC-12/23/2021 14:33: 138 KV Colon - Aya Line 1 energized at 1431H [WEBSMS] | CVIS
12/23/2021 1:06:00 PM | LRCC-12/23/2021 13:04: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=12253MW, PK=9260MW, RR=381MW, NetOpMargin: PM=2612, EVE=2406 Highest Unit O/L: Sual 1 @647MW Derated Plant: Sual 2 @590MW, SCPC 1 @130MW, GN Power 1/2 @165MW/290MW & Iljan A/B @360MW/585MW [WEBSMS] | CLUZ
12/23/2021 1:06:00 PM | VRCC-12/23/2021 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=1532MW, PK=915MW, RR=0MW, NetOpMargin: PM=617, EVE=365 Highest Unit O/L: PEDC U # 3 at 150 MW Derated Plant: EDC at 300 MW [WEBSMS] | CVIS
12/23/2021 12:01:00 PM | LEYTE ACC-12/23/21 11:50: TABANGO SS, Tabango-Daan Bantayan 230kV SC L2 energized at 1142H. WEATHER: FAIR | CVIS
12/23/2021 12:01:00 PM | VRCC-12/23/2021 11:45: 230 KV Leyte - Cebu Sub Cable 2 energized at 1142H , Double circuit [WEBSMS] | CVIS
12/23/2021 11:25:00 AM | LRCC-12/23/2021 11:25: Bantay 115kV Bus 1 restored at 1124H (Planned Outage) [WEBSMS] | CLUZ
12/23/2021 11:17:00 AM | NEGROS ACC: 12/23/2021, PGPP1 U1 re-online at 1105H. | CVIS
12/23/2021 9:46:00 AM | VRCC-12/23/2021 09:45: 69 KV Calong calong - Toledo BESS energized 0939H [WEBSMS] | CVIS
12/23/2021 9:38:00 AM | VRCC-12/23/2021 09:36: 69 KV Calongcalong - Toledo Solar energized at 0930 H [WEBSMS] | CVIS
12/23/2021 9:00:00 AM | VRCC-12/23/2021 08:42: 230 KV Compostela - Daan Bantayan energized at 0837 H , double circuit. [WEBSMS] | CVIS
12/23/2021 9:00:00 AM | VRCC-12/23/2021 08:57: 138 KV Compostela - Cebu Line 2 energized at 0849H, double circuit. [WEBSMS] | CVIS
12/23/2021 8:39:00 AM | LRCC-12/23/2021 08:35: Bantay 115kV Bus 1 de-energized at 0829H (Planned Outage) [WEBSMS] | CLUZ
12/23/2021 8:26:00 AM | LEYTE ACC-12/23/21 08:00: PARANAS SS, 69kV Paranas-Bliss line tripped at 0741H, phase CN, 51.52kms., Z3, load=6.3MW. Restored at 0743H. WEATHER: FAIR | CVIS
12/23/2021 6:40:00 AM | LRCC-12/23/2021 05:58: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=12584MW, PK=9465MW, RR=379MW, NetOpMargin: AM=2740, PM=2670, EVE=2653 Highest Unit O/L: SUAL 1 @647MW Derated Plant: SUAL 2 @590MW; SCPC 1 @115MW; ILJJAN A / B @945MW [WEBSMS] | CLUZ
12/23/2021 6:40:00 AM | VRCC-12/23/2021 06:00: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=1560MW, PK=1122MW, RR=0MW, NetOpMargin: AM=438, PM=404, EVE=205 Highest Unit O/L: PEDC U3 at 150 MW, Derated Plant: EDC at 301 MW [WEBSMS] | CVIS
12/23/2021 5:55:00 AM | LRCC-12/23/2021 05:33: Hermosa - Balsik 230kV Line energized (looped) @ 0529H (Ongoing Commissioning Test). [WEBSMS] | CLUZ
12/23/2021 4:09:00 AM | LRCC-12/23/2021 04:08: Olongapo-Balsik 230kV Line looped at 0404H on-going commissioning test 0404H (Planned outage). [WEBSMS] | CLUZ
12/21/2021 3:51:00 PM | VRCC-12/21/2021 15:49: 230 KV Leyte - Cebu Sub Cable energized at 1525H, Double circuit. [WEBSMS] | CVIS
12/21/2021 5:17:00 AM | LRCC-12/21/2021 05:16: Weather Update: Shear Line affecting eastern section of Northern and Central Luzon. Northeast Monsoon affecting the rest of Northern Luzon. Intertropical Convergence Zone (ITCZ) affecting Southern Mindanao. [WEBSMS] | CLUZ
12/20/2021 7:57:00 PM | NEGROS ACC: 12/20/2021, 69kV Amlan-Pulantubig Line section (15.31MW) auto-tripped at 1929H with indication Z3 CA, START, 35.51km. Line auto-tripped during closing of ABS Pulangtubig to energize 69kV Pulangtubig-Siaton Line section. | CVIS
12/20/2021 7:57:00 PM | NEGROS ACC: 12/20/2021, 69kV Bacolod-Silay Sub T/L restored at 1935H. Customer owned and maintained line. | CVIS
12/20/2021 4:08:00 PM | NEGROS ACC: 12/20/2021, 69kV Cadiz-Manapla Line section(1.93MW) de-energized at 1602H as per customers request to facilitate normalization 69kV Cadiz-VMC Sub T/L. NNBP isolated, customer-owned and maintained line. | CVIS
12/20/2021 4:06:00 PM | NEGROS ACC: 12/20/2021, 69kV Cadiz-Manapla Line section de-energized at 1602H as per customers request to facilitate normalization 69kV Cadiz-VMC Sub T/L. NNBP isolated, customer-owned and maintained line. | CVIS
12/20/2021 3:31:00 PM | NEGROS ACC: 12/20/2021, 69kV Kabankalan-Naga line section restored at 1524H. 69kV Naga-Sipalay Line section and 69kV Naga-Overflow Line section still isolated. | CVIS
12/20/2021 3:27:00 PM | NEGROS ACC: 12/20/2021, PGPP2 SOG1 re-online at 1519H. | CVIS
12/20/2021 3:26:00 PM | NEGROS ACC: 12/20/2021, PGPP2 SOG1 re-online at 1519H. | CVIS
12/20/2021 2:59:00 PM | NEGROS ACC: 12/20/2021, Amlan 50 MVA TR No. 3 energized and parallel operation with 50MVA TR 1 & 2 at 1445H & 1455H respectively. | CVIS
12/20/2021 2:51:00 PM | NEGROS ACC: 12/20/2021, 138kV Amlan-PGPP1 L2 restored at 1436H. | CVIS
12/20/2021 2:33:00 PM | NEGROS ACC: 12/20/2021, 138kV Mabinay-Kabankalan Line 2 restored at 1415H. | CVIS
12/20/2021 1:54:00 PM | VRCC-12/20/2021 13:54: Compostela SS 69 KV Consolacion feeder energized at 1345H [WEBSMS] | CVIS
12/20/2021 1:07:00 PM | LRCC-12/20/2021 13:05: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10920MW, PK=9469MW, RR=357MW, NetOpMargin: PM=1094, EVE=1266 Highest Unit O/L: SUAL 2 @590MW Derated Plant: SUAL 2 @590MW; ILJJAN A / B @946MW [WEBSMS] | CLUZ
12/20/2021 1:05:00 PM | VRCC-12/20/2021 13:03: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=1685MW, PK=835MW, RR=0MW, NetOpMargin: PM=850, EVE=733 Highest Unit O/L: PEDC U3 at 150 MW, Derated Plant: EDC at 355 MW [WEBSMS] | CVIS
12/20/2021 10:59:00 AM | VRCC-12/20/2021 10:58: Daan Bantayan SS 69 KV Lanao feeder re-energized at 1040H [WEBSMS] | CVIS
12/20/2021 10:45:00 AM | LEYTE ACC-12/20/21: EDC-Leyte A, Malitbog Unit #2 cut-in at 1021H | CVIS
12/20/2021 10:02:00 AM | LRCC-12/20/2021 10:00: Salong 230kV Bus 2 restored at 0941H (Planned Outage) [WEBSMS] | CLUZ
12/20/2021 9:34:00 AM | LRCC-12/20/2021 09:32: Salong - SLTEC 230kV Line 2 restored at 0930H (Planned Outage). [WEBSMS] | CLUZ
12/20/2021 9:21:00 AM | LRCC-12/20/2021 09:20: Calaca - Salong 230kV Line restored at 0915H (Planned Outage). [WEBSMS] | CLUZ
12/20/2021 8:58:00 AM | VRCC-12/20/2021 08:57: Daan Bantayan SS 69 KV Lanao Feeder tripped at 0851H with 13.4 MW load [WEBSMS] | CVIS
12/20/2021 6:14:00 AM | VRCC-12/20/2021 06:11: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=1745MW, PK=540MW, RR=36MW, NetOpMargin: AM=1205, PM=1060, EVE=938 Highest Unit O/L: TVI U1 @ 166 MW Derated Plant: EDC = 355 MW, TPC = 82 MW [WEBSMS] | CVIS
12/20/2021 5:43:00 AM | LRCC-12/20/2021 05:42: Weather Update: Shear Line affecting eastern section of Northern and Central Luzon. Northeast Monsoon affecting the rest of Northern Luzon. [WEBSMS] | CLUZ
12/20/2021 3:46:00 AM | LRCC-12/20/2021 03:46: Dasmarinas 115kV Bus 1 restored at 0345H (Planned Outage) [WEBSMS] | CLUZ
12/20/2021 1:38:00 AM | VRCC-12/20/2021 01:37: 138KV Mandaue-Lapu-Lapu energized at 0131H. [WEBSMS] | CVIS
12/20/2021 1:28:00 AM | LRCC-12/20/2021 01:25: Dasmarinas 115kV Bus 1 de-energized at 0123H (Planned Outage) [WEBSMS] | CLUZ
12/20/2021 1:27:00 AM | LRCC-12/20/2021 01:25: Dasmarinas 115kV Bus 1 de-energized at 0123H (Planned Outage) [WEBSMS] | CLUZ
12/20/2021 1:20:00 AM | VRCC-12/20/2021 01:18: 138KV Cebu-Mandaue energized @0113H. [WEBSMS] | CVIS
12/20/2021 12:57:00 AM | VRCC-12/20/2021 00:57: 138KV Compostela-Cebu energized at 0020H. [WEBSMS] | CVIS
12/19/2021 11:24:00 PM | VRCC-12/19/2021 23:23: 230KV Tabango -Daanbantayan sub-cable energized @2048H and 230KV Daan-bantayan-Compostela line energized @2240H. [WEBSMS] | CVIS
12/19/2021 7:43:00 PM | LEYTE ACC-12/19/21: EDC-Leyte A, Malitbog Unit #1 synchronized to grid at 1916H | CVIS
12/19/2021 7:41:00 PM | LEYTE ACC-12/19/21: EDC-Leyte A, Malitbog Unit #1 synchronized to grid at 1916H | CVIS
12/19/2021 7:05:00 PM | LRCC-12/19/2021 19:04: Calaca 230kV Bus 1 restored at 1902H (Planned Outage) [WEBSMS] | CLUZ
12/19/2021 6:33:00 PM | LRCC-12/19/2021 18:33: Quezon (Balintawak) - Mexico 230kV Line restored at 1831H (Planned Outage) [WEBSMS] | CLUZ
12/19/2021 6:14:00 PM | PANAY ACC 12/19/2021, 18:08: PEDC U1 synchronized at 06:06:00, Initial load: 8.1mw | CVIS
12/19/2021 5:50:00 PM | LRCC-12/19/2021 17:50: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10618MW, PK=7973MW, RR=316MW, NetOpMargin: EVE=2329 Highest Unit O/L: SUAL 2 @590MW Derated Plant: SUAL 2 @590MW; ILJJAN A / B @946MW [WEBSMS] | CLUZ
12/19/2021 5:21:00 PM | LRCC-12/19/2021 17:19: Dona Imelda 115kV Bus 1 restored at 1719H (Planned Outage) [WEBSMS] | CLUZ
12/19/2021 3:05:00 PM | NEGROS ACC: 12/19/2021, 138kV Kabankalan-Bacolod Line 2 restored at 1455H. | CVIS
12/19/2021 2:41:00 PM | LRCC-12/19/2021 14:41: Nagsaag 500kV Bus 2 restored at 1440H (Planned Outage) [WEBSMS] | CLUZ
12/19/2021 2:39:00 PM | NEGROS ACC: 12/19/2021, 69kV Cadiz-Manapla Line section restored at 1435H. Customer-owned and maintained line. | CVIS
12/19/2021 2:27:00 PM | NEGROS ACC: 12/19/2021, PGPP2 SOG2 re-online at 1407H. | CVIS
12/19/2021 1:02:00 PM | VRCC-12/19/2021 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2013MW, PK=528MW, RR=0MW, NetOpMargin: PM=1485, EVE=1246 Highest Unit O/L: PEDC U3 at 150 MW, Derated Plant: EDC at 355 MW [WEBSMS] | CVIS
12/19/2021 12:55:00 PM | LRCC-12/19/2021 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10860MW, PK=7486MW, RR=293MW, NetOpMargin: PM=3081, EVE=2117 Highest Unit O/L: SUAL 2 @590MW Derated Plant: SUAL 2 @590MW; ILJJAN A / B @946MW [WEBSMS] | CLUZ
12/19/2021 9:19:00 AM | LRCC-12/19/2021 08:37: Calaca 230kV Bus 1 de-energized at 0836H (Planned Outage) [WEBSMS] | CLUZ
12/19/2021 9:19:00 AM | LRCC-12/19/2021 08:59: Sta. Rita Module 10 online at 0855H (Unplanned outage). [WEBSMS] | CLUZ
12/19/2021 9:19:00 AM | LRCC-12/19/2021 09:11: Calaca - Salong 230kV Line de-energized at 0817H (Planned Outage) [WEBSMS] | CLUZ
12/19/2021 8:30:00 AM | LRCC-12/19/2021 07:55: Salong - SLTEC 230kV Lines 1 & 2 de-energized at 0752H & 0755H, respectively (Planned Outage) [WEBSMS] | CLUZ
12/19/2021 8:30:00 AM | LRCC-12/19/2021 07:57: Salong 230kV Bus 2 de-energized at 0753H (Planned Outage) [WEBSMS] | CLUZ
12/19/2021 8:30:00 AM | LRCC-12/19/2021 08:28: Salong 230kV Bus 1 de-energized at 0815H (Planned Outage) [WEBSMS] | CLUZ
12/19/2021 7:31:00 AM | LRCC-12/19/2021 06:19: Dasmarinas 300MVA T01 (T04 old no.) restored at 0619H (Planned Outage) [WEBSMS] | CLUZ
12/19/2021 7:31:00 AM | LRCC-12/19/2021 06:43: Nagsaag 500kV Bus 2 de-energized at 0642H (Planned Outage) [WEBSMS] | CLUZ
12/19/2021 7:31:00 AM | LRCC-12/19/2021 07:20: Sta. Rita Module 10 offline at 0718H (Unplanned outage). [WEBSMS] | CLUZ
12/19/2021 6:15:00 AM | LRCC-12/19/2021 06:12: Quezon (Balintawak) - Mexico 230kV Line de-energized at 0611H (Planned Outage) [WEBSMS] | CLUZ
12/19/2021 6:01:00 AM | LRCC-12/19/2021 05:34: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=10807MW, PK=7805MW, RR=300MW, NetOpMargin: AM=2702, PM=2825, EVE=2055 Highest Unit O/L: Sual 2 @590MW Derated Plant: Sual 2 @590MW, & Iljan A/B @473MW each block [WEBSMS] | CLUZ
12/19/2021 6:01:00 AM | LRCC-12/19/2021 05:39: Sta. Rita Module 10 synchronized at 0536H (Planned outage). [WEBSMS] | CLUZ
12/19/2021 5:04:00 AM | LRCC-12/19/2021 05:02: Weather Update: At 3:00 AM today, the center of the eye of Typhoon {RAI} (formerly Typhoon ``ODETTE``) was located based on all available data at 295 km Northwest of Pag-asa Island, Kalayaan, Palawan (12.7?N,112.0?E) (OUTSIDE PAR) with maximum sustained winds of 195 km/h near the center and gustiness of up to 240 km/h. It is moving West Northwestward at 25 km/h., the Shear line affecting the eastern section of Luzon. Northeast monsoon affecting the rest of Northern and Central Luzon. [WEBSMS] | CLUZ
12/19/2021 4:30:00 AM | LRCC-12/19/2021 04:29: Bay 230kV Bus 2 restored at 0426H (Planned Outage) [WEBSMS] | CLUZ
12/19/2021 3:39:00 AM | LRCC-12/19/2021 03:38: San Gabriel shutdown at 0335H (Planned Outage). [WEBSMS] | CLUZ
12/19/2021 2:02:00 AM | LRCC-12/19/2021 02:02: Sta. Rita-San Lorenzo Tie Bus 1 and 2 looped at 0159H. [WEBSMS] | CLUZ
12/19/2021 2:00:00 AM | LRCC-12/19/2021 01:58: Batangas transformers unparalleled at 0155H. [WEBSMS] | CLUZ
12/19/2021 12:07:00 AM | LRCC-12/19/2021 00:05: Kalayaan 4 as pump (-160MW) tripped at 0000H . Highest Frequency is 60.473Hz (Unplanned Outage) [WEBSMS] | CLUZ
12/18/2021 11:26:00 PM | LRCC-12/18/2021 23:24: Hermosa-Calaguiman 69kV Line restored at 2324H (Planned Outage). [WEBSMS] | CLUZ
12/18/2021 10:45:00 PM | LRCC-12/18/2021 22:44: Dasmarinas 300MVA T01 (T04 old no.) de-energized at 2244H (Planned Outage). [WEBSMS] | CLUZ
12/18/2021 7:37:00 PM | LRCC-12/18/2021 19:36: San Jose 750MVA TO3 restored at 1934H (Planned Outage) [WEBSMS] | CLUZ
12/18/2021 6:41:00 PM | LRCC-12/18/2021 18:40: Hermosa-Calaguiman 69kV Line de-energized at 1823H (Planned Outage). [WEBSMS] | CLUZ
12/18/2021 6:03:00 PM | LRCC-12/18/2021 18:02: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10522MW, PK=8986MW, RR=345MW, NetOpMargin: EVE=1191 Highest Unit O/L: Sual 2 @590MW Derated Plant: Sual 2 @590MW, San Gabriel @250MW & Iljan A/B @473MW each block [WEBSMS] | CLUZ
12/18/2021 4:47:00 PM | LRCC-12/18/2021 16:46: Naga 230kV Bus 1 restored at 1640H (Planned outage) [WEBSMS] | CLUZ
12/18/2021 4:45:00 PM | LRCC-12/18/2021 16:45: System Advisory: Weather Disturbance Alert Notice (WDAN) is lifted effective 1600H of December 18, 2021 since Typhoon ``ODETTE? is already outside the Philippine Area of Responsibility (PAR). At 03:00 PM today, the center of Typhoon ``ODETTE? was estimated at 55km Northeast of Pag-asa Island, Kalayaan, Palawan (11.3?N, 114.5?E) (OUTSIDE PAR) with maximum sustained winds of 165kph near the center & gustiness of up to 205kph. It is moving Westward at 25kph. [WEBSMS] | CLUZ
12/18/2021 4:19:00 PM | LRCC-12/18/2021 16:19: Bay 230kV Bus 2 de-energized at 1616H (Planned Outage) [WEBSMS] | CLUZ
12/18/2021 1:01:00 PM | VRCC-12/18/2021 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2626MW, PK=335MW, RR=0MW, NetOpMargin: PM=2291, EVE=2117 Highest Unit O/L: PEDC U3 at 150 MW, Derated Plant: EDC at 355 MW, TPC at 82 MW [WEBSMS] | CVIS
12/18/2021 12:44:00 PM | LRCC-12/18/2021 12:42: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10782MW, PK=8697MW, RR=334MW, NetOpMargin: PM=1751, EVE=1321 Highest Unit O/L: Sual 2 @590MW Derated Plant: Sual 2 @590MW, San Gabriel @250MW & Iljan A/B @473MW each block [WEBSMS] | CLUZ
12/18/2021 12:07:00 PM | LRCC-12/18/2021 12:06: Binga-Ambuklao 230kV Line 1 restored at 1205H (Planned Outage) [WEBSMS] | CLUZ
12/18/2021 11:49:00 AM | LRCC-12/18/2021 11:48: Lamao-GN Power 230kV Line 2 restored at 1146H (Planned Outage) [WEBSMS] | CLUZ
12/18/2021 11:45:00 AM | NEGROS ACC: 12/18/2021, PGPP1 Unit 1 synchronized to the grid at 1135H | CVIS
12/18/2021 11:41:00 AM | VRCC-12/18/2021 11:38: PGPP1 Unit 1 synchronized at 1135H [WEBSMS] | CVIS
12/18/2021 11:27:00 AM | VRCC-12/18/2021 11:26: 138 KV Amlan - PGPP1 Line 1 energized at 1121H, provided feedback power to PGPP1 [WEBSMS] | CVIS
12/18/2021 10:12:00 AM | LRCC-12/18/2021 10:11: Lamao-GN Power 230kV Line 2 de-energized at 1011H (Planned Outage) [WEBSMS] | CLUZ
12/18/2021 9:59:00 AM | LRCC-12/18/2021 09:57: Lamao-GN Power 230kV Line 1 restored at 0955H (Planned Outage) [WEBSMS] | CLUZ
12/18/2021 8:15:00 AM | LRCC-12/18/2021 08:13: Binga-Ambuklao 230kV Line 1 de-energized at 0813H (Planned Outage) [WEBSMS] | CLUZ
12/18/2021 7:57:00 AM | LRCC-12/18/2021 07:56: San Jose 750MVA TO3 de-energized at 0753H (Planned Outage) [WEBSMS] | CLUZ
12/18/2021 7:34:00 AM | LRCC-12/18/2021 07:33: Lamao-GN Power 230kV Line 1 de-energized at 0629H (Planned Outage) [WEBSMS] | CLUZ
12/18/2021 7:32:00 AM | LRCC-12/18/2021 07:31: Naga 230kV Bus 1 de-energized at 0726H (Planned outage) [WEBSMS] | CLUZ
12/18/2021 7:31:00 AM | LRCC-12/18/2021 07:31: Naga 230kV Bus 1 de-energized at 0726H (Planned outage) [WEBSMS] | CLUZ
12/18/2021 6:36:00 AM | LRCC-12/18/2021 06:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11040MW, PK=8881MW, RR=339MW, NetOpMargin: AM=1820, PM=1934, EVE=1511 Highest Unit O/L: SUAL 2 @590MW Derated Plant: MASINLOC 2 @270MW; SUAL 2 @590MW; ILJJAN A / B @946MW; SAN GABRIEL @250MW [WEBSMS] | CLUZ
12/18/2021 6:34:00 AM | LRCC-12/18/2021 06:33: Hermosa-Olongapo 230kV Line de-energized at 0611H (Planned Outage) [WEBSMS] | CLUZ
12/18/2021 5:11:00 AM | LRCC-12/18/2021 05:10: Botolan - Subic (Hanjin) 230kV Line restored at 0503H (Planned outage). [WEBSMS] | CLUZ
12/18/2021 4:33:00 AM | LRCC-12/18/2021 04:32: Dona Imelda 115kV Bus A de-energized at 0431H (Planned outage). [WEBSMS] | CLUZ
12/18/2021 4:28:00 AM | LRCC-12/18/2021 04:27: Ilijan GT 2-1 online at 0406H (Unplanned outage). [WEBSMS] | CLUZ
12/18/2021 3:17:00 AM | PANAY ACC-12/18/21 2:35:PEDC U2 synchronized at 0236H with an initial load of 8MW | CVIS
12/18/2021 2:49:00 AM | LRCC-12/18/2021 02:48: San Lorenzo Module 50 shutdown at 0243H (Planned outage). [WEBSMS] | CLUZ
12/17/2021 11:16:00 PM | LRCC-12/17/2021 23:14: Dasmarinas 300MVA T03 (formerly T09) de-energized AT 2314h (Planned Outage) [WEBSMS] | CLUZ
12/17/2021 11:15:00 PM | LRCC-12/17/2021 23:14: Dasmarinas 300MVA T03 (formerly T09) de-energized AT 2314h (Planned Outage) [WEBSMS] | CLUZ
12/17/2021 10:38:00 PM | LRCC-12/17/2021 22:37: Botolan - Subic (Hanjin) 230kV Line de-energized at 2237H (Planned Outage) [WEBSMS] | CLUZ
12/17/2021 7:32:00 PM | NEGROS ACC: 12/17/2021, 138kV Kabankalan - Mabinay L1 restored at 1724H. | CVIS
12/17/2021 7:32:00 PM | NEGROS ACC: 12/17/2021, 138kV Mabinay - Amlan L1 restored at 1758H. | CVIS
12/17/2021 7:30:00 PM | NEGROS ACC: 12/17/2021, 138kV Bacolod- Kabankalan L1 restored at 1626H. | CVIS
12/17/2021 6:54:00 PM | PANAY ACC-12/17/21 18:41: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME OUT: 18:34, TIME IN: 18:40:00, Manually open to restore ANTECOs Bugasong SS | CVIS
12/17/2021 5:56:00 PM | VRCC-12/17/2021 17:55: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2441MW, PK=856MW, RR=36MW, NetOpMargin: EVE=1550 Highest Unit O/L: PEDC U3 @ 150 MW Derated Plant: EDC = 355 MW, TPC = 82 MW [WEBSMS] | CVIS
12/17/2021 5:21:00 PM | LRCC-12/17/2021 17:21: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10305MW, PK=9254MW, RR=361MW, NetOpMargin: EVE=690 Highest Unit O/L: Sual 2 @590MW Derated Plant: Sual 2 @590MW, Sta Rita 30 @173MW, San Gabriel @211MW & Iljan A/B @360MW/180MW [WEBSMS] | CLUZ
12/17/2021 5:15:00 PM | LRCC-12/17/2021 17:14: SLPGC 1 on line at 1709H (Unplanned Outage). [WEBSMS] | CLUZ
12/17/2021 4:55:00 PM | LRCC-12/17/2021 16:54: Sta. Rita 10 shutdown at 1651H, on testing. [WEBSMS] | CLUZ
12/17/2021 2:20:00 PM | LRCC-12/17/2021 14:18: Sta. Rita 10 on line at 1414H (Extended Outage). [WEBSMS] | CLUZ
12/17/2021 1:23:00 PM | NEGROS ACC: 12/17/2021, 69kV Mt. View-Panaogao Line section restored at 1245H. ABS Mc Kinley open, isolating 69kV Panaogao-Silay Line section. Customer owned and maintained line. | CVIS
12/17/2021 12:57:00 PM | VRCC-12/17/2021 12:57: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2601MW, PK=820MW, RR=36MW, NetOpMargin: PM=1746, EVE=1550 Highest Unit O/L: TVI U1 @ 166 MW Derated Plant: EDC = 355 MW, TPC = 82 MW [WEBSMS] | CVIS
12/17/2021 12:31:00 PM | LRCC-12/17/2021 12:30: Gumaca-Lumban 230kV L1 restored at 1229H (Unplanned Outage). [WEBSMS] | CLUZ
12/17/2021 12:25:00 PM | LRCC-12/17/2021 12:23: Masinloc 1 unit transformer restored at 1151H (Planned Outage). [WEBSMS] | CLUZ
12/17/2021 12:23:00 PM | LRCC-12/17/2021 12:21: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=10633MW, PK=9636MW, RR=369MW, NetOpMargin: PM=629, EVE=983 Highest Unit O/L: Sual 2 @590MW Derated Plant: Sual 2 @590MW, Sta Rita 30 @173MW, San Gabriel @211MW & Iljan A/B @360MW/180MW [WEBSMS] | CLUZ
12/17/2021 11:29:00 AM | NEGROS ACC: 12/17/2021, 69kV Bacolod-Alijis Sub T/L restored at 1114H. Customer-owned and maintained line. | CVIS
12/17/2021 11:22:00 AM | NEGROS ACC: 12/17/2021, 69kV Bacolod-Alijis Sub T/L restored at 1114H. Customer-owned and maintained line. | CVIS
12/17/2021 9:58:00 AM | VRCC-12/17/2021 09:57: Total Power Loss of Leyte-Samar Sub-grid during energization of 138KV Paranas -Calbayog Line 2 at 0903H. [WEBSMS] | CVIS
12/17/2021 9:21:00 AM | NEGROS ACC: 12/17/2021, 69kV Cadiz-Tinampaan Sub T/L restored at 0915H. Customer-owned and maintained line. | CVIS
12/17/2021 8:30:00 AM | LRCC-12/17/2021 08:29: Dona Imelda(Araneta)-Valencia-Kamuning 115kV restored at 0828H (Planned Outage) [WEBSMS] | CLUZ
12/17/2021 8:26:00 AM | NEGROS ACC: 12/17/2021, 69kV Bacolod-Reclamation Sub T/L restored at 0820H. Customer-owned and maintained line. | CVIS
12/17/2021 8:06:00 AM | NEGROS ACC: 12/17/2021, 69kV Bacolod-Mt. View Line section restored at 0748H. ABS Abkasa open, isolating 69kV Mt. View-Silay Line section. Customer owned and maintained line. | CVIS
12/17/2021 7:05:00 AM | LRCC-12/17/2021 07:05: Dona Imelda(Araneta)-ValenciaKamuning 115kV de-energized at 0701H (Planned Outage) [WEBSMS] | CLUZ
12/17/2021 6:28:00 AM | LRCC-12/17/2021 06:27: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=10592MW, PK=9460MW, RR=364MW, NetOpMargin: AM=768, PM=655, EVE=660 Highest Unit O/L: Sual 2 @590MW Derated Plant: Sual 2 @590MW, Sta Rita 30 @173MW, San Gabriel @211MW & Iljan A/B @360MW/180MW [WEBSMS] | CLUZ
12/17/2021 5:32:00 AM | LRCC-12/17/2021 05:32: San Jose - Camarin 115kV Line restored at 0519H (Planned Outage) [WEBSMS] | CLUZ
12/17/2021 5:28:00 AM | PANAY ACC-12/17/21 03:58: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN), TIME IN: 03:57:00, RELAY: Z2 AC at29.56kms, WEATHER: FAIR | CVIS
12/17/2021 5:24:00 AM | PANAY ACC-12/17/21 01:03: STA. BARBARA SS, Sta. Barbara-Baldoza 69 kV L (5LI1SBA-BAL), TIME OUT: 22:35:00, TIME IN: 01:01:00, RELAY: Z2 L123 at 17.1kms, Affected by typhoon ODETTE | CVIS
12/17/2021 12:26:00 AM | VRCC-12/17/2021 00:24: 138KV Bacolod- Kabankalan Line 1 & 2 tripped at 2344H load involved L1-0.8MW, L2 - 0.9MW [WEBSMS] | CVIS
12/17/2021 12:12:00 AM | LRCC-12/17/2021 00:11: SLTEC 2 shutdown at 0009H (Planned Outage) [WEBSMS] | CLUZ
12/16/2021 11:50:00 PM | LRCC-12/16/2021 23:50: System Advisory: December 16, 2021: Market intervention initiated by Market Operator is lifted at 2345H, Market will resume starting 2350H trading interval. [WEBSMS] | CLUZ
12/16/2021 11:15:00 PM | LRCC-12/16/2021 23:12: San Jose - Camarin 115kV Line de-energized at 2311H (Planned Outage) [WEBSMS] | CLUZ
12/16/2021 10:17:00 PM | LRCC-12/16/2021 22:15: System Advisory: December 16, 2021: Market Intervention starting 2215H trading interval was declared by Market Operator at 2210H due to power flow divergence. [WEBSMS] | CLUZ
12/16/2021 9:34:00 PM | VRCC-12/16/2021 21:33: SCADA display at RCC for Negros & Panay Sub-grid non-updating due to telecom failure at 2129H. [WEBSMS] | CVIS
12/16/2021 9:18:00 PM | LRCC-12/16/2021 21:16: HVDC @118MW tripped at 2108H. Lowest Frequency is 59.57Hz (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2021 9:18:00 PM | LRCC-12/16/2021 21:17: San Jose-Taytay 230kV Line 2 restored at 2114H (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2021 9:14:00 PM | VRCC-12/16/2021 21:14: 350KV HVDC auto-blocked at 2108H.load involved 119MW. [WEBSMS] | CVIS
12/16/2021 9:12:00 PM | LRCC-12/16/2021 21:11: San Jose-Taytay 230kV Line 2 tripped at 2058H (Unplanned Outage) [WEBSMS] | CLUZ
12/16/2021 9:12:00 PM | VRCC-12/16/2021 21:11: Cebu South, Negros, Panay isolated on islanding operation from Cebu North, Leyte, Samar Grid at 2047H due to Typhoon Odette [WEBSMS] | CVIS
12/16/2021 9:03:00 PM | VRCC-12/16/2021 21:02: Cebu South, Negros and Panay Sub-Grids isolated from Cebu North, Leyte-Samar Sub-Grids after tripping of 138 KV Colon-Cebu Line 1 and 138 KV Colon-Quiot Line at 2047H affected by Typhoon Odette [WEBSMS] | CVIS
12/16/2021 8:55:00 PM | VRCC-12/16/2021 20:54: 138KV CEBU-Mandaue line 1 de-energized at 2021H, 138KV Mandaue-Lapulapu line 1 de-energized at 2014H, due to system high voltage & low demandaffected by tropical storm Odette. [WEBSMS] | CVIS
12/16/2021 8:44:00 PM | PANAY ACC-12/16/21 20:41: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN), TIME IN: 08:37:00, Sigma-Dao 69kv L isolated (CO) | CVIS
12/16/2021 8:33:00 PM | PANAY ACC-12/16/21 20:25: PANIT-AN SS, Panit-an-Sapian 69 kV Line (5LI1PNT-SPN), TIME OUT: 08:20:00, RELAY: Z2 BN 12.91 KMS, Load: 3.7mw, Affected by typhoon ``Odette``, WEATHER: FAIR | CVIS
12/16/2021 8:25:00 PM | NEGROS ACC: 12/16/2021, 69kV Kabankalan-La Castellana Sub T/L (5.68 MW) auto-tripped at 2018H with indication Z1 AN, 3.4km. Customer-owned and maintained line. | CVIS
12/16/2021 8:19:00 PM | NEGROS ACC: 12/16/2021, 69kV Cadiz-VMC Sub T/L restored at 2001H. Customer owned and maintained line. | CVIS
12/16/2021 8:16:00 PM | VRCC-12/16/2021 20:15: 230KV Daanbantayan-Tabango line 2 de-energized at 2009H, due to system high voltage, & system low demand cause by Tropical Storm Odette. [WEBSMS] | CVIS
12/16/2021 8:14:00 PM | NEGROS ACC: 12/16/2021, 69kV Amlan-Siaton Sub T/L (25.34 MW) auto-tripped at 1945H with indication Z1 CA DELAY, 9.089km. | CVIS
12/16/2021 8:10:00 PM | NEGROS ACC: 12/16/2021, 69kV Cadiz-VMC Sub T/L (1.57 MW) auto-tripped at 1947H with indication: Z2 CA Delay , 34.61 km. VMC & NNBP isolated. Customer owned and maintained line. | CVIS
12/16/2021 8:07:00 PM | NEGROS ACC: 12/16/2021, 69kV Kabankalan-La Castellana Sub T/L (8.65 MW) auto-tripped at 1945H with indication Z1 AN, 3.4km. Restored at 1958H. Customer-owned and maintained line. | CVIS
12/16/2021 7:44:00 PM | VRCC-12/16/2021 19:43: SO Iniated Market Intervention at 1942H due to Visayas Grid is now the center of Tropical Storm Odette. [WEBSMS] | CVIS
12/16/2021 7:25:00 PM | PANAY ACC-12/16/21 19:11: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME OUT: 19:07, TIME IN: 19:10, RELAY: BN at 83.92kms, Affected by strong winds and heavy rains brought by typhoon ``Odette`` | CVIS
12/16/2021 7:19:00 PM | VRCC-12/16/2021 19:17: 69KV COMPOSTELA-CONSOLACION TRIPPED FAILED TO RECLOSE. AT 1906H. [WEBSMS] | CVIS
12/16/2021 7:17:00 PM | VRCC-12/16/2021 19:15: 69 KV Mandaue GIS fdr#5 energized at 1909H. [WEBSMS] | CVIS
12/16/2021 7:05:00 PM | NEGROS ACC: 12/16/2021, 34.5kV Amlan-AHEP Line(0.0MW) auto tripped at 1700H with ind.; Z1 BN 11.29KM. | CVIS
12/16/2021 6:53:00 PM | VRCC-12/16/2021 18:53: TPC 1 A on houseload @1851H. [WEBSMS] | CVIS
12/16/2021 6:47:00 PM | VRCC-12/16/2021 18:46: 13.8KV VSO building station service auto tripped @1844H. [WEBSMS] | CVIS
12/16/2021 6:45:00 PM | VRCC-12/16/2021 18:44: 69KV Lapulapu Meco fdr. auto tripped @1835H. [WEBSMS] | CVIS
12/16/2021 6:36:00 PM | NEGROS ACC: 12/16/2021, 69kV Cadiz-Escalante Line section restored at 1832H isolating 69kV Escalante-San Carlos Line section. Customer-owned and maintained line. | CVIS
12/16/2021 6:30:00 PM | VRCC-12/16/2021 18:28: TVI unit # 1 auto tripped @1825H. [WEBSMS] | CVIS
12/16/2021 6:28:00 PM | NEGROS ACC: 12/16/2021, 69kV Cadiz-San Carlos Sub T/L (2.65MW) auto-tripped at 1818H with indication: Z2, BN DELAY, 51.5 km. SACASUN North, SACASOL AB, SACASOL CD,SCBI & SCBP. Customer-owned and maintained line. | CVIS
12/16/2021 6:26:00 PM | NEGROS ACC: 12/16/2021, 69kV Cadiz-San Carlos Sub T/L (2.65MW) auto-tripped at 1818H with indication: Z2, BN DELAY, 51.5 km. SACASUN North, SACASOL AB, SACASOL CD,SCBI & SCBP. Customer-owned and maintained line. | CVIS
12/16/2021 6:18:00 PM | VRCC-12/16/2021 18:18: 34.5KV Carcon-Dascon line 1 & 2 auto tripped @1809H. [WEBSMS] | CVIS
12/16/2021 6:14:00 PM | VRCC-12/16/2021 18:13: 230KV TVI -Magdugo line auto tripped @1809H, TVI unit #2 tripped while unit# 1 on house load. [WEBSMS] | CVIS
12/16/2021 6:08:00 PM | VRCC-12/16/2021 18:06: Three (3) 69KV Mandaue frds. Pacna-an, North Reclamation and Guizo manually open (no more load) @1802H Veco customers request. [WEBSMS] | CVIS
12/16/2021 6:02:00 PM | NEGROS ACC: 12/12/2021, 69kV Escalante - San Carlos Line Section restored at 1756H. Customer owned and maintained line. | CVIS
12/16/2021 6:00:00 PM | VRCC-12/16/2021 18:00: GRID UPDATE AS OF 6:00 PM System Condition: CAP=2444MW, PK=1300MW, RR=36MW, NetOpMargin: EVE=1108 Highest Unit O/L: TVI U1 @ 166 MW Derated Plant: EDC = 355 MW, TPC = 82 MW [WEBSMS] | CVIS
12/16/2021 5:32:00 PM | LRCC-12/16/2021 17:30: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10997MW, PK=9161MW, RR=287MW, NetOpMargin: EVE=1549 Highest Unit O/L: SUAL 2 @590MW Derated Plant: SUAL 2 @590MW; ILJJAN A / B @540MW , STA. RITA 30 @ 173MW, SAN GABRIEL @ 210MW, [WEBSMS] | CLUZ
12/16/2021 5:32:00 PM | VRCC-12/16/2021 17:30: 69KV CEBECO 3- Pinamongahan line auto tripped @1714H with phase B to ground indication. [WEBSMS] | CVIS
12/16/2021 5:28:00 PM | NEGROS ACC: 12/16/2021, 34.5kV Amlan-AHEP Line(0.85MW) auto tripped at 1719H with ind.; Z1 BN 12.38KM. Restored at 1724H. AHEP plant isolated. | CVIS
12/16/2021 5:24:00 PM | VRCC-12/16/2021 17:24: test [WEBSMS] | CVIS
12/16/2021 5:22:00 PM | NEGROS ACC: 12/16/2021, 69kV Amlan-San Carlos (13.83MW) auto-tripped at 1654H with indication Z2 AN DELAY , 25.96km. Sacasun South & Montesol isolated. | CVIS
12/16/2021 5:20:00 PM | VRCC-12/16/2021 17:18: 69KV Calong-Calong -Asturias line auto tripped @1702H, load of 3.65MW phase AC to ground indication. [WEBSMS] | CVIS
12/16/2021 5:18:00 PM | VRCC-12/16/2021 17:17: 69KV Calong-Calong Asturias line auto tripped @1702H, load of 3.65MW with phase AC to ground indication. [WEBSMS] | CVIS
12/16/2021 5:16:00 PM | VRCC-12/16/2021 17:15: 230KV Colon-Magdugo auto tripped @1647H, phase BC fd=13.7KMS indication. [WEBSMS] | CVIS
12/16/2021 5:04:00 PM | NEGROS ACC: 12/16/2021, 69kV Amlan-San Carlos (13.83MW) auto-tripped at 1654H with indication Z2 AN DELAY , 25.96km. Sacasun South & Montesol isolated. | CVIS
12/16/2021 4:45:00 PM | VRCC-12/16/2021 16:43: Station service of VSO building restored @1635H. [WEBSMS] | CVIS
12/16/2021 4:43:00 PM | VRCC-12/16/2021 16:41: 69KV Naga-Sibonga auto trip at 1636H. [WEBSMS] | CVIS
12/16/2021 4:01:00 PM | NEGROS ACC: 12/16/2021, 69kV Cadiz-San Carlos Sub T/L (13.9MW) auto-tripped at 1547H with indication: Z3, BCN DELAY, 58.23 km. SACASUN North, SACASOL AB, SACASOL CD,SCBI & SCBP isolated.Customer-owned and maintained line. | CVIS
12/16/2021 3:54:00 PM | LRCC-12/16/2021 15:52: Calaca-BCF 230kV Line 2 restored at 1547H (Planned Outage). [WEBSMS] | CLUZ
12/16/2021 3:45:00 PM | VRCC-12/16/2021 15:44: 138KV Colon-Samboan energized at 1544H. [WEBSMS] | CVIS
12/16/2021 3:39:00 PM | VRCC-12/16/2021 15:38: 138kv Colon-Samboan line 2 auto tripped again @1530H with same indication. [WEBSMS] | CVIS
12/16/2021 3:37:00 PM | LRCC-12/16/2021 15:37: Integrated Renewable Power Facility Hub-San Manuel 69kV/13.8kV 20MW BESS (AS LOAD) energized at 1502H, on commissioning (Planned Outage). [WEBSMS] | CLUZ
12/16/2021 3:30:00 PM | LRCC-12/16/2021 15:30: test [WEBSMS] | CLUZ
12/16/2021 2:45:00 PM | VRCC-12/16/2021 14:43: 13.8KV station service of VSO building auto tripped at 1440H. [WEBSMS] | CVIS
12/16/2021 2:32:00 PM | VRCC-12/16/2021 14:31: 69KV Naga-Sibonga energized back at 1430H. [WEBSMS] | CVIS
12/16/2021 2:25:00 PM | VRCC-12/16/2021 14:23: 69KV Naga-Sibonga auto tripped @1415H with load of 23.4MW. [WEBSMS] | CVIS
12/16/2021 1:45:00 PM | LRCC-12/16/2021 13:44: San Lorenzo 50 change-over from gas to oil at 1339H. [WEBSMS] | CLUZ
12/16/2021 1:02:00 PM | VRCC-12/16/2021 13:02: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2577MW, PK=2060MW, RR=36MW, NetOpMargin: PM=481, EVE=290 Highest Unit O/L: TVI U1 @ 166 MW Derated Plant: EDC = 355 MW, TPC = 82 MW [WEBSMS] | CVIS
12/16/2021 12:58:00 PM | LRCC-12/16/2021 12:57: Salong-Steel Asia 230kV Line de-energized at 1253H (Planned Outage). [WEBSMS] | CLUZ
12/16/2021 12:38:00 PM | LRCC-12/16/2021 12:36: Sta. Rita 40 changed over from gas to oil at 1232H. [WEBSMS] | CLUZ
12/16/2021 12:34:00 PM | VRCC-12/16/2021 12:33: 138KV Colon-Samboan line 2 energized @1253H. [WEBSMS] | CVIS
12/16/2021 12:25:00 PM | LRCC-12/16/2021 12:24: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11700MW, PK=8958MW, RR=380MW, NetOpMargin: PM=2362, EVE=1882 Highest Unit O/L: SUAL 2 @590MW Derated Plant: SUAL 2 @590MW; ILJJAN A / B @603MW [WEBSMS] | CLUZ
12/16/2021 12:23:00 PM | VRCC-12/16/2021 12:21: 138KV Colon-Samboan line 2 auto tripped @1214H phase C to ground fd=2.6KMS indication. [WEBSMS] | CVIS
12/16/2021 12:21:00 PM | LRCC-12/16/2021 12:20: Bakun 60MVA Main Transformer No. 2 restored at 1219H (Planned Outage). [WEBSMS] | CLUZ
12/16/2021 10:17:00 AM | LRCC-12/16/2021 10:16: San Esteban 230kV Bus 1 restored at 1014H (Planned Outage). [WEBSMS] | CLUZ
12/16/2021 10:10:00 AM | LRCC-12/16/2021 10:09: Limay-BCCPP 230kV Line 1 restored at 1009H (Planned Outage). [WEBSMS] | CLUZ
12/16/2021 9:19:00 AM | LEYTE ACC-12/16/21: ORMOC SS, 69kV Tunga Feeder restored up to ABS 1 Lemon at 0858H with all customers unloaded due to imbalance in sending current (phase B=0) | CVIS
12/16/2021 8:14:00 AM | LRCC-12/16/2021 08:13: Calaca-BCF 230kV Line 2 de-energized at 0813H (Planned Outage). [WEBSMS] | CLUZ
12/16/2021 8:08:00 AM | LRCC-12/16/2021 08:08: Limay-BCCPP 230kV Line 1 de-energized at 0806H (Planned Outage). [WEBSMS] | CLUZ
12/16/2021 8:07:00 AM | LRCC-12/16/2021 08:05: San Esteban 230kV Bus 1 de-energized at 0805H (Planned Outage). [WEBSMS] | CLUZ
12/16/2021 7:53:00 AM | LEYTE ACC-12/16/21: ORMOC SS, 69kV Ormoc-Lemon-Tolosa-San Isidro, fault sustained after two attempts, ind: phase BC, WEATHER: Signal # 2 Typhoon Odette | CVIS
12/16/2021 7:41:00 AM | LEYTE ACC-12/16/21: ORMOC SS, 69kV Ormoc-Lemon-Tolosa-San Isidro tripped at 0735H. Indications to follow. WEATHER: Signal # 2 Typhoon Odette. | CVIS
12/16/2021 6:18:00 AM | LRCC-12/16/2021 06:17: Bakun 60MVA Main Transformer No. 2 de-energized at 0612H (Planned Outage). [WEBSMS] | CLUZ
12/16/2021 6:05:00 AM | VRCC-12/16/2021 06:03: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=2628MW, PK=2028MW, RR=36MW, NetOpMargin: AM=564, PM=481, EVE=326 Highest Unit O/L: TVI U1 @ 166 MW. Derated Plant: EDC = 355 MW, TPC = 82 MW [WEBSMS] | CVIS
12/16/2021 5:37:00 AM | LRCC-12/16/2021 05:35: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11592MW, PK=9093MW, RR=378MW, NetOpMargin: AM=2121, PM=1975, EVE=1734 Highest Unit O/L: SUAL 2 @590MW Derated Plant: SUAL 2 @590MW; ILJJAN A / B @603MW [WEBSMS] | CLUZ
12/16/2021 5:19:00 AM | LRCC-12/16/2021 05:19: Dona Imelda (Araneta) 300MVA T02 restored AT 0519h (Planned Outage) [WEBSMS] | CLUZ
12/16/2021 1:41:00 AM | LRCC-12/16/2021 01:40: Bi?an - Muntinlupa (Sucat) 230kV Line 1 restored at 0126H (Planned Outage) [WEBSMS] | CLUZ
12/16/2021 12:54:00 AM | LEYTE ACC-12/16/21 00:40: ORMOC SS, 69kV Ormoc-Lemon-Tolosa-San Isidro line tripped at 0029H, indications: Start-up, O/C Inverse Trip, phase AB, load=23.96MW. Restored per advise from Line Engineer at 0045H. WEATHER: FAIR | CVIS
12/15/2021 11:38:00 PM | LRCC-12/15/2021 23:37: San Jose - Camarin 115kV Line de-energized at 2337H (Planned Outage) [WEBSMS] | CLUZ
12/15/2021 10:20:00 PM | LRCC-12/15/2021 22:19: Bi?an - Muntinlupa (Sucat) 230kV Line 1 de-energized at 2219H (Planned Outage) [WEBSMS] | CLUZ
12/15/2021 10:09:00 PM | LRCC-12/15/2021 22:08: Do?a Imelda (Araneta) 300MVA T02 de-energized AT 2207h (Planned Outage) [WEBSMS] | CLUZ
12/15/2021 9:06:00 PM | VRCC-12/15/2021 21:04: Visayas SO issuance of ``Blue Alert Notice``. Based on forecast position at 5:00 PM today December 15, 2021 the center of Typhoon ? ODETTE? was estimated based on all available data at 485 km East of Hinatuan, Surigao del Sur (9.1 ?N, 130.7 ?E). [WEBSMS] | CVIS
12/15/2021 1:25:00 AM | LRCC-12/15/2021 01:22: Binan 230kV Bus 1 restored at 0121H (Planned Outage). [WEBSMS] | CLUZ
12/15/2021 1:24:00 AM | LRCC-12/15/2021 01:22: Binan 230kV Bus 1 restored at 0121H (Planned Outage). [WEBSMS] | CLUZ
12/15/2021 12:09:00 AM | LRCC-12/15/2021 00:08: System Advisory: Weather Disturbance Alert Notice (WDAN) is issued at 1900H, December 14, 2021, TROPICAL DEPRESSION ``ODETTE`` ENTERS THE PHILIPPINE AREA OF RESPONSIBILITY. At 10:00 PM today, the center of Tropical Depression ``ODETTE`` was estimated at 890 km East of Mindanao (8.3?N, 134.4?E) with maximum sustained winds of 100 km/h near the center and gustiness of up to 125 km/h. It is moving West Northwestward at 15 km/h. [WEBSMS] | CLUZ
12/14/2021 11:03:00 PM | LRCC-12/14/2021 23:04: San Jose-Camarin 115kV Line de-energized at 2302H (Planned Outage). [WEBSMS] | CLUZ
12/14/2021 10:40:00 PM | LRCC-12/14/2021 22:39: Binan 230kV Bus 1 de-energized at 2239H (Planned Outage). [WEBSMS] | CLUZ
12/14/2021 10:08:00 PM | LRCC-12/14/2021 22:08: Dona Imelda(Araneta) 300MVA T01 de-energized AT 2204h (Planned Outage). [WEBSMS] | CLUZ
12/14/2021 7:15:00 PM | PANAY ACC-12/14/21 19:05: PEDC U1 (82MW) OUT:1901H due to excessive steam leak at high-pressure heater inlet isolation valve | CVIS
12/14/2021 6:36:00 PM | LRCC-12/14/2021 18:34: Daraga-Bacman 230kV Line 1 restored at 1834H (Planned Outage) [WEBSMS] | CLUZ
12/14/2021 6:04:00 PM | VRCC-12/14/2021 18:05: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2479MW, PK=2144MW, RR=0MW, NetOpMargin: EVE=335 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 355 MW, TPC at 82 MW [WEBSMS] | CVIS
12/14/2021 5:45:00 PM | LRCC-12/14/2021 17:45: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=10992MW, PK=9214MW, RR=365MW, NetOpMargin: EVE=1413 Highest Unit O/L: Sual 2 @590MW Derated Plant: Sual 2 @590MW & Iljan A/B @400MW/203MW [WEBSMS] | CLUZ
12/14/2021 1:11:00 PM | VRCC-12/14/2021 13:11: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2638MW, PK=2055MW, RR=0MW, NetOpMargin: PM=583, EVE=335 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 355 MW, TPC at 82 MW [WEBSMS] | CVIS
12/14/2021 12:59:00 PM | LRCC-12/14/2021 12:58: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11352MW, PK=9203MW, RR=358MW, NetOpMargin: PM=1791, EVE=1519 Highest Unit O/L: Sual 2 @590MW Derated Plant: Sual 2 @590MW & Iljan A/B @400MW/203MW [WEBSMS] | CLUZ
12/14/2021 12:37:00 PM | NEGROS ACC: 12/14/2021, 69kV Bacolod-San Enrique Sub T/L restored at 1236H. | CVIS
12/14/2021 12:14:00 PM | PANAY ACC-12/14/21 12:14: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME OUT: 12:03:00, TIME IN: 12:11:00, RELAY: TRIP AN 27.59KMS, Load: 2.48mw, under investigation, WEATHER: FAIR | CVIS
12/14/2021 12:12:00 PM | LEYTE ACC-12/14/21 12:21: CALBAYOG SS, Palanas-Cara-Allen-Lao-ang 69 KV Line, tripped/restored at 1200H/1205H, Z1, Phase BN, fd=10.54kms,load=16.93mw,weather:cloudy | CVIS
12/14/2021 10:36:00 AM | NEGROS ACC: 12/14/2021, 69kV Bacolod-San Enrique Sub T/L (10.84MW) auto-tripped at 1025H with indication Z2 L3E, 16.2km. CENPRI, ISLASOL II and SNBP isolated. | CVIS
12/14/2021 10:34:00 AM | LRCC-12/14/2021 10:33: Sta. Rita 10 New 375MVA Main Transformer energized at high side at 1023H for 24hrs soaking (Planned Outage) [WEBSMS] | CLUZ
12/14/2021 8:54:00 AM | LEYTE ACC-12/14/21 09:01: ORMOC SS,Ormoc 230/138/13.8 kV T1(150MVA),Deenergized at 0841H,Pre arranged per PANR No. VRCC- 2021-12-0022,7am-5pm WEATHER:Cloudy/Windy | CVIS
12/14/2021 8:18:00 AM | LRCC-12/14/2021 08:19: Daraga-Bacman 230kV Line 1 de-energized at 0818H (Planned Outage) [WEBSMS] | CLUZ
12/14/2021 5:58:00 AM | LRCC-12/14/2021 05:57: GRID UPDATE AS OF 6:00 AM System Condition: NORMAL CAP=11571MW, PK=9396MW, RR=364MW, NetOpMargin: AM=1811, PM=1723, EVE=1565 Highest Unit O/L: Sual 2 @590MW Derated Plant: Plant: Sual 2 @590MW & Iljan A/B @400MW/203MW [WEBSMS] | CLUZ
12/14/2021 5:39:00 AM | LRCC-12/14/2021 05:37: Weather Update: Issued at 0400H, Northeast Monsoon affecting Northern and Central Luzon. [WEBSMS] | CLUZ
12/14/2021 5:26:00 AM | LRCC-12/14/2021 05:26: San Jose-Camarin 115kV Line restored at 0508H (Planned Outage). [WEBSMS] | CLUZ
12/13/2021 11:20:00 PM | LRCC-12/13/2021 23:19: San Jose-Camarin 115kV Line de-energized at 2319H (Planned Outage). [WEBSMS] | CLUZ
12/13/2021 10:14:00 PM | LRCC-12/13/2021 22:13: Dona imelda-Valencia-Kamuning 115kV Line restored at 2211H (Planned Outage). [WEBSMS] | CLUZ
12/13/2021 9:10:00 PM | LRCC-12/13/2021 21:09: Dona imelda-Valencia-Kamuning 115kV Line de-energized at 2103H (Planned Outage). [WEBSMS] | CLUZ
12/13/2021 6:01:00 PM | VRCC-12/13/2021 18:01: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2441MW, PK=2084MW, RR=36MW, NetOpMargin: EVE=321 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 329 MW, TPC at 82 MW [WEBSMS] | CVIS
12/13/2021 5:50:00 PM | LEYTE ACC-12/13/21 17:58: TABANGO SS, Leyco V (Tambis),energized at 1634H with customer,s clearance,load=2.2mw, WEATHER: Cloudy | CVIS
12/13/2021 5:44:00 PM | LRCC-12/13/2021 17:44: Dona Imelda(Araneta)-Sta. Mesa 115kV Line 1 restored at 1742H (Planned Outage). [WEBSMS] | CLUZ
12/13/2021 5:39:00 PM | LRCC-12/13/2021 17:39: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11126MW, PK=9100MW, RR=357MW, NetOpMargin: EVE=1669 Highest Unit O/L: Sual 2 @590MW Derated Plant: Sual 2 @590MW & Iljan A/B @400MW/203MW [WEBSMS] | CLUZ
12/13/2021 4:23:00 PM | LEYTE ACC-12/13/21 16:32: TABANGO SS, Leyco V (Tambis), tripped at 1610H,with Over current,load=2.2mw, WEATHER: Cloudy | CVIS
12/13/2021 1:25:00 PM | NEGROS ACC: 12/13/2021: 69kV Silay-VMC Line section energized at 1318H after replacement of defective polymer insulator. | CVIS
12/13/2021 1:11:00 PM | VRCC-12/13/2021 13:10: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2619MW, PK=2099MW, RR=36MW, NetOpMargin: PM=483, EVE=321 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 329 MW, TPC at 82 MW [WEBSMS] | CVIS
12/13/2021 1:02:00 PM | LRCC-12/13/2021 13:01: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11434MW, PK=9491MW, RR=357MW, NetOpMargin: PM=1586, EVE=1449 Highest Unit O/L: Sual 2 @590MW Derated Plant: Sual 2 @590MW, San Gabriel @250MW & Iljan A/B @400MW/203MW [WEBSMS] | CLUZ
12/13/2021 9:23:00 AM | PANAY ACC-12/13/21 06:07: DINGLE SS, Dingle-Calinog 69KV (5LI1DIN-CLI), TIME OUT: 06:05:00, Load: 4.84mw, Customers request to conduct emergency clearing, ETR: 0700H, WEATHER: FAIR | CVIS
12/11/2021 9:23:00 PM | LRCC-12/11/2021 21:22: Hermosa-Malolos 230kV Line tripped at 2108H (Unplanned Outage) [WEBSMS] | CLUZ
12/11/2021 7:56:00 PM | PANAY ACC-12/11/21 19:53: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME IN: 19:52:00, WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 7:52:00 PM | PANAY ACC-12/11/21 19:45: NABAS SS, Caticlan-Malay 69kV L (5LI1CTC-MLA), TIME IN: 19:43:00, WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 7:45:00 PM | PANAY ACC-12/11/21 19:45: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME IN: 19:43:00, WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 7:41:00 PM | PANAY ACC-12/11/21 19:37: NABAS SS, Nabas-Avon 69KV (5LI1NBS-ARP), TIME IN: 19:36:00, WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 7:41:00 PM | PANAY ACC-12/11/21 19:38: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME IN: 19:36:00, WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 7:39:00 PM | PANAY ACC-12/11/21 19:32: NABAS SS, Nabas 138/69/13.8 kV T1 (50MVA) (7XF01NBS), TIME IN: 19:31:00, WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 7:22:00 PM | PANAY ACC-12/11/21 19:20: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME IN: 19:19:00, WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 7:20:00 PM | PANAY ACC-12/11/21 19:11: NABAS SS, Nabas-Culasi 69KV (5LI1NBS-CSI), TIME OUT: 19:10:00, TIME IN: , WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 7:20:00 PM | PANAY ACC-12/11/21 19:11: SAN JOSE SS, San Jose - Bugasong - SUWECO 69 kV L (5LI1SJB-CUL), TIME OUT: 19:10:00, WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 7:18:00 PM | PANAY ACC-12/11/21 19:11: NABAS SS, Avon-Caticlan 69 kV L (CO) (5LI1GBP-CTC), TIME OUT: 19:09:00, TIME IN: , WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 7:18:00 PM | PANAY ACC-12/11/21 19:11: NABAS SS, Caticlan-Malay 69kV L (5LI1CTC-MLA), TIME OUT: 19:09:00, TIME IN: , WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 7:18:00 PM | PANAY ACC-12/11/21 19:11: NABAS SS, Nabas 138/69/13.8 kV T1 (50MVA) (7XF01NBS), TIME OUT: 19:09:00, WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 7:18:00 PM | PANAY ACC-12/11/21 19:11: NABAS SS, Nabas Sapian 69 kV Line (5LI1NBS-SPN), TIME OUT: 07:09:00, TIME IN: , WEATHER: FAIR;Pre-arranged maintenance activity | CVIS
12/11/2021 7:18:00 PM | PANAY ACC-12/11/21 19:11: NABAS SS, Nabas-Avon 69KV (5LI1NBS-ARP), TIME OUT: 19:09:00, TIME IN: , WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 6:49:00 PM | PANAY ACC-12/11/21 18:46: PANIT-AN SS, Panit-an-Nabas 138 kV L (7LI1PNT-NBS), TIME IN: 18:45:00, WEATHER: FAIR; Pre-arranged maintenance activity | CVIS
12/11/2021 6:00:00 PM | VRCC-12/11/2021 18:00: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=2413MW, PK=1984MW, RR=36MW, NetOpMargin: EVE=393 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 350 MW, TPC at 82 MW [WEBSMS] | CVIS
12/11/2021 5:56:00 PM | LEYTE ACC-12/11/21: ORMOC SS, 69kV Ormoc-Lemon-Tolosa-San Isidro re-energized at 1747H, pre-arranged activity to be continued for another schedule. WEATHER: RAINY | CVIS
12/11/2021 5:42:00 PM | VRCC-12/11/2021 17:42: 138 KV Cebu - Colon Line 1 energized at 1739H, APMS completed [WEBSMS] | CVIS
12/11/2021 5:39:00 PM | LEYTE ACC-12/11/21: CALBAYOG SS, 69kV PCB Palanas Cara tripped/restored at 1732H/1736H, z2, phase BN, 77.15kms, load=18MW, WEATHER: RAINY | CVIS
12/11/2021 5:27:00 PM | LRCC-12/11/2021 17:27: GRID UPDATE AS OF 6:00 PM System Condition: NORMAL CAP=11019MW, PK=8674MW, RR=340MW, NetOpMargin: EVE=2006 Highest Unit O/L: Sual 2 at 590MW Derated Plant: Sual 2 at 590MW, Ilijan A/B at 540MW, San Gabriel at 211MW [WEBSMS] | CLUZ
12/11/2021 5:21:00 PM | LEYTE ACC-12/11/21: MAASIN SS, 69kV PCB SOLECO re-energized at 1717H up to ABS San Isidro (normal configuration), WEATHER: RAINY | CVIS
12/11/2021 5:14:00 PM | LRCC-12/11/2021 17:13: Bolo-Balingueo 230kV Line 1 restored at 1712H. (Planned Outage) [WEBSMS] | CLUZ
12/11/2021 5:08:00 PM | LEYTE ACC-12/11/21: MAASIN SS, PCB SOLECO tripped at 1657H, phase ABCN, load=37.5MW, WEATHER: RAINY | CVIS
12/11/2021 5:06:00 PM | LEYTE ACC-12/11/21: MAASIN SS, PCB SOLECO tripped at 1657H, phase ABCN, load=37.5MW, WEATHER: RAINY | CVIS
12/11/2021 4:49:00 PM | LRCC-12/11/2021 16:48: Muntinlupa(Sucat) 115kV Bus 1 restored at 1648H. (Planned Outage) [WEBSMS] | CLUZ
12/11/2021 4:42:00 PM | NEGROS ACC: 12/11/2021, 69KV Cadiz-San Carlos Sub T/L energized at 1634H after PMS. Customer owned and maintained line. | CVIS
12/11/2021 4:40:00 PM | LRCC-12/11/2021 16:40: Dasmarinas-MEC-Rosario 115kV line restored at 1638H. (Unplanned Outage) [WEBSMS] | CLUZ
12/11/2021 4:34:00 PM | VRCC-12/11/2021 16:35: 34.5 KV CARCON - Sangi Line 2 energized at 1632H, Metering activity completed [WEBSMS] | CVIS
12/11/2021 4:15:00 PM | LRCC-12/11/2021 16:15: Lumban-Bay 230 kV L2 restored at 1614H. (Planned Outage) [WEBSMS] | CLUZ
12/11/2021 4:08:00 PM | LRCC-12/11/2021 16:08: Daraga 230kV Bus 1 restored at 1606H. (Planned Outage) [WEBSMS] | CLUZ
12/11/2021 1:24:00 PM | VRCC-12/11/2021 09:21: 34.5 KV CARCON - Sangi Line 2 de-energized at 0919H, Metering activity, ETC: 1700H [WEBSMS] | CVIS
12/11/2021 1:24:00 PM | VRCC-12/11/2021 13:00: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=2570MW, PK=1864MW, RR=36MW, NetOpMargin: PM=670, EVE=393 Highest Unit O/L: TVI at 169 MW per unit, Derated Plant: EDC at 350 MW, TPC at 82 MW [WEBSMS] | CVIS
12/11/2021 1:23:00 PM | LRCC-12/11/2021 12:53: GRID UPDATE AS OF 1:00 PM System Condition: NORMAL CAP=11677MW, PK=8457MW, RR=336MW, NetOpMargin: PM=2884, EVE=2628 Highest Unit O/L: Sual 2 at 590MW Derated Plant: Sual 2 at 590MW, Ilijan A/B at 540MW, San Gabriel at 211MW [WEBSMS] | CLUZ
12/11/2021 1:22:00 PM | LRCC-12/11/2021 09:04: Tayabas-Mauban 230kV Line 1 de-energized at 0903H. (Planned Outage) [WEBSMS] | CLUZ
12/11/2021 1:22:00 PM | LRCC-12/11/2021 10:29: Dasmarinas-MEC-Rosario 115kV line de-energized at 1012H. (Unplanned Outage) [WEBSMS] | CLUZ